## 119_42S5
S&C Power Fuses - Type SM-4 (15E thru 200E at 7.2 and 14.4 kV) and SM-5 (15E thru 2-400E at 4.16, 7.2, 14.4kV) | [9 empty] | S&C Power Fuses - Type SM-4 (15E thru 200E at 7.2 and 14.4 kV) and SM-5 (15E thru 2-400E at 4.16, 7.2, 14.4kV) | [9 empty] | S&C Power Fuses - Type SM-4 (15E thru 200E at 7.2 and 14.4 kV) and SM-5 (15E thru 2-400E at 4.16, 7.2, 14.4kV) | [9 empty] | S&C Power Fuses - Type SM-4 (15E thru 200E at 7.2 and 14.4 kV) and SM-5 (15E thru 2-400E at 4.16, 7.2, 14.4kV)
Slow Speed (TCC 119-4-2) | [9 empty] | Slow Speed (TCC 119-4-2) | [9 empty] | Slow Speed (TCC 119-4-2) | [9 empty] | Slow Speed (TCC 119-4-2)
Total Clearing Time-Current Characteristic Curves Dated March 18, 1985 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated March 18, 1985 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated March 18, 1985 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated March 18, 1985
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 2-200E |  | 2-250E |  | 2-300E |  | 2-400E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
47399 | 0.013964 | 47646.8 | 0.014008 | 47597.1 | 0.014022 | 47696.5 | 0.014022 | 47746.3 | 0.013978 | 47300.3 | 0.013964 | 47597.1 | 0.014125 | 47300.3 | 0.014081 | 47746.3 | 0.01411 | 47349.6 | 0.014066 | 47646.8 | 0.014125 | 47251 | 0.01411 | 47547.5 | 0.014155 | 47547.5 | 0.014666 | 47448.5 | 0.015101 | 47448.5 | 0.016796 | 47746.3 | 0.018644 | 47696.5 | 0.022898 | 47349.6 | 0.030128
38880.4 | 0.014348 | 27218.3 | 0.015516 | 24370.3 | 0.015695 | 35806.1 | 0.014789 | 34812.1 | 0.014681 | 33740 | 0.01482 | 35360.8 | 0.014959 | 33043.7 | 0.015022 | 31627.8 | 0.015323 | 32906.1 | 0.015291 | 33704.8 | 0.015148 | 35250.4 | 0.015211 | 37448 | 0.015085 | 38316.9 | 0.016143 | 38038.3 | 0.01753 | 38197.3 | 0.019662 | 37959.1 | 0.022826 | 39658.3 | 0.027658 | 38839.9 | 0.037314
29218.2 | 0.015132 | 14289.2 | 0.017677 | 14651.3 | 0.01753 | 19907.2 | 0.016518 | 21820.2 | 0.016279 | 23743.2 | 0.016026 | 24294.1 | 0.016143 | 24702.8 | 0.016177 | 20518.3 | 0.01715 | 26052 | 0.016674 | 26133.7 | 0.017186 | 28200.5 | 0.016744 | 28347.9 | 0.017168 | 30335.8 | 0.018316 | 27048.5 | 0.022495 | 27532.3 | 0.026115 | 28945.3 | 0.030223 | 30494.4 | 0.038021 | 31627.8 | 0.048334
20647.1 | 0.016245 | 10987.3 | 0.018412 | 9847.97 | 0.018761 | 11696.7 | 0.018278 | 13145.6 | 0.018182 | 18505.9 | 0.016761 | 16278.4 | 0.017476 | 18876.2 | 0.017348 | 14408.9 | 0.019499 | 21347.6 | 0.017937 | 20647.1 | 0.019216 | 22443.3 | 0.018938 | 22868.5 | 0.019642 | 22071.9 | 0.022542 | 20604.1 | 0.028656 | 20841.8 | 0.035269 | 22631.3 | 0.040859 | 23595.1 | 0.053649 | 25567.6 | 0.065618
15646 | 0.017168 | 7157.79 | 0.02014 | 6302.8 | 0.020889 | 7285.8 | 0.02033 | 9940.82 | 0.019458 | 11733.3 | 0.018663 | 11807 | 0.019236 | 15339.1 | 0.018702 | 11265.8 | 0.022031 | 15727.8 | 0.020543 | 16586.8 | 0.021666 | 17973.5 | 0.021598 | 18161.9 | 0.023042 | 17694.5 | 0.026722 | 15843 | 0.037982 | 16278.4 | 0.048032 | 17936 | 0.056346 | 19334.4 | 0.072455 | 20284.3 | 0.093853
11289.3 | 0.018278 | 5132.45 | 0.021734 | 4989.97 | 0.022008 | 4736.49 | 0.023259 | 7862.02 | 0.020933 | 9145.25 | 0.020565 | 8753.39 | 0.021531 | 12156.8 | 0.02014 | 9357.46 | 0.024276 | 11980.6 | 0.023799 | 12322.7 | 0.026197 | 14274.3 | 0.025074 | 14274.3 | 0.027658 | 14423.9 | 0.032717 | 13159.3 | 0.048182 | 13283.4 | 0.064195 | 14096.8 | 0.083241 | 15711.4 | 0.10192 | 16312.4 | 0.13721
9231.47 | 0.019076 | 3529.85 | 0.0237 | 3453.4 | 0.024352 | 3687.87 | 0.025523 | 5768.22 | 0.02343 | 7572.38 | 0.021985 | 6879.73 | 0.023949 | 9202.64 | 0.022755 | 7278.21 | 0.028927 | 9426.01 | 0.02786 | 9674.95 | 0.032209 | 11195.5 | 0.030508 | 10896.1 | 0.035454 | 11195.5 | 0.044093 | 10214 | 0.069348 | 10342.6 | 0.094049 | 11336.5 | 0.11981 | 13118.2 | 0.13923 | 13834.7 | 0.18492
6922.91 | 0.020182 | 2552.26 | 0.026334 | 3140.79 | 0.025736 | 2669.29 | 0.029599 | 4196.89 | 0.026889 | 5608.1 | 0.024995 | 5362.21 | 0.027456 | 7323.89 | 0.025523 | 5643.29 | 0.035788 | 7400.65 | 0.034397 | 7150.33 | 0.044742 | 9337.96 | 0.036277 | 8789.98 | 0.045259 | 9107.19 | 0.057956 | 8061.25 | 0.10096 | 8422.12 | 0.13298 | 9347.71 | 0.17065 | 11114.1 | 0.18922 | 12005.6 | 0.24255
5068.63 | 0.021734 | 2108.9 | 0.028597 | 2445.45 | 0.028507 | 1910.01 | 0.036467 | 3315.78 | 0.030635 | 4285.33 | 0.028957 | 4088.9 | 0.033095 | 5828.68 | 0.029722 | 4658.12 | 0.043454 | 6140.62 | 0.041808 | 5549.93 | 0.062152 | 7796.72 | 0.044789 | 7187.71 | 0.058993 | 7408.37 | 0.07901 | 6476 | 0.14623 | 6591.82 | 0.20526 | 7486.02 | 0.25742 | 9116.69 | 0.27925 | 10615.7 | 0.31223
3548.3 | 0.023651 | 1647.15 | 0.032008 | 1667.89 | 0.034722 | 1432.36 | 0.045733 | 2355.35 | 0.039189 | 3533.53 | 0.032888 | 3220.38 | 0.040945 | 4751.32 | 0.034649 | 3676.35 | 0.057594 | 5079.21 | 0.052596 | 4467.84 | 0.086337 | 6503.07 | 0.056405 | 5810.48 | 0.079672 | 6289.67 | 0.10299 | 5257.02 | 0.21379 | 5284.5 | 0.31649 | 6362.22 | 0.35314 | 7572.38 | 0.40571 | 9088.21 | 0.43012
2523.15 | 0.025817 | 1342.69 | 0.035788 | 1266.54 | 0.042335 | 1116.41 | 0.059549 | 1676.61 | 0.055297 | 2904.53 | 0.038945 | 2674.87 | 0.050131 | 3897.41 | 0.041852 | 2736.93 | 0.087699 | 4263.04 | 0.066514 | 3642.01 | 0.11918 | 5379.01 | 0.073829 | 4771.18 | 0.10964 | 6153.44 | 0.10715 | 4008.69 | 0.3561 | 4063.4 | 0.53716 | 5429.72 | 0.48953 | 6469.25 | 0.55598 | 7911.36 | 0.57306
2052.49 | 0.027543 | 1040 | 0.042779 | 986.142 | 0.053259 | 915.773 | 0.075859 | 1306.78 | 0.07578 | 2311.56 | 0.048637 | 2151.09 | 0.065823 | 3127.72 | 0.053986 | 2043.95 | 0.14069 | 3619.3 | 0.084642 | 2874.4 | 0.17922 | 4495.88 | 0.097344 | 3711.01 | 0.16747 | 5127.1 | 0.14562 | 3240.59 | 0.54621 | 3213.67 | 0.88915 | 4614.61 | 0.67577 | 5278.99 | 0.84837 | 6716.7 | 0.81795
1704.81 | 0.029414 | 788.097 | 0.055471 | 748.843 | 0.072834 | 746.504 | 0.10054 | 1055.29 | 0.10256 | 1845.41 | 0.064128 | 1773.72 | 0.085441 | 2463.36 | 0.073521 | 1669.63 | 0.19873 | 3075.97 | 0.10941 | 2348 | 0.25931 | 3809.02 | 0.12768 | 3012.49 | 0.24408 | 3921.87 | 0.23557 | 2630.61 | 0.82566 | 2549.6 | 1.495 | 3873.1 | 0.96858 | 4384.77 | 1.2586 | 5708.39 | 1.1724
1349.71 | 0.03231 | 613.619 | 0.073829 | 594.722 | 0.098983 | 605.989 | 0.13764 | 812.291 | 0.1539 | 1536.01 | 0.081777 | 1435.35 | 0.11782 | 2003.86 | 0.10002 | 1291.88 | 0.32148 | 2595.19 | 0.14501 | 1906.03 | 0.38669 | 3066.36 | 0.18823 | 2420.08 | 0.37517 | 3160.5 | 0.3513 | 2135.45 | 1.3108 | 2061.07 | 2.5215 | 3257.53 | 1.3897 | 3797.13 | 1.7247 | 4927.92 | 1.6422
1099.09 | 0.036164 | 475.781 | 0.10439 | 482.777 | 0.13382 | 504.389 | 0.18492 | 643.097 | 0.22736 | 1224.98 | 0.11467 | 1172.49 | 0.16418 | 1579.86 | 0.14792 | 1048.71 | 0.48445 | 2189.56 | 0.19523 | 1589.78 | 0.56064 | 2504.8 | 0.27177 | 2043.95 | 0.52662 | 2557.59 | 0.53773 | 1794.18 | 1.996 | 1645.43 | 4.7109 | 2734.08 | 2.0746 | 3147.35 | 2.6761 | 4285.33 | 2.3003
903.444 | 0.040859 | 384.617 | 0.14366 | 381.82 | 0.19646 | 425.11 | 0.24587 | 515.556 | 0.33799 | 967.806 | 0.16765 | 930.209 | 0.24306 | 1299.99 | 0.20591 | 867.442 | 0.70457 | 1841.56 | 0.26895 | 1271.83 | 0.88915 | 2054.63 | 0.40317 | 1692.42 | 0.76911 | 2016.43 | 0.86716 | 1491.81 | 3.1623 | 1417.51 | 7.8549 | 2275.69 | 3.2425 | 2748.37 | 3.776 | 3714.89 | 3.3178
742.622 | 0.047583 | 311.895 | 0.20039 | 315.164 | 0.27348 | 358.665 | 0.33275 | 419.824 | 0.50037 | 781.55 | 0.2418 | 736.453 | 0.37634 | 1005.87 | 0.32998 | 715.263 | 1.0551 | 1618.21 | 0.3444 | 1040 | 1.3653 | 1708.37 | 0.57907 | 1439.85 | 1.0841 | 1598.09 | 1.4429 | 1436.85 | 3.4628 | 1301.34 | 11.58 | 1860.87 | 5.7139 | 2427.66 | 5.384 | 3322.71 | 4.5514
605.358 | 0.057594 | 240.075 | 0.31583 | 264.521 | 0.37871 | 289.941 | 0.49985 | 326.197 | 0.83085 | 651.874 | 0.33799 | 590.397 | 0.57426 | 806.384 | 0.51146 | 593.483 | 1.5571 | 1346.9 | 0.49569 | 876.534 | 1.9815 | 1420.46 | 0.85637 | 1150.69 | 1.7446 | 1239.11 | 2.6483 | 1216.07 | 5.5668 | 1198.44 | 19.3288 | 1652.31 | 8.3537 | 2135.45 | 8.1812 | 3037.72 | 6.1212
492.437 | 0.072304 | 183.832 | 0.52443 | 224.811 | 0.52388 | 242.086 | 0.71345 | 265.35 | 1.2625 | 519.332 | 0.52497 | 486.314 | 0.84307 | 658.706 | 0.77233 | 499.157 | 2.2788 | 1142.32 | 0.69146 | 734.153 | 2.9735 | 1211.01 | 1.1871 | 965.79 | 2.6263 | 1028.14 | 4.3291 | 1023.86 | 9.4187 | 1126.94 | 30.7828 | 1494.92 | 12.2385 | 1906.03 | 12.4965 | 2791.7 | 8.3799
402.254 | 0.093462 | 139.45 | 0.90318 | 193.468 | 0.71122 | 199.2 | 1.054 | 219.713 | 1.9224 | 419.824 | 0.80608 | 390.273 | 1.3582 | 529.723 | 1.2172 | 406.047 | 3.6635 | 957.767 | 0.9921 | 621.994 | 4.5277 | 1038.91 | 1.6525 | 824.236 | 3.9493 | 895.939 | 6.4828 | 895.005 | 15.6556 | 1088.82 | 46.7756 | 1335.71 | 22.4157 | 1740.74 | 18.9692 | 2644.36 | 10.9799
325.857 | 0.12518 | 112.495 | 1.4324 | 163.399 | 1.0067 | 167.191 | 1.517 | 178.915 | 3.1164 | 333.071 | 1.3232 | 325.518 | 2.0339 | 434.521 | 1.8749 | 344.013 | 5.7139 | 788.919 | 1.5281 | 555.75 | 6.283 | 878.364 | 2.4387 | 712.286 | 6.2569 | 829.409 | 8.3363 | 825.957 | 23.9387 | 1045.43 | 73.7209 | 1242.99 | 39.2546 | 1626.67 | 28.0822 | 2499.58 | 14.7209
265.627 | 0.17083 | 91.3207 | 2.3834 | 141.796 | 1.3696 | 139.45 | 2.2836 | 150.793 | 4.8759 | 269.814 | 2.1029 | 270.659 | 3.1821 | 369.29 | 2.7325 | 293.286 | 9.1379 | 683.189 | 2.1361 | 500.199 | 8.9213 | 736.453 | 3.7879 | 631.798 | 9.5473 | 758.271 | 11.58 | 780.736 | 36.3378 | 1028.14 | 102.835 | 1205.97 | 57.4499 | 1558.59 | 40.7997 | 2404.99 | 19.5723
208.117 | 0.25448 | 75.5358 | 3.8758 | 122.537 | 1.9005 | 118.763 | 3.3281 | 127.091 | 8.1471 | 232.197 | 2.9922 | 227.879 | 5.0257 | 312.872 | 4.0919 | 260.145 | 14.0897 | 541.45 | 3.776 | 454.446 | 13.3595 | 632.457 | 5.8222 | 583.056 | 13.3317 | 709.322 | 15.6719 | 735.686 | 79.5555 | 1009.02 | 149.406 | 1193.46 | 80.39 | 1512.17 | 58.5391 | 2301.94 | 26.6825
172.683 | 0.36021 | 63.6631 | 6.3556 | 106.225 | 2.6733 | 103.061 | 4.8354 | 107.675 | 14.8753 | 191.262 | 4.9322 | 199.2 | 7.6049 | 274.353 | 5.9699 | 239.575 | 21.3207 | 463.056 | 5.9264 | 417.641 | 20.3003 | 553.437 | 9.2338 | 542.581 | 19.7983 | 648.484 | 26.7104 | 719.752 | 122.538 | 992.33 | 223.037 | 1194.7 | 131.961 | 1476.34 | 79.7217 | 2238.04 | 34.7797
145.389 | 0.50089 | 56.6461 | 9.5672 | 92.8569 | 3.7407 | 89.3428 | 7.4091 | 97.0138 | 27.2452 | 158.532 | 8.6193 | 179.289 | 11.2115 | 246.93 | 8.4766 | 229.07 | 30.7507 | 413.74 | 8.6644 | 388.648 | 35.5502 | 489.366 | 15.3803 | 512.875 | 31.0085 | 614.259 | 46.2901 | 712.286 | 207.76 | 979.991 | 329.842 | 1194.7 | 211.699 | 1451.91 | 111.206 | 2169.11 | 48.2629
126.167 | 0.66528 | 50.5605 | 16.494 | 78.9996 | 5.8833 | 82.1069 | 10.346 | 93.0508 | 40.0406 | 139.16 | 13.9289 | 162.211 | 18.0049 | 220.631 | 12.8134 | 222.016 | 46.9223 | 373.161 | 13.1658 | 375.112 | 53.9073 | 454.92 | 23.1526 | 494.495 | 50.3724 | 598.454 | 73.5672 | 716.009 | 322.357 | 977.95 | 454.857 | 1195.95 | 305.971 | 1433.86 | 171.647 | 2119.92 | 65.1128
106.225 | 0.94956 | 47.6928 | 25.0633 | 69.5631 | 9.062 | 77.208 | 14.3269 | 89.5293 | 62.4512 | 124.339 | 23.4933 | 153.49 | 27.1601 | 201.078 | 19.6132 | 217.888 | 72.8796 | 349.072 | 19.349 | 365.079 | 83.0327 | 436.337 | 34.2396 | 486.821 | 74.0293 | 592.865 | 113.078 | 717.504 | 490.857 | 966.797 | 589.805 | 1192.21 | 418.868 | 1430.87 | 242.453 | 2076.17 | 92.3571
89.9035 | 1.3596 | 46.1758 | 37.1816 | 61.574 | 15.6883 | 73.5155 | 19.0684 | 87.5902 | 95.1944 | 115.828 | 37.1816 | 148.608 | 39.0097 | 188.884 | 27.8779 | 216.981 | 108.682 | 332.377 | 27.6461 | 359.413 | 127.494 | 426.886 | 51.4346 | 479.766 | 109.822 | 593.483 | 159.225 | 714.518 | 587.962 |  |  | 1194.7 | 534.145 | 1433.86 | 337.854 | 2050.35 | 127.761
78.2617 | 1.8458 | 44.521 | 57.4499 | 57.2996 | 27.8779 | 70.8072 | 26.5992 | 87.2257 | 138.593 | 112.144 | 54.872 | 145.541 | 55.6794 | 180.226 | 41.1847 | 217.888 | 164.116 | 320.132 | 40.4184 | 357.917 | 186.59 | 419.824 | 82.7732 | 479.766 | 163.262 | 592.247 | 244.741 | [6 empty] | 1439.85 | 450.606 | 2012.23 | 182.166
67.1402 | 2.6677 | 43.8301 | 96.0925 | 55.1886 | 51.9741 | 68.9852 | 36.2242 | 87.1348 | 211.258 | 109.601 | 85.8519 | 143.432 | 76.7827 | 175.588 | 61.2892 | 217.888 | 243.468 | 312.546 | 57.63 | 357.172 | 298.715 | 419.386 | 134.603 | 480.267 | 227.265 | 594.722 | 378.154 | [6 empty] | 1439.85 | 536.379 | 1981 | 270.808
59.8023 | 3.5247 | 43.6022 | 151.289 | 54.219 | 96.7969 | 67.5615 | 50.6359 | 87.4077 | 343.541 | 109.031 | 116.188 | 141.944 | 119.383 | 172.683 | 97.7102 | 218.57 | 360.056 | 305.777 | 85.8519 | 356.428 | 428.147 | 420.262 | 222.108 | 479.766 | 326.759 | 594.102 | 530.812 | [8 empty] | 1960.45 | 371.893
52.7138 | 5.089 | 43.3303 | 259.467 | 54.3321 | 184.268 | 66.0983 | 71.1515 | 87.4077 | 484.244 | 108.69 | 190.128 | 142.389 | 179.15 | 172.144 | 154.963 | 218.343 | 494.971 | 301.66 | 133.902 | 356.8 | 552.281 | 421.139 | 359.306 | 480.768 | 439.004 | 596.585 | 595.37 | [8 empty] | 1944.17 | 501.731
47.3459 | 7.1285 | 43.24 | 425.919 | 54.4456 | 307.571 | 65.4809 | 92.8402 | 87.5902 | 589.805 | 108.804 | 292.241 | 142.686 | 253.844 | 172.503 | 230.61 | 218.57 | 592.272 | 299.466 | 227.978 | 356.8 | 600.987 | 421.139 | 503.304 | 481.269 | 594.128 | [10 empty] | 1940.12 | 539.185
43.5568 | 9.4088 | 43.3755 | 593.509 | 54.3888 | 466.392 | 64.9369 | 135.873 |  |  | 108.464 | 436.719 | 142.537 | 365.355 | 173.405 | 379.339 |  |  | 298.22 | 357.063 |  |  | 420.262 | 594.749
38.9179 | 15.8694 |  |  | 54.5592 | 597.86 | 65.0047 | 190.923 |  |  | 108.69 | 597.86 | 142.835 | 508.583 | 172.503 | 522.569 |  |  | 296.669 | 590.421
36.1785 | 26.2956 |  |  |  |  | 64.8017 | 259.738 |  |  |  |  | 143.282 | 587.348 | 172.863 | 597.86
34.5202 | 43.8912 |  |  |  |  | 64.8693 | 345.338
33.5969 | 68.3855 |  |  |  |  | 64.9369 | 457.714
33.0066 | 115.102 |  |  |  |  | 65.0725 | 570.437
32.7666 | 198.438 |  |  |  |  | 65.1404 | 598.484
32.6302 | 284.717
32.6643 | 390.585
32.6643 | 536.379
32.7325 | 600.987