## 119_155
S&C Power Fuses - Type SMD-50 (34.5 and 46 kV) | [9 empty] | S&C Power Fuses - Type SMD-50 (34.5 and 46 kV)
Slow Speed (TCC 119-1-5-5) | [9 empty] | Slow Speed (TCC 119-1-5-5)
Total Clearing Time-Current Characteristic Curves Dated January 25, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 25, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
8602.47 | 0.018605 | 8602.47 | 0.018698 | 8602.47 | 0.018791 | 8602.47 | 0.018997 | 8602.47 | 0.019591 | 8602.47 | 0.020204 | 8602.47 | 0.021002 | 8602.47 | 0.022898 | 8602.47 | 0.025797
8174.72 | 0.019206 | 8449 | 0.018903 | 7214.12 | 0.020898 | 7683.25 | 0.020406 | 8576.7 | 0.019591 | 7901.44 | 0.021509 | 7199.7 | 0.024112 | 8593.87 | 0.022898 | 7381.97 | 0.03021
6739.84 | 0.021509 | 7014.92 | 0.021107 | 5783.62 | 0.023802 | 6252.82 | 0.023103 | 7142.33 | 0.022203 | 6469.08 | 0.024792 | 5766.29 | 0.028804 | 7163.79 | 0.026896 | 7264.8 | 0.030786
5312.3 | 0.024498 | 5584.68 | 0.024112 | 4353.65 | 0.027902 | 4821.19 | 0.027003 | 5714.62 | 0.025694 | 5043.11 | 0.029912 | 4336.27 | 0.036813 | 5731.79 | 0.0332 | 6979.93 | 0.032002
3884.56 | 0.02889 | 4153.75 | 0.028293 | 2924.12 | 0.034787 | 3390.58 | 0.033399 | 4284.54 | 0.031404 | 3611.07 | 0.039191 | 4263.17 | 0.037403 | 5523.58 | 0.034409 | 6639.5 | 0.033799
2452.2 | 0.036413 | 2726.42 | 0.035414 | 1494.75 | 0.052016 | 1960.06 | 0.047994 | 2854.78 | 0.042517 | 3532.49 | 0.039898 | 4112.42 | 0.038688 | 5285.8 | 0.036018 | 6334.64 | 0.035591
1023.2 | 0.057677 | 1295.57 | 0.054124 | 1456.39 | 0.053007 | 1921.24 | 0.048715 | 2778.72 | 0.043499 | 3421.24 | 0.041105 | 3955.12 | 0.040096 | 5038.07 | 0.037702 | 5847.59 | 0.038997
969.419 | 0.059599 | 1233.62 | 0.055928 | 1374.32 | 0.054991 | 1844.06 | 0.050188 | 2653.79 | 0.044993 | 3260.89 | 0.042813 | 3739.71 | 0.04218 | 4787.55 | 0.039819 | 5496.03 | 0.041888
885.978 | 0.063071 | 1144.47 | 0.058776 | 1294.28 | 0.057505 | 1762.91 | 0.051912 | 2514.28 | 0.047097 | 3074.05 | 0.045217 | 3543.11 | 0.044504 | 4499.73 | 0.042517 | 5170.78 | 0.044993
820.315 | 0.066414 | 1060.71 | 0.062015 | 1191.18 | 0.061219 | 1668.57 | 0.054178 | 2377.34 | 0.049397 | 2912.45 | 0.04752 | 3360.2 | 0.04691 | 4241.91 | 0.045397 | 4830.84 | 0.048909
765.619 | 0.069727 | 975.253 | 0.066085 | 1100.7 | 0.065108 | 1560.43 | 0.057107 | 2225.5 | 0.052483 | 2737.35 | 0.050388 | 3174.02 | 0.049692 | 3982.9 | 0.048618 | 4554.05 | 0.052483
701.121 | 0.074377 | 886.865 | 0.071197 | 974.278 | 0.072122 | 1453.48 | 0.060674 | 2070.89 | 0.055983 | 2567.64 | 0.053696 | 3010.17 | 0.052692 | 3709.91 | 0.052797 | 4149.6 | 0.059303
634.397 | 0.080529 | 807.294 | 0.076932 | 853.794 | 0.08093 | 1349.8 | 0.064785 | 1944.44 | 0.059599 | 2403.64 | 0.057505 | 2806.65 | 0.056598 | 3469.47 | 0.057107 | 3830.55 | 0.065823
572.877 | 0.087798 | 744.478 | 0.082636 | 761.8 | 0.090724 | 1267.38 | 0.068696 | 1814.79 | 0.063827 | 2241.13 | 0.061891 | 2637.92 | 0.060674 | 3234.91 | 0.0622 | 3582.3 | 0.072122
509.62 | 0.097547 | 685.864 | 0.089293 | 692.757 | 0.1001 | 1169.93 | 0.074082 | 1688.71 | 0.068627 | 2100.08 | 0.066414 | 2410.86 | 0.067277 | 2971.29 | 0.069106 | 3313.49 | 0.080369
456.989 | 0.10881 | 637.577 | 0.095819 | 624.952 | 0.11221 | 1085.39 | 0.079733 | 1557.31 | 0.074822 | 1936.68 | 0.07277 | 2218.83 | 0.074377 | 2742.83 | 0.076932 | 3098.75 | 0.088675
412.26 | 0.12137 | 586.206 | 0.10457 | 560.971 | 0.12755 | 983.087 | 0.088323 | 1433.27 | 0.081819 | 1785.98 | 0.08013 | 2075.03 | 0.081011 | 2547.18 | 0.084714 | 2877.71 | 0.098815
362.001 | 0.14088 | 535.75 | 0.11561 | 507.585 | 0.14485 | 892.202 | 0.098619 | 1316.47 | 0.090364 | 1661.91 | 0.087711 | 1898.33 | 0.090724 | 2325.61 | 0.096105 | 2565.08 | 0.11758
330.182 | 0.15792 | 496.54 | 0.12617 | 474.215 | 0.1584 | 793.685 | 0.11288 | 1209.19 | 0.1002 | 1558.87 | 0.09506 | 1734.93 | 0.10251 | 2121.19 | 0.10946 | 2363.12 | 0.13365
293.136 | 0.18494 | 456.532 | 0.13948 | 440.829 | 0.17494 | 731.197 | 0.12529 | 1129.69 | 0.10924 | 1456.39 | 0.10385 | 1598.34 | 0.11469 | 1942.5 | 0.12517 | 2161.88 | 0.15405
253.821 | 0.22626 | 416.82 | 0.15714 | 400.075 | 0.20064 | 673.628 | 0.1399 | 1038.67 | 0.12198 | 1359.28 | 0.11367 | 1466.62 | 0.12973 | 1773.52 | 0.1437 | 1987.69 | 0.17668
221.544 | 0.27792 | 379.802 | 0.17827 | 363.816 | 0.2308 | 615.647 | 0.15777 | 967.482 | 0.13432 | 1256.02 | 0.12654 | 1383.97 | 0.14172 | 1627.37 | 0.16367 | 1825.71 | 0.20325
199.86 | 0.32644 | 345.035 | 0.20325 | 334.168 | 0.26314 | 554.834 | 0.18275 | 901.169 | 0.14834 | 1161.77 | 0.14214 | 1296.87 | 0.15605 | 1503.75 | 0.18605 | 1715.95 | 0.22581
178.504 | 0.39425 | 315.968 | 0.23149 | 305.405 | 0.30331 | 506.571 | 0.20919 | 838.563 | 0.16449 | 1079.98 | 0.15777 | 1218.9 | 0.17218 | 1390.91 | 0.21044 | 1568.25 | 0.2634
162.977 | 0.45896 | 290.8 | 0.26262 | 280.798 | 0.34891 | 450.185 | 0.25039 | 772.541 | 0.1855 | 1007.97 | 0.17581 | 1144.47 | 0.18997 | 1278.84 | 0.24256 | 1478.4 | 0.29207
150.145 | 0.52902 | 266.302 | 0.3024 | 258.431 | 0.39977 | 406.122 | 0.29557 | 721.752 | 0.2063 | 926.76 | 0.20004 | 1068.16 | 0.21212 | 1179.33 | 0.27792 | 1402.08 | 0.32193
139.714 | 0.60254 | 247.306 | 0.34035 | 238.8 | 0.45805 | 379.422 | 0.33134 | 668.261 | 0.23357 | 817.04 | 0.24449 | 984.07 | 0.2428 | 1094.11 | 0.3156 | 1303.37 | 0.36777
121.218 | 0.77777 | 226.926 | 0.39191 | 224.219 | 0.51196 | 340.238 | 0.39819 | 623.08 | 0.26106 | 734.862 | 0.29207 | 923.984 | 0.27003 | 1021.16 | 0.35591 | 1217.68 | 0.41805
107.833 | 0.96775 | 207.601 | 0.45533 | 210.528 | 0.5705 | 309.092 | 0.47097 | 575.748 | 0.29675 | 668.261 | 0.34238 | 860.652 | 0.30512 | 952.125 | 0.40296 | 1129.69 | 0.48233
97.4738 | 1.1723 | 189.164 | 0.53377 | 196.884 | 0.64018 | 288.195 | 0.53324 | 541.134 | 0.32937 | 605.269 | 0.40618 | 803.267 | 0.34375 | 888.64 | 0.45533 | 1054.37 | 0.54937
89.2623 | 1.399 | 165.771 | 0.68287 | 178.861 | 0.76323 | 270.327 | 0.5954 | 502.534 | 0.37329 | 549.313 | 0.48377 | 749.708 | 0.38881 | 824.427 | 0.51912 | 969.419 | 0.64657
81.3349 | 1.6829 | 148.354 | 0.83461 | 166.435 | 0.87363 | 254.838 | 0.65889 | 465.755 | 0.42644 | 500.528 | 0.5722 | 702.525 | 0.43629 | 765.619 | 0.59717 | 915.705 | 0.7277
75.1564 | 1.9885 | 134.639 | 1.003 | 155.805 | 0.99406 | 236.424 | 0.75344 | 429.944 | 0.49152 | 460.199 | 0.66217 | 640.133 | 0.51809 | 723.197 | 0.66151 | 854.649 | 0.83793
70.2154 | 2.3058 | 122.192 | 1.2149 | 145.416 | 1.1412 | 222.21 | 0.84883 | 398.08 | 0.56262 | 420.589 | 0.77855 | 582.117 | 0.62014 | 675.652 | 0.74896 | 803.267 | 0.95439
66.2585 | 2.6445 | 110.784 | 1.4864 | 134.101 | 1.3472 | 206.153 | 0.97741 | 368.208 | 0.64528 | 387.475 | 0.90634 | 532.012 | 0.73862 | 622.457 | 0.87711 | 743.734 | 1.1244
62.3998 | 3.0421 | 99.9415 | 1.8531 | 124.785 | 1.5636 | 194.341 | 1.0957 | 325.591 | 0.81172 | 362.001 | 1.0302 | 497.534 | 0.84378 | 583.282 | 0.98913 | 698.322 | 1.2806
59.1194 | 3.4752 | 93.4645 | 2.1423 | 114.731 | 1.8809 | 183.023 | 1.2344 | 297.566 | 0.96009 | 337.864 | 1.1793 | 468.09 | 0.95249 | 550.963 | 1.1066 | 649.808 | 1.4879
55.6764 | 4.0216 | 87.3199 | 2.5014 | 108.482 | 2.1275 | 173.749 | 1.3742 | 272.226 | 1.1424 | 314.392 | 1.3606 | 437.754 | 1.0968 | 516.288 | 1.2542 | 610.131 | 1.6997
52.1202 | 4.8042 | 82.1523 | 2.8832 | 103.088 | 2.3661 | 164.121 | 1.5436 | 252.303 | 1.3259 | 292.843 | 1.5745 | 414.741 | 1.2283 | 491.107 | 1.3865 | 577.478 | 1.9168
49.1339 | 5.688 | 77.2133 | 3.3465 | 98.3551 | 2.6158 | 155.493 | 1.7321 | 235.244 | 1.5298 | 276.064 | 1.7809 | 394.908 | 1.362 | 468.558 | 1.5298 | 551.515 | 2.136
46.3651 | 6.6811 | 73.7418 | 3.7739 | 93.2777 | 2.9645 | 147.91 | 1.9282 | 222.655 | 1.7201 | 257.657 | 2.065 | 372.653 | 1.5482 | 444.37 | 1.7167 | 527.246 | 2.3567
44.1478 | 7.7623 | 69.6559 | 4.3977 | 89.2623 | 3.32 | 139.714 | 2.1919 | 209.269 | 1.9669 | 242.894 | 2.3661 | 355.188 | 1.7235 | 420.168 | 1.9494 | 498.032 | 2.6976
42.2051 | 8.8763 | 66.0601 | 5.0841 | 85.0787 | 3.7627 | 132.369 | 2.489 | 196.687 | 2.2425 | 229.666 | 2.6922 | 335.172 | 1.9669 | 399.276 | 2.1962 | 470.907 | 3.0786
40.6313 | 10.2107 | 62.5247 | 5.9539 | 81.8244 | 4.1888 | 126.671 | 2.7709 | 183.023 | 2.655 | 219.559 | 3.012 | 322.351 | 2.153 | 381.706 | 2.4498 | 446.151 | 3.4891
39.3123 | 11.7809 | 59.5347 | 6.9935 | 78.3803 | 4.7097 | 120.372 | 3.1466 | 174.271 | 2.9734 | 207.601 | 3.4752 | 310.021 | 2.3614 | 362.726 | 2.7709 | 425.666 | 3.9464
37.8086 | 14.3844 | 56.9149 | 8.1982 | 75.5331 | 5.2954 | 114.731 | 3.5591 | 164.286 | 3.4238 | 197.871 | 3.9269 | 300.257 | 2.5694 | 344.001 | 3.1812 | 408.975 | 4.389
36.6544 | 17.6508 | 54.5738 | 9.6105 | 73.3006 | 5.9068 | 110.012 | 3.9819 | 155.028 | 3.974 | 189.732 | 4.4196 | 287.331 | 2.8491 | 328.535 | 3.6018 | 393.331 | 4.9006
35.6423 | 21.8099 | 52.5914 | 11.2659 | 70.5673 | 6.8696 | 105.171 | 4.5217 | 148.949 | 4.446 | 183.206 | 4.9006 | 278.56 | 3.0939 | 313.137 | 4.1146 | 377.908 | 5.4991
35.0064 | 26.0023 | 50.8841 | 13.3252 | 68.1401 | 7.9338 | 101.148 | 5.074 | 144.113 | 4.8666 | 178.147 | 5.343 | 268.173 | 3.417 | 299.058 | 4.7426 | 363.816 | 6.1158
34.3132 | 32.6117 | 49.6277 | 15.5279 | 65.6649 | 9.3376 | 97.3764 | 5.6937 | 138.601 | 5.3963 | 171.504 | 6.0015 | 258.173 | 3.7927 | 287.906 | 5.3059 | 351.653 | 6.7747
33.8024 | 39.3077 | 48.354 | 18.6049 | 63.5332 | 10.9243 | 94.027 | 6.4081 | 133.433 | 5.9896 | 165.937 | 6.7011 | 249.792 | 4.1639 | 278.282 | 5.9599 | 337.864 | 7.6475
33.4325 | 48.4254 | 47.5389 | 21.6587 | 62.0265 | 12.4672 | 90.9746 | 7.1836 | 128.2 | 6.7949 | 161.678 | 7.4156 | 240.718 | 4.6678 | 267.637 | 6.7949 | 328.535 | 8.4967
33.1993 | 60.1339 | 46.9718 | 25.2891 | 60.5555 | 14.4704 | 88.2857 | 8.085 | 123.543 | 7.7469 | 156.899 | 8.371 | 233.137 | 5.1502 | 259.467 | 7.7009 | 319.782 | 9.4683
33.0668 | 79.0235 | 46.3187 | 29.7044 | 59.4157 | 16.8122 | 85.8479 | 9.1721 | 119.772 | 8.719 | 151.806 | 9.4683 | 226.246 | 5.6767 | 251.295 | 8.9382 | 313.45 | 10.3435
33.0007 | 108.271 | 45.812 | 34.7523 | 58.5311 | 19.4168 | 83.8959 | 10.3846 | 115.768 | 10.2209 | 147.762 | 10.8378 | 219.779 | 6.2447 | 244.112 | 10.2006 | 304.795 | 11.8161
33.0007 | 153.286 | 45.3108 | 40.9416 | 57.6596 | 23.2645 | 81.5792 | 12.0892 | 112.234 | 11.8632 | 143.825 | 12.4301 | 212.219 | 7.1197 | 239.278 | 11.4692 | 298.759 | 13.1673
33.0007 | 221.153 | 44.9048 | 48.5217 | 56.9149 | 27.6541 | 79.6445 | 14.0177 | 109.135 | 13.6875 | 140.555 | 14.2423 | 204.715 | 8.1011 | 233.603 | 12.9597 | 291.966 | 14.7902
33.0007 | 317.486 | 44.547 | 58.659 | 56.2922 | 33.3985 | 77.9114 | 16.0453 | 106.44 | 16.0135 | 136.947 | 16.7455 | 198.466 | 9.2269 | 229.666 | 14.4992 | 285.327 | 16.8791
32.9677 | 467.707 | 44.3691 | 72.553 | 55.7321 | 40.0964 | 76.8282 | 18.1126 | 104.541 | 18.3116 | 133.967 | 19.4168 | 192.215 | 10.6246 | 225.568 | 16.2216 | 279.677 | 19.0727
32.9348 | 545.559 | 44.1478 | 91.6296 | 55.3433 | 49.348 | 75.3822 | 21.3384 | 102.471 | 21.4234 | 130.268 | 23.5435 | 187.094 | 12.1253 | 221.766 | 18.1847 | 273.317 | 22.0495
32.9019 | 600.146 | 44.1478 | 121.614 | 55.1775 | 62.5093 | 74.1114 | 24.8162 | 100.442 | 25.1138 | 127.944 | 27.8747 | 182.11 | 14.3702 | 216.507 | 21.3596 | 266.569 | 26.0799
|  | 44.1478 | 157.141 | 55.1775 | 81.9006 | 73.1542 | 29.0623 | 98.552 | 29.178 | 125.536 | 33.0027 | 178.326 | 16.6295 | 213.07 | 24.7916 | 262.075 | 29.7339
|  | 44.1478 | 198.261 | 55.1775 | 111.103 | 72.065 | 34.4088 | 97.3764 | 33.6315 | 123.667 | 38.7648 | 174.445 | 19.2823 | 209.269 | 29.4986 | 257.657 | 34.7178
|  | 44.1478 | 274.08 | 55.1775 | 143.987 | 71.1342 | 41.3914 | 95.8307 | 39.8978 | 122.07 | 45.6688 | 170.138 | 23.2877 | 204.92 | 36.1968 | 253.567 | 39.3077
|  | 44.1478 | 356.969 | 55.1775 | 187.907 | 70.356 | 50.3382 | 94.5929 | 46.8172 | 120.372 | 55.5401 | 167.437 | 27.7366 | 201.063 | 44.0645 | 249.792 | 45.3974
|  | 44.0596 | 437.592 | 55.1775 | 253.645 | 69.5167 | 61.3406 | 93.3711 | 56.0946 | 119.056 | 65.7576 | 164.615 | 33.233 | 197.673 | 54.0703 | 246.073 | 54.5017
|  | 44.0156 | 541.779 | 55.1775 | 345.457 | 68.9627 | 73.9354 | 92.627 | 65.9539 | 117.518 | 81.8193 | 162.326 | 40.0168 | 195.12 | 63.5107 | 242.894 | 63.637
|  | 43.9716 | 600.146 | 55.1775 | 466.778 | 68.2765 | 90.9044 | 91.7971 | 77.3153 | 116.116 | 103.229 | 160.39 | 47.097 | 192.793 | 74.3035 | 239.517 | 76.3992
|  |  |  | 55.1775 | 566.546 | 67.8002 | 113.671 | 91.0656 | 91.9945 | 115.075 | 126.796 | 158.476 | 56.3739 | 190.683 | 87.1898 | 236.187 | 91.6296
|  |  |  | 55.1223 | 600.146 | 67.3946 | 140.595 | 90.5208 | 108.702 | 113.476 | 168.122 | 156.429 | 67.7467 | 188.22 | 102.616 | 232.671 | 113.784
[6 empty] | 66.9914 | 180.228 | 90.0693 | 131.543 | 112.684 | 205.072 | 154.718 | 80.3693 | 186.721 | 118.044 | 229.666 | 135.926
[6 empty] | 66.724 | 228.523 | 89.7098 | 152.982 | 112.122 | 254.908 | 152.262 | 103.024 | 185.048 | 137.011 | 227.153 | 161.733
[6 empty] | 66.4576 | 295.279 | 88.8171 | 188.093 | 111.563 | 314.348 | 150.295 | 130.631 | 183.573 | 161.252 | 224.443 | 196.692
[6 empty] | 66.2585 | 365.582 | 88.551 | 239.207 | 111.117 | 384.962 | 148.206 | 168.959 | 181.746 | 191.677 | 222.21 | 237.314
[6 empty] | 66.1923 | 452.174 | 88.1093 | 309.699 | 110.453 | 487.148 | 146.731 | 205.684 | 180.298 | 226.714 | 220.439 | 280.971
[6 empty] | 66.0601 | 540.166 | 88.0213 | 415.975 | 110.232 | 569.933 | 145.416 | 269.223 | 178.861 | 269.223 | 218.683 | 330.684
[6 empty] | 66.0601 | 600.146 | 88.0213 | 527.965 | 110.012 | 600.146 | 144.402 | 324.501 | 177.969 | 311.55 | 216.94 | 414.326
[8 empty] | 88.0213 | 573.91 |  |  | 143.538 | 405.772 | 176.905 | 372.177 | 215.858 | 496.923
[8 empty] | 88.0213 | 600.146 |  |  | 142.965 | 501.884 | 175.846 | 451.725 | 215.642 | 566.546
[12 empty] | 142.537 | 572.202 | 175.144 | 532.178 | 215.211 | 600.146
[12 empty] | 142.537 | 600.146 | 174.445 | 573.34
[14 empty] | 173.922 | 600.146