## 123_62U
S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links | [9 empty] | S&C Positrol Fuse Links
Universal Style (1 std. thru 200 std.) Extra Performance Style (1 std. thru 100 std.) | [9 empty] | Universal Style (1 std. thru 200 std.) Extra Performance Style (1 std. thru 100 std.) | [9 empty] | Universal Style (1 std. thru 200 std.) Extra Performance Style (1 std. thru 100 std.) | [9 empty] | Universal Style (1 std. thru 200 std.) Extra Performance Style (1 std. thru 100 std.)
Indicating Style (3 std. thru 100 std.) Open Style (1 std. thru 25 std.) Styles | [9 empty] | Indicating Style (3 std. thru 100 std.) Open Style (1 std. thru 25 std.) Styles | [9 empty] | Indicating Style (3 std. thru 100 std.) Open Style (1 std. thru 25 std.) Styles | [9 empty] | Indicating Style (3 std. thru 100 std.) Open Style (1 std. thru 25 std.) Styles
Standard Speed (TCC 123-62) | [9 empty] | Standard Speed (TCC 123-62) | [9 empty] | Standard Speed (TCC 123-62) | [9 empty] | Standard Speed (TCC 123-62)
Total Clearing Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 20, 1986 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 20, 1986
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
1 |  | 2 |  | 3 |  | 5 |  | 7 |  | 10 |  | 15 |  | 20 |  | 25 |  | 30 |  | 40 |  | 50 |  | 65 |  | 80 |  | 100 |  | 125 |  | 150 |  | 200
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
10000 | 0.013445 | 10000 | 0.013445 | 10000 | 0.013445 | 10000 | 0.013445 | 10000 | 0.013445 | 10000 | 0.013566 | 10000 | 0.013566 | 10000 | 0.013566 | 10000 | 0.013566 | 10000 | 0.013716 | 10000 | 0.013716 | 10000 | 0.014106 | 10000 | 0.014477 | 10000 | 0.015129 | 10000 | 0.016356 | 10000 | 0.018908 | 10000 | 0.022682 | 10000 | 0.028349
1556.72 | 0.013472 | 1559.84 | 0.013485 | 1558.28 | 0.013485 | 2385.92 | 0.01358 | 2388.31 | 0.013607 | 3671.44 | 0.013634 | 4970.82 | 0.013716 | 4965.85 | 0.013854 | 6059.24 | 0.013854 | 8361.06 | 0.013785 | 8824.97 | 0.01391 | 9121.05 | 0.014276 | 9139.31 | 0.014667 | 9021.27 | 0.015512 | 9286.71 | 0.01677 | 9333.26 | 0.019739 | 9342.6 | 0.023845 | 9512.29 | 0.029892
1164.84 | 0.013539 | 1345.26 | 0.013499 | 1347.95 | 0.013526 | 2025.03 | 0.013634 | 2070.07 | 0.013716 | 3172.71 | 0.013689 | 4360.49 | 0.013785 | 4240.09 | 0.014035 | 5471.68 | 0.013965 | 7334.47 | 0.013868 | 7969.21 | 0.014092 | 8386.18 | 0.014448 | 8253.07 | 0.014948 | 8138.33 | 0.016016 | 8658.87 | 0.017246 | 8658.87 | 0.02073 | 8745.9 | 0.025345 | 8869.2 | 0.03222
1013.68 | 0.013593 | 1166.01 | 0.013526 | 1211.17 | 0.013634 | 1790.66 | 0.013662 | 1843.35 | 0.013826 | 2833.7 | 0.013744 | 3886.8 | 0.013896 | 3937.65 | 0.014162 | 4946.03 | 0.014106 | 6676.44 | 0.013979 | 7261.49 | 0.014276 | 7535.2 | 0.014726 | 7535.2 | 0.01522 | 7430.44 | 0.016504 | 8033.21 | 0.017878 | 8057.35 | 0.021946 | 8041.25 | 0.027401 | 8344.35 | 0.034591
876.856 | 0.013662 | 1013.68 | 0.01358 | 1081.75 | 0.013744 | 1633.27 | 0.013716 | 1652.99 | 0.013965 | 2528.4 | 0.01384 | 3502.88 | 0.014035 | 3602.34 | 0.014362 | 4444.13 | 0.014262 | 6053.19 | 0.01412 | 6716.62 | 0.014463 | 6845.45 | 0.014993 | 6962.82 | 0.015527 | 6777.34 | 0.017075 | 7460.22 | 0.018645 | 7497.61 | 0.023303 | 7497.61 | 0.029506 | 7874.15 | 0.036988
805.403 | 0.01373 | 876.856 | 0.013662 | 947.989 | 0.013896 | 1464.6 | 0.013826 | 1492.7 | 0.014148 | 2299.25 | 0.013979 | 3138 | 0.014233 | 3295.59 | 0.014594 | 4009.17 | 0.014492 | 5554.37 | 0.014262 | 6156.97 | 0.014726 | 6268.8 | 0.01525 | 6479.12 | 0.015872 | 6206.42 | 0.017665 | 7011.73 | 0.019425 | 6990.73 | 0.024843 | 6969.79 | 0.031868 | 7445.31 | 0.039709
751.704 | 0.013785 | 791.036 | 0.013799 | 835.761 | 0.014106 | 1334.54 | 0.013924 | 1339.89 | 0.014362 | 2086.7 | 0.014162 | 2813.94 | 0.014506 | 3017.97 | 0.014844 | 3634.91 | 0.014726 | 5025.8 | 0.014506 | 5632.68 | 0.014978 | 5769.5 | 0.015512 | 6029.02 | 0.016291 | 5660.91 | 0.018441 | 6505.09 | 0.020401 | 6446.81 | 0.026805 | 6453.26 | 0.034764 | 7089.29 | 0.042292
691.832 | 0.013882 | 725.124 | 0.013965 | 741.995 | 0.014348 | 1209.96 | 0.014092 | 1205.13 | 0.014637 | 1884.35 | 0.014391 | 2510.76 | 0.014814 | 2760.98 | 0.015113 | 3233.56 | 0.015068 | 4529.38 | 0.014755 | 5096.66 | 0.015327 | 5304.66 | 0.015888 | 5604.58 | 0.01677 | 5241.38 | 0.019271 | 6010.96 | 0.021706 | 5980.98 | 0.028979 | 6029.02 | 0.037697 | 6750.29 | 0.045267
639.28 | 0.013979 | 665.37 | 0.014106 | 660.068 | 0.014623 | 1099.2 | 0.014276 | 1086.09 | 0.014933 | 1667.93 | 0.014726 | 2213.52 | 0.015204 | 2538.53 | 0.015403 | 2958.21 | 0.015373 | 4073.84 | 0.015038 | 4644.04 | 0.015699 | 4896.81 | 0.016291 | 5127.33 | 0.017367 | 4970.82 | 0.019957 | 5571.06 | 0.023094 | 5593.39 | 0.031112 | 5649.6 | 0.040878 | 6433.93 | 0.048211
585.428 | 0.014134 | 612.374 | 0.014305 | 605.069 | 0.014859 | 999.588 | 0.014506 | 971.987 | 0.015296 | 1458.76 | 0.015144 | 2002.88 | 0.015605 | 2313.09 | 0.015793 | 2700.9 | 0.01573 | 3741.87 | 0.015311 | 4240.09 | 0.016128 | 4533.91 | 0.016787 | 4723.66 | 0.018058 | 4686.03 | 0.020792 | 5076.31 | 0.025194 | 5158.19 | 0.034008 | 5299.35 | 0.044504 | 6059.24 | 0.052646
537.185 | 0.014319 | 554.099 | 0.01455 | 539.878 | 0.01525 | 886.555 | 0.014829 | 866.397 | 0.015715 | 1297.69 | 0.015558 | 1815.91 | 0.016048 | 2120.36 | 0.016258 | 2456.12 | 0.016193 | 3395.95 | 0.015636 | 3898.47 | 0.01657 | 4240.09 | 0.017246 | 4347.43 | 0.019003 | 4343.09 | 0.022078 | 4634.76 | 0.027429 | 4790.26 | 0.037062 | 4990.74 | 0.048356 | 5763.73 | 0.056803
488.502 | 0.014535 | 496.381 | 0.014844 | 483.641 | 0.015746 | 769.963 | 0.015281 | 775.372 | 0.016226 | 1125.9 | 0.016193 | 1639.82 | 0.01657 | 1943.68 | 0.016753 | 2260.5 | 0.01667 | 3131.73 | 0.016 | 3591.55 | 0.017057 | 3989.18 | 0.017736 | 3993.17 | 0.020057 | 4073.84 | 0.023326 | 4265.61 | 0.029952 | 4502.28 | 0.040149 | 4657.99 | 0.053549 | 5482.63 | 0.061411
436.306 | 0.014829 | 450.493 | 0.015129 | 440.25 | 0.016307 | 691.14 | 0.015715 | 699.484 | 0.01682 | 1017.74 | 0.016753 | 1501.68 | 0.017109 | 1788.87 | 0.017315 | 2078.37 | 0.017212 | 2879.41 | 0.016438 | 3322.06 | 0.017559 | 3756.87 | 0.018349 | 3704.64 | 0.021234 | 3779.47 | 0.025068 | 3997.16 | 0.032059 | 4227.39 | 0.043667 | 4413.13 | 0.058183 | 5194.42 | 0.066993
394.786 | 0.015144 | 407.216 | 0.015512 | 408.031 | 0.016854 | 624.12 | 0.016161 | 646.998 | 0.01735 | 930.147 | 0.017385 | 1379.31 | 0.017665 | 1639.82 | 0.018004 | 1922.42 | 0.017843 | 2650.07 | 0.016972 | 3063.58 | 0.018276 | 3523.96 | 0.019098 | 3372.27 | 0.022956 | 3485.41 | 0.027047 | 3723.21 | 0.034729 | 3918.01 | 0.048453 | 4164.45 | 0.063662 | 4975.79 | 0.072211
349.444 | 0.015574 | 368.096 | 0.016016 | 371.052 | 0.017647 | 562.473 | 0.016736 | 596.061 | 0.017986 | 852.645 | 0.01813 | 1249.3 | 0.018515 | 1521.33 | 0.01872 | 1755.2 | 0.018739 | 2417.14 | 0.017647 | 2836.54 | 0.019041 | 3292.3 | 0.020037 | 3128.6 | 0.024547 | 3223.88 | 0.029388 | 3481.92 | 0.037622 | 3634.91 | 0.054195 | 3981.21 | 0.068895 | 4728.39 | 0.078696
315.558 | 0.016 | 331.406 | 0.016653 | 335.742 | 0.018664 | 506.408 | 0.017437 | 543.127 | 0.018965 | 791.827 | 0.018927 | 1147.5 | 0.019406 | 1411.4 | 0.019621 | 1631.64 | 0.019621 | 2222.39 | 0.018478 | 2615.84 | 0.020017 | 3091.28 | 0.02098 | 2859.32 | 0.026805 | 2996.92 | 0.031645 | 3243.28 | 0.041124 | 3389.17 | 0.060315 | 3977.23 | 0.069172 | 4502.28 | 0.085677
286.96 | 0.016553 | 300.168 | 0.017385 | 307.152 | 0.01968 | 458.217 | 0.018276 | 502.373 | 0.019877 | 741.254 | 0.019699 | 1066.71 | 0.02034 | 1322.58 | 0.020483 | 1525.9 | 0.020524 | 2041.3 | 0.019484 | 2426.83 | 0.021086 | 2862.18 | 0.022367 | 2628.95 | 0.029212 | 2813.94 | 0.034076 | 3045.26 | 0.044817 | 3207.8 | 0.06593 | 3616.78 | 0.081092 | 4257.09 | 0.095353
261.476 | 0.017194 | 272.692 | 0.018276 | 278.758 | 0.020834 | 405.59 | 0.01968 | 461.898 | 0.021064 | 702.288 | 0.020421 | 987.664 | 0.02149 | 1225.79 | 0.021749 | 1407.17 | 0.021924 | 1890.01 | 0.020565 | 2276.38 | 0.022189 | 2668.68 | 0.02375 | 2405.08 | 0.032091 | 2579.47 | 0.037886 | 2876.53 | 0.048356 | 3005.92 | 0.073375 | 3259.54 | 0.097474 | 3848.12 | 0.1145
234.708 | 0.018058 | 237.779 | 0.019818 | 245.021 | 0.022773 | 361.891 | 0.021191 | 426.385 | 0.022614 | 662.051 | 0.021404 | 913.554 | 0.02291 | 1137.22 | 0.023164 | 1308.11 | 0.023326 | 1732.53 | 0.022034 | 2099.26 | 0.023655 | 2448.77 | 0.025831 | 2200.28 | 0.035573 | 2405.08 | 0.041537 | 2615.84 | 0.055734 | 2808.32 | 0.082731 | 2967.1 | 0.11542 | 3506.38 | 0.13736
210.681 | 0.019155 | 211.102 | 0.021469 | 220.819 | 0.024547 | 332.401 | 0.022728 | 392.817 | 0.024376 | 614.214 | 0.022796 | 845.851 | 0.024498 | 1039.34 | 0.025194 | 1200.31 | 0.025396 | 1600.93 | 0.023561 | 1949.52 | 0.025345 | 2224.62 | 0.028377 | 2031.11 | 0.039354 | 2262.76 | 0.045267 | 2369.28 | 0.064883 | 2513.27 | 0.10024 | 2687.43 | 0.13916 | 3236.8 | 0.16119
187.981 | 0.020401 | 186.67 | 0.023467 | 197.027 | 0.026886 | 303.488 | 0.024596 | 365.528 | 0.026143 | 554.099 | 0.024993 | 776.148 | 0.026591 | 966.173 | 0.02702 | 1109.14 | 0.027539 | 1471.94 | 0.025523 | 1815.91 | 0.027183 | 2041.3 | 0.031019 | 1869.34 | 0.043842 | 2156.71 | 0.048356 | 2105.57 | 0.078147 | 2280.93 | 0.11989 | 2483.29 | 0.16297 | 3002.92 | 0.18746
168.737 | 0.021815 | 165.231 | 0.025961 | 179.171 | 0.029212 | 272.692 | 0.027129 | 338.777 | 0.028179 | 513.035 | 0.026886 | 711.477 | 0.029037 | 891.89 | 0.029329 | 1034.15 | 0.029832 | 1365.59 | 0.027346 | 1681.33 | 0.029447 | 1890.01 | 0.033974 | 1741.22 | 0.048259 | 2114.01 | 0.049878 | 1878.71 | 0.09431 | 2090.88 | 0.1414 | 2313.09 | 0.18935 | 2769.27 | 0.22065
152.832 | 0.023233 | 146.693 | 0.028806 | 164.736 | 0.031614 | 247.979 | 0.029832 | 311.171 | 0.030895 | 467.941 | 0.029506 | 662.051 | 0.031362 | 824.142 | 0.031868 | 952.741 | 0.032772 | 1244.31 | 0.030132 | 1559.84 | 0.031995 | 1715.29 | 0.038114 | 1566.09 | 0.056407 | 1893.8 | 0.058709 | 1677.97 | 0.11439 | 1888.13 | 0.17322 | 2128.86 | 0.22624 | 2576.89 | 0.25662
136.776 | 0.025118 | 128.168 | 0.032707 | 152.527 | 0.034247 | 226.862 | 0.032772 | 286.387 | 0.034008 | 422.565 | 0.032871 | 598.45 | 0.035325 | 755.472 | 0.035184 | 883.899 | 0.035895 | 1137.22 | 0.033201 | 1441.36 | 0.035149 | 1591.35 | 0.042039 | 1417.06 | 0.065601 | 1667.93 | 0.071635 | 1503.18 | 0.13985 | 1698.23 | 0.21564 | 1933.99 | 0.27716 | 2381.15 | 0.30266
117.842 | 0.028095 | 111.647 | 0.037697 | 137.599 | 0.038305 | 208.584 | 0.036111 | 266.758 | 0.037025 | 388.131 | 0.036255 | 557.991 | 0.038574 | 691.832 | 0.039197 | 805.403 | 0.040471 | 1051.88 | 0.036292 | 1322.58 | 0.039157 | 1437.04 | 0.048501 | 1278.37 | 0.077138 | 1477.84 | 0.087234 | 1358.78 | 0.16946 | 1528.95 | 0.26816 | 1762.24 | 0.33751 | 2226.84 | 0.34988
102.14 | 0.031582 | 99.8177 | 0.042589 | 127.02 | 0.041955 | 187.981 | 0.041165 | 246.989 | 0.04096 | 354.725 | 0.040512 | 514.576 | 0.042931 | 642.485 | 0.043146 | 742.738 | 0.045403 | 965.207 | 0.04035 | 1220.89 | 0.043536 | 1343.91 | 0.053763 | 1142.92 | 0.092813 | 1313.35 | 0.10644 | 1230.7 | 0.20471 | 1379.31 | 0.33116 | 1591.35 | 0.42225 | 2041.3 | 0.42521
90.6808 | 0.035114 | 89.0632 | 0.048598 | 119.145 | 0.045585 | 173.529 | 0.045722 | 232.141 | 0.044504 | 327.78 | 0.044997 | 473.591 | 0.048115 | 595.465 | 0.047971 | 709.346 | 0.048647 | 889.218 | 0.044772 | 1134.94 | 0.048115 | 1209.96 | 0.063029 | 1021.82 | 0.11235 | 1170.68 | 0.13079 | 1120.29 | 0.24557 | 1253.05 | 0.40691 | 1451.48 | 0.51936 | 1897.59 | 0.50603
80.5071 | 0.039275 | 88.7076 | 0.048842 | 113.108 | 0.048598 | 157.33 | 0.052593 | 217.531 | 0.048744 | 307.152 | 0.049136 | 471.7 | 0.048598 | 576.712 | 0.050329 | 660.068 | 0.054358 | 837.434 | 0.048598 | 1067.78 | 0.053016 | 1108.03 | 0.072645 | 894.57 | 0.14268 | 1056.1 | 0.15784 | 1011.65 | 0.29964 | 1144.06 | 0.49502 | 1346.6 | 0.61745 | 1748.2 | 0.6156
71.1895 | 0.044371 | 78.3625 | 0.056803 | 110.095 | 0.05043 | 139.121 | 0.062903 | 197.225 | 0.05652 | 288.687 | 0.054033 | 421.299 | 0.057145 | 514.062 | 0.060015 | 595.465 | 0.063662 | 795.001 | 0.052541 | 960.393 | 0.062277 | 1002.59 | 0.08508 | 807.016 | 0.17288 | 952.741 | 0.19395 | 900.854 | 0.37338 | 1056.1 | 0.59324 | 1245.56 | 0.74292 | 1633.27 | 0.72821
65.5194 | 0.048259 | 69.0856 | 0.066194 | 98.0371 | 0.059596 | 121.067 | 0.078382 | 175.273 | 0.067599 | 260.172 | 0.063345 | 377.037 | 0.067734 | 459.594 | 0.071564 | 535.041 | 0.075233 | 708.637 | 0.062464 | 874.229 | 0.072139 | 886.555 | 0.10496 | 720.787 | 0.21564 | 864.666 | 0.23313 | 807.016 | 0.46619 | 980.775 | 0.70598 | 1145.2 | 0.91561 | 1538.16 | 0.85713
58.1105 | 0.055069 | 62.0752 | 0.076676 | 88.0008 | 0.069449 | 107.484 | 0.094405 | 156.701 | 0.081011 | 231.909 | 0.075761 | 336.751 | 0.080769 | 418.36 | 0.082979 | 476.441 | 0.090794 | 633.553 | 0.074559 | 792.619 | 0.08491 | 815.942 | 0.12122 | 633.553 | 0.27827 | 782.382 | 0.28219 | 725.124 | 0.57975 | 908.089 | 0.84353 | 1069.92 | 1.0951 | 1435.6 | 1.0293
50.5188 | 0.064431 | 54.2361 | 0.091158 | 79.2293 | 0.08158 | 95.7122 | 0.11439 | 140.378 | 0.096988 | 206.509 | 0.091431 | 305.926 | 0.094499 | 377.037 | 0.098849 | 425.108 | 0.11001 | 567.558 | 0.088996 | 719.346 | 0.10004 | 748.703 | 0.14154 | 563.599 | 0.35023 | 735.347 | 0.31913 | 653.5 | 0.72386 | 852.645 | 0.98397 | 1004.59 | 1.2993 | 1321.26 | 1.3111
44.1391 | 0.075308 | 47.5768 | 0.10946 | 72.6277 | 0.09384 | 85.9139 | 0.1364 | 126.386 | 0.11635 | 184.998 | 0.1109 | 275.433 | 0.11314 | 338.1 | 0.11894 | 387.743 | 0.12975 | 509.456 | 0.10697 | 660.068 | 0.11646 | 694.605 | 0.162 | 503.883 | 0.43992 | 680.851 | 0.37077 | 597.852 | 0.8762 | 807.823 | 1.1251 | 950.837 | 1.5263 | 1231.93 | 1.6239
39.0306 | 0.086972 | 42.2391 | 0.1291 | 64.6731 | 0.11359 | 77.0416 | 0.16593 | 115.047 | 0.13777 | 166.391 | 0.13356 | 249.721 | 0.13437 | 309.001 | 0.13999 | 357.574 | 0.15014 | 457.759 | 0.12949 | 611.15 | 0.13423 | 633.553 | 0.19221 | 445.12 | 0.566 | 624.745 | 0.4408 | 544.759 | 1.0799 | 766.123 | 1.2954 | 905.369 | 1.7857 | 1147.5 | 2.05
34.5479 | 0.10064 | 37.8014 | 0.1515 | 57.4748 | 0.13819 | 68.6037 | 0.20328 | 105.145 | 0.16249 | 149.507 | 0.1633 | 225.28 | 0.16265 | 277.645 | 0.17014 | 325.168 | 0.1785 | 419.198 | 0.15226 | 562.473 | 0.1569 | 579.024 | 0.22737 | 392.032 | 0.74144 | 564.163 | 0.54218 | 497.872 | 1.3322 | 714.329 | 1.5681 | 857.776 | 2.0914 | 1097 | 2.4057
30.9492 | 0.11554 | 33.8299 | 0.17832 | 50.9246 | 0.16777 | 60.2406 | 0.25713 | 97.0616 | 0.18992 | 135.686 | 0.19629 | 203.638 | 0.19727 | 251.475 | 0.2041 | 290.424 | 0.2211 | 384.654 | 0.17797 | 522.875 | 0.17993 | 521.831 | 0.27605 | 349.794 | 0.9568 | 518.709 | 0.64458 | 463.749 | 1.587 | 671.385 | 1.8792 | 815.942 | 2.4989 | 1049.78 | 2.8288
27.6699 | 0.1333 | 30.58 | 0.2076 | 44.5827 | 0.2078 | 54.5079 | 0.30723 | 87.9128 | 0.22874 | 122.896 | 0.23951 | 183.157 | 0.24168 | 227.999 | 0.24484 | 265.428 | 0.26154 | 356.503 | 0.20615 | 486.065 | 0.20656 | 474.064 | 0.33215 | 320.969 | 1.1616 | 480.267 | 0.75793 | 431.533 | 1.9171 | 638.003 | 2.1899 | 784.733 | 2.9207 | 1011.65 | 3.2604
24.7381 | 0.15441 | 27.6423 | 0.24362 | 39.5018 | 0.2533 | 48.6838 | 0.37675 | 80.1858 | 0.2744 | 111.535 | 0.29137 | 161.797 | 0.30723 | 205.684 | 0.29755 | 241.373 | 0.31187 | 325.168 | 0.24631 | 450.493 | 0.23879 | 432.397 | 0.39806 | 297.182 | 1.4146 | 437.617 | 0.92852 | 402.761 | 2.3091 | 609.32 | 2.5519 | 756.228 | 3.4036 | 970.045 | 3.8956
22.2278 | 0.17832 | 24.7877 | 0.29108 | 35.07 | 0.30815 | 43.3951 | 0.46619 | 72.121 | 0.33683 | 101.427 | 0.35128 | 145.524 | 0.37675 | 186.857 | 0.35695 | 217.097 | 0.38168 | 296.588 | 0.2943 | 417.942 | 0.27605 | 393.603 | 0.47895 | 273.511 | 1.7574 | 403.971 | 1.1139 | 375.156 | 2.8316 | 577.289 | 3.043 | 730.948 | 3.9822 | 935.745 | 4.5669
19.8926 | 0.2076 | 22.3616 | 0.34467 | 31.5744 | 0.36782 | 38.6422 | 0.58091 | 65.3231 | 0.40977 | 91.0443 | 0.43685 | 130.235 | 0.47041 | 167.56 | 0.4408 | 195.653 | 0.46572 | 275.433 | 0.34056 | 377.037 | 0.33819 | 356.86 | 0.58557 | 256.299 | 2.0977 | 372.54 | 1.3429 | 354.725 | 3.39 | 547.489 | 3.7019 | 708.637 | 4.6128 | 905.369 | 5.4132
17.2075 | 0.25457 | 20.1327 | 0.41141 | 27.5319 | 0.46666 | 34.93 | 0.71023 | 59.1659 | 0.497 | 81.479 | 0.54708 | 117.842 | 0.57341 | 152.07 | 0.53464 | 173.009 | 0.59324 | 251.475 | 0.40773 | 347.701 | 0.39686 | 325.494 | 0.71237 | 238.732 | 2.5931 | 347.354 | 1.5934 | 338.777 | 4.0263 | 521.831 | 4.4855 | 688.381 | 5.3007 | 883.016 | 6.2641
14.8106 | 0.31438 | 17.9636 | 0.4965 | 24.664 | 0.56543 | 31.0732 | 0.89033 | 54.4534 | 0.5891 | 74.169 | 0.66354 | 104.725 | 0.73113 | 138.704 | 0.64008 | 159.867 | 0.69408 | 232.605 | 0.47799 | 320.648 | 0.46526 | 302.579 | 0.83514 | 225.505 | 3.1294 | 320.327 | 1.9637 | 325.168 | 4.7819 | 497.872 | 5.4349 | 669.374 | 6.1524 | 860.353 | 7.4547
12.684 | 0.39488 | 16.0121 | 0.60704 | 21.9408 | 0.69756 | 27.6976 | 1.1262 | 50.1664 | 0.70036 | 67.178 | 0.8186 | 92.7906 | 0.93973 | 126.893 | 0.76939 | 146.107 | 0.83597 | 213.865 | 0.566 | 293.05 | 0.55702 | 278.758 | 1.0018 | 211.948 | 3.8761 | 301.975 | 2.3068 | 312.418 | 5.7883 | 479.787 | 6.4292 | 650.892 | 7.2127 | 839.95 | 9.0326
11.016 | 0.48619 | 14.3012 | 0.74441 | 19.6553 | 0.85542 | 25.339 | 1.3646 | 46.1707 | 0.83264 | 60.7244 | 1.0139 | 83.6253 | 1.1757 | 115.971 | 0.93038 | 133.399 | 1.0079 | 199.805 | 0.65236 | 269.709 | 0.66156 | 262 | 1.1582 | 203.028 | 4.6221 | 284.389 | 2.726 | 300.769 | 7.1267 | 467.941 | 7.2416 | 632.919 | 8.6871 | 822.495 | 10.7924
9.9976 | 0.5643 | 13.0703 | 0.87883 | 17.7848 | 1.0417 | 23.5316 | 1.6158 | 42.2391 | 1.0038 | 56.4495 | 1.1982 | 75.3652 | 1.4782 | 107.377 | 1.1039 | 121.795 | 1.236 | 186.297 | 0.75642 | 242.34 | 0.83097 | 246.989 | 1.3349 | 194.094 | 5.5948 | 265.959 | 3.3429 | 291.588 | 8.6093 | 455.932 | 8.3465 | 617.293 | 10.2763 | 809.44 | 12.7795
8.9026 | 0.67695 | 11.7558 | 1.082 | 15.9163 | 1.3058 | 21.9847 | 1.8981 | 39.0306 | 1.1934 | 52.3183 | 1.4245 | 68.8786 | 1.8218 | 99.9176 | 1.298 | 112.431 | 1.4886 | 171.287 | 0.9065 | 225.731 | 0.97223 | 234.943 | 1.5202 | 184.813 | 7.3144 | 253.748 | 3.8995 | 282.688 | 10.5787 | 444.675 | 9.9527 | 605.069 | 12.0232 | 797.389 | 15.1628
7.8566 | 0.83014 | 10.7118 | 1.3045 | 14.5464 | 1.587 | 20.335 | 2.3021 | 36.0298 | 1.426 | 48.7325 | 1.6801 | 63.774 | 2.2052 | 92.6052 | 1.5478 | 103.787 | 1.8073 | 159.548 | 1.0606 | 205.068 | 1.2054 | 222.148 | 1.7697 | 178.1 | 9.0326 | 243.555 | 4.5442 | 274.882 | 13.0246 | 436.742 | 11.6562 | 594.87 | 14.1518 | 786.304 | 18.0445
7.0805 | 0.9889 | 9.7703 | 1.5902 | 13.3344 | 1.9481 | 18.9224 | 2.7617 | 33.0938 | 1.7209 | 45.3925 | 1.9834 | 59.522 | 2.627 | 85.4854 | 1.8848 | 95.1396 | 2.2701 | 146.107 | 1.2915 | 189.491 | 1.4548 | 210.891 | 2.048 | 173.529 | 10.9118 | 234.708 | 5.338 | 268.095 | 16.1649 | 430.24 | 13.969 | 586.014 | 16.7073 | 779.259 | 21.3456
6.4646 | 1.1605 | 8.9741 | 1.9248 | 12.4329 | 2.3021 | 17.8204 | 3.3262 | 30.58 | 2.0665 | 42.3237 | 2.3487 | 55.0557 | 3.2636 | 79.3879 | 2.2792 | 88.8852 | 2.7397 | 134.336 | 1.5712 | 176.327 | 1.7486 | 198.61 | 2.4445 | 168.232 | 13.3543 | 227.544 | 6.2516 | 262 | 20.0423 | 426.385 | 16.4092 | 578.445 | 19.3529 | 772.277 | 23.8514
5.8495 | 1.3921 | 8.2759 | 2.3276 | 11.5576 | 2.7645 | 16.9683 | 3.9387 | 28.4272 | 2.4543 | 39.8191 | 2.7424 | 51.8495 | 3.8607 | 74.3918 | 2.6962 | 83.6253 | 3.2898 | 123.512 | 1.9325 | 165.727 | 2.048 | 188.358 | 2.8601 | 163.75 | 16.6906 | 221.926 | 7.1053 | 256.042 | 25.5553 | 422.565 | 19.7834 | 569.833 | 23.0541 | 760.779 | 27.3809
5.2036 | 1.7469 | 7.7784 | 2.7124 | 10.972 | 3.2344 | 16.3193 | 4.6639 | 26.2679 | 2.9768 | 37.09 | 3.2964 | 49.0258 | 4.5624 | 70.0596 | 3.1831 | 79.1501 | 4.0102 | 115.047 | 2.3323 | 154.832 | 2.4641 | 178.813 | 3.39 | 160.027 | 20.3655 | 216.88 | 8.0837 | 251.978 | 30.841 | 419.198 | 23.2393 | 562.473 | 27.3262 | 750.953 | 31.6534
4.7748 | 2.0747 | 7.3621 | 3.2118 | 10.3952 | 3.9112 | 15.695 | 5.6908 | 24.5901 | 3.539 | 34.5479 | 4.0303 | 46.5881 | 5.3701 | 66.1779 | 3.7391 | 74.8395 | 4.9671 | 106.414 | 2.8801 | 148.019 | 2.8203 | 171.63 | 3.919 | 156.388 | 26.0977 | 213.011 | 9.252 | 247.979 | 37.896 | 415.442 | 27.1356 | 555.208 | 33.6781 | 739.773 | 36.5195
4.3464 | 2.5468 | 6.9751 | 3.8723 | 9.9478 | 4.7107 | 15.277 | 6.7656 | 22.9506 | 4.2795 | 32.2767 | 4.8981 | 44.095 | 6.4485 | 63.1395 | 4.2795 | 71.4749 | 6.0125 | 97.6457 | 3.713 | 140.098 | 3.3429 | 165.231 | 4.517 | 153.599 | 32.3575 | 208.584 | 10.653 | 244.043 | 46.5184 | 409.666 | 33.0773 | 549.684 | 39.1283 | 725.85 | 42.3872
4.0688 | 3.0187 | 6.6815 | 4.5852 | 9.6152 | 5.5503 | 14.8254 | 8.2305 | 21.6574 | 5.0776 | 30.4579 | 5.8641 | 42.1969 | 7.5674 | 59.7008 | 5.1184 | 68.1933 | 7.3437 | 90.6808 | 4.7486 | 133.132 | 3.9545 | 160.347 | 5.1389 | 151.161 | 41.0523 | 204.25 | 12.4764 | 241.132 | 55.7484 | 404.375 | 38.5458 | 542.584 | 46.0095 | 711.477 | 49.0504
3.8472 | 3.5143 | 6.4646 | 5.3433 | 9.3124 | 6.7318 | 14.4884 | 9.8143 | 20.3961 | 6.0973 | 28.7416 | 7.1195 | 40.7048 | 8.8538 | 56.846 | 6.0427 | 65.0623 | 9.16 | 85.828 | 5.8524 | 127.656 | 4.6732 | 155.453 | 6.0125 | 148.761 | 52.3969 | 199.605 | 14.9072 | 237.542 | 67.2118 | 397.559 | 44.7391 | 530.778 | 53.0825 | 697.389 | 56.6475
3.6559 | 4.1864 | 6.2736 | 6.2454 | 9.0191 | 8.3298 | 14.1165 | 12.303 | 19.382 | 7.1624 | 27.587 | 8.247 | 39.3048 | 10.6636 | 54.399 | 7.1195 | 62.6364 | 11.2779 | 82.3803 | 7.0982 | 122.651 | 5.5669 | 150.859 | 7.077 | 147.428 | 63.361 | 195.653 | 18.3173 | 234.474 | 80.5477 | 389.297 | 52.7122 | 520.268 | 62.1685 | 681.532 | 65.8809
3.4603 | 5.2114 | 6.1126 | 7.3805 | 8.7965 | 10.0829 | 13.8647 | 14.9969 | 18.5663 | 8.38 | 26.7717 | 9.5053 | 38.2577 | 12.6271 | 52.7385 | 8.2717 | 60.7852 | 13.6924 | 79.7858 | 8.5151 | 118.432 | 6.6848 | 146.84 | 8.2058 | 145.961 | 79.2692 | 192.355 | 21.9298 | 231.677 | 95.3782 | 379.306 | 62.7933 | 507.93 | 73.9101 | 664.705 | 76.0088
3.3446 | 6.2641 | 5.9557 | 8.916 | 8.5964 | 12.464 | 13.5766 | 19.0457 | 17.9277 | 9.9726 | 25.9286 | 11.2216 | 37.3132 | 14.8923 | 51.1799 | 9.6682 | 59.6412 | 16.4421 | 77.5053 | 10.4734 | 114.817 | 7.9553 | 142.5 | 9.7167 | 145.088 | 96.9165 | 189.871 | 25.8897 | 228.456 | 118.137 | 370.681 | 73.0284 | 492.425 | 89.6443 | 647.645 | 87.4309
3.249 | 7.5071 | 5.7855 | 11.3117 | 8.4262 | 15.2846 | 13.4146 | 23.4025 | 17.3978 | 12.1927 | 25.339 | 12.9986 | 36.6109 | 17.4239 | 49.9162 | 11.3004 | 58.7532 | 19.6651 | 75.6673 | 12.8051 | 111.982 | 9.317 | 138.427 | 11.6213 | 144.076 | 119.803 | 187.418 | 31.0887 | 225.505 | 144.005 | 361.529 | 84.0868 | 476.441 | 109.382 | 632.287 | 100.368
3.1751 | 8.8804 | 5.6766 | 13.6924 | 8.2759 | 19.1221 | 13.2679 | 29.074 | 17.0875 | 14.039 | 24.7629 | 15.2693 | 35.9578 | 20.3045 | 48.7813 | 13.3543 | 57.9944 | 23.1697 | 74.0208 | 15.7816 | 109.546 | 10.7493 | 135.279 | 13.7061 | 143.214 | 148.985 | 185.368 | 38.1241 | 223.261 | 173.27 | 354.371 | 97.3049 | 462.36 | 128.747 | 613.6 | 118.611
3.0998 | 10.8573 | 5.5753 | 17.1645 | 8.169 | 23.2858 | 13.1753 | 35.7248 | 16.8162 | 16.3764 | 24.2725 | 17.9546 | 35.3517 | 23.947 | 47.7198 | 16.1165 | 57.3026 | 29.1906 | 72.7003 | 19.4889 | 107.377 | 12.464 | 131.413 | 17.1473 | 142.643 | 186.205 | 183.523 | 45.6429 | 220.819 | 217.207 | 347.006 | 113.618 | 446.011 | 153.523 | 596.657 | 135.483
3.0476 | 12.9856 | 5.5033 | 20.8185 | 8.0797 | 29.016 | 13.0834 | 45.2792 | 16.6157 | 19.0267 | 23.8157 | 21.2604 | 34.7906 | 28.4983 | 46.8217 | 19.1795 | 56.7324 | 36.0118 | 71.5464 | 23.7325 | 105.356 | 14.6266 | 127.912 | 21.755 | 142.358 | 229.947 | 182.061 | 55.5258 | 219.498 | 255.66 | 337.425 | 138.082 | 430.67 | 181.789 | 581.344 | 154.911
2.9962 | 16.2297 | 5.4486 | 25.377 | 8.0073 | 35.8322 | 13.0442 | 55.4149 | 16.4503 | 22.3504 | 23.4612 | 25.1497 | 34.3069 | 34.3584 | 45.9405 | 23.3324 | 56.2804 | 44.8286 | 70.4812 | 29.3956 | 103.373 | 17.1131 | 125.505 | 26.0977 | 142.215 | 266.894 | 180.069 | 66.7429 | 218.403 | 301.826 | 329.753 | 161.071 | 418.36 | 208.065 | 562.473 | 176.77
2.9605 | 19.5084 | 5.3943 | 30.9956 | 7.9514 | 44.8735 | 13.0312 | 69.328 | 16.2541 | 26.1761 | 23.1813 | 29.6317 | 33.8977 | 40.4816 | 45.2565 | 29.1322 | 55.9437 | 55.0834 | 69.6405 | 35.868 | 101.63 | 20.264 | 123.266 | 31.7803 | 141.931 | 305.165 | 178.813 | 82.5042 |  |  | 321.611 | 188.83 | 404.375 | 239.332 | 542.042 | 205.172
2.9281 | 23.3324 | 5.346 | 38.5073 | 7.9276 | 55.1385 | 12.9792 | 86.6476 | 16.1407 | 31.0577 | 22.9506 | 35.334 | 33.6276 | 47.8393 | 44.7614 | 35.4756 | 55.7761 | 69.1203 | 68.9475 | 44.8735 | 100.017 | 24.043 | 121.188 | 39.4426 |  |  | 177.922 | 97.6949 |  |  | 312.418 | 219.39 | 392.424 | 279.178 | 520.268 | 237.9
2.8932 | 28.6412 | 5.2981 | 47.6483 | 7.9197 | 68.4326 | 12.9403 | 107.002 | 16.0602 | 37.22 | 22.7678 | 42.7277 | 33.3596 | 57.6764 | 44.316 | 44.2939 | 55.6091 | 84.6774 | 68.3298 | 55.4149 | 98.5285 | 29.1614 | 119.503 | 47.2687 |  |  | 176.327 | 122.345 |  |  | 305.62 | 252.864 | 384.654 | 321.453 | 500.868 | 272.558
2.8701 | 34.2212 | 5.2611 | 59.5519 | 7.9038 | 84.7622 | 12.9273 | 130.171 | 15.9961 | 45.0984 | 22.6316 | 51.8756 | 33.1601 | 70.0948 | 44.1391 | 53.5089 | 55.4979 | 105.725 | 67.921 | 68.2958 | 96.8677 | 35.6178 | 117.489 | 59.4924 |  |  | 175.624 | 145.307 |  |  | 298.671 | 292.613 | 378.17 | 371.241 | 482.192 | 306.694
2.8501 | 41.4234 | 5.2401 | 73.9101 | 7.8802 | 105.514 | 12.9273 | 161.555 | 15.9641 | 55.0283 | 22.4962 | 62.1685 | 33.0277 | 85.1019 | 43.9629 | 70.2351 | 55.4425 | 130.301 | 67.4473 | 84.5083 | 95.4255 | 43.8971 | 116.32 | 69.5363 |  |  | 174.922 | 172.751 |  |  | 292.757 | 338.95 | 373.659 | 424.899 | 471.7 | 338.611
2.8245 | 50.7468 | 5.214 | 97.8905 | 7.8644 | 131.479 | 12.9144 | 205.583 | 16.0121 | 66.3437 | 22.384 | 72.9554 | 32.9617 | 102.909 | 43.8751 | 86.6476 | 55.2211 | 160.91 | 67.1109 | 104.569 | 94.2872 | 53.0295 | 115.162 | 82.6694 |  |  | 174.398 | 213.759 |  |  | 287.822 | 391.448 | 371.424 | 498.126 | 460.054 | 390.275
2.8077 | 59.7308 | 5.1984 | 121.613 | 7.833 | 164.654 | 12.9273 | 250.348 | 16.0281 | 82.0927 | 22.2946 | 90.4547 | 32.9617 | 122.468 | 43.9629 | 109.93 | 55.166 | 200.908 | 66.7094 | 130.041 | 93.0694 | 63.9978 | 114.016 | 98.4796 |  |  | 174.224 | 252.611 |  |  | 283.537 | 443.125 | 371.052 | 601.155 | 454.566 | 433.917
2.7797 | 73.4679 | 5.188 | 150.483 | 7.8018 | 199.906 | 12.9144 | 303.642 | 16.0281 | 97.1105 | 22.2056 | 109.054 | 32.9287 | 149.134 | 43.9629 | 135.754 | 55.0557 | 248.105 | 66.3767 | 164.49 | 91.8674 | 80.4672 | 112.769 | 121.249 |  |  | 174.05 | 303.339 |  |  | 280.435 | 499.123 |  |  | 450.493 | 478.116
2.7466 | 91.2725 | 5.1932 | 188.83 | 7.7862 | 249.099 |  |  | 16.0442 | 121.735 | 22.1391 | 129.781 | 32.8958 | 189.208 | 43.919 | 164.984 | 54.9457 | 305.165 | 66.0456 | 201.109 | 91.0443 | 98.5782 | 111.759 | 148.094 | [6 empty] | 278.758 | 546.674 |  |  | 446.904 | 542.318
2.7165 | 112.826 | 5.1828 | 230.177 | 7.7396 | 302.128 |  |  | 16.0281 | 149.882 | 22.0728 | 155.221 | 32.8301 | 230.869 | 43.919 | 214.616 |  |  | 65.782 | 245.882 | 90.1384 | 121.735 | 110.868 | 176.947 | [6 empty] | 277.367 | 605.378 |  |  | 444.675 | 599.954
2.6895 | 141.012 | 5.1673 | 267.161 |  |  |  |  | 16.0602 | 184.906 | 22.0949 | 184.721 | 32.8301 | 266.36 | 43.919 | 266.094 |  |  | 65.5194 | 304.555 | 89.4201 | 149.134 | 110.095 | 215.907
2.6574 | 172.923 | 5.157 | 301.223 |  |  |  |  | 16.0602 | 228.572 | 22.0287 | 222.483 | 32.863 | 302.733 | 43.919 | 307.001 |  |  |  |  | 88.8852 | 186.019 | 109.655 | 259.524
2.631 | 216.123 | [6 empty] | 16.0602 | 265.828 | 22.0067 | 265.563 | [8 empty] | 88.3535 | 229.947 | 108.999 | 305.47
2.6152 | 247.857 | [6 empty] | 16.0924 | 302.43 | 21.9627 | 301.524 | [8 empty] | 88.0888 | 267.161
2.5944 | 301.826 | [18 empty] | 88.0008 | 303.339