## 153_165
S&C Power Fuses - Type SMD-50 (69 kV) | [9 empty] | S&C Power Fuses - Type SMD-50 (69 kV) | [9 empty] | S&C Power Fuses - Type SMD-50 (69 kV)
Standard Speed (TCC 153-1-6-5) | [9 empty] | Standard Speed (TCC 153-1-6-5) | [9 empty] | Standard Speed (TCC 153-1-6-5)
Total Clearing Time-Current Characteristic Curves Dated January 25, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 25, 1988 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated January 25, 1988
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
5E |  | 7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
4297.42 | 0.025289 | 4297.42 | 0.02539 | 4297.42 | 0.025491 | 4297.42 | 0.025592 | 4297.42 | 0.025694 | 4297.42 | 0.026002 | 4297.42 | 0.026393 | 4297.42 | 0.026709 | 4297.42 | 0.027599 | 4297.42 | 0.028689 | 4297.42 | 0.031686 | 4297.42 | 0.035591 | 4297.42 | 0.041309
1793.14 | 0.037403 | 1925.09 | 0.036595 | 3417.82 | 0.028491 | 3582.3 | 0.028014 | 3687.71 | 0.027709 | 3998.86 | 0.027003 | 2889.24 | 0.033003 | 3037.38 | 0.032515 | 3493.85 | 0.031404 | 3947.21 | 0.030391 | 3445.27 | 0.038116 | 4178.75 | 0.036486 | 4166.23 | 0.042686
299.058 | 0.07587 | 429.944 | 0.070004 | 1987.69 | 0.036413 | 2151.1 | 0.035591 | 2256.88 | 0.035204 | 2567.64 | 0.034001 | 1457.84 | 0.050288 | 1607.96 | 0.048812 | 2064.68 | 0.045083 | 2516.8 | 0.042306 | 3397.37 | 0.038611 | 3896.23 | 0.039113 | 3888.44 | 0.045988
294.311 | 0.076475 | 420.168 | 0.070773 | 558.173 | 0.065692 | 721.752 | 0.061402 | 826.078 | 0.059186 | 1137.63 | 0.054124 | 1424.69 | 0.050993 | 1579.27 | 0.049495 | 2033.94 | 0.045578 | 2486.77 | 0.042813 | 3277.24 | 0.0397 | 3582.3 | 0.042517 | 3585.88 | 0.050488
284.472 | 0.077778 | 403.289 | 0.072409 | 544.936 | 0.06648 | 711.718 | 0.062015 | 813.778 | 0.059777 | 1110.65 | 0.054991 | 1344.41 | 0.053218 | 1535.66 | 0.050488 | 1977.78 | 0.046585 | 2427.8 | 0.043586 | 3161.35 | 0.041105 | 3326.77 | 0.045714 | 3336.76 | 0.054882
274.962 | 0.079102 | 381.324 | 0.074599 | 526.718 | 0.067814 | 685.179 | 0.063322 | 787.361 | 0.060976 | 1075.67 | 0.056206 | 1266.11 | 0.055706 | 1476.92 | 0.051912 | 1896.43 | 0.04809 | 2351.34 | 0.044682 | 3037.38 | 0.042517 | 3064.84 | 0.04989 | 3016.2 | 0.0622
263.126 | 0.08093 | 360.196 | 0.077085 | 508.601 | 0.069175 | 664.927 | 0.064592 | 755.73 | 0.062696 | 1041.79 | 0.057391 | 1158.29 | 0.059599 | 1404.89 | 0.053909 | 1812.98 | 0.049989 | 2265.92 | 0.046217 | 2924.12 | 0.044108 | 2795.45 | 0.05521 | 2759.34 | 0.069727
247.554 | 0.083627 | 336.179 | 0.08029 | 491.107 | 0.070703 | 641.415 | 0.066019 | 719.59 | 0.064785 | 997.945 | 0.059186 | 1077.82 | 0.063322 | 1316.47 | 0.056711 | 1714.24 | 0.052275 | 2181.43 | 0.047709 | 2710.11 | 0.047379 | 2601.24 | 0.059777 | 2469.43 | 0.080609
235.244 | 0.085986 | 299.058 | 0.086586 | 452.442 | 0.07423 | 612.576 | 0.067882 | 674.302 | 0.06768 | 944.538 | 0.061585 | 987.027 | 0.068017 | 1232.38 | 0.059896 | 1598.34 | 0.055595 | 2081.27 | 0.049692 | 2524.36 | 0.05079 | 2442.41 | 0.064592 | 2272.73 | 0.090634
219.34 | 0.089471 | 268.441 | 0.093283 | 418.072 | 0.078165 | 580.373 | 0.070423 | 616.263 | 0.072122 | 894.883 | 0.064081 | 912.049 | 0.072914 | 1145.62 | 0.0637 | 1427.55 | 0.061402 | 1958.1 | 0.052483 | 2337.27 | 0.054882 | 2290.99 | 0.069796 | 2046.18 | 0.10509
205.125 | 0.093098 | 237.371 | 0.10251 | 385.928 | 0.082472 | 549.313 | 0.073132 | 572.877 | 0.076172 | 841.924 | 0.067077 | 845.299 | 0.07832 | 1058.59 | 0.068287 | 1303.37 | 0.067011 | 1853.31 | 0.055101 | 2106.39 | 0.06128 | 2136.09 | 0.076096 | 1879.44 | 0.1191
190.302 | 0.097838 | 212.219 | 0.11232 | 351.302 | 0.088411 | 507.078 | 0.077315 | 535.75 | 0.08029 | 784.217 | 0.071126 | 779.526 | 0.084798 | 988.015 | 0.07277 | 1198.35 | 0.07277 | 1733.2 | 0.058776 | 1927.02 | 0.067814 | 1963.98 | 0.084882 | 1719.39 | 0.13647
176.375 | 0.10303 | 187.282 | 0.12567 | 317.869 | 0.095533 | 471.378 | 0.081738 | 492.583 | 0.085986 | 728.278 | 0.075719 | 708.168 | 0.093654 | 904.781 | 0.079338 | 1110.65 | 0.078867 | 1645.37 | 0.06183 | 1729.73 | 0.076932 | 1794.94 | 0.095628 | 1577.69 | 0.15636
160.711 | 0.11033 | 170.138 | 0.13824 | 289.06 | 0.10354 | 439.948 | 0.086328 | 447.044 | 0.093561 | 674.302 | 0.081011 | 655.683 | 0.1017 | 830.219 | 0.086672 | 1019.12 | 0.086672 | 1532.59 | 0.066414 | 1558.87 | 0.087537 | 1670.24 | 0.10583 | 1424.69 | 0.18439
147.467 | 0.11804 | 151.806 | 0.15636 | 263.916 | 0.11244 | 398.478 | 0.093561 | 398.877 | 0.10426 | 634.397 | 0.085815 | 605.875 | 0.11132 | 753.466 | 0.096105 | 932.337 | 0.096009 | 1460.76 | 0.069865 | 1427.55 | 0.09813 | 1565.12 | 0.11607 | 1300.77 | 0.21466
130.398 | 0.13154 | 139.296 | 0.17235 | 240.718 | 0.12271 | 365.639 | 0.1012 | 353.77 | 0.11758 | 595.661 | 0.090904 | 540.593 | 0.12768 | 686.55 | 0.10709 | 856.36 | 0.10635 | 1390.91 | 0.073789 | 1308.59 | 0.11066 | 1424.69 | 0.13325 | 1198.35 | 0.24767
115.884 | 0.14717 | 123.42 | 0.20044 | 219.779 | 0.13485 | 330.512 | 0.11155 | 315.337 | 0.13365 | 551.515 | 0.098033 | 494.063 | 0.14356 | 641.415 | 0.11607 | 778.747 | 0.11982 | 1321.75 | 0.078087 | 1195.96 | 0.12554 | 1315.15 | 0.15042 | 1128.56 | 0.2749
103.294 | 0.16597 | 108.591 | 0.23731 | 201.465 | 0.1482 | 296.082 | 0.1248 | 283.053 | 0.15177 | 497.036 | 0.10935 | 453.801 | 0.16013 | 599.846 | 0.12604 | 712.43 | 0.13458 | 1239.8 | 0.08396 | 1093.02 | 0.14356 | 1211.61 | 0.16997 | 1064.96 | 0.30603
92.627 | 0.18735 | 97.8645 | 0.27463 | 185.975 | 0.1627 | 268.173 | 0.13934 | 251.295 | 0.17598 | 460.199 | 0.1191 | 421.009 | 0.17792 | 547.667 | 0.14186 | 642.056 | 0.15543 | 1180.51 | 0.088939 | 952.125 | 0.17633 | 1097.4 | 0.19866 | 1004.95 | 0.34103
83.6445 | 0.21191 | 88.1093 | 0.32129 | 171.848 | 0.17863 | 245.581 | 0.15436 | 230.356 | 0.19767 | 416.82 | 0.13418 | 390.587 | 0.19806 | 512.687 | 0.15497 | 583.282 | 0.17863 | 1117.33 | 0.09506 | 867.566 | 0.20446 | 977.206 | 0.2404 | 952.125 | 0.37889
72.2093 | 0.25745 | 78.9309 | 0.38078 | 156.743 | 0.20144 | 226.02 | 0.17065 | 211.372 | 0.22358 | 384.387 | 0.1482 | 354.478 | 0.2283 | 473.268 | 0.17338 | 533.611 | 0.20406 | 1049.11 | 0.10323 | 791.307 | 0.23779 | 885.978 | 0.28378 | 880.678 | 0.4389
61.9645 | 0.32066 | 70.0751 | 0.46171 | 145.707 | 0.22248 | 206.979 | 0.19149 | 195.511 | 0.25014 | 352.71 | 0.16547 | 333.5 | 0.25089 | 436.879 | 0.19475 | 485.249 | 0.2359 | 990.983 | 0.11099 | 729.006 | 0.27272 | 795.274 | 0.34103 | 831.881 | 0.49006
55.2327 | 0.38154 | 62.9639 | 0.55155 | 134.639 | 0.24841 | 188.597 | 0.21788 | 173.228 | 0.30001 | 323.967 | 0.18587 | 310.642 | 0.28014 | 404.5 | 0.2181 | 442.154 | 0.27354 | 902.071 | 0.12567 | 680.399 | 0.30603 | 727.55 | 0.397 | 784.217 | 0.55265
50.2269 | 0.44284 | 55.5096 | 0.68559 | 123.915 | 0.2793 | 168.108 | 0.25694 | 153.332 | 0.36558 | 297.269 | 0.2096 | 286.184 | 0.31843 | 374.521 | 0.24571 | 389.807 | 0.33732 | 840.242 | 0.13838 | 641.415 | 0.33934 | 685.864 | 0.44152 | 740.024 | 0.62138
46.2724 | 0.50539 | 50.1265 | 0.82227 | 115.537 | 0.31032 | 150.145 | 0.30482 | 140.274 | 0.42264 | 273.591 | 0.23637 | 261.813 | 0.3685 | 350.951 | 0.27272 | 362.726 | 0.38267 | 788.148 | 0.15162 | 596.854 | 0.38496 | 649.808 | 0.48281 | 701.823 | 0.69244
43.2736 | 0.56655 | 45.2203 | 0.98521 | 106.76 | 0.3496 | 138.739 | 0.34409 | 127.179 | 0.50089 | 245.827 | 0.2782 | 241.441 | 0.42222 | 323.643 | 0.31032 | 337.189 | 0.43284 | 725.37 | 0.1715 | 561.532 | 0.42644 | 616.263 | 0.53271 | 669.598 | 0.76475
40.835 | 0.62385 | 41.9946 | 1.1322 | 98.7493 | 0.39582 | 130.138 | 0.3804 | 119.892 | 0.55155 | 217.81 | 0.33531 | 212.432 | 0.52379 | 302.971 | 0.34649 | 320.423 | 0.4752 | 666.925 | 0.19475 | 530.949 | 0.47004 | 587.38 | 0.5831 | 626.203 | 0.88235
38.5339 | 0.68764 | 39.4699 | 1.2705 | 90.6114 | 0.45488 | 123.173 | 0.41391 | 112.91 | 0.60674 | 197.871 | 0.39308 | 192.215 | 0.62509 | 274.138 | 0.41023 | 305.405 | 0.51758 | 577.478 | 0.24401 | 509.11 | 0.50841 | 551.515 | 0.65758 | 597.451 | 0.97838
35.8568 | 0.78087 | 37.3202 | 1.42 | 83.4774 | 0.52067 | 116.932 | 0.45128 | 106.653 | 0.67077 | 175.671 | 0.4809 | 175.495 | 0.73277 | 253.567 | 0.47004 | 294.017 | 0.55651 | 504.044 | 0.30542 | 489.636 | 0.54828 | 520.956 | 0.73569 | 561.532 | 1.1277
33.466 | 0.88148 | 35.9645 | 1.5283 | 78.5372 | 0.57906 | 111.006 | 0.49397 | 98.3551 | 0.77469 | 157.056 | 0.58543 | 161.516 | 0.84967 | 231.048 | 0.55265 | 278.004 | 0.61585 | 456.989 | 0.36053 | 470.436 | 0.58951 | 490.126 | 0.83295 | 530.419 | 1.2857
31.6433 | 0.97644 | 34.4852 | 1.6646 | 74.7815 | 0.63385 | 104.646 | 0.54448 | 92.7197 | 0.865 | 143.251 | 0.68764 | 150.747 | 0.96391 | 211.372 | 0.64528 | 267.102 | 0.6648 | 409.384 | 0.43716 | 440.388 | 0.66878 | 461.121 | 0.94401 | 504.044 | 1.4528
29.6518 | 1.0979 | 33.2325 | 1.7969 | 69.7256 | 0.71551 | 99.5425 | 0.59303 | 85.9338 | 0.99406 | 129.101 | 0.83295 | 140.836 | 1.1022 | 188.597 | 0.79496 | 257.657 | 0.71338 | 381.706 | 0.49594 | 417.655 | 0.74525 | 439.069 | 1.0457 | 485.734 | 1.5855
27.2355 | 1.2806 | 31.9614 | 1.9591 | 65.7963 | 0.79575 | 93.7453 | 0.66019 | 81.9882 | 1.0903 | 120.132 | 0.95249 | 131.314 | 1.2604 | 173.401 | 0.93747 | 246.812 | 0.77546 | 361.278 | 0.54556 | 389.417 | 0.86071 | 423.967 | 1.1311 | 472.322 | 1.7048
25.3941 | 1.4615 | 30.862 | 2.1128 | 62.3998 | 0.8745 | 86.2783 | 0.76475 | 77.5228 | 1.2162 | 112.797 | 1.0752 | 123.05 | 1.4342 | 163.794 | 1.0488 | 234.54 | 0.85815 | 343.657 | 0.59717 | 367.472 | 0.9716 | 407.75 | 1.2406 | 456.076 | 1.8753
23.8913 | 1.6367 | 29.7112 | 2.2966 | 58.7657 | 0.98325 | 79.8839 | 0.87973 | 73.3006 | 1.3593 | 106.228 | 1.2041 | 116.815 | 1.5982 | 153.792 | 1.1934 | 221.323 | 0.96775 | 330.182 | 0.64528 | 347.459 | 1.0924 | 394.908 | 1.3272 | 439.509 | 2.0671
22.6806 | 1.8059 | 28.7754 | 2.4792 | 56.1236 | 1.0784 | 74.5575 | 1.001 | 70.2154 | 1.4893 | 101.553 | 1.322 | 109.902 | 1.8312 | 145.271 | 1.3458 | 208.225 | 1.1012 | 314.078 | 0.71055 | 327.223 | 1.2418 | 382.088 | 1.4299 | 421.009 | 2.3241
21.6176 | 1.9866 | 27.6747 | 2.7056 | 53.7613 | 1.1769 | 69.8652 | 1.1344 | 66.724 | 1.6613 | 96.5039 | 1.4673 | 104.646 | 2.0345 | 136.947 | 1.5329 | 198.466 | 1.2198 | 297.864 | 0.78554 | 310.021 | 1.4032 | 367.105 | 1.5761 | 406.935 | 2.5567
20.7699 | 2.1573 | 26.5364 | 2.9941 | 51.6532 | 1.2743 | 65.5337 | 1.2857 | 63.3429 | 1.866 | 92.9054 | 1.5871 | 98.947 | 2.3172 | 130.66 | 1.7014 | 190.302 | 1.3352 | 283.904 | 0.86242 | 296.378 | 1.5512 | 354.478 | 1.7235 | 393.725 | 2.8181
19.8758 | 2.3684 | 25.5214 | 3.2807 | 49.6774 | 1.3824 | 62.1506 | 1.4299 | 60.4345 | 2.0732 | 89.0839 | 1.7424 | 93.2777 | 2.655 | 124.411 | 1.9054 | 183.023 | 1.4673 | 268.71 | 0.96296 | 282.205 | 1.7546 | 341.943 | 1.8828 | 379.802 | 3.1279
19.1347 | 2.5771 | 24.6189 | 3.591 | 47.5864 | 1.5132 | 58.8245 | 1.6029 | 57.7173 | 2.3172 | 85.5052 | 1.9054 | 89.7995 | 2.9149 | 118.699 | 2.1423 | 176.198 | 1.5998 | 256.629 | 1.0572 | 270.598 | 1.9436 | 330.512 | 2.0548 | 368.576 | 3.4341
18.366 | 2.8321 | 23.8435 | 3.9152 | 45.0848 | 1.6846 | 55.7878 | 1.7898 | 55.1775 | 2.5925 | 81.2536 | 2.1423 | 85.0787 | 3.3365 | 113.023 | 2.428 | 170.82 | 1.7321 | 244.601 | 1.1664 | 263.126 | 2.0939 | 318.187 | 2.2784 | 359.476 | 3.7552
17.7342 | 3.0816 | 23.162 | 4.2222 | 43.2736 | 1.8513 | 53.12 | 1.9866 | 52.7494 | 2.9091 | 77.4453 | 2.4064 | 80.6867 | 3.8535 | 108.049 | 2.7164 | 165.109 | 1.8828 | 232.671 | 1.2986 | 254.584 | 2.2875 | 304.795 | 2.5643 | 349.899 | 4.1391
17.1585 | 3.3365 | 22.0764 | 4.8281 | 41.2042 | 2.0528 | 50.4282 | 2.2203 | 50.8333 | 3.2321 | 73.8156 | 2.6922 | 76.2923 | 4.5038 | 103.605 | 3.0512 | 160.39 | 2.0184 | 223.547 | 1.4285 | 246.812 | 2.5114 | 295.786 | 2.8181 | 343.314 | 4.4726
16.5352 | 3.6595 | 21.3811 | 5.3165 | 39.3123 | 2.2807 | 47.9207 | 2.4915 | 48.645 | 3.6704 | 70.992 | 2.9764 | 73.5945 | 5.0288 | 99.7418 | 3.4069 | 155.183 | 2.2093 | 212.644 | 1.6014 | 239.757 | 2.7299 | 284.188 | 3.178 | 336.179 | 4.8957
15.9027 | 4.0457 | 20.7699 | 5.8195 | 37.7708 | 2.4965 | 45.3108 | 2.8378 | 46.9718 | 4.1105 | 68.2765 | 3.297 | 70.992 | 5.6262 | 96.1186 | 3.8116 | 150.295 | 2.4064 | 204.51 | 1.7563 | 231.51 | 3.015 | 277.448 | 3.4787 | 329.192 | 5.3696
15.3251 | 4.4771 | 20.2368 | 6.3133 | 35.8927 | 2.8041 | 43.534 | 3.1529 | 45.3561 | 4.6171 | 65.1416 | 3.7552 | 68.4817 | 6.3511 | 93.1845 | 4.2432 | 144.691 | 2.6683 | 196.687 | 1.9321 | 224.443 | 3.3134 | 268.441 | 3.8958 | 322.029 | 5.9599
14.9019 | 4.8473 | 19.6977 | 6.9244 | 34.6235 | 3.0482 | 41.7852 | 3.4856 | 43.7523 | 5.2171 | 62.901 | 4.1309 | 66.3248 | 7.148 | 90.5208 | 4.7332 | 139.574 | 2.9793 | 189.732 | 2.1233 | 216.29 | 3.6813 | 263.916 | 4.2517 | 316.6 | 6.5108
14.447 | 5.3377 | 19.2691 | 7.4896 | 33.4995 | 3.3003 | 40.1065 | 3.8765 | 42.1208 | 5.9421 | 60.9199 | 4.5488 | 64.4934 | 8.013 | 88.1093 | 5.3059 | 134.236 | 3.3531 | 181.565 | 2.3897 | 209.478 | 4.0901 | 257.657 | 4.705 | 310.952 | 7.1693
14.034 | 5.8776 | 18.8121 | 8.2308 | 32.5419 | 3.5379 | 38.4953 | 4.3155 | 40.7534 | 6.7277 | 58.7657 | 5.0891 | 62.8381 | 8.9649 | 85.4197 | 6.0553 | 128.714 | 3.823 | 173.401 | 2.711 | 204.92 | 4.4416 | 252.808 | 5.1707 | 304.795 | 7.9259
13.6465 | 6.5367 | 18.3843 | 9.0274 | 31.454 | 3.8496 | 37.0228 | 4.8138 | 39.5094 | 7.6021 | 57.2002 | 5.5817 | 60.9199 | 10.2922 | 83.3106 | 6.8627 | 125.16 | 4.239 | 166.103 | 3.0542 | 199.86 | 4.8618 | 248.298 | 5.7619 | 297.864 | 9.1176
13.4031 | 7.0493 | 18.0744 | 9.8325 | 30.3721 | 4.2306 | 35.8927 | 5.2483 | 38.4953 | 8.522 | 55.6207 | 6.183 | 59.5347 | 11.7342 | 80.7675 | 8.1901 | 122.314 | 4.6308 | 160.069 | 3.4306 | 195.511 | 5.3112 | 243.137 | 6.4978 | 292.258 | 10.2209
13.0721 | 7.8087 | 17.752 | 10.7307 | 29.3861 | 4.6308 | 35.0415 | 5.6039 | 37.5073 | 9.5914 | 54.139 | 6.7881 | 58.6483 | 13.2198 | 78.6158 | 9.716 | 119.652 | 5.1604 | 154.718 | 3.8267 | 191.065 | 5.9068 | 237.134 | 7.4599 | 286.757 | 11.6182
12.7239 | 8.7017 | 17.4877 | 11.6645 | 28.4322 | 5.1043 | 34.1763 | 6.0433 | 36.6544 | 10.6563 | 52.8022 | 7.4748 | 57.5444 | 15.3134 | 76.5215 | 11.7576 | 117.166 | 5.7964 | 150.446 | 4.1722 | 187.282 | 6.4914 | 232.671 | 8.421 | 281.36 | 13.4182
12.447 | 9.6967 | 17.2791 | 12.8061 | 27.2627 | 5.7391 | 33.3991 | 6.5302 | 36.0366 | 11.8396 | 51.6016 | 8.2472 | 56.5178 | 18.1486 | 74.6321 | 14.2423 | 114.273 | 6.5954 | 147.467 | 4.4993 | 183.39 | 7.2337 | 228.292 | 9.5533 | 276.617 | 15.3591
12.1883 | 10.9134 | 17.0559 | 14.214 | 26.5364 | 6.2261 | 32.7378 | 7.0004 | 35.5 | 13.0891 | 50.681 | 9.0454 | 55.6207 | 22.1373 | 72.935 | 17.7916 | 112.571 | 7.3642 | 144.691 | 4.8377 | 179.938 | 8.0369 | 223.995 | 11.0553 | 272.226 | 17.4243
11.9589 | 12.6544 | 16.8693 | 15.7297 | 25.8037 | 6.7881 | 31.9614 | 7.6172 | 35.0064 | 15.042 | 49.8267 | 9.9603 | 54.9572 | 26.5768 | 71.993 | 20.0241 | 110.012 | 8.59 | 142.252 | 5.2431 | 176.375 | 9.0095 | 219.779 | 12.7934 | 267.905 | 20.0639
11.8281 | 13.9482 | 16.6847 | 17.6157 | 25.1665 | 7.335 | 31.3912 | 8.1901 | 34.4852 | 17.9514 | 49.1831 | 10.8702 | 54.5738 | 32.2573 | 71.3479 | 22.6039 | 107.941 | 9.8913 | 139.854 | 5.6937 | 173.922 | 10.0198 | 215.427 | 15.2073 | 262.337 | 24.2316
11.687 | 15.6207 | 16.5352 | 19.8064 | 24.6929 | 7.9024 | 30.7696 | 8.8411 | 34.1421 | 20.4462 | 48.2574 | 12.3809 | 54.5738 | 39.8186 | 70.4263 | 26.5504 | 105.803 | 11.4578 | 137.496 | 6.2509 | 170.649 | 11.2436 | 210.739 | 18.2027 | 258.69 | 27.7918
11.5939 | 17.5284 | 16.3871 | 22.2917 | 24.2281 | 8.4714 | 30.1904 | 9.7257 | 33.8024 | 24.3765 | 47.3018 | 14.3559 | 54.5738 | 49.1035 | 69.7953 | 30.5119 | 103.916 | 13.4449 | 135.043 | 6.9727 | 167.94 | 12.6042 | 206.359 | 22.8296 | 255.093 | 32.1293
11.513 | 19.8261 | 16.2565 | 25.2891 | 23.8435 | 9.1903 | 29.7409 | 10.426 | 33.6001 | 28.6325 | 46.5975 | 16.5965 | 54.5738 | 65.1077 | 69.17 | 35.3792 | 101.96 | 16.3186 | 132.502 | 7.7932 | 165.771 | 14.0456 | 202.678 | 28.5473 | 251.547 | 37.107
11.4556 | 22.1373 | 16.1431 | 28.6894 | 23.465 | 10.0099 | 29.2688 | 11.4578 | 33.533 | 33.7319 | 45.8578 | 19.7083 | 54.5738 | 85.5596 | 68.4817 | 43.4992 | 99.443 | 21.2538 | 130.529 | 8.65 | 163.466 | 15.5124 | 199.062 | 34.9253 | 248.049 | 42.8984
11.3756 | 25.5669 | 16.0465 | 32.0974 | 23.0695 | 10.9678 | 28.9776 | 12.3195 | 33.466 | 39.2687 | 45.4469 | 23.3804 | 54.5738 | 123.563 | 67.8681 | 54.2856 | 98.0604 | 25.5669 | 128.457 | 9.7064 | 161.355 | 17.4937 | 195.706 | 45.9418 | 245.09 | 48.4735
11.3529 | 30.0009 | 15.9346 | 37.2547 | 22.7943 | 11.8514 | 28.7179 | 13.3385 | 33.2991 | 47.1907 | 44.9947 | 27.4625 | 54.5738 | 169.969 | 67.3273 | 67.7467 | 96.9876 | 30.0606 | 126.544 | 10.8918 | 159.43 | 19.7475 | 192.6 | 59.2446 | 242.167 | 56.3179
11.3416 | 34.6144 | 15.8868 | 42.9411 | 22.5224 | 12.9855 | 28.347 | 15.2375 | 33.1661 | 57.1066 | 44.5916 | 32.8719 | 54.5738 | 228.069 | 66.8576 | 88.4108 | 95.7349 | 36.8133 | 124.91 | 12.1012 | 157.528 | 22.4027 | 189.732 | 75.644 | 239.039 | 64.5282
11.3416 | 40.7388 | 15.8551 | 49.4461 | 22.276 | 14.1015 | 28.2904 | 17.4763 | 33.0668 | 69.1748 | 44.3691 | 39.0353 | 54.5738 | 306.029 | 66.3248 | 117.226 | 94.972 | 43.0692 | 123.173 | 13.9899 | 155.805 | 26.0282 | 187.282 | 94.9657 | 235.951 | 76.7033
11.3416 | 49.5937 | 15.8551 | 57.6194 | 22.1206 | 15.4817 | 28.2904 | 20.2642 | 32.9677 | 84.7139 | 44.1478 | 49.3971 | 54.5193 | 429.411 | 66.1262 | 161.252 | 93.8391 | 52.7965 | 121.339 | 16.0453 | 154.1 | 29.236 | 184.678 | 124.301 | 233.37 | 88.851
11.3416 | 59.8955 | 15.8393 | 69.1061 | 21.9883 | 17.0307 | 28.2904 | 24.1595 | 32.9019 | 98.2278 | 44.0596 | 60.1937 | 54.5193 | 520.674 | 65.8622 | 210.437 | 92.9983 | 67.2105 | 119.892 | 18.7907 | 152.262 | 34.3746 | 182.657 | 159.341 | 230.817 | 101.602
11.3416 | 74.6735 | 15.8393 | 82.145 | 21.8786 | 18.7347 | 28.2904 | 28.8036 | 32.9019 | 120.054 | 44.0596 | 76.7033 | 54.5193 | 577.34 | 65.8622 | 270.563 | 91.9809 | 85.9857 | 118.343 | 21.9839 | 150.446 | 40.8604 | 181.202 | 207.119 | 228.063 | 122.22
11.3416 | 93.7472 | 15.8393 | 100.497 | 21.8786 | 21.0228 | 28.2904 | 35.0295 | 32.9019 | 146.877 | 44.0156 | 103.846 | 54.5193 | 600.146 | 65.8622 | 332.66 | 91.3392 | 104.987 | 117.166 | 25.415 | 148.502 | 53.5359 | 179.938 | 258.735 | 225.794 | 146.877
11.3416 | 118.749 | 15.8393 | 118.161 | 21.8786 | 23.6843 | 28.2904 | 45.4426 | 32.9019 | 184.393 | 43.9716 | 130.761 |  |  | 65.8622 | 414.738 | 90.7928 | 126.67 | 116.116 | 29.6454 | 147.319 | 64.1447 | 178.683 | 326.117 | 223.547 | 178.27
11.3416 | 149.082 | 15.8393 | 138.104 | 21.8786 | 27.8194 | 28.2904 | 58.951 | 32.9019 | 229.432 | 43.796 | 176.508 |  |  | 65.8622 | 491.523 | 90.34 | 155.124 | 114.846 | 35.8747 | 146.145 | 76.4751 | 177.436 | 415.15 | 221.323 | 209.187
11.3302 | 202.24 | 15.8393 | 163.024 | 21.8786 | 32.4179 | 28.2904 | 74.6735 | 32.9019 | 271.64 | 43.7523 | 238.732 |  |  | 65.8622 | 565.983 | 89.7995 | 201.638 | 113.93 | 42.8133 | 144.836 | 98.1303 | 176.375 | 498.902 | 219.999 | 251.638
11.3302 | 258.992 | 15.8393 | 201.838 | 21.8786 | 38.6111 | 28.2904 | 86.844 | 32.9019 | 367.037 | 43.6649 | 305.422 |  |  | 65.8622 | 600.146 | 89.3516 | 255.669 | 113.023 | 51.964 | 143.969 | 115.492 | 175.846 | 559.277 | 218.683 | 299.117
11.3302 | 319.702 | 15.8393 | 248.162 | 21.8786 | 45.8051 | 28.2904 | 108.163 | 32.9019 | 453.524 | 43.6212 | 375.52 |  |  |  |  | 88.7283 | 336.315 | 112.459 | 61.2188 | 142.822 | 141.155 | 175.144 | 600.146 | 217.592 | 361.968
11.3302 | 399.771 | 15.8393 | 305.725 | 21.8786 | 56.7673 | 28.2904 | 129.726 | 32.9019 | 529.541 | 43.4471 | 473.786 |  |  |  |  | 88.2857 | 422.64 | 111.563 | 74.9708 | 142.252 | 170.815 |  |  | 216.29 | 446.816
11.3302 | 489.088 | 15.8393 | 366.673 | 21.8786 | 68.4231 | 28.2904 | 164.651 | 32.9019 | 573.34 | 43.3602 | 550.458 |  |  |  |  | 87.8454 | 513.993 | 111.228 | 87.1032 | 141.826 | 216.372 |  |  | 215.427 | 553.749
11.3302 | 571.634 | 15.8393 | 436.29 | 21.8786 | 80.1302 | 28.2904 | 205.684 | 32.9019 | 600.146 | 43.2736 | 600.146 |  |  |  |  | 87.6699 | 578.488 | 110.674 | 106.035 | 141.684 | 278.747 |  |  | 214.567 | 600.146
11.3302 | 600.146 | 15.8393 | 503.882 | 21.8786 | 94.3076 | 28.2904 | 248.409 | [8 empty] | 87.4947 | 600.146 | 110.232 | 127.554 | 141.26 | 359.46
|  | 15.8234 | 573.91 | 21.8786 | 113.897 | 28.2904 | 301.803 | [10 empty] | 109.902 | 173.897 | 141.26 | 461.247
|  | 15.8234 | 600.146 | 21.8786 | 134.984 | 28.2904 | 377.765 | [10 empty] | 109.572 | 223.583 | 141.26 | 569.367
|  |  |  | 21.8786 | 156.052 | 28.2904 | 467.242 | [10 empty] | 109.353 | 282.651 | 141.118 | 600.146
|  |  |  | 21.8786 | 186.419 | 28.2904 | 552.65 | [10 empty] | 108.917 | 347.868
|  |  |  | 21.8786 | 222.917 | 28.2904 | 600.146 | [10 empty] | 108.482 | 424.744
|  |  |  | 21.8786 | 282.37 | [12 empty] | 108.157 | 488.117
|  |  |  | 21.8786 | 346.833 | [12 empty] | 107.833 | 568.802
|  |  |  | 21.8786 | 423.901 | [12 empty] | 107.725 | 600.146
|  |  |  | 21.8786 | 500.391
|  |  |  | 21.8786 | 564.86
|  |  |  | 21.8786 | 600.146