## 165_24
S&C Power Fuses - Type SMU-20 (25 and 34.5 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (25 and 34.5 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (25 and 34.5 kV) | [9 empty] | S&C Power Fuses - Type SMU-20 (25 and 34.5 kV)
"K" Speed (TCC 165-2-4) | [9 empty] | "K" Speed (TCC 165-2-4) | [9 empty] | "K" Speed (TCC 165-2-4) | [9 empty] | "K" Speed (TCC 165-2-4)
Total Clearing Time-Current Characteristic Curves Dated August 29, 1998 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1998 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1998 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated August 29, 1998
Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus. | [9 empty] | Tolerance: Curves are plotted to maximum test points. All variations are minus.
3K |  | 6K |  | 8K |  | 10K |  | 12K |  | 15K |  | 20K |  | 25K |  | 30K |  | 40K |  | 50K |  | 65K |  | 80K |  | 100K |  | 140K |  | 200K
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
15770.9 | 0.015968 | 15770.9 | 0.015968 | 15770.9 | 0.015968 | 15770.9 | 0.015968 | 15770.9 | 0.015968 | 15770.9 | 0.015968 | 15770.9 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016161 | 15786.7 | 0.016161 | 15770.9 | 0.016161 | 15770.9 | 0.016323 | 15770.9 | 0.016323 | 15770.9 | 0.016323 | 15770.9 | 0.024794 | 15770.9 | 0.033201
5281.3 | 0.019022 | 4084.39 | 0.019798 | 5033.79 | 0.019484 | 3987.53 | 0.020259 | 3025.79 | 0.021641 | 3456.21 | 0.021191 | 5669.91 | 0.019997 | 7638.28 | 0.018739 | 7973.89 | 0.019232 | 8552.06 | 0.019155 | 10904.4 | 0.017878 | 12631.2 | 0.017577 | 12809.3 | 0.017507 | 14399.1 | 0.017057 | 14941.9 | 0.0256 | 14912 | 0.034247
2335.38 | 0.021533 | 2413.73 | 0.022034 | 2157.98 | 0.023071 | 1868.57 | 0.023869 | 1862.97 | 0.024327 | 2094.2 | 0.024133 | 4702.87 | 0.020938 | 6185.28 | 0.019778 | 6925.24 | 0.020158 | 7338.78 | 0.020381 | 8883.3 | 0.019503 | 10926.3 | 0.018739 | 11270.3 | 0.018645 | 13015.9 | 0.018022 | 14029.6 | 0.026459 | 13903.9 | 0.035502
1933.19 | 0.022144 | 1815.16 | 0.023326 | 1548.32 | 0.024968 | 1373.24 | 0.025831 | 1667.24 | 0.025168 | 1791.71 | 0.025345 | 4047.8 | 0.021858 | 5270.75 | 0.020668 | 6247.45 | 0.02098 | 6412.01 | 0.021533 | 7479.55 | 0.021212 | 9642.42 | 0.019858 | 10157.1 | 0.019818 | 11883.7 | 0.019022 | 13068 | 0.027566 | 13068 | 0.036951
1632.6 | 0.022819 | 1525.27 | 0.024037 | 1267.66 | 0.026091 | 1227.74 | 0.026618 | 1511.61 | 0.025805 | 1568.58 | 0.026432 | 3579.32 | 0.022796 | 4600.54 | 0.021684 | 5436.7 | 0.0221 | 5518.87 | 0.023025 | 6476.45 | 0.02275 | 8768.56 | 0.020834 | 9366.81 | 0.020855 | 10882.6 | 0.020017 | 12221.2 | 0.028749 | 12257.9 | 0.038613
1256.3 | 0.023726 | 1262.6 | 0.024744 | 1128.82 | 0.026805 | 1109.79 | 0.027511 | 1363.66 | 0.026698 | 1347.39 | 0.027899 | 3193.68 | 0.023679 | 3967.65 | 0.022933 | 4769.17 | 0.023443 | 4821.92 | 0.024473 | 5669.91 | 0.024376 | 7745.97 | 0.022367 | 8509.41 | 0.0223 | 9995.88 | 0.021149 | 10992 | 0.030802 | 11497.9 | 0.04031
1055.67 | 0.024473 | 1066.27 | 0.0256 | 993.199 | 0.02776 | 944.76 | 0.029154 | 1271.47 | 0.027374 | 1192.64 | 0.029359 | 2702.49 | 0.025118 | 3408.16 | 0.02423 | 4162.74 | 0.024769 | 4125.44 | 0.026274 | 4880.14 | 0.026222 | 6747.51 | 0.02423 | 7745.97 | 0.023941 | 9135.54 | 0.022637 | 10066 | 0.032576 | 10839.2 | 0.042165
916.838 | 0.025018 | 885.304 | 0.026538 | 859.999 | 0.028893 | 821.335 | 0.030649 | 1164.36 | 0.028264 | 1055.67 | 0.031081 | 2316.77 | 0.026459 | 2841.05 | 0.026039 | 3533.09 | 0.026459 | 3554.35 | 0.028207 | 4096.66 | 0.028777 | 5948.7 | 0.026169 | 6932.17 | 0.025987 | 8399.5 | 0.024181 | 9208.92 | 0.034695 | 10187.6 | 0.044238
807.49 | 0.025651 | 742.432 | 0.027815 | 728.459 | 0.030465 | 717.613 | 0.032252 | 1045.16 | 0.029476 | 943.816 | 0.032707 | 1978.17 | 0.028236 | 2404.09 | 0.027955 | 3062.32 | 0.028207 | 3127.31 | 0.030162 | 3593.67 | 0.03105 | 5013.69 | 0.029388 | 6297.63 | 0.027955 | 7502.02 | 0.0263 | 8577.76 | 0.036693 | 9632.79 | 0.046506
730.647 | 0.026222 | 625.112 | 0.029067 | 638.378 | 0.031836 | 630.133 | 0.033974 | 917.755 | 0.031112 | 833.748 | 0.034938 | 1658.93 | 0.030496 | 1948.72 | 0.031019 | 2599.12 | 0.030465 | 2768.13 | 0.03222 | 3130.44 | 0.033636 | 4125.44 | 0.033468 | 5574.33 | 0.030926 | 6720.57 | 0.028835 | 8045.98 | 0.038807 | 8856.69 | 0.050582
648.026 | 0.026886 | 535.891 | 0.030404 | 564.495 | 0.033234 | 540.736 | 0.036437 | 816.422 | 0.03274 | 759.706 | 0.036988 | 1391.21 | 0.033102 | 1685.69 | 0.033468 | 2275.44 | 0.032285 | 2492.22 | 0.03411 | 2694.39 | 0.036877 | 3470.06 | 0.038038 | 4993.68 | 0.033737 | 6050.69 | 0.031582 | 7449.69 | 0.041662 | 8307.62 | 0.054195
585.187 | 0.027539 | 438.312 | 0.032479 | 495.68 | 0.034869 | 476.721 | 0.038923 | 727.731 | 0.034487 | 692.931 | 0.039314 | 1225.28 | 0.035114 | 1466.93 | 0.036183 | 2028.25 | 0.033974 | 2205.98 | 0.036693 | 2368.3 | 0.040269 | 2956.99 | 0.042802 | 4363.06 | 0.037622 | 5409.59 | 0.034869 | 6808.51 | 0.045177 | 7707.34 | 0.058885
514.364 | 0.028491 | 386.422 | 0.03394 | 422.813 | 0.03736 | 430.063 | 0.041413 | 634.559 | 0.03721 | 625.112 | 0.042504 | 1036.83 | 0.038652 | 1290.68 | 0.039197 | 1855.53 | 0.035396 | 1986.1 | 0.039157 | 2140.79 | 0.043232 | 2596.52 | 0.047875 | 3804.46 | 0.042165 | 4860.65 | 0.038652 | 6316.55 | 0.048842 | 7164.75 | 0.064366
455.288 | 0.029535 | 338.977 | 0.036111 | 375.002 | 0.03967 | 392.262 | 0.04393 | 555.535 | 0.040471 | 559.997 | 0.046136 | 902.285 | 0.041997 | 1105.36 | 0.043146 | 1714.59 | 0.036877 | 1786.35 | 0.042039 | 1944.83 | 0.04646 | 2323.73 | 0.053016 | 3347.36 | 0.047162 | 4420.15 | 0.042334 | 5877.74 | 0.052857 | 6700.44 | 0.070007
405.018 | 0.030741 | 286.842 | 0.039551 | 337.961 | 0.041997 | 355.644 | 0.047209 | 488.301 | 0.044018 | 501.664 | 0.050734 | 794.673 | 0.04586 | 983.316 | 0.046786 | 1562.32 | 0.038845 | 1640.78 | 0.044638 | 1786.35 | 0.050028 | 2028.25 | 0.060315 | 2989.7 | 0.052279 | 4011.53 | 0.046274 | 5366.48 | 0.058241 | 6266.22 | 0.076141
365.012 | 0.031899 | 245.41 | 0.043232 | 306.106 | 0.044549 | 322.122 | 0.051397 | 430.063 | 0.04855 | 447.167 | 0.05635 | 699.196 | 0.050481 | 880.008 | 0.05109 | 1389.82 | 0.041496 | 1531.38 | 0.047209 | 1650.66 | 0.053817 | 1795.3 | 0.068895 | 2635.76 | 0.05865 | 3669.93 | 0.050835 | 4909.5 | 0.064624 | 5848.43 | 0.083981
326.991 | 0.033135 | 208.707 | 0.047875 | 273.672 | 0.048211 | 286.842 | 0.057031 | 383.343 | 0.053817 | 411.139 | 0.061166 | 633.292 | 0.054959 | 782.06 | 0.056294 | 1271.47 | 0.043798 | 1398.18 | 0.051192 | 1529.85 | 0.057777 | 1563.88 | 0.079805 | 2330.71 | 0.066194 | 3287.65 | 0.056917 | 4477.98 | 0.072067 | 5507.84 | 0.091431
288.857 | 0.034625 | 183.448 | 0.052174 | 245.41 | 0.052383 | 257.22 | 0.063535 | 346.17 | 0.05924 | 373.505 | 0.068074 | 568.46 | 0.060983 | 712.608 | 0.061288 | 1171.37 | 0.046321 | 1272.74 | 0.056013 | 1388.43 | 0.064173 | 1333.99 | 0.096023 | 2119.48 | 0.072718 | 3004.69 | 0.063092 | 4191.98 | 0.077991 | 5140.62 | 0.10105
252.379 | 0.036656 | 164.833 | 0.056463 | 222.723 | 0.056689 | 231.813 | 0.071994 | 308.565 | 0.067329 | 339.655 | 0.075989 | 521.616 | 0.066993 | 649.973 | 0.06706 | 1064.14 | 0.049928 | 1145.88 | 0.062339 | 1267.66 | 0.070781 | 1148.17 | 0.116 | 1861.11 | 0.083562 | 2784.79 | 0.069033 | 3793.06 | 0.089174 | 4688.78 | 0.11693
221.391 | 0.038962 | 148.998 | 0.06135 | 200.523 | 0.062777 | 204.779 | 0.084233 | 280.881 | 0.074933 | 313.228 | 0.084233 | 480.07 | 0.073965 | 598.802 | 0.072864 | 983.316 | 0.053228 | 1023.44 | 0.070852 | 1176.06 | 0.076983 | 1021.4 | 0.13681 | 1685.69 | 0.093465 | 2578.41 | 0.075761 | 3418.4 | 0.10217 | 4336.96 | 0.13145
188.657 | 0.041997 | 135.088 | 0.067396 | 178.919 | 0.071207 | 180.536 | 0.10044 | 254.406 | 0.085677 | 275.87 | 0.099643 | 437.874 | 0.082813 | 537.501 | 0.082813 | 919.593 | 0.056633 | 890.632 | 0.083312 | 1052.5 | 0.088996 | 901.384 | 0.16445 | 1548.32 | 0.10381 | 2347.08 | 0.085335 | 3059.26 | 0.11882 | 3932.1 | 0.15503
165.163 | 0.045087 | 121.745 | 0.074858 | 162.704 | 0.079726 | 159.641 | 0.12134 | 229.048 | 0.098454 | 244.186 | 0.11858 | 397.793 | 0.094405 | 490.748 | 0.092906 | 838.765 | 0.061904 | 796.264 | 0.096408 | 956.165 | 0.10105 | 803.463 | 0.19767 | 1412.23 | 0.11728 | 2155.82 | 0.095163 | 2782.01 | 0.13545 | 3526.03 | 0.18597
148.403 | 0.048067 | 112.723 | 0.081907 | 144.884 | 0.092999 | 139.76 | 0.14895 | 201.327 | 0.11929 | 217.007 | 0.14154 | 368.312 | 0.10496 | 443.16 | 0.10751 | 758.946 | 0.069657 | 697.101 | 0.11623 | 866.906 | 0.116 | 724.826 | 0.23571 | 1312.81 | 0.13027 | 1990.08 | 0.10591 | 2537.48 | 0.15565 | 3216.11 | 0.21824
133.878 | 0.051655 | 102.098 | 0.092074 | 127.859 | 0.11224 | 119.813 | 0.18973 | 179.456 | 0.14197 | 194.402 | 0.16777 | 331.269 | 0.12317 | 404.209 | 0.12342 | 699.895 | 0.076065 | 622.617 | 0.13681 | 761.226 | 0.14126 | 663.767 | 0.27468 | 1197.42 | 0.14954 | 1770.34 | 0.12466 | 2314.45 | 0.17814 | 2939.3 | 0.25894
119.334 | 0.056407 | 86.7416 | 0.11439 | 112.61 | 0.13626 | 99.5772 | 0.26128 | 159.641 | 0.1715 | 163.847 | 0.22399 | 299.445 | 0.14382 | 363.919 | 0.14717 | 640.296 | 0.085763 | 550.557 | 0.16593 | 688.786 | 0.16527 | 594.031 | 0.33683 | 1117.59 | 0.16677 | 1606.68 | 0.14253 | 2038.42 | 0.21824 | 2659.59 | 0.31063
106.69 | 0.06209 | 74.4356 | 0.14239 | 93.3106 | 0.18579 | 81.4455 | 0.37115 | 137.68 | 0.21955 | 138.786 | 0.30145 | 266.915 | 0.17219 | 326.991 | 0.17637 | 583.434 | 0.096215 | 482.476 | 0.20739 | 606.637 | 0.20512 | 517.977 | 0.43641 | 1027.54 | 0.19202 | 1481.67 | 0.15991 | 1864.83 | 0.25381 | 2430.68 | 0.3704
96.4412 | 0.068552 | 62.9874 | 0.1856 | 79.753 | 0.24289 | 70.4522 | 0.48425 | 118.739 | 0.28446 | 116.272 | 0.42098 | 235.787 | 0.21137 | 292.929 | 0.21179 | 531.621 | 0.10979 | 429.633 | 0.2556 | 541.819 | 0.25028 | 451.661 | 0.57112 | 954.255 | 0.21737 | 1295.86 | 0.19668 | 1680.64 | 0.30387 | 2248.3 | 0.43294
85.6213 | 0.078069 | 55.0881 | 0.23266 | 66.2168 | 0.34227 | 60.8818 | 0.64136 | 103.641 | 0.36599 | 101.792 | 0.54872 | 205.6 | 0.26816 | 251.875 | 0.27633 | 488.789 | 0.12429 | 384.88 | 0.31156 | 458.487 | 0.33717 | 400.587 | 0.73922 | 881.77 | 0.25407 | 1181.96 | 0.22646 | 1537.52 | 0.35731 | 2075.44 | 0.51316
77.2413 | 0.087934 | 45.6468 | 0.33049 | 51.6729 | 0.54763 | 53.9433 | 0.8137 | 88.9375 | 0.49255 | 88.0525 | 0.74441 | 184.921 | 0.32558 | 218.75 | 0.35481 | 448.51 | 0.14296 | 328.63 | 0.42183 | 397.395 | 0.44036 | 367.576 | 0.89033 | 817.238 | 0.29079 | 1091.08 | 0.25946 | 1398.18 | 0.42352 | 1915.87 | 0.61008
67.2848 | 0.10412 | 35.8712 | 0.53357 | 43.857 | 0.7534 | 49.1528 | 0.99684 | 76.856 | 0.66354 | 78.1737 | 0.96932 | 162.216 | 0.41472 | 186.593 | 0.47324 | 409.498 | 0.16627 | 273.399 | 0.61008 | 345.479 | 0.58033 | 337.623 | 1.0842 | 754.406 | 0.33852 | 1024.47 | 0.29079 | 1258.82 | 0.51728 | 1782.78 | 0.72458
60.276 | 0.12061 | 29.9621 | 0.78572 | 38.9366 | 0.98594 | 45.6925 | 1.2018 | 68.37 | 0.85542 | 70.1008 | 1.2471 | 144.017 | 0.52248 | 161.085 | 0.62866 | 360.658 | 0.20635 | 231.581 | 0.86316 | 298.548 | 0.7952 | 305.8 | 1.3741 | 701.998 | 0.38591 | 950.445 | 0.33315 | 1151.62 | 0.61683 | 1678.96 | 0.83764
55.0331 | 0.13626 | 27.3286 | 0.97418 | 34.5682 | 1.3203 | 41.4685 | 1.5293 | 60.3363 | 1.1443 | 65.6235 | 1.4797 | 126.587 | 0.68239 | 144.305 | 0.79441 | 326.664 | 0.2441 | 200.925 | 1.1958 | 267.985 | 1.0139 | 283.137 | 1.6734 | 651.274 | 0.44568 | 880.008 | 0.38475 | 1040.99 | 0.76862 | 1554.53 | 1.0241
47.6048 | 0.16811 | 24.7527 | 1.2471 | 30.2935 | 1.8792 | 37.1489 | 2.052 | 54.6492 | 1.4519 | 61.6784 | 1.7451 | 112.385 | 0.87358 | 130.834 | 0.98004 | 294.398 | 0.29137 | 177.493 | 1.6174 | 243.698 | 1.2685 | 261.107 | 2.0706 | 597.606 | 0.52773 | 819.694 | 0.44612 | 975.481 | 0.88589 | 1425 | 1.271
42.0111 | 0.20471 | 23.1486 | 1.5036 | 27.1108 | 2.5801 | 34.4646 | 2.5468 | 48.7124 | 1.9598 | 58.2028 | 2.0603 | 100.578 | 1.1105 | 118.739 | 1.2139 | 265.85 | 0.35234 | 161.246 | 2.0727 | 224.962 | 1.5509 | 244.675 | 2.4839 | 532.685 | 0.66487 | 735.78 | 0.55646 | 923.278 | 1.02 | 1342.01 | 1.5202
36.5592 | 0.2592 | 21.3902 | 1.9152 | 25.481 | 3.1045 | 32.1025 | 3.0983 | 44.6089 | 2.4939 | 55.2536 | 2.4299 | 91.0068 | 1.3852 | 108.411 | 1.4991 | 237.681 | 0.43554 | 150.495 | 2.4691 | 209.753 | 1.8531 | 231.119 | 2.9091 | 488.301 | 0.80159 | 651.926 | 0.71522 | 872.996 | 1.1922 | 1255.05 | 1.8164
32.6203 | 0.31532 | 19.9441 | 2.4617 | 23.9971 | 3.8261 | 30.7821 | 3.6286 | 41.6347 | 3.0308 | 51.6729 | 3.0582 | 83.6745 | 1.7243 | 101.996 | 1.7627 | 217.224 | 0.5204 | 143.012 | 2.8543 | 197.933 | 2.1551 | 223.393 | 3.2931 | 450.758 | 0.94918 | 583.434 | 0.90923 | 827.932 | 1.3921 | 1171.37 | 2.2363
25.7371 | 0.502 | 18.264 | 3.5003 | 22.5996 | 4.8542 | 29.6343 | 4.1572 | 39.8425 | 3.5567 | 49.3005 | 3.6504 | 77.6284 | 2.1594 | 96.2485 | 2.0789 | 197.538 | 0.62615 | 135.901 | 3.3698 | 186.967 | 2.5468 | 215.278 | 3.7242 | 414.441 | 1.1524 | 525.28 | 1.1651 | 785.98 | 1.6174 | 1105.36 | 2.6827
21.7352 | 0.72025 | 17.0122 | 4.7202 | 21.3048 | 6.3334 | 28.4439 | 4.8348 | 38.5106 | 4.0263 | 47.32 | 4.2582 | 72.6704 | 2.6962 | 91.4629 | 2.4226 | 180.356 | 0.76402 | 129.792 | 3.9505 | 179.277 | 2.8946 | 209.543 | 4.1572 | 384.111 | 1.37 | 463.558 | 1.5775 | 746.153 | 1.9114 | 1074.84 | 2.9827
18.0462 | 1.0777 | 16.0215 | 6.3525 | 20.3877 | 7.9078 | 27.4931 | 5.6341 | 37.0006 | 4.8059 | 45.4646 | 5.1082 | 67.2848 | 3.5354 | 87.701 | 2.8118 | 168.331 | 0.90018 | 124.453 | 4.5578 | 173.111 | 3.2898 | 203.35 | 4.6825 | 351.754 | 1.7106 | 412.787 | 2.123 | 687.41 | 2.479 | 1035.8 | 3.5143
15.5325 | 1.5309 | 15.3472 | 8.3049 | 19.7852 | 9.4863 | 26.5475 | 6.7453 | 35.7995 | 5.6794 | 43.5946 | 6.2516 | 62.2983 | 4.8059 | 84.0939 | 3.2833 | 156.324 | 1.0734 | 119.334 | 5.3433 | 166.656 | 3.7541 | 196.946 | 5.3647 | 333.93 | 1.9578 | 378.392 | 2.7287 | 640.296 | 3.1482 | 995.187 | 4.1117
13.1436 | 2.2296 | 14.8193 | 11.0214 | 19.2389 | 11.7852 | 25.481 | 8.28 | 34.7415 | 6.5853 | 42.3062 | 7.3144 | 60.7601 | 5.4078 | 79.5141 | 4.0586 | 143.012 | 1.3429 | 115.692 | 6.208 | 161.569 | 4.3096 | 192.853 | 6.0185 | 320.516 | 2.2097 | 359.578 | 3.1704 | 611.51 | 3.7805 | 955.21 | 4.9771
11.5992 | 3.0491 | 14.4969 | 16.3764 | 18.7451 | 16.8921 | 24.7032 | 9.8932 | 33.6137 | 7.8998 | 40.9739 | 8.8538 | 59.0234 | 6.283 | 76.0152 | 4.8688 | 131.227 | 1.6868 | 111.155 | 7.4846 | 156.48 | 4.9276 | 188.468 | 6.7995 | 307.333 | 2.4939 | 345.479 | 3.6177 | 585.772 | 4.4497 | 927.906 | 5.8057
10.6967 | 3.7391 | 14.3526 | 25.5298 | 18.4291 | 23.947 | 24.1174 | 12.0594 | 32.6203 | 9.6876 | 40.0422 | 10.653 | 56.5392 | 7.9793 | 72.7431 | 6.0851 | 121.017 | 2.1508 | 107.762 | 9.087 | 152.617 | 5.7136 | 184.921 | 7.6741 | 297.059 | 2.7978 | 332.264 | 4.1655 | 558.878 | 5.4512 | 897.785 | 6.8747
10.1445 | 4.3791 | 14.3526 | 40.0387 | 18.3556 | 38.7003 | 23.5926 | 15.1173 | 31.9424 | 11.6679 | 39.2101 | 13.0377 | 54.6492 | 9.9926 | 70.2411 | 7.6587 | 113.061 | 2.6694 | 103.744 | 11.7499 | 148.551 | 6.5919 | 180.717 | 8.9249 | 285.983 | 3.215 | 318.598 | 4.9276 | 535.356 | 6.6648 | 869.511 | 8.1976
9.6788 | 5.0624 | 14.3526 | 67.3463 | 18.2093 | 76.5427 | 23.2414 | 19.3529 | 31.3726 | 13.7473 | 38.3953 | 16.4915 | 53.3532 | 12.2661 | 68.0971 | 9.8143 | 105.734 | 3.3799 | 100.981 | 14.4811 | 145.028 | 7.8134 | 175.551 | 10.7278 | 277.531 | 3.5925 | 307.64 | 5.7595 | 513.85 | 8.3215 | 841.285 | 10.0226
9.2807 | 5.7999 | 14.3526 | 126.324 | 18.1004 | 170.349 | 22.9412 | 25.0493 | 30.9364 | 16.8415 | 37.4473 | 21.9298 | 52.088 | 15.2693 | 66.0845 | 13.0377 | 100.578 | 4.1282 | 98.5864 | 18.0807 | 142.015 | 9.2984 | 171.217 | 13.4347 | 267.182 | 4.1406 | 295.873 | 7.0417 | 496.176 | 10.0627 | 813.976 | 12.539
8.9884 | 6.5787 | 14.3526 | 222.483 | 18.0823 | 324.684 | 22.7812 | 37.1085 | 30.4149 | 21.6465 | 36.8898 | 29.8697 | 50.9545 | 19.0839 | 64.1314 | 17.2851 | 97.0216 | 4.859 | 96.3448 | 23.0772 | 137.817 | 11.5749 | 166.656 | 16.6406 | 258.768 | 4.7676 | 286.842 | 8.4052 | 479.11 | 12.5766 | 794.673 | 15.0871
8.6966 | 7.6817 | 14.3526 | 370.129 | 17.9562 | 557.718 | 22.6902 | 62.0443 | 30.0521 | 29.543 | 36.6324 | 38.7778 | 49.9456 | 24.9742 | 62.7987 | 22.2835 | 93.0311 | 6.0608 | 93.8721 | 31.4955 | 134.953 | 14.3513 | 162.541 | 21.1967 | 251.875 | 5.495 | 277.808 | 10.4944 | 464.022 | 15.6558 | 774.278 | 18.5384
8.4819 | 8.8361 | 14.3526 | 547.769 | 17.8845 | 611.462 | 22.6222 | 130.954 | 29.7829 | 40.7659 | 36.4497 | 57.2168 | 48.9077 | 36.301 | 62.0496 | 28.987 | 89.3833 | 7.8134 | 92.2898 | 43.5908 | 132.944 | 17.337 | 159.482 | 26.1499 | 241.756 | 6.6515 | 267.717 | 13.5562 | 449.408 | 20.1226 | 752.146 | 23.6851
8.2477 | 10.463 | 14.3526 | 605.984 |  |  | 22.4196 | 271.741 | 29.6937 | 56.4778 | 36.4497 | 84.4238 | 48.518 | 50.2418 | 61.0037 | 42.4721 | 86.8284 | 9.8242 | 90.5529 | 66.3437 | 130.442 | 22.0397 | 156.637 | 32.8465 | 233.909 | 7.892 | 258.509 | 18.0085 | 436.999 | 25.4788 | 733.576 | 29.9595
8.012 | 12.703 |  |  |  |  | 22.3301 | 524.189 | 29.6937 | 83.6674 | 36.4133 | 144.438 | 48.1795 | 73.3211 | 60.3967 | 70.3757 | 84.0939 | 12.703 | 88.9375 | 109.054 | 128.115 | 29.7208 | 154.151 | 42.685 | 226.996 | 9.317 | 251.12 | 23.6377 | 425.784 | 32.1961 | 716.896 | 38.3152
7.8141 | 15.5 |  |  |  |  | 22.1965 | 610.851 | 29.6937 | 148.094 | 36.4133 | 246.62 | 47.9392 | 111.927 | 60.0954 | 108.294 | 81.6085 | 16.8921 | 88.3171 | 181.064 | 125.956 | 40.8476 | 152.464 | 55.9718 | 221.391 | 10.9227 | 245.901 | 31.0266 | 415.271 | 41.6727 | 693.625 | 54.3719
7.6441 | 20.1025 | [6 empty] | 29.6937 | 252.611 | 36.4133 | 407.423 | 47.5097 | 175.186 | 59.6762 | 177.834 | 79.5141 | 23.7562 | 87.701 | 282.266 | 124.329 | 56.9884 | 150.495 | 78.1671 | 215.709 | 13.1424 | 241.032 | 41.6727 | 403.401 | 57.5036 | 673.798 | 76.6193
7.4703 | 27.0272 | [6 empty] | 29.6937 | 404.986 | 36.3769 | 540.153 | 47.1783 | 272.558 | 59.3193 | 308.231 | 77.9396 | 33.6108 | 87.1764 | 392.624 | 122.6 | 85.614 | 149.595 | 106.895 | 210.804 | 15.8765 | 236.023 | 58.1978 | 390.697 | 84.4238 | 659.796 | 101.58
7.3444 | 36.9234 | [6 empty] | 29.6937 | 536.385 | 36.2679 | 602.961 | 46.8024 | 421.514 | 59.0825 | 466.777 | 76.856 | 48.8057 | 86.6549 | 552.721 | 121.623 | 136.845 | 148.403 | 159.628 | 206.217 | 19.0457 | 231.119 | 85.3576 | 381.05 | 116.611 | 641.578 | 141.719
7.2495 | 56.4214 | [6 empty] | 29.664 | 606.59 |  |  | 46.4759 | 546.128 | 58.9055 | 562.76 | 75.9393 | 74.4292 | 86.2227 | 607.197 | 120.896 | 226.977 | 146.779 | 241.254 | 200.724 | 24.7752 | 226.542 | 130.171 | 372.386 | 160.589 | 627.618 | 187.138
7.2495 | 97.4023 | [10 empty] | 46.4759 | 605.984 | 58.729 | 608.413 | 75.4095 | 112.488 |  |  | 120.293 | 341.331 | 145.61 | 342.014 | 196.16 | 32.65 | 222.946 | 229.717 | 363.192 | 228.343 | 609.678 | 267.428
7.2278 | 183.984 | [14 empty] | 74.6592 | 189.019 |  |  | 119.693 | 493.169 | 144.594 | 479.552 | 192.853 | 41.6727 | 220.728 | 345.106 | 357.427 | 324.035 | 596.412 | 357.041
7.2062 | 325.985 | [14 empty] | 73.9903 | 293.492 |  |  | 119.334 | 558.834 | 143.729 | 562.197 | 190.172 | 56.1961 | 219.847 | 537.997 | 352.106 | 457.535 | 579.944 | 478.594
7.1918 | 562.197 | [14 empty] | 73.3274 | 448.923 |  |  | 118.977 | 607.805 | 143.155 | 609.021 | 187.341 | 80.9514 | 219.408 | 607.197 | 348.602 | 567.848 | 571.881 | 572.981
7.1918 | 609.631 | [14 empty] | 72.9616 | 560.513 | [6 empty] | 183.631 | 133.6 |  |  | 346.17 | 618.226 | 565.625 | 612.074
[16 empty] | 72.8159 | 607.197 | [6 empty] | 181.441 | 204.558
[24 empty] | 179.815 | 322.419
[24 empty] | 178.919 | 487.774
[24 empty] | 178.74 | 576.43
[24 empty] | 178.74 | 612.074