## 176-1
S&C Power Fuses - Types SMD-1A, -2B, -2C, -3, and -50 | [9 empty] | S&C Power Fuses - Types SMD-1A, -2B, -2C, -3, and -50 | [9 empty] | S&C Power Fuses - Types SMD-1A, -2B, -2C, -3, and -50
Very Slow Speed (TCC 176-1) | [9 empty] | Very Slow Speed (TCC 176-1) | [9 empty] | Very Slow Speed (TCC 176-1)
Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988 | [9 empty] | Minimum Melting Time-Current Characteristic Curves Dated August 29, 1988
Tolerance in Terms of Curent: |  |  | Plus 10% | [6 empty] | Tolerance in Terms of Curent: |  |  | Plus 10% | [6 empty] | Tolerance in Terms of Curent: |  |  | Plus 10%
50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 2-175E |  | 2-200E |  | 2-250E
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
98.7838 | 609.6307 | 127.4767 | 613.913 | 155.5447 | 598.7557 | 194.987 | 597.5594 | 278.3647 | 598.7557 | 333.9304 | 599.3544 | 383.7272 | 597.5594 | 445.3819 | 601.1553 | 556.0909 | 601.757 | 685.3512 | 600.5542 | 789.9196 | 604.1687 | 991.2144 | 599.9543
98.6851 | 573.5547 | 127.6042 | 584.5565 | 155.8561 | 540.1533 | 195.3773 | 502.127 | 277.2536 | 314.4584 | 333.5965 | 442.6824 | 386.4227 | 357.7564 | 444.4919 | 417.3197 | 561.6796 | 328.9322 | 686.0368 | 414.4087 | 789.9196 | 399.7552 | 998.1772 | 332.2381
98.8827 | 445.3467 | 128.1156 | 471.9404 | 156.9509 | 391.4479 | 197.1437 | 386.7786 | 279.7601 | 185.2767 | 334.2644 | 283.9651 | 391.479 | 210.9986 | 445.8275 | 281.421 | 570.1685 | 188.0769 | 689.4757 | 255.4052 | 793.8792 | 239.5714 | 1017.324 | 158.1985
99.2789 | 342.0142 | 129.0156 | 339.2889 | 159.0046 | 290.2817 | 200.3233 | 283.9651 | 285.6971 | 110.8136 | 338.6382 | 173.6169 | 400.5875 | 111.8154 | 448.9592 | 172.2334 | 587.5325 | 105.8317 | 696.4048 | 163.8334 | 807.4906 | 145.4527 | 1054.615 | 83.2501
99.7766 | 279.7376 | 130.0519 | 254.1314 | 160.4421 | 239.3318 | 203.5544 | 214.8309 | 294.6925 | 69.0512 | 344.4442 | 108.1857 | 413.2 | 71.012 | 456.6566 | 118.8486 | 606.6376 | 67.1446 | 706.2234 | 116.3788 | 838.7654 | 87.606 | 1092.18 | 56.0838
100.3771 | 220.2693 | 131.7536 | 181.9716 | 162.8669 | 188.642 | 206.6307 | 166.1432 | 308.2566 | 43.7218 | 354.9342 | 70.3054 | 432.2188 | 43.8971 | 469.6239 | 74.6529 | 630.7639 | 45.7343 | 724.1013 | 80.7897 | 877.3721 | 54.5899 | 1143.594 | 37.4815
100.8802 | 172.2334 | 133.3441 | 130.6929 | 164.833 | 154.4469 | 210.5942 | 128.6184 | 323.4137 | 29.5135 | 365.0127 | 49.9413 | 451.2097 | 31.1199 | 487.3253 | 48.2718 | 660.4568 | 31.7168 | 751.395 | 52.9235 | 931.6257 | 32.5197 | 1210.672 | 25.8639
101.7922 | 126.7036 | 135.0889 | 104.1518 | 167.3242 | 120.8863 | 215.2786 | 99.968 | 342.3837 | 20.2437 | 379.5295 | 35.6892 | 470.564 | 23.8992 | 513.3366 | 31.7803 | 703.404 | 21.886 | 782.8423 | 37.444 | 984.3002 | 22.5074 | 1297.157 | 18.4829
102.9181 | 99.868 | 136.7198 | 82.752 | 169.8529 | 99.968 | 221.613 | 76.0849 | 366.4756 | 14.6559 | 398.5895 | 26.36 | 491.7309 | 19.0839 | 542.9035 | 22.5525 | 746.9 | 16.4257 | 831.2505 | 26.281 | 1068.414 | 14.967 | 1392.604 | 13.9412
104.3691 | 82.0106 | 138.232 | 69.1895 | 172.938 | 81.1135 | 228.5906 | 58.6653 | 396.2051 | 10.7601 | 423.2369 | 19.9823 | 517.4597 | 15.4536 | 588.1203 | 15.8925 | 817.2385 | 11.8088 | 891.5227 | 18.706 | 1162.038 | 10.7924 | 1511.61 | 10.5365
105.9464 | 68.7755 | 140.3211 | 57.2741 | 175.9031 | 67.8194 | 236.26 | 46.5184 | 436.1262 | 7.8841 | 457.1135 | 14.9072 | 547.8118 | 12.539 | 637.7404 | 11.7382 | 880.8887 | 9.1143 | 964.8098 | 13.5698 | 1288.109 | 7.7048 | 1655.619 | 7.9553
107.4401 | 57.5037 | 142.8698 | 47.4107 | 178.9189 | 56.8177 | 243.4551 | 38.1623 | 487.3253 | 5.8057 | 500.1619 | 10.9446 | 581.105 | 10.2763 | 706.2234 | 8.28 | 977.4341 | 6.7116 | 1056.726 | 9.9428 | 1465.469 | 5.338 | 1838.913 | 5.9171
109.501 | 46.9859 | 145.174 | 40.159 | 182.1687 | 47.6483 | 252.127 | 31.4012 | 548.3599 | 4.2795 | 571.8814 | 7.3658 | 640.2966 | 7.7048 | 784.4094 | 6.1278 | 1103.156 | 4.8493 | 1196.23 | 6.8747 | 1752.73 | 3.3934 | 2067.158 | 4.2881
111.4899 | 40.0388 | 147.6631 | 34.3241 | 185.8487 | 40.8068 | 262.9418 | 25.2505 | 646.0852 | 2.912 | 677.8535 | 4.7296 | 728.4589 | 5.4458 | 888.8524 | 4.3879 | 1268.932 | 3.4139 | 1348.746 | 4.9276 | 2060.966 | 2.3299 | 2309.832 | 3.2669
113.8559 | 34.0165 | 151.5526 | 28.3562 | 189.7928 | 34.9475 | 275.595 | 19.9424 | 763.5138 | 2.0014 | 801.0562 | 3.1672 | 850.5906 | 3.6908 | 1028.576 | 3.0767 | 1498.066 | 2.2884 | 1532.921 | 3.5355 | 2570.69 | 1.4475 | 2721.476 | 2.2274
116.6215 | 28.8713 | 155.0788 | 24.5042 | 193.8206 | 30.2304 | 286.5556 | 17.0619 | 900.4828 | 1.4061 | 957.1221 | 2.1273 | 1044.121 | 2.2975 | 1205.839 | 2.1401 | 1824.261 | 1.4738 | 1777.442 | 2.5014 | 3074.599 | 0.99784 | 3209.69 | 1.5447
119.933 | 24.4308 | 159.9615 | 20.7562 | 198.1319 | 26.2023 | 298.8472 | 14.4666 | 1070.553 | 0.97613 | 1165.529 | 1.3687 | 1314.13 | 1.3783 | 1427.858 | 1.4782 | 2273.169 | 0.91745 | 2184.037 | 1.5886 | 3759.079 | 0.65957 | 3747.819 | 1.1072
123.9568 | 20.5497 | 165.6593 | 17.5991 | 203.3508 | 22.5525 | 315.4286 | 12.0353 | 1294.566 | 0.66089 | 1426.431 | 0.87971 | 1611.516 | 0.88767 | 1689.065 | 1.0396 | 2875.35 | 0.55368 | 2762.606 | 0.97711 | 4712.29 | 0.4193 | 4424.574 | 0.78336
127.4767 | 17.9008 | 171.7316 | 14.9969 | 208.9161 | 19.5866 | 333.9304 | 9.9826 | 1568.587 | 0.45106 | 1820.616 | 0.52615 | 2024.201 | 0.54927 | 2008.072 | 0.72025 | 3543.709 | 0.3591 | 3565.036 | 0.58091 | 6335.53 | 0.23127 | 5334.386 | 0.52879
133.3441 | 14.612 | 177.8486 | 12.9467 | 215.4939 | 16.9428 | 352.4583 | 8.4811 | 1956.535 | 0.28963 | 2291.427 | 0.32753 | 2659.597 | 0.31659 | 2601.725 | 0.42735 | 4464.574 | 0.22647 | 4482.469 | 0.36234 | 8167.584 | 0.13985 | 6700.442 | 0.33017
137.5426 | 12.7413 | 184.9218 | 11.1768 | 221.1703 | 14.9819 | 378.7711 | 6.9577 | 2472.364 | 0.18192 | 2875.35 | 0.2076 | 3618.915 | 0.17099 | 3473.54 | 0.23975 | 5784.452 | 0.13477 | 5624.733 | 0.22966 | 11124.75 | 0.075158 | 8918.903 | 0.18579
142.8698 | 10.9337 | 193.0469 | 9.6296 | 227.9058 | 13.3144 | 402.9982 | 5.8524 | 3152.432 | 0.11167 | 3827.355 | 0.11705 | 5109.869 | 0.086021 | 4670.069 | 0.1329 | 8349.263 | 0.064818 | 7397.73 | 0.13277 | 15505.15 | 0.038729 | 11555.63 | 0.11012
147.5155 | 9.8143 | 201.3275 | 8.3382 | 237.6818 | 11.4369 | 432.2188 | 4.8785 | 4217.21 | 0.062464 | 5135.482 | 0.065078 | 7784.802 | 0.036988 | 6781.331 | 0.063218 | 10904.47 | 0.038 | 10157.1 | 0.070994 | 21161.26 | 0.020709 | 15645.33 | 0.060015
153.0758 | 8.8008 | 210.8049 | 7.1911 | 247.6293 | 9.9031 | 462.6319 | 4.1241 | 5355.766 | 0.038923 | 7171.919 | 0.033434 | 11372.21 | 0.017315 | 8963.61 | 0.036183 | 15259.04 | 0.019445 | 13493.02 | 0.040108 | 30544.1 | 0.01 | 22024.86 | 0.030072
158.6869 | 7.9315 | 222.0567 | 6.1524 | 256.7063 | 8.722 | 493.2084 | 3.5319 | 7464.6 | 0.019957 | 9255.083 | 0.019957 | 14956.9 | 0.01 | 12770.95 | 0.017807 | 21246.07 | 0.01 | 18451.99 | 0.021447 |  |  | 32955.94 | 0.013472
167.9948 | 6.7723 | 232.5098 | 5.3647 | 266.6488 | 7.7667 | 530.0291 | 2.9827 | 10561.05 | 0.01 | 13094.24 | 0.01 |  |  | 17033.34 | 0.01 |  |  | 27036.07 | 0.01 |  |  | 38442.8 | 0.01
177.4933 | 5.829 | 244.9202 | 4.6966 | 276.9765 | 6.9646 | 574.748 | 2.4889
189.6031 | 4.9374 | 258.7681 | 4.0953 | 292.0522 | 6.0065 | 617.0385 | 2.1251
202.5391 | 4.1655 | 278.6432 | 3.431 | 303.6671 | 5.3701 | 675.8232 | 1.7347
218.3136 | 3.5003 | 302.1527 | 2.8373 | 317.0097 | 4.7676 | 738.7291 | 1.4317
236.9698 | 2.9033 | 329.2878 | 2.3346 | 330.6076 | 4.2667 | 822.1567 | 1.1375
257.7352 | 2.4057 | 357.785 | 1.9481 | 344.7888 | 3.8491 | 901.3837 | 0.94067
278.3647 | 2.0459 | 388.3597 | 1.6337 | 362.1043 | 3.407 | 989.2341 | 0.77557
294.398 | 1.8146 | 426.2099 | 1.3362 | 381.0505 | 3.0067 | 1112.017 | 0.61621
318.2802 | 1.5324 | 464.022 | 1.1183 | 402.5955 | 2.6323 | 1220.396 | 0.50907
349.6498 | 1.2597 | 508.2287 | 0.92852 | 424.5084 | 2.3323 | 1356.863 | 0.40895
382.1955 | 1.0501 | 569.0291 | 0.73553 | 455.7443 | 1.9815 | 1481.678 | 0.34227
416.9357 | 0.8762 | 636.4663 | 0.5891 | 486.3517 | 1.7123 | 1616.357 | 0.28646
448.0622 | 0.75717 | 697.7993 | 0.48911 | 517.4597 | 1.4946 | 1761.516 | 0.23975
480.07 | 0.65957 | 754.4063 | 0.41888 | 551.1083 | 1.3006 | 1910.137 | 0.20267
523.7067 | 0.55479 | 829.5898 | 0.34536 | 589.2976 | 1.1296 | 2100.499 | 0.1666
563.3672 | 0.47991 | 902.2855 | 0.29166 | 634.5599 | 0.96835 | 2305.217 | 0.13846
612.1219 | 0.40773 | 981.3519 | 0.24656 | 680.5705 | 0.83597 | 2532.418 | 0.11382
673.7986 | 0.33717 | 1055.67 | 0.2137 | 731.3787 | 0.71881 | 2726.925 | 0.09767
736.5164 | 0.28248 | 1128.823 | 0.18634 | 784.4094 | 0.62116 | 3007.696 | 0.080286
790.7098 | 0.24533 | 1235.129 | 0.1558 | 838.7654 | 0.54109 | 3254.941 | 0.068415
871.2519 | 0.20207 | 1335.326 | 0.1333 | 918.6738 | 0.45196 | 3508.449 | 0.058944
954.2553 | 0.16878 | 1447.988 | 0.11314 | 1003.181 | 0.3794 | 3804.46 | 0.050329
1036.838 | 0.14339 | 1545.234 | 0.099742 | 1085.646 | 0.32298 | 4251.084 | 0.04039
1113.13 | 0.12404 | 1660.593 | 0.086452 | 1205.839 | 0.2618 | 4609.751 | 0.034212
1213.095 | 0.10496 | 1822.437 | 0.072067 | 1316.762 | 0.21955 | 5069.152 | 0.028264
1337.999 | 0.086107 | 1974.223 | 0.06135 | 1440.766 | 0.18357 | 5529.921 | 0.023703
1492.086 | 0.069518 | 2197.18 | 0.049382 | 1563.888 | 0.1558 | 6099.297 | 0.019503
1642.427 | 0.057317 | 2396.896 | 0.041496 | 1724.91 | 0.12859 | 6587.497 | 0.016686
1809.725 | 0.047304 | 2643.687 | 0.03411 | 1893.023 | 0.10676 | 7179.094 | 0.014021
1939.005 | 0.041165 | 2901.345 | 0.028377 | 2100.499 | 0.086452 | 7722.771 | 0.012153
2092.114 | 0.035431 | 3184.115 | 0.023537 | 2351.785 | 0.069379 | 8183.937 | 0.0108
2237.087 | 0.031019 | 3483.976 | 0.01966 | 2599.125 | 0.056633 | 8492.413 | 0.01
2408.911 | 0.026725 | 3744.073 | 0.01704 | 2881.106 | 0.046228
2591.339 | 0.023141 | 4039.715 | 0.014681 | 3146.134 | 0.038884
2804.357 | 0.019818 | 4289.516 | 0.012956 | 3334.005 | 0.034487
2998.686 | 0.017298 | 4554.764 | 0.011503 | 3540.168 | 0.030587
3200.075 | 0.015159 | 4750.139 | 0.010597 | 3835.018 | 0.026169
3418.406 | 0.013311 | 4870.388 | 0.01 | 4129.573 | 0.022569
3622.535 | 0.011829 |  |  | 4491.442 | 0.019117
3762.84 | 0.011008 |  |  | 4865.521 | 0.016274
3865.821 | 0.010429 |  |  | 5207.884 | 0.014176
3947.862 | 0.01 |  |  | 5540.993 | 0.012561
|  |  |  | 5836.748 | 0.01132
|  |  |  | 6056.751 | 0.01046
|  |  |  | 6197.67 | 0.01