## 420_7MM
S&C Fault Fiter Electronic Power Fuses | [7 empty] | S&C Fault Fiter Electronic Power Fuses | [7 empty] | S&C Fault Fiter Electronic Power Fuses | [7 empty] | S&C Fault Fiter Electronic Power Fuses
Compound-Curve-Type Control Module (TCC 420-7) | [7 empty] | Compound Curve Type Control Module (TCC 420-7) | [7 empty] | Compound Curve Type Control Module (TCC 420-7) | [7 empty] | Compound Curve Type Control Module (TCC 420-7)
Minimum Tripping Time-Current Characteristic Curve Dated September 8, 1986 | [7 empty] | Minimum Tripping Time-Current Characteristic Curve Dated September 8, 1986 | [7 empty] | Minimum Tripping Time-Current Characteristic Curve Dated September 8, 1986 | [7 empty] | Minimum Tripping Time-Current Characteristic Curve Dated September 8, 1986
Tolerance in Terms of Current: Plus 10% | [7 empty] | Tolerance in Terms of Current: Plus 10% | [7 empty] | Tolerance in Terms of Current: Plus 10% | [7 empty] | Tolerance in Terms of Current: Plus 10%
Short Time Delay Band: 1 | [7 empty] | Short Time Delay Band: 2 | [7 empty] | Short Time Delay Band: 3 | [7 empty] | Short Time Delay Band: 4
Min P/U = 400A |  | Min P/U = 600A |  | Min P/U = 800A |  | Min P/U = 1100A |  | Min P/U = 400A |  | Min P/U = 600A |  | Min P/U = 800A |  | Min P/U = 1100A |  | Min P/U = 400A |  | Min P/U = 600A |  | Min P/U = 800A |  | Min P/U = 1100A |  | Min P/U = 400A |  | Min P/U = 600A |  | Min P/U = 800A |  | Min P/U = 1100A
Current | Time | Current | Time | Current | Current | Current | Time | Current | Time | Current | Time | Current | Current | Current | Time | Current | Time | Current | Time | Current | Current | Current | Time | Current | Time | Current | Time | Current | Current | Current | Time
5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01 | 5996.48 | 0.01
5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523 | 5996.48 | 0.019523
5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763 | 5996.48 | 0.053763
5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395 | 5996.48 | 0.083395
5842.58 | 0.08508 | 5842.58 | 0.08508 | 5842.58 | 0.08508 | 5842.58 | 0.08508 | 5996.48 | 0.10751 | 5996.48 | 0.10751 | 5996.48 | 0.10751 | 5996.48 | 0.10751 | 5996.48 | 0.10751 | 5996.48 | 0.10751 | 5996.48 | 0.10751 | 5996.48 | 0.10751 | 5996.48 | 0.10751 | 5996.48 | 0.10751 | 5996.48 | 0.10751 | 5996.48 | 0.10751
4637.49 | 0.099643 | 4637.49 | 0.099643 | 4637.49 | 0.099643 | 4637.49 | 0.099643 | 5996.48 | 0.13237 | 5996.48 | 0.13237 | 5996.48 | 0.13237 | 5996.48 | 0.13237 | 5996.48 | 0.13237 | 5996.48 | 0.13237 | 5996.48 | 0.13237 | 5996.48 | 0.13237 | 5996.48 | 0.13237 | 5996.48 | 0.13237 | 5996.48 | 0.13237 | 5996.48 | 0.13237
3626.16 | 0.12061 | 3626.16 | 0.12061 | 3626.16 | 0.12061 | 3626.16 | 0.12061 | 5996.48 | 0.15029 | 5996.48 | 0.15029 | 5996.48 | 0.15029 | 5996.48 | 0.15029 | 5996.48 | 0.15029 | 5996.48 | 0.15029 | 5996.48 | 0.15029 | 5996.48 | 0.15029 | 5996.48 | 0.15029 | 5996.48 | 0.15029 | 5996.48 | 0.15029 | 5996.48 | 0.15029
2861 | 0.15029 | 2861 | 0.15029 | 2861 | 0.15029 | 2861 | 0.15029 | 5228.75 | 0.16743 | 5228.75 | 0.16743 | 5228.75 | 0.16743 | 5228.75 | 0.16743 | 5996.48 | 0.18394 | 5996.48 | 0.18394 | 5996.48 | 0.18394 | 5996.48 | 0.18394 | 5996.48 | 0.18394 | 5996.48 | 0.18394 | 5996.48 | 0.18394 | 5996.48 | 0.18394
2100.49 | 0.20369 | 2100.49 | 0.20369 | 2100.49 | 0.20369 | 2100.49 | 0.20369 | 4137.84 | 0.20227 | 4137.84 | 0.20227 | 4137.84 | 0.20227 | 4137.84 | 0.20227 | 5996.48 | 0.22332 | 5996.48 | 0.22332 | 5996.48 | 0.22332 | 5996.48 | 0.22332 | 5996.48 | 0.22332 | 5996.48 | 0.22332 | 5996.48 | 0.22332 | 5996.48 | 0.22332
1517.66 | 0.2905 | 1517.66 | 0.2905 | 1517.66 | 0.2905 | 1517.66 | 0.2905 | 3090.01 | 0.26233 | 3090.01 | 0.26233 | 3090.01 | 0.26233 | 3090.01 | 0.26233 | 5996.48 | 0.26496 | 5996.48 | 0.26496 | 5996.48 | 0.26496 | 5996.48 | 0.26496 | 5996.48 | 0.26496 | 5996.48 | 0.26496 | 5996.48 | 0.26496 | 5996.48 | 0.26496
1197.42 | 0.37789 | 1197.42 | 0.37789 | 1197.42 | 0.37789 | 1197.42 | 0.37789 | 2344.74 | 0.34398 | 2344.74 | 0.34398 | 2344.74 | 0.34398 | 2344.74 | 0.34398 | 5996.48 | 0.28304 | 5996.48 | 0.28304 | 5996.48 | 0.28304 | 5996.48 | 0.28304 | 5996.48 | 0.28304 | 5996.48 | 0.28304 | 5996.48 | 0.28304 | 5996.48 | 0.28304
1099.85 | 0.42352 | 1099.85 | 0.42352 | 1099.85 | 0.42352 | 1099.85 | 0.42352 | 1700.93 | 0.48328 | 1700.93 | 0.48328 | 1700.93 | 0.48328 | 1700.93 | 0.48328 | 5318.4 | 0.3097 | 5318.4 | 0.3097 | 5318.4 | 0.3097 | 5318.4 | 0.3097 | 5996.48 | 0.34158 | 5996.48 | 0.34158 | 5996.48 | 0.34158 | 5996.48 | 0.34158
1043.07 | 0.44746 | 1043.07 | 0.44746 | 1043.07 | 0.44746 | 1104.26 | 0.46619 | 1293.27 | 0.65171 | 1293.27 | 0.65171 | 1293.27 | 0.65171 | 1293.27 | 0.65171 | 4162.74 | 0.37864 | 4162.74 | 0.37864 | 4162.74 | 0.37864 | 4162.74 | 0.37864 | 5996.48 | 0.42692 | 5996.48 | 0.42692 | 5996.48 | 0.42692 | 5996.48 | 0.42692
911.353 | 0.52405 | 911.353 | 0.52405 | 911.353 | 0.52405 | 1104.26 | 0.78336 | 1164.36 | 0.74218 | 1164.36 | 0.74218 | 1164.36 | 0.74218 | 1164.36 | 0.74218 | 3050.1 | 0.50049 | 3050.1 | 0.50049 | 3050.1 | 0.50049 | 3050.1 | 0.50049 | 5996.48 | 0.52721 | 5996.48 | 0.52721 | 5996.48 | 0.52721 | 5996.48 | 0.52721
797.061 | 0.62553 | 797.061 | 0.62553 | 797.061 | 0.62553 | 1104.26 | 2.2656 | 1104.26 | 0.78102 | 1104.26 | 0.78102 | 1104.26 | 0.78102 | 1104.26 | 0.78102 | 2298.31 | 0.66754 | 2298.31 | 0.66754 | 2298.31 | 0.66754 | 2298.31 | 0.66754 | 5996.48 | 0.55479 | 5996.48 | 0.55479 | 5996.48 | 0.55479 | 5996.48 | 0.55479
748.395 | 0.66554 | 748.395 | 0.66554 | 797.858 | 1.1028 | 1104.26 | 13.8162 | 1039.95 | 0.83764 | 1039.95 | 0.83764 | 1039.95 | 0.83764 | 1104.26 | 0.78336 | 1657.27 | 0.95584 | 1657.27 | 0.95584 | 1657.27 | 0.95584 | 1657.27 | 0.95584 | 5120.09 | 0.62241 | 5120.09 | 0.62241 | 5120.09 | 0.62241 | 5120.09 | 0.62241
640.296 | 0.82765 | 640.296 | 0.82765 | 797.061 | 2.2952 | 1104.26 | 197.917 | 918.674 | 0.97418 | 918.674 | 0.97418 | 918.674 | 0.97418 | 1104.26 | 2.2656 | 1319.39 | 1.2446 | 1319.39 | 1.2446 | 1319.39 | 1.2446 | 1319.39 | 1.2446 | 3999.51 | 0.76555 | 3999.51 | 0.76555 | 3999.51 | 0.76555 | 3999.51 | 0.76555
595.816 | 0.91745 | 595.816 | 0.91745 | 797.061 | 6.8063 | 1104.26 | 686.67 | 797.858 | 1.1489 | 797.858 | 1.1489 | 797.858 | 1.1489 | 1104.26 | 13.8162 | 1104.26 | 1.5217 | 1104.26 | 1.5217 | 1104.26 | 1.5217 | 1104.26 | 1.5217 | 3059.26 | 0.97808 | 3059.26 | 0.97808 | 3059.26 | 0.97808 | 3059.26 | 0.97808
573.599 | 0.9732 | 597.008 | 1.2322 | 797.061 | 35.0174 | 1104.26 | 1000.1 | 757.43 | 1.2286 | 757.43 | 1.2286 | 797.061 | 2.2952 | 1104.26 | 197.917 | 1071.62 | 1.5838 | 1071.62 | 1.5838 | 1071.62 | 1.5838 | 1104.26 | 2.2656 | 2323.73 | 1.3006 | 2323.73 | 1.3006 | 2323.73 | 1.3006 | 2323.73 | 1.3006
523.706 | 1.1251 | 595.816 | 2.3276 | 797.061 | 167.31 |  |  | 685.351 | 1.3991 | 685.351 | 1.3991 | 797.061 | 6.8063 | 1104.26 | 686.67 | 978.412 | 1.7556 | 978.412 | 1.7556 | 978.412 | 1.7556 | 1104.26 | 13.8162 | 1759.75 | 1.7609 | 1759.75 | 1.7609 | 1759.75 | 1.7609 | 1759.75 | 1.7609
465.881 | 1.3659 | 595.816 | 5.1287 | 797.061 | 498.624 |  |  | 632.659 | 1.5681 | 632.659 | 1.5681 | 797.061 | 35.0174 | 1104.26 | 1000.1 | 879.128 | 1.9934 | 879.128 | 1.9934 | 879.128 | 1.9934 | 1104.26 | 197.917 | 1342.01 | 2.4009 | 1342.01 | 2.4009 | 1342.01 | 2.4009 | 1342.01 | 2.4009
424.084 | 1.6634 | 595.816 | 13.341 | 797.061 | 997.104 |  |  | 595.816 | 1.6953 | 595.816 | 1.6953 | 797.061 | 167.31 |  |  | 827.932 | 2.1486 | 827.932 | 2.1486 | 827.932 | 2.1486 | 1104.26 | 686.67 | 1153.93 | 2.8458 | 1153.93 | 2.8458 | 1153.93 | 2.8458 | 1153.93 | 2.8458
406.641 | 1.8475 | 595.816 | 39.6007 |  |  |  |  | 566.757 | 1.8127 | 595.816 | 2.3276 | 797.061 | 498.624 |  |  | 797.061 | 2.2274 | 797.061 | 2.2274 | 797.061 | 2.2274 | 1104.26 | 1000.1 | 1104.26 | 3.0127 | 1104.26 | 3.0127 | 1104.26 | 3.0127 | 1104.26 | 3.0127
406.641 | 2.6854 | 595.816 | 123.205 |  |  |  |  | 508.737 | 2.1401 | 595.816 | 5.1287 | 797.061 | 997.104 |  |  | 763.514 | 2.3746 | 763.514 | 2.3746 | 797.061 | 2.2952 |  |  | 1049.35 | 3.2022 | 1049.35 | 3.2022 | 1049.35 | 3.2022 | 1104.26 | 13.8162
406.641 | 5.6341 | 595.816 | 315.719 |  |  |  |  | 469.623 | 2.4469 | 595.816 | 13.341 |  |  |  |  | 704.107 | 2.6191 | 704.107 | 2.6191 | 797.061 | 6.8063 |  |  | 975.481 | 3.5108 | 975.481 | 3.5108 | 975.481 | 3.5108 | 1104.26 | 197.917
406.641 | 16.5245 | 595.816 | 633.876 |  |  |  |  | 427.063 | 2.8946 | 595.816 | 39.6007 |  |  |  |  | 653.885 | 2.8715 | 653.885 | 2.8715 | 797.061 | 35.0174 |  |  | 909.533 | 3.8184 | 909.533 | 3.8184 | 909.533 | 3.8184 | 1104.26 | 686.67
406.641 | 53.6697 | 595.816 | 1000.1 |  |  |  |  | 411.55 | 3.1767 | 595.816 | 123.205 |  |  |  |  | 619.511 | 3.1014 | 619.511 | 3.1014 | 797.061 | 167.31 |  |  | 844.657 | 4.1948 | 844.657 | 4.1948 | 844.657 | 4.1948 | 1104.26 | 1000.1
406.641 | 152.604 | [6 empty] | 406.641 | 3.3462 | 595.816 | 315.719 |  |  |  |  | 595.816 | 3.2964 | 595.816 | 3.2964 | 797.061 | 498.624 |  |  | 818.056 | 4.3572 | 818.056 | 4.3572 | 818.056 | 4.3572
406.641 | 372.729 | [6 empty] | 406.641 | 5.6341 | 595.816 | 633.876 |  |  |  |  | 552.764 | 3.6359 | 595.816 | 5.1287 | 797.061 | 1000.1 |  |  | 797.061 | 4.4989 | 797.061 | 4.4989 | 797.061 | 4.4989
406.641 | 690.112 | [6 empty] | 406.641 | 16.5245 | 595.816 | 1000.1 |  |  |  |  | 500.662 | 4.1323 | 595.816 | 13.341 |  |  |  |  | 760.466 | 4.7819 | 760.466 | 4.7819 | 797.061 | 6.8063
406.641 | 1000.1 | [6 empty] | 406.641 | 53.6697 | [6 empty] | 464.951 | 4.6872 | 595.816 | 39.6007 |  |  |  |  | 697.799 | 5.3486 | 697.799 | 5.3486 | 797.061 | 35.0174
[8 empty] | 406.641 | 152.604 | [6 empty] | 419.864 | 5.484 | 595.816 | 123.205 |  |  |  |  | 634.559 | 6.134 | 634.559 | 6.134 | 797.061 | 167.31
[8 empty] | 406.641 | 372.729 | [6 empty] | 406.641 | 5.829 | 595.816 | 315.719 |  |  |  |  | 595.816 | 6.7318 | 595.816 | 6.7318 | 797.061 | 498.624
[8 empty] | 406.641 | 690.112 | [6 empty] | 406.641 | 16.5245 | 595.816 | 633.876 |  |  |  |  | 569.598 | 7.1767 | 595.816 | 13.341 | 797.061 | 1000.1
[8 empty] | 406.641 | 1000.1 | [6 empty] | 406.641 | 53.6697 | 595.816 | 1000.1 |  |  |  |  | 520.574 | 8.1812 | 595.816 | 39.6007
[16 empty] | 406.641 | 152.604 | [6 empty] | 478.632 | 9.5434 | 595.816 | 123.205
[16 empty] | 406.641 | 372.729 | [6 empty] | 433.084 | 11.3231 | 595.816 | 315.719
[16 empty] | 406.641 | 690.112 | [6 empty] | 416.102 | 12.4142 | 595.816 | 633.876
[16 empty] | 406.641 | 1000.1 | [6 empty] | 406.641 | 13.3277 | 595.816 | 1000.1
[24 empty] | 406.641 | 16.5245
[24 empty] | 406.641 | 53.6697
[24 empty] | 406.641 | 152.604
[24 empty] | 406.641 | 372.729
[24 empty] | 406.641 | 690.112
[24 empty] | 406.641 | 1000.1