## Points
Vista Underground Distribution Switchgear Overcurrent Control 2.0
S&C Standard ("E") Speed, Main Interrupter Speed, Tap Interrupter Speed, "T" Speed (TCC 680-9-3)
Curves are plotted in 680-211
Maximum Trip Times - Dated October 25, 2021
7E |  | 10E |  | 13E |  | 15E |  | 20E |  | 25E |  | 30E |  | 40E |  | 50E |  | 65E |  | 80E |  | 100E |  | 125E |  | 150E |  | 175E |  | 200E |  | 250E |  | 300E |  | 400E |  | 8T |  | 10T |  | 12T |  | 15T |  | 20T |  | 25T |  | 30T |  | 40T |  | 50T |  | 65T |  | 80T |  | 100T |  | 140T |  | 200T |  | 15Tap |  | 20Tap |  | 25Tap |  | 30Tap |  | 40Tap |  | 50Tap |  | 65Tap |  | 80Tap |  | 100Tap |  | 150Tap |  | 200Tap |  | 250Tap |  | 300Tap |  | 350Tap |  | 400Tap |  | 25Main |  | 30Main |  | 40Main |  | 50Main |  | 65Main |  | 80Main |  | 100Main |  | 150Main |  | 200Main |  | 250Main |  | 300Main |  | 350Main |  | 400Main |  | 450Main |  | 500Main |  | 600Main |  | 700Main |  | 800Main
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
17.5225 | 111.8768 | 23.7069 | 118.2059 | 29.8914 | 121.916 | 34.0143 | 279.2439 | 45.3524 | 279.2439 | 55.5789 | 26.9855 | 67.6072 | 696.7135 | 90.6978 | 281.4942 | 112.4729 | 1605.2161 | 146.4539 | 819.5794 | 180.6772 | 479.1934 | 226.0396 | 416.4039 | 333.4737 | 115.8085 | 406.9591 | 1615.3968 | 474.3941 | 1662.8744 | 546.5978 | 252.3019 | 657.6757 | 424.1758 | 780.3262 | 229.5154 | 1021.1787 | 211.3229 | 19.2851 | 232.6691 | 23.9131 | 272.498 | 30.9633 | 301.2904 | 38.2774 | 670.9521 | 48.1869 | 685.224 | 61.1351 | 709.4827 | 79.8203 | 668.6928 | 101.1359 | 685.6911 | 128.4607 | 675.7704 | 161.7948 | 676.2171 | 200.0042 | 695.8708 | 243.5425 | 764.0825 | 340.1432 | 788.682 | 544.2291 | 788.682 | 18.5533 | 43.3984 | 23.7069 | 45.3051 | 28.8606 | 46.5309 | 34.0143 | 106.9469 | 45.3524 | 106.9469 | 56.2159 | 781.9267 | 73.3653 | 200.1886 | 90.3947 | 165.3721 | 114.0191 | 67.5249 | 168.7021 | 630.3053 | 226.0418 | 159.2083 | 284.3463 | 80.6087 | 341.9461 | 69.0055 | 397.4384 | 92.3708 | 453.5075 | 107.3554 | 28.8606 | 44.1934 | 34.0143 | 101.5883 | 45.3524 | 101.5883 | 56.6905 | 101.5883 | 73.6977 | 101.5883 | 90.7048 | 101.5883 | 112.4918 | 531.4604 | 168.7377 | 531.4604 | 226.661 | 106.5043 | 284.4442 | 74.554 | 337.3976 | 605.9736 | 393.918 | 419.5977 | 451.4556 | 192.0752 | 507.6603 | 210.321 | 562.5412 | 493.0023 | 681.9437 | 81.1131 | 786.8256 | 912.7277 | 898.865 | 1449.8189
17.6842 | 75.6491 | 23.9495 | 77.2201 | 30.2147 | 78.0928 | 34.6946 | 90.3242 | 46.2595 | 90.3242 | 56.2449 | 24.0848 | 68.0822 | 232.3625 | 91.695 | 130.7006 | 112.8108 | 581.0949 | 147.7778 | 220.056 | 181.9466 | 213.6696 | 228.3116 | 163.3041 | 333.8572 | 108.3406 | 409.4079 | 274.4061 | 480.9257 | 132.4569 | 552.6437 | 104.0288 | 674.3249 | 65.3756 | 792.1201 | 82.6186 | 1043.8927 | 61.7661 | 19.5032 | 146.5726 | 24.1516 | 179.5901 | 31.2253 | 209.118 | 39.043 | 217.0262 | 49.1507 | 221.6425 | 62.3578 | 229.4892 | 81.4167 | 216.2953 | 103.1586 | 221.7936 | 131.0299 | 218.5846 | 165.0307 | 218.7291 | 204.0043 | 225.0863 | 248.4134 | 247.15 | 346.946 | 255.3629 | 555.1136 | 255.3629 | 18.6947 | 31.1198 | 23.9495 | 29.6164 | 29.1032 | 32.4353 | 34.6946 | 34.6325 | 46.2595 | 34.6325 | 56.8739 | 80.0928 | 74.5391 | 48.8887 | 91.6263 | 52.015 | 115.8421 | 32.727 | 171.5166 | 56.808 | 230.2502 | 41.0907 | 290.3244 | 30.2473 | 349.6138 | 27.304 | 405.8397 | 31.7144 | 464.3265 | 30.636 | 29.1032 | 30.8029 | 34.6946 | 32.8902 | 46.2595 | 32.8902 | 57.8243 | 32.8902 | 75.1716 | 32.8902 | 92.5189 | 32.8902 | 114.7149 | 45.6758 | 170.0716 | 101.5883 | 234.3987 | 22.3834 | 291.9595 | 24.4888 | 341.2625 | 75.7498 | 396.3957 | 114.681 | 455.8808 | 66.0072 | 513.0326 | 64.581 | 570.2255 | 63.1854 | 702.1778 | 23.1988 | 797.5779 | 67.2285 | 910.1975 | 74.7033
17.873 | 54.715 | 24.1811 | 57.8469 | 30.4892 | 60.5897 | 35.0653 | 65.7258 | 46.6863 | 68.2719 | 57.1521 | 20.9766 | 68.629 | 131.097 | 92.3621 | 95.9893 | 113.7167 | 213.6488 | 148.9649 | 132.4399 | 183.2249 | 136.8004 | 230.6059 | 100.8088 | 335.4947 | 84.8939 | 413.5229 | 114.0414 | 485.7589 | 78.4178 | 556.2947 | 76.6031 | 683.52 | 44.2856 | 798.1137 | 62.1687 | 1056 | 44.6417 | 19.6708 | 113.8164 | 24.3914 | 133.3555 | 31.5826 | 147.1089 | 39.4105 | 163.2313 | 49.6168 | 166.3925 | 62.9558 | 171.8022 | 82.2568 | 158.8726 | 104.1853 | 164.4732 | 132.3789 | 160.6542 | 166.6358 | 163.1623 | 206.0463 | 166.6638 | 250.9137 | 182.7372 | 350.4505 | 188.7308 | 560.64 | 189.4467 | 18.9243 | 21.2569 | 24.1811 | 22.2004 | 29.4378 | 22.8071 | 35.0653 | 25.2165 | 46.6863 | 26.1911 | 57.7032 | 37.3526 | 74.88 | 40.025 | 92.16 | 40.025 | 117.12 | 23.966 | 173.6084 | 33.7166 | 233.7347 | 25.3107 | 293.9621 | 21.8265 | 355.7053 | 18.3428 | 410.5768 | 23.0546 | 469.1874 | 23.1053 | 29.4378 | 21.6565 | 35.0653 | 23.9453 | 46.6863 | 24.8711 | 58.4084 | 24.3074 | 75.8905 | 24.6513 | 93.4737 | 24.1703 | 115.8063 | 31.3999 | 172.6282 | 39.5832 | 240 | 14.1071 | 298.0042 | 15.7832 | 346.9738 | 32.7987 | 402.2393 | 42.004 | 462.1933 | 33.9139 | 524.5085 | 25.8081 | 578.0144 | 33.3496 | 711.5116 | 17.3681 | 810.1665 | 32.0283 | 921.6746 | 37.8905
18.0884 | 41.4456 | 24.4547 | 44.4984 | 30.8211 | 47.9726 | 35.3885 | 53.0111 | 47.1847 | 53.0111 | 57.7011 | 19.4416 | 68.9179 | 106.4506 | 93.0108 | 76.175 | 114.287 | 152.5393 | 149.5579 | 110.3605 | 183.9158 | 114.4306 | 232.0168 | 81.4788 | 337.2119 | 69.1274 | 414.72 | 97.3796 | 488.1853 | 65.004 | 559.8745 | 60.7875 | 692.7805 | 33.3148 | 804.0906 | 49.787 | 1068.1807 | 34.8178 | 19.9074 | 86.2732 | 24.6568 | 103.5017 | 31.9326 | 113.7088 | 39.8239 | 127.3723 | 50.1337 | 130.0816 | 63.6049 | 134.6868 | 83.045 | 126.9433 | 105.2218 | 130.1703 | 133.6505 | 128.2869 | 168.3313 | 128.3718 | 208.0843 | 132.1028 | 253.3816 | 145.052 | 353.8849 | 150.0244 | 566.2159 | 150.0244 | 19.0989 | 17.0905 | 24.4547 | 17.0905 | 29.7095 | 18.3428 | 35.3885 | 20.3493 | 47.1847 | 20.3493 | 58.3074 | 26.8122 | 75.3184 | 32.4286 | 92.7779 | 31.5557 | 118.3887 | 18.8955 | 175.6828 | 23.9565 | 237.1498 | 18.3234 | 297.6631 | 16.9673 | 361.76 | 13.7792 | 415.2525 | 18.1209 | 473.975 | 18.5685 | 29.7095 | 17.4158 | 35.3885 | 19.3218 | 47.1847 | 19.3218 | 58.9808 | 19.3218 | 76.6751 | 19.3218 | 94.3693 | 19.3218 | 116.9381 | 23.6632 | 173.6084 | 32.0201 | 245.5156 | 10.2841 | 304.0802 | 11.5718 | 351.9663 | 21.8277 | 407.7474 | 26.1702 | 462.4869 | 33.1591 | 529.2126 | 20.6536 | 582.2653 | 26.4648 | 720.75 | 13.8755 | 819.1326 | 23.252 | 931.9074 | 26.2387
18.2304 | 35.6744 | 24.6647 | 37.7402 | 31.099 | 40.7885 | 35.7726 | 43.0212 | 47.6968 | 43.0212 | 58.1902 | 18.2432 | 69.2495 | 87.4945 | 93.5747 | 64.5214 | 114.7958 | 121.4081 | 150.161 | 94.3064 | 184.6966 | 96.5212 | 233.3905 | 68.5961 | 338.7284 | 59.3469 | 416.0118 | 84.0833 | 490.6409 | 55.3702 | 563.7726 | 49.5688 | 703.3263 | 25.9022 | 808.5221 | 43.345 | 1079.5453 | 28.8324 | 20.0642 | 74.2257 | 24.8792 | 87.0045 | 32.2143 | 95.9984 | 40.2189 | 105.0809 | 50.6274 | 107.4571 | 64.2695 | 110.0865 | 83.8737 | 104.6201 | 106.3074 | 106.6405 | 135.0063 | 105.4186 | 169.9705 | 106.2497 | 210.1895 | 108.6068 | 255.8653 | 119.9196 | 357.4232 | 123.6633 | 571.8568 | 123.7413 | 19.3028 | 13.8809 | 24.6647 | 14.5033 | 30.0266 | 14.9035 | 35.7726 | 16.525 | 47.6968 | 16.525 | 58.8848 | 21.077 | 76.1937 | 23.4666 | 93.6758 | 24.0941 | 120.4547 | 14.0086 | 177.5495 | 18.9666 | 240.2021 | 14.6619 | 301.44 | 13.7975 | 367.6295 | 11.0701 | 423.2084 | 13.236 | 484.2442 | 13.0113 | 30.0266 | 14.1488 | 35.7726 | 15.6891 | 47.6968 | 15.6891 | 59.6211 | 15.6891 | 77.4063 | 16.0572 | 95.2926 | 15.9869 | 119.6463 | 14.8048 | 174.5179 | 27.1782 | 251.1158 | 8.0296 | 311.2421 | 8.762 | 356.9258 | 16.3314 | 413.3184 | 18.8821 | 470.0923 | 20.9743 | 533.9481 | 17.1731 | 586.5224 | 21.9058 | 731.4189 | 11.2342 | 828.1252 | 18.2004 | 942.1065 | 20.0363
18.3916 | 30.7648 | 24.96 | 31.034 | 31.4274 | 34.6053 | 36.0963 | 37.0762 | 48.1284 | 37.0761 | 58.7116 | 17.1104 | 69.6253 | 72.7459 | 94.0396 | 57.2607 | 115.2052 | 104.2255 | 151.1747 | 75.6965 | 185.7347 | 79.8287 | 234.6442 | 59.9024 | 340.261 | 51.8935 | 417.4484 | 72.9664 | 494.1474 | 45.6508 | 567.7678 | 41.6376 | 713.8782 | 21.1276 | 812.9844 | 38.3241 | 1090.8502 | 24.584 | 20.3116 | 60.6973 | 25.1621 | 72.1924 | 32.5389 | 81.2669 | 40.6203 | 89.0845 | 51.1364 | 90.9795 | 64.877 | 94.2004 | 84.7059 | 88.7846 | 107.3262 | 91.0415 | 136.3236 | 89.7243 | 171.6979 | 89.7836 | 212.246 | 92.3931 | 258.4493 | 101.4498 | 360.9626 | 105.0354 | 577.5402 | 105.0354 | 19.5032 | 11.6981 | 24.96 | 11.9359 | 30.3158 | 12.7088 | 36.0963 | 14.2491 | 48.1284 | 14.2491 | 59.52 | 17.0323 | 76.9835 | 18.7464 | 94.6321 | 19.2129 | 122.5505 | 11.0619 | 179.4022 | 15.6923 | 243.1912 | 12.2398 | 305.1873 | 11.6198 | 373.4227 | 9.2498 | 431.0814 | 10.4121 | 494.5804 | 9.9554 | 30.3158 | 12.0642 | 36.0963 | 13.5272 | 48.1284 | 13.5272 | 60.1604 | 13.5272 | 78.2086 | 13.5272 | 96.2567 | 13.5272 | 122.2737 | 10.8023 | 176.7411 | 19.8 | 256.6858 | 6.5687 | 318.3607 | 7.0302 | 363.3853 | 12.2543 | 416.5389 | 16.2421 | 478.6564 | 14.7681 | 536.9937 | 15.4838 | 593.9874 | 16.7886 | 742.1346 | 9.4111 | 841.2632 | 13.7752 | 954.0379 | 15.6599
18.595 | 26.1641 | 25.158 | 27.6966 | 31.721 | 30.439 | 36.48 | 31.8123 | 48.6063 | 32.114 | 59.3063 | 15.9702 | 69.9454 | 63.5741 | 94.4842 | 51.6718 | 115.7053 | 88.8096 | 152.1262 | 63.8022 | 186.7386 | 68.3374 | 235.9715 | 52.7815 | 342.1642 | 44.8612 | 418.9341 | 64.163 | 497.5583 | 38.9528 | 572.9684 | 34.4121 | 728.0842 | 16.8683 | 819.1326 | 33.0197 | 1103.4947 | 21.0728 | 20.4655 | 54.4505 | 25.3768 | 63.8513 | 32.8585 | 70.5108 | 41.0274 | 77.0682 | 51.6379 | 78.935 | 65.4821 | 82.266 | 85.5916 | 76.3589 | 108.4295 | 78.4863 | 137.7347 | 77.2754 | 173.4063 | 77.747 | 214.3326 | 80.1359 | 261.0189 | 87.858 | 364.5979 | 90.8533 | 583.2758 | 91.0249 | 19.6889 | 10.1963 | 25.158 | 10.6581 | 30.6271 | 11.109 | 36.48 | 12.2339 | 48.6063 | 12.3494 | 60.0753 | 14.5669 | 77.7095 | 15.7997 | 96 | 14.8595 | 123.5874 | 10.0084 | 181.9958 | 12.611 | 248.4884 | 9.4357 | 309.8274 | 9.7008 | 379.7558 | 7.8232 | 435.9411 | 9.1865 | 503.2421 | 8.2949 | 30.6271 | 10.5447 | 36.48 | 11.6131 | 48.6063 | 11.7228 | 60.7326 | 11.7896 | 79.0232 | 11.6467 | 97.2126 | 11.7228 | 123.0821 | 9.963 | 178.9642 | 15.5346 | 263.04 | 5.4205 | 322.0547 | 6.3672 | 369.8379 | 9.777 | 419.8489 | 14.1888 | 480.6456 | 13.8095 | 540.1029 | 14.0642 | 601.3998 | 13.5986 | 753.9537 | 7.9659 | 854.4718 | 11.0387 | 966.0132 | 12.818
18.7958 | 22.7618 | 25.3642 | 24.8841 | 32.0337 | 26.9497 | 36.8182 | 28.2433 | 49.0909 | 28.2433 | 59.7221 | 15.2543 | 70.2316 | 57.1136 | 94.8897 | 47.4307 | 116.13 | 78.8636 | 153.0947 | 54.957 | 188.0589 | 57.4014 | 237.2716 | 47.2494 | 344.0248 | 39.5878 | 420.5811 | 56.5687 | 500.8168 | 34.1358 | 578.08 | 29.3592 | 742.2691 | 13.9955 | 825.2718 | 28.9838 | 1116.2253 | 18.3967 | 20.7158 | 46.5659 | 25.6674 | 55.1302 | 33.1453 | 62.9648 | 41.4327 | 67.8615 | 52.1591 | 69.3049 | 66.1746 | 71.7585 | 86.4 | 67.633 | 109.4727 | 69.3522 | 139.05 | 68.3488 | 175.1319 | 68.394 | 216.491 | 70.3818 | 263.6182 | 77.2809 | 368.1819 | 80.0956 | 589.091 | 80.0956 | 19.9074 | 8.8458 | 25.3642 | 9.5812 | 30.9221 | 9.916 | 36.8182 | 10.8674 | 49.0909 | 10.8674 | 60.6316 | 12.7088 | 78.4397 | 13.6272 | 97.431 | 11.9825 | 124.7158 | 9.0619 | 184.6077 | 10.5069 | 253.8079 | 7.6437 | 314.5335 | 8.293 | 386.0069 | 6.7763 | 440.7677 | 8.2163 | 511.8754 | 7.0969 | 30.9221 | 9.4117 | 36.8182 | 10.3153 | 49.0909 | 10.3153 | 61.3636 | 10.3153 | 79.7727 | 10.3153 | 98.1818 | 10.3153 | 123.8699 | 9.2579 | 180.6821 | 13.2988 | 269.3067 | 4.609 | 325.7504 | 5.8132 | 377.7347 | 7.8108 | 425.6337 | 11.6007 | 489.765 | 10.6173 | 544.9768 | 12.2866 | 610.3579 | 11.0338 | 765.7512 | 6.8943 | 869.8611 | 8.9386 | 978.7958 | 10.7178
18.9669 | 20.4658 | 25.6612 | 21.6781 | 32.3554 | 24.0817 | 37.1874 | 25.1353 | 49.6168 | 24.9464 | 60.2026 | 14.4986 | 70.5778 | 50.837 | 95.4947 | 42.2314 | 116.8168 | 66.7215 | 153.9626 | 48.8518 | 189.3719 | 49.4732 | 238.5815 | 42.7136 | 346.4084 | 34.3786 | 422.2988 | 50.3306 | 504.0688 | 30.3641 | 583.8821 | 25.1309 | 756.9853 | 11.859 | 832.3705 | 25.3695 | 1129.1621 | 16.2725 | 20.8748 | 42.6014 | 25.8843 | 49.9771 | 33.5157 | 55.2495 | 41.8358 | 60.5936 | 52.6484 | 62.1206 | 66.7958 | 64.3152 | 87.3095 | 59.8607 | 110.5516 | 61.8379 | 140.4632 | 60.7365 | 176.8421 | 61.0437 | 218.6779 | 62.5851 | 266.2737 | 68.7416 | 371.8737 | 71.3193 | 594.9979 | 71.3193 | 20.0826 | 7.9882 | 25.6612 | 8.3536 | 31.2397 | 8.8803 | 37.1874 | 9.6774 | 49.6168 | 9.6051 | 61.148 | 11.3539 | 79.2253 | 11.858 | 99.2337 | 9.6051 | 127.1242 | 7.5241 | 187.3516 | 8.9227 | 258.4926 | 6.5319 | 320.2358 | 7.0374 | 391.2758 | 6.0814 | 447.9663 | 7.0867 | 521.8358 | 6.0694 | 31.2397 | 8.4281 | 37.1874 | 9.1851 | 49.6168 | 9.1164 | 61.9453 | 9.2408 | 80.5389 | 9.2279 | 99.1326 | 9.2198 | 126.1137 | 7.6909 | 182.2989 | 11.7007 | 279.9078 | 3.6572 | 329.5326 | 5.3335 | 385.5434 | 6.4952 | 431.4138 | 9.7939 | 492.2485 | 9.9822 | 549.7714 | 10.9182 | 619.2328 | 9.2774 | 781.2379 | 5.8457 | 885.3482 | 7.4832 | 991.5607 | 9.1956
19.3463 | 16.6735 | 25.8695 | 19.8628 | 32.64 | 21.9916 | 37.5546 | 22.6334 | 50.0727 | 22.6334 | 60.9347 | 13.4726 | 70.9389 | 45.5879 | 96.0352 | 38.4443 | 117.415 | 58.7951 | 154.9137 | 43.5216 | 190.5853 | 43.8402 | 240.1011 | 38.4109 | 348.8746 | 30.2336 | 424.4211 | 44.2716 | 507.8905 | 26.8528 | 589.7582 | 21.904 | 771.7904 | 10.2533 | 839.4211 | 22.5524 | 1142.1918 | 14.5597 | 21.12 | 37.6078 | 26.1726 | 44.3998 | 33.8526 | 49.6567 | 42.2614 | 54.3823 | 53.2023 | 55.5391 | 67.4981 | 57.5053 | 88.128 | 54.1992 | 111.6622 | 55.5769 | 141.831 | 54.7728 | 178.6345 | 54.809 | 220.8208 | 56.402 | 268.8906 | 61.9307 | 375.5455 | 64.2541 | 600.8728 | 64.2541 | 20.4843 | 6.5184 | 25.8695 | 7.6584 | 31.5284 | 8.104 | 37.5546 | 8.7194 | 50.0727 | 8.7194 | 61.9453 | 9.736 | 80.0893 | 10.3644 | 101.0459 | 7.9864 | 129.549 | 6.4104 | 190.1756 | 7.7104 | 263.2208 | 5.6841 | 325.856 | 6.1111 | 396.5714 | 5.5069 | 455.2283 | 6.2126 | 531.8072 | 5.2896 | 31.5284 | 7.6909 | 37.5546 | 8.2753 | 50.0727 | 8.2753 | 62.5909 | 8.2753 | 81.3682 | 8.2753 | 100.1455 | 8.2753 | 128.3429 | 6.5687 | 183.9158 | 10.4366 | 299.2382 | 2.6234 | 333.3114 | 4.9234 | 394.8126 | 5.3952 | 435.9411 | 8.7188 | 500.624 | 8.2927 | 555.8905 | 9.5489 | 627.4358 | 8.0747 | 796.7476 | 5.0611 | 900.8842 | 6.4183 | 1009.5158 | 7.6468
19.7332 | 13.9704 | 26.1744 | 17.6722 | 33.0025 | 19.783 | 37.8947 | 20.7059 | 50.5263 | 20.7059 | 61.6033 | 12.6475 | 71.2159 | 42.2308 | 96.4042 | 36.2162 | 117.9284 | 53.3307 | 155.8211 | 39.3958 | 191.8496 | 39.1631 | 241.7039 | 34.6996 | 351.4611 | 26.8178 | 426.5429 | 39.4943 | 511.6865 | 24.0675 | 596.0084 | 19.2479 | 785.1789 | 9.1165 | 846.2147 | 20.3563 | 1157.8611 | 12.9055 | 21.2923 | 34.7153 | 26.402 | 40.7423 | 34.186 | 45.0948 | 42.6442 | 49.751 | 53.76 | 50.1343 | 68.2105 | 51.874 | 89.0274 | 49.052 | 112.7747 | 50.4128 | 143.2926 | 49.5247 | 180.3789 | 49.8086 | 223.0232 | 51.1563 | 271.6295 | 56.0593 | 379.2505 | 58.3679 | 606.9221 | 58.2582 | 20.894 | 5.4705 | 26.1744 | 6.8195 | 31.8645 | 7.3497 | 37.8947 | 7.9813 | 50.5263 | 7.9813 | 62.6942 | 8.5755 | 81.1453 | 8.969 | 103.4779 | 6.4909 | 132.3789 | 5.4516 | 193.1116 | 6.7449 | 267.9916 | 5.0165 | 333.2716 | 5.1932 | 405.2211 | 4.7609 | 463.2253 | 5.46 | 538.6105 | 4.8578 | 31.8645 | 6.9747 | 37.8947 | 7.5744 | 50.5263 | 7.5744 | 63.2589 | 7.4612 | 82.1558 | 7.5305 | 101.1537 | 7.5033 | 131.4695 | 5.4357 | 185.4747 | 9.445 | 317.2224 | 2.054 | 338.8295 | 4.421 | 404.069 | 4.6009 | 440.5265 | 7.8392 | 510.8028 | 6.8586 | 561.9543 | 8.4841 | 635.6031 | 7.1421 | 813.2716 | 4.4182 | 916.3812 | 5.6099 | 1027.3935 | 6.5337
20.1279 | 11.9478 | 26.4758 | 15.9144 | 33.3474 | 18.0407 | 38.3056 | 18.7572 | 51.0742 | 18.7572 | 62.5516 | 11.6261 | 71.6463 | 37.8756 | 96.8066 | 34.0553 | 118.4765 | 48.4974 | 156.7326 | 35.9523 | 193.3137 | 34.8299 | 243.3347 | 31.5749 | 354.1468 | 23.983 | 429.9789 | 33.5866 | 516.0758 | 21.4716 | 602.2746 | 17.142 | 798.4816 | 8.1979 | 852.9601 | 18.5485 | 1173.4605 | 11.5781 | 21.7181 | 29.0936 | 26.6779 | 37.0327 | 34.56 | 40.8422 | 43.1066 | 45.0687 | 54.2663 | 46.0274 | 68.848 | 47.6569 | 89.8906 | 44.917 | 113.8954 | 46.0588 | 144.6677 | 45.3924 | 182.2072 | 45.4224 | 225.2372 | 46.7425 | 274.2684 | 51.3244 | 383.0564 | 53.3067 | 612.8903 | 53.3067 | 21.3119 | 4.6862 | 26.4758 | 6.1462 | 32.1347 | 6.8338 | 38.3056 | 7.235 | 51.0742 | 7.235 | 63.36 | 7.7463 | 82.1157 | 7.9717 | 105.8923 | 5.4555 | 135.198 | 4.733 | 195.9892 | 5.9988 | 272.7103 | 4.487 | 340.7623 | 4.4972 | 413.8742 | 4.1832 | 471.135 | 4.8678 | 545.4396 | 4.4861 | 32.1347 | 6.4848 | 38.3056 | 6.8658 | 51.0742 | 6.8658 | 63.8427 | 6.8658 | 82.9956 | 6.8658 | 102.1484 | 6.8658 | 134.6533 | 4.609 | 189.1705 | 7.6909 | 349.9395 | 1.4452 | 344.3016 | 4.0094 | 422.161 | 3.5492 | 446.8547 | 6.8718 | 513.3294 | 6.5733 | 568.5221 | 7.5617 | 643.7053 | 6.4004 | 829.8648 | 3.9104 | 935.4442 | 4.8464 | 1045.9958 | 5.6625
20.5304 | 10.379 | 26.6979 | 14.8162 | 33.6625 | 16.6845 | 38.7032 | 17.1767 | 51.5368 | 17.3635 | 63.543 | 10.7098 | 72.1477 | 33.7926 | 97.4147 | 31.2251 | 119.04 | 44.3462 | 157.5452 | 33.3401 | 194.7486 | 31.3991 | 244.8664 | 29.0979 | 356.5137 | 21.9259 | 433.4224 | 29.1776 | 520.4602 | 19.3672 | 609.8526 | 15.1185 | 824.447 | 6.8228 | 861.1705 | 16.7248 | 1186.56 | 10.6472 | 22.1525 | 24.8871 | 26.93 | 34.1586 | 34.8697 | 37.856 | 43.5537 | 41.2734 | 54.7705 | 42.526 | 69.5242 | 43.8401 | 90.7453 | 41.4261 | 114.9979 | 42.4194 | 146.1221 | 41.6777 | 184.0168 | 41.7469 | 227.4695 | 42.9676 | 276.9853 | 47.1814 | 386.9305 | 48.9472 | 619.0484 | 48.9734 | 21.7381 | 4.0776 | 26.6979 | 5.7255 | 32.5018 | 6.2343 | 38.7032 | 6.6297 | 51.5368 | 6.7013 | 64.0136 | 7.0691 | 83.8737 | 6.6188 | 108.2274 | 4.7138 | 143.1636 | 3.4157 | 198.9726 | 5.3742 | 285.738 | 3.4521 | 358.9533 | 3.3653 | 430.35 | 3.381 | 493.2009 | 3.7128 | 570.5768 | 3.4804 | 32.5018 | 5.9157 | 38.7032 | 6.2911 | 51.5368 | 6.359 | 64.4716 | 6.3181 | 83.8737 | 6.2807 | 103.1747 | 6.3079 | 139.9545 | 3.6572 | 192.7722 | 6.495 | 384.3951 | 1.0812 | 354.1335 | 3.4255 | 437.3996 | 2.9597 | 453.134 | 6.1137 | 527.4564 | 5.3186 | 575.0065 | 6.8219 | 651.7243 | 5.7979 | 857.1685 | 3.2765 | 954.4628 | 4.2579 | 1064.5214 | 4.9895
20.941 | 9.1278 | 27.2318 | 12.679 | 33.9537 | 15.5919 | 39.0718 | 15.9205 | 52.0957 | 15.9205 | 64.3705 | 10.0412 | 72.4547 | 31.69 | 98.0733 | 28.6315 | 119.667 | 40.4719 | 158.4505 | 30.8307 | 196.3453 | 28.2758 | 246.3663 | 27.01 | 358.781 | 20.2511 | 436.2442 | 26.3252 | 524.3621 | 17.802 | 617.521 | 13.4871 | 852.1075 | 5.7595 | 869.3214 | 15.2245 | 1199.5604 | 9.8523 | 22.5956 | 21.6241 | 27.1832 | 31.6652 | 35.2674 | 34.5774 | 43.9688 | 38.2528 | 55.3517 | 39.0665 | 70.225 | 40.4496 | 91.6884 | 38.124 | 116.1734 | 39.0931 | 147.561 | 38.5275 | 185.8513 | 38.553 | 229.7419 | 39.6735 | 279.7538 | 43.5624 | 390.7176 | 45.2938 | 625.1481 | 45.2938 | 22.1729 | 3.5921 | 27.2318 | 4.9067 | 32.8421 | 5.7611 | 39.0718 | 6.1485 | 52.0957 | 6.1485 | 64.9768 | 6.2543 | 85.6071 | 5.655 | 110.5098 | 4.1516 | 151.4415 | 2.6194 | 201.9972 | 4.8549 | 302.4128 | 2.6373 | 376.9375 | 2.6707 | 454.6469 | 2.6113 | 516.3006 | 2.9499 | 604.3555 | 2.6463 | 32.8421 | 5.4665 | 39.0718 | 5.8343 | 52.0957 | 5.8343 | 65.1196 | 5.8343 | 84.6555 | 5.8343 | 104.1914 | 5.8343 | 149.6185 | 2.6234 | 197.3558 | 5.4053 | 415.6861 | 0.8692 | 365.7339 | 2.9119 | 456.9846 | 2.4244 | 458.1726 | 5.6115 | 537.5291 | 4.67 | 583.5789 | 6.0326 | 660.6821 | 5.2404 | 887.2212 | 2.7683 | 999.3306 | 3.2884 | 1084.9011 | 4.4044
21.3599 | 8.1075 | 27.7765 | 11.021 | 34.3358 | 14.3466 | 39.5116 | 14.6304 | 52.6484 | 14.6992 | 65.2167 | 9.4324 | 72.8 | 29.61 | 98.6274 | 26.7505 | 120.4547 | 36.448 | 159.2882 | 28.8131 | 197.89 | 25.7755 | 247.8221 | 25.2415 | 361.4653 | 18.5609 | 439.0937 | 23.9459 | 528.3257 | 16.4421 | 624.7074 | 12.2349 | 878.9366 | 4.982 | 876.7326 | 14.0668 | 1215.36 | 9.0237 | 23.0475 | 19.0214 | 27.4686 | 29.2318 | 35.5671 | 32.4384 | 44.3621 | 35.7504 | 55.8821 | 36.3408 | 70.9389 | 37.4673 | 92.5642 | 35.4721 | 117.3221 | 36.2846 | 149.0526 | 35.7022 | 187.7558 | 35.6897 | 232.0168 | 36.8196 | 282.5432 | 40.4085 | 394.6105 | 42.0396 | 631.3768 | 42.0396 | 22.6163 | 3.196 | 27.7765 | 4.2713 | 33.1518 | 5.3859 | 39.5116 | 5.6544 | 52.6484 | 5.6807 | 66.0345 | 5.5432 | 87.6126 | 4.8261 | 114.7305 | 3.3855 | 161.8737 | 1.9994 | 211.907 | 3.6625 | 322.7592 | 2.0227 | 399.547 | 2.0996 | 478.2702 | 2.1199 | 542.7362 | 2.369 | 635.7654 | 2.1451 | 33.1518 | 5.1104 | 39.5116 | 5.3652 | 52.6484 | 5.3902 | 65.7853 | 5.4053 | 85.4905 | 5.4193 | 105.1958 | 5.4281 | 156.9761 | 2.1401 | 202.0339 | 4.601 | 453.7654 | 0.6937 | 380.1244 | 2.4435 | 479.2228 | 1.998 | 463.1894 | 5.1835 | 544.8104 | 4.2868 | 592.0581 | 5.4059 | 669.6518 | 4.7752 | 918.3276 | 2.3756 | 1046.307 | 2.635 | 1105.2963 | 3.935
21.7871 | 7.2603 | 28.332 | 9.6983 | 34.6611 | 13.4245 | 39.8532 | 13.756 | 53.1376 | 13.756 | 66.1895 | 8.8109 | 73.2632 | 27.2026 | 99.1581 | 25.1586 | 121.2321 | 33.1718 | 160.2695 | 26.7505 | 199.5789 | 23.486 | 249.2968 | 23.6627 | 364.2033 | 17.0947 | 443.7221 | 20.8576 | 532.3453 | 15.2516 | 631.8882 | 11.1853 | 902.9912 | 4.4301 | 884.2255 | 13.0547 | 1231.1515 | 8.3155 | 23.5084 | 16.8989 | 28.018 | 25.4094 | 35.8737 | 30.4929 | 44.8481 | 33.0523 | 56.4587 | 33.7553 | 71.6295 | 34.9504 | 93.5222 | 32.941 | 118.4968 | 33.7783 | 150.5122 | 33.2896 | 189.5684 | 33.3116 | 234.3368 | 34.2798 | 285.3489 | 37.64 | 398.5319 | 39.1787 | 637.6511 | 39.1787 | 23.0687 | 2.867 | 28.332 | 3.7642 | 33.4484 | 5.0673 | 39.8532 | 5.3194 | 53.1376 | 5.3194 | 67.0989 | 4.9666 | 89.6188 | 4.198 | 118.7633 | 2.8642 | 171.9479 | 1.6104 | 221.1486 | 2.9576 | 341.0569 | 1.6568 | 428.8305 | 1.6237 | 507.4903 | 1.7037 | 568.1558 | 1.9783 | 673.0522 | 1.736 | 33.4484 | 4.8079 | 39.8532 | 5.0472 | 53.1376 | 5.0472 | 66.422 | 5.0472 | 86.3486 | 5.0472 | 106.2752 | 5.0472 | 174.9692 | 1.4452 | 211.0799 | 3.5493 | 490.1919 | 0.5762 | 397.9764 | 2.0249 | 504.7024 | 1.6514 | 472.32 | 4.5441 | 561.5608 | 3.595 | 601.1621 | 4.857 | 692.3947 | 3.883 | 951.5171 | 2.0553 | 1095.4922 | 2.1665 | 1151.2334 | 3.1573
22.2228 | 6.5464 | 28.8986 | 8.6194 | 35.0225 | 12.5212 | 40.2189 | 12.9218 | 53.6589 | 12.8677 | 67.0686 | 8.3102 | 73.7525 | 25.0393 | 99.84 | 23.3613 | 121.9705 | 30.5475 | 161.2101 | 25.0231 | 201.2836 | 21.5386 | 250.8145 | 22.2237 | 367.5284 | 15.5869 | 448.4121 | 18.4245 | 536.3102 | 14.2277 | 640.8758 | 10.0881 | 930.4905 | 3.9193 | 892.2947 | 12.1081 | 1261.0641 | 7.2219 | 23.9786 | 15.1365 | 28.5784 | 22.3601 | 36.2785 | 28.2345 | 45.2716 | 30.9935 | 56.9937 | 31.6456 | 72.3537 | 32.6287 | 94.4842 | 30.717 | 119.6463 | 31.6201 | 151.9832 | 31.1477 | 191.4947 | 31.0883 | 236.6653 | 32.0395 | 288.2021 | 35.1656 | 402.4926 | 36.638 | 644.0084 | 36.6304 | 23.53 | 2.5896 | 28.8986 | 3.3506 | 33.8148 | 4.7193 | 40.2189 | 4.9997 | 53.6589 | 4.979 | 68.0675 | 4.532 | 94.3086 | 3.194 | 126.0264 | 2.222 | 184.9456 | 1.2719 | 233.2082 | 2.3437 | 366.0596 | 1.3137 | 454.0789 | 1.3458 | 538.4966 | 1.3973 | 608.2138 | 1.5538 | 712.3943 | 1.433 | 33.8148 | 4.4777 | 40.2189 | 4.7439 | 53.6589 | 4.7242 | 67.0989 | 4.7124 | 87.2084 | 4.7196 | 107.3179 | 4.7242 | 192.1976 | 1.0812 | 218.6998 | 2.9597 | 529.9069 | 0.4828 | 418.8441 | 1.6757 | 530.4966 | 1.396 | 481.4515 | 4.0376 | 569.0582 | 3.3486 | 610.2513 | 4.4046 | 716.6572 | 3.2218 | 998.338 | 1.7172 | 1163.8765 | 1.7217 | 1194.0826 | 2.652
22.6673 | 5.9371 | 29.4766 | 7.7235 | 35.723 | 11.0575 | 40.6503 | 12.0514 | 54.2003 | 12.0514 | 69.2495 | 7.2659 | 74.5768 | 22.06 | 100.556 | 21.7207 | 122.6961 | 28.3317 | 162.1895 | 23.4379 | 203.1158 | 19.7619 | 252.6316 | 20.7059 | 370.8183 | 14.3255 | 454.1305 | 16.1067 | 540.1263 | 13.3584 | 649.8313 | 9.1783 | 956.9127 | 3.5181 | 900.2856 | 11.2902 | 1290.3987 | 6.3796 | 24.4582 | 13.6511 | 29.1499 | 19.8731 | 37.0041 | 24.8799 | 45.7451 | 28.9565 | 57.5879 | 29.5725 | 73.0621 | 30.6194 | 95.3926 | 28.859 | 120.8668 | 29.5926 | 153.5225 | 29.1645 | 193.3597 | 29.1838 | 239.0235 | 30.032 | 291.0558 | 32.9758 | 406.5026 | 34.3618 | 650.4041 | 34.3618 | 24.0006 | 2.3527 | 29.4766 | 3.0069 | 34.4911 | 4.1821 | 40.6503 | 4.6662 | 54.2003 | 4.6662 | 70.4452 | 3.7162 | 101.2259 | 2.3277 | 134.8623 | 1.7246 | 195.639 | 1.0754 | 246.1825 | 1.8991 | 396.179 | 1.0375 | 488.3755 | 1.08 | 577.3719 | 1.1281 | 649.7524 | 1.2573 | 758.5493 | 1.1787 | 34.4911 | 3.968 | 40.6503 | 4.4273 | 54.2003 | 4.4273 | 67.7504 | 4.4273 | 88.0756 | 4.4273 | 108.4007 | 4.4273 | 207.843 | 0.8692 | 228.4917 | 2.4244 | 596.8441 | 0.3748 | 445.4286 | 1.3625 | 568.2825 | 1.1283 | 497.3049 | 3.3706 | 580.6433 | 3.0237 | 629.0036 | 3.6828 | 749.5521 | 2.6006 | 1054.047 | 1.4262 | 1230.091 | 1.4248 | 1242.4129 | 2.2353
23.1206 | 5.4115 | 30.0661 | 6.9682 | 36.4374 | 9.8585 | 41.4633 | 10.6752 | 55.2843 | 10.6752 | 71.7879 | 6.315 | 75.4685 | 19.5214 | 101.8611 | 19.2337 | 123.5874 | 25.9998 | 163.1564 | 22.0504 | 204.9385 | 18.2507 | 254.3504 | 19.4411 | 373.2884 | 13.4988 | 459.7635 | 14.3111 | 543.8711 | 12.5977 | 671.6338 | 7.4938 | 998.9571 | 3.0101 | 908.9684 | 10.5114 | 1327.0474 | 5.5499 | 24.9473 | 12.3832 | 29.7329 | 17.8076 | 37.7441 | 22.1428 | 46.66 | 25.6497 | 58.7396 | 26.1953 | 74.5233 | 27.1227 | 97.3005 | 25.5633 | 123.2841 | 26.2132 | 156.5929 | 25.8339 | 197.2269 | 25.851 | 243.804 | 26.6023 | 296.877 | 29.21 | 414.6326 | 30.4716 | 663.4122 | 30.4716 | 24.4806 | 2.1483 | 30.0661 | 2.717 | 35.1809 | 3.7401 | 41.4633 | 4.1387 | 55.2843 | 4.1387 | 73.3642 | 3.0252 | 108.0866 | 1.8106 | 146.0303 | 1.3248 | 211.0844 | 0.8698 | 260.4196 | 1.5587 | 423.8973 | 0.8603 | 530.202 | 0.8588 | 616.4839 | 0.9359 | 689.4457 | 1.0543 | 804.6253 | 0.9933 | 35.1809 | 3.5488 | 41.4633 | 3.9269 | 55.2843 | 3.9269 | 69.1054 | 3.9269 | 89.8371 | 3.9269 | 110.5687 | 3.9269 | 226.8822 | 0.6937 | 238.9895 | 2.0182 | 665.953 | 0.3016 | 469.2753 | 1.1593 | 597.4537 | 0.977 | 509.9368 | 2.9699 | 596.0008 | 2.6731 | 644.2856 | 3.2399 | 781.5056 | 2.1776 | 1123.3717 | 1.1682 | 1312.5458 | 1.163 | 1300.8219 | 1.8678
23.583 | 4.9539 | 30.6675 | 6.3582 | 37.1662 | 8.8591 | 42.2925 | 9.5415 | 56.39 | 9.5415 | 74.4193 | 5.5401 | 76.3958 | 17.4147 | 103.1016 | 17.3245 | 124.5502 | 23.8621 | 164.2105 | 20.7059 | 206.7537 | 16.9485 | 256.1684 | 18.2536 | 375.6703 | 12.7829 | 464.64 | 13.0382 | 548.8168 | 11.71 | 688.6354 | 6.5316 | 1037.6489 | 2.6441 | 917.5551 | 9.8342 | 1355.2037 | 5.0345 | 25.4463 | 11.2893 | 30.3276 | 16.0696 | 38.499 | 19.8687 | 47.5932 | 22.9258 | 59.9144 | 23.4135 | 76.0138 | 24.2423 | 99.2465 | 22.8486 | 125.7498 | 23.4294 | 159.7248 | 23.0904 | 201.1715 | 23.1057 | 248.6801 | 23.7772 | 302.8145 | 26.108 | 422.9253 | 27.2664 | 676.6804 | 27.2664 | 24.9703 | 1.9702 | 30.6675 | 2.4828 | 35.8846 | 3.3705 | 42.2925 | 3.7041 | 56.39 | 3.7041 | 73.6699 | 2.9664 | 114.6938 | 1.477 | 156.8238 | 1.0692 | 226.8032 | 0.7205 | 277.2522 | 1.2743 | 453.5553 | 0.7207 | 579.8174 | 0.6808 | 671.3859 | 0.7456 | 727.0115 | 0.9086 | 852.9079 | 0.8465 | 35.8846 | 3.1982 | 42.2925 | 3.5146 | 56.39 | 3.5146 | 70.4875 | 3.5146 | 91.6338 | 3.5146 | 112.7801 | 3.5146 | 245.0965 | 0.5762 | 251.2391 | 1.6773 | 752.4268 | 0.2406 | 495.9476 | 0.9877 | 632.7263 | 0.836 | 529.4884 | 2.4979 | 605.456 | 2.492 | 667.5587 | 2.7274 | 825.0917 | 1.7691 | 1188.5369 | 0.9917 | 1400.1037 | 0.9653 | 1347.8306 | 1.643
24.0547 | 4.5522 | 31.2808 | 5.8487 | 37.9095 | 8.0138 | 43.1384 | 8.5922 | 57.5178 | 8.5922 | 77.1472 | 4.8977 | 77.379 | 15.6085 | 104.0842 | 16.0489 | 125.4063 | 22.2253 | 165.2918 | 19.4796 | 208.6612 | 15.7564 | 257.9363 | 17.2233 | 378.1389 | 12.1128 | 469.5209 | 11.9621 | 553.7497 | 10.9345 | 703.2504 | 5.8688 | 1106.2289 | 2.1553 | 931.5032 | 8.8921 | 1388.1287 | 4.5311 | 25.9552 | 10.3368 | 30.9341 | 14.7202 | 39.269 | 17.9506 | 48.5451 | 20.6448 | 61.1127 | 21.084 | 77.534 | 21.8304 | 101.2314 | 20.5753 | 128.2648 | 21.0983 | 162.9193 | 20.7931 | 205.1949 | 20.8068 | 253.6537 | 21.4116 | 308.8708 | 23.5104 | 431.3838 | 24.5817 | 690.214 | 24.5817 | 25.4697 | 1.8137 | 31.2808 | 2.2872 | 36.6023 | 3.0569 | 43.1384 | 3.3401 | 57.5178 | 3.3401 | 77.5249 | 2.3701 | 121.8246 | 1.2212 | 167.0681 | 0.8954 | 246.2425 | 0.5873 | 295.6911 | 1.0521 | 487.8186 | 0.6011 | 631.4424 | 0.5525 | 711.664 | 0.6435 | 767.4219 | 0.7862 | 917.3539 | 0.7004 | 36.6023 | 2.9009 | 43.1384 | 3.1694 | 57.5178 | 3.1694 | 71.8973 | 3.1694 | 93.4665 | 3.1694 | 115.0357 | 3.1694 | 264.9539 | 0.4828 | 265.6674 | 1.3889 | 825.6515 | 0.207 | 520.4113 | 0.8656 | 673.5835 | 0.7119 | 543.5043 | 2.2362 | 620.7735 | 2.2417 | 683.7767 | 2.4505 | 874.7515 | 1.4457 | 1276.0015 | 0.818 | 1492.1691 | 0.8129 | 1409.7233 | 1.412
24.5358 | 4.1971 | 31.9064 | 5.3987 | 38.6677 | 7.2902 | 44.0011 | 7.7862 | 58.6682 | 7.7862 | 81.5907 | 4.0936 | 78.4168 | 14.0518 | 105.0793 | 14.9254 | 126.3065 | 20.7204 | 166.4337 | 18.3256 | 210.8968 | 14.5453 | 259.7053 | 16.2967 | 380.5857 | 11.5108 | 475.4526 | 10.8602 | 557.6084 | 10.3919 | 723.2188 | 5.1386 | 1182.8756 | 1.7657 | 945.499 | 8.1015 | 1414.751 | 4.1855 | 26.4743 | 9.5006 | 31.5528 | 13.5375 | 40.0544 | 16.3123 | 49.516 | 18.7083 | 62.335 | 19.1062 | 79.0847 | 19.7826 | 103.256 | 18.6453 | 130.8301 | 19.1192 | 166.1777 | 18.8426 | 209.2988 | 18.8551 | 258.7267 | 19.4031 | 315.0482 | 21.305 | 440.0114 | 22.3015 | 704.0183 | 22.3015 | 25.979 | 1.6754 | 31.9064 | 2.1143 | 37.3343 | 2.7877 | 44.0011 | 3.0309 | 58.6682 | 3.0309 | 82.0067 | 1.9038 | 131.4698 | 0.9781 | 180.8239 | 0.7268 | 270.9907 | 0.4685 | 318.7097 | 0.8546 | 517.5578 | 0.5216 | 676.3146 | 0.4703 | 760.6635 | 0.5474 | 827.1092 | 0.6497 | 994.9187 | 0.5732 | 37.3343 | 2.6458 | 44.0011 | 2.8763 | 58.6682 | 2.8763 | 73.3352 | 2.8763 | 95.3358 | 2.8763 | 117.3364 | 2.8763 | 298.4226 | 0.3748 | 284.1418 | 1.1283 | 900.3466 | 0.1814 | 544.7582 | 0.768 | 708.9006 | 0.6282 | 562.5768 | 1.9509 | 634.5921 | 2.0521 | 716.6572 | 2.0216 | 924.5024 | 1.2133 | 1369.901 | 0.683 | 1577.0615 | 0.7059 | 1482.176 | 1.2059
25.0265 | 3.8812 | 32.5446 | 4.9985 | 39.441 | 6.6641 | 44.8812 | 7.0939 | 59.8416 | 7.0939 | 86.0317 | 3.4932 | 79.4967 | 12.7162 | 106.0042 | 14.0058 | 127.1242 | 19.5121 | 167.6217 | 17.2548 | 213.0897 | 13.5156 | 261.5723 | 15.4151 | 383.2926 | 10.907 | 481.4071 | 9.9303 | 561.5563 | 9.8864 | 747.4835 | 4.4456 | 1287.8198 | 1.3935 | 971.3744 | 6.9371 | 1452.0111 | 3.7734 | 27.0038 | 8.7613 | 32.1839 | 12.4931 | 40.8555 | 14.8977 | 50.5063 | 17.0448 | 63.5817 | 17.4074 | 80.6664 | 18.0236 | 105.3211 | 16.9874 | 133.4467 | 17.4192 | 169.5012 | 17.1672 | 213.4848 | 17.1786 | 263.9013 | 17.6778 | 321.3492 | 19.4107 | 448.8117 | 20.3423 | 718.0987 | 20.3423 | 26.4986 | 1.5522 | 32.5446 | 1.9605 | 38.081 | 2.5542 | 44.8812 | 2.7653 | 59.8416 | 2.7653 | 86.7476 | 1.5623 | 142.5689 | 0.7855 | 197.143 | 0.5862 | 293.3001 | 0.3917 | 340.3155 | 0.7199 | 553.8375 | 0.4458 | 716.8695 | 0.412 | 821.5391 | 0.4573 | 875.8131 | 0.565 | 1068.9832 | 0.4838 | 38.081 | 2.4247 | 44.8812 | 2.6246 | 59.8416 | 2.6246 | 74.8019 | 2.6246 | 97.2425 | 2.6246 | 119.6831 | 2.6246 | 332.9765 | 0.3016 | 298.7268 | 0.977 | 1005.6475 | 0.155 | 570.9358 | 0.6826 | 743.6374 | 0.5613 | 579.8885 | 1.7436 | 647.2524 | 1.9022 | 735.6018 | 1.8314 | 968.9578 | 1.0556 | 1460.0011 | 0.586 | 1686.0352 | 0.6003 | 1556.7263 | 1.0432
25.527 | 3.5986 | 33.1955 | 4.6407 | 40.2298 | 6.1175 | 45.7788 | 6.4932 | 61.0384 | 6.4932 | 90.8051 | 2.9985 | 80.5389 | 11.6358 | 106.9878 | 13.1371 | 127.9594 | 18.4084 | 168.7579 | 16.3354 | 215.4442 | 12.5513 | 263.4442 | 14.6167 | 385.9513 | 10.369 | 489.4989 | 8.8818 | 566.7032 | 9.2924 | 772.5618 | 3.8859 | 1379.8252 | 1.1617 | 1010.0073 | 5.6777 | 1481.3457 | 3.4961 | 27.5439 | 8.1036 | 32.8276 | 11.5649 | 41.6726 | 13.6647 | 51.5164 | 15.6015 | 64.8533 | 15.9334 | 82.2797 | 16.4975 | 107.4276 | 15.549 | 136.1156 | 15.9443 | 172.8912 | 15.7136 | 217.7544 | 15.724 | 269.1793 | 16.181 | 327.7761 | 17.7671 | 457.7879 | 18.6418 | 732.4606 | 18.6418 | 27.0286 | 1.4419 | 33.1955 | 1.8228 | 38.8426 | 2.35 | 45.7788 | 2.5347 | 61.0384 | 2.5347 | 91.7631 | 1.3027 | 154.1449 | 0.644 | 217.6372 | 0.4643 | 319.7668 | 0.3242 | 369.49 | 0.5868 | 593.203 | 0.3821 | 779.8971 | 0.342 | 886.3642 | 0.3854 | 943.9306 | 0.4737 | 1154.5526 | 0.406 | 38.8426 | 2.2312 | 45.7788 | 2.4062 | 61.0384 | 2.4062 | 76.298 | 2.4062 | 99.1874 | 2.4062 | 122.0768 | 2.4062 | 376.2129 | 0.2406 | 316.3631 | 0.836 | 1116.2526 | 0.1353 | 600.2471 | 0.6048 | 790.9384 | 0.4881 | 604.012 | 1.513 | 667.153 | 1.7026 | 758.2069 | 1.6426 | 1020.8641 | 0.9121 | 1531.8425 | 0.5246 | 1796.9029 | 0.5182 | 1635.0259 | 0.9096
26.0376 | 3.3447 | 33.8594 | 4.3189 | 41.0344 | 5.6365 | 46.6944 | 5.9675 | 62.2592 | 5.9675 | 94.322 | 2.7051 | 81.6724 | 10.6406 | 109.1492 | 11.5411 | 128.9432 | 17.251 | 169.8159 | 15.5585 | 217.8295 | 11.6966 | 265.2605 | 13.9126 | 388.8505 | 9.8362 | 497.5583 | 8.0239 | 571.7562 | 8.7703 | 800.0801 | 3.3999 | 1515.8157 | 0.917 | 1045.9825 | 4.8303 | 1517.3275 | 3.2011 | 28.0947 | 7.5152 | 33.4841 | 10.7351 | 42.506 | 12.5815 | 52.5467 | 14.3384 | 66.1504 | 14.6434 | 83.9253 | 15.1618 | 109.5761 | 14.2901 | 138.8379 | 14.6534 | 176.3491 | 14.4414 | 222.1095 | 14.4509 | 274.5629 | 14.8709 | 334.3317 | 16.3286 | 466.9437 | 17.1529 | 747.1099 | 17.1529 | 27.5692 | 1.3428 | 33.8594 | 1.6991 | 39.6195 | 2.1699 | 46.6944 | 2.3328 | 62.2592 | 2.3328 | 96.7663 | 1.1098 | 166.3144 | 0.5358 | 240.2622 | 0.3717 | 342.8643 | 0.2795 | 398.6678 | 0.49 | 658.9295 | 0.3041 | 846.6908 | 0.2868 | 969.3269 | 0.3171 | 1007.8664 | 0.4081 | 1241.7926 | 0.3457 | 39.6195 | 2.0608 | 46.6944 | 2.215 | 62.2592 | 2.215 | 77.8239 | 2.215 | 101.1711 | 2.215 | 124.5183 | 2.215 | 412.8263 | 0.207 | 336.7917 | 0.7119 | 1254.6351 | 0.1179 | 633.042 | 0.5345 | 848.1825 | 0.4195 | 629.1403 | 1.3246 | 678.567 | 1.6042 | 794.6656 | 1.4022 | 1076.6754 | 0.7918 | 1591.7325 | 0.4814 | 1867.102 | 0.4757 | 1724.4513 | 0.7897
26.5583 | 3.1153 | 34.5365 | 4.0284 | 41.8551 | 5.2103 | 47.6283 | 5.5039 | 63.5043 | 5.5039 | 100.0546 | 2.3194 | 84.2438 | 8.8819 | 111.2424 | 10.3047 | 129.8936 | 16.2561 | 171.1832 | 14.6515 | 222.2302 | 10.3729 | 268.0926 | 12.9327 | 391.7849 | 9.3464 | 522.023 | 6.1586 | 580.9779 | 7.9455 | 826.9236 | 3.0188 | 1670.2141 | 0.7259 | 1084.3241 | 4.1469 | 1551.0861 | 2.9613 | 28.6566 | 6.9862 | 34.1538 | 9.9894 | 43.3561 | 11.6228 | 53.5977 | 13.2244 | 67.4734 | 13.5057 | 85.6038 | 13.9839 | 111.7676 | 13.1799 | 141.6147 | 13.5149 | 179.876 | 13.3194 | 226.5517 | 13.3282 | 280.0541 | 13.7156 | 341.0183 | 15.06 | 476.2825 | 15.8394 | 762.0521 | 15.8394 | 28.1206 | 1.2531 | 34.5365 | 1.5872 | 40.4119 | 2.01 | 47.6283 | 2.1547 | 63.5043 | 2.1547 | 102.5732 | 0.9403 | 178.514 | 0.4543 | 258.9634 | 0.3158 | 369.5489 | 0.2391 | 428.8083 | 0.4148 | 711.2125 | 0.2589 | 923.3937 | 0.2394 | 1044.7264 | 0.2705 | 1062.7817 | 0.3628 | 1334.2349 | 0.2962 | 40.4119 | 1.9095 | 47.6283 | 2.0464 | 63.5043 | 2.0464 | 79.3804 | 2.0464 | 103.1946 | 2.0464 | 127.0087 | 2.0464 | 450.1733 | 0.1814 | 354.4503 | 0.6282 | 1378.1699 | 0.1067 | 662.6578 | 0.4824 | 896.385 | 0.3739 | 650.5371 | 1.1942 | 694.1577 | 1.4851 | 824.2313 | 1.249 | 1136.7229 | 0.6902 | 1716.0202 | 0.4094 | 2025.508 | 0.3995 | 1813.0797 | 0.6956
27.0895 | 2.9073 | 35.2273 | 3.7649 | 42.6922 | 4.8303 | 48.5808 | 5.0923 | 64.7744 | 5.0923 | 105.8174 | 2.016 | 86.3765 | 7.7872 | 113.8301 | 9.0771 | 130.9642 | 15.2571 | 172.5537 | 13.8365 | 226.4931 | 9.33 | 270.8896 | 12.0833 | 398.1042 | 8.4316 | 554.858 | 4.6322 | 590.3485 | 7.2422 | 858.0934 | 2.6603 | 1856.9816 | 0.5676 | 1130.8315 | 3.5189 | 1582.4216 | 2.7649 | 29.2298 | 6.5085 | 34.8369 | 9.3161 | 44.2233 | 10.7691 | 54.6696 | 12.2355 | 68.8228 | 12.4957 | 87.3159 | 12.9381 | 114.003 | 12.1943 | 144.447 | 12.5042 | 183.4736 | 12.3233 | 231.0828 | 12.3315 | 285.6552 | 12.6899 | 347.8387 | 13.9338 | 485.8082 | 14.6727 | 777.2931 | 14.6727 | 28.683 | 1.1718 | 35.2273 | 1.4857 | 41.2201 | 1.8673 | 48.5808 | 1.9965 | 64.7744 | 1.9965 | 108.957 | 0.7991 | 193.6126 | 0.3785 | 282.0409 | 0.2636 | 405.6061 | 0.1979 | 469.8744 | 0.339 | 773.7459 | 0.2177 | 998.2616 | 0.2042 | 1096.3857 | 0.2447 | 1144.9263 | 0.3088 | 1462.1854 | 0.2446 | 41.2201 | 1.7745 | 48.5808 | 1.8967 | 64.7744 | 1.8967 | 80.968 | 1.8967 | 105.2584 | 1.8967 | 129.5488 | 1.8967 | 502.8237 | 0.155 | 370.7071 | 0.5652 | 1566.9049 | 0.0946 | 705.5736 | 0.4211 | 929.3325 | 0.3475 | 674.7729 | 1.0715 | 711.2203 | 1.3715 | 857.5765 | 1.1084 | 1192.6264 | 0.6143 | 1844.2257 | 0.353 | 2165.47 | 0.3484 | 1910.2473 | 0.6128
27.6313 | 2.7181 | 35.9318 | 3.525 | 43.5461 | 4.4896 | 49.5524 | 4.7247 | 66.0699 | 4.7247 | 111.1316 | 1.7903 | 89.0961 | 6.7062 | 115.5509 | 8.399 | 131.9878 | 14.404 | 174.2147 | 12.9554 | 230.8372 | 8.4478 | 275.2592 | 10.9454 | 402.9096 | 7.8398 | 599.27 | 3.4078 | 602.8771 | 6.463 | 884.2255 | 2.412 | 2102.1403 | 0.4295 | 1182.8756 | 2.9897 | 1625.7287 | 2.5277 | 29.8144 | 6.0752 | 35.5336 | 8.7057 | 45.1077 | 10.0046 | 55.763 | 11.3522 | 70.1993 | 11.5937 | 89.0622 | 12.0041 | 116.283 | 11.314 | 147.3359 | 11.6016 | 187.143 | 11.4337 | 235.7044 | 11.4413 | 291.3683 | 11.7738 | 354.7954 | 12.9279 | 495.5244 | 13.6302 | 792.839 | 13.6302 | 29.2566 | 1.0977 | 35.9318 | 1.3933 | 42.0445 | 1.7391 | 49.5524 | 1.8552 | 66.0699 | 1.8552 | 116.5835 | 0.6718 | 205.4487 | 0.3325 | 307.9589 | 0.22 | 445.442 | 0.1643 | 510.7727 | 0.2836 | 855.0164 | 0.1782 | 1102.0032 | 0.1677 | 1197.8365 | 0.2043 | 1217.6842 | 0.271 | 1599.7551 | 0.2036 | 42.0445 | 1.6534 | 49.5524 | 1.7631 | 66.0699 | 1.7631 | 82.5874 | 1.7631 | 107.3636 | 1.7631 | 132.1398 | 1.7631 | 558.1258 | 0.1353 | 395.4687 | 0.4881 | 1759.3182 | 0.0861 | 751.9231 | 0.3689 | 989.3437 | 0.3072 | 708.7461 | 0.9329 | 743.6863 | 1.1932 | 891.3407 | 0.9919 | 1272.3511 | 0.5285 | 1961.4205 | 0.3125 | 2295.8471 | 0.3105 | 2021.0462 | 0.5373
28.1839 | 2.5453 | 36.6505 | 3.3058 | 44.417 | 4.1827 | 50.5435 | 4.3946 | 67.3913 | 4.3946 | 118.1208 | 1.5509 | 91.5344 | 5.9466 | 118.4765 | 7.4354 | 132.9853 | 13.6543 | 175.864 | 12.178 | 235.2646 | 7.6924 | 279.6988 | 9.9754 | 408.1818 | 7.2727 | 647.2369 | 2.6047 | 616.2872 | 5.7826 | 915.7221 | 2.1608 | 2355.9693 | 0.3346 | 1227.4722 | 2.6359 | 1656.9085 | 2.3774 | 30.4106 | 5.6868 | 36.2443 | 8.15 | 46.0099 | 9.3165 | 56.8783 | 10.5592 | 71.6033 | 10.7838 | 90.8435 | 11.1655 | 118.6087 | 10.5236 | 150.2826 | 10.7911 | 190.8859 | 10.635 | 240.4185 | 10.642 | 297.1957 | 10.9513 | 361.8913 | 12.0248 | 505.4348 | 12.6937 | 808.6957 | 12.6937 | 29.8418 | 1.03 | 36.6505 | 1.3088 | 42.8854 | 1.6234 | 50.5435 | 1.7282 | 67.3913 | 1.7282 | 125.1338 | 0.5648 | 220.7474 | 0.2852 | 337.4622 | 0.183 | 490.2093 | 0.1365 | 560.0478 | 0.2341 | 918.6523 | 0.1548 | 1190.1777 | 0.1444 | 1284.2284 | 0.1777 | 1311.8289 | 0.2323 | 1760.4803 | 0.1682 | 42.8854 | 1.5441 | 50.5435 | 1.643 | 67.3913 | 1.643 | 84.2391 | 1.643 | 109.5109 | 1.643 | 134.7826 | 1.643 | 627.3176 | 0.1179 | 424.0918 | 0.4195 | 1967.132 | 0.0796 | 786.1046 | 0.3373 | 1036.8808 | 0.281 | 738.2307 | 0.8359 | 749.9321 | 1.1635 | 930.3093 | 0.8818 | 1346.1188 | 0.4661 | 2127.8653 | 0.2678 | 2485.4329 | 0.2672 | 2153.9577 | 0.466
28.7476 | 2.387 | 37.3835 | 3.105 | 45.3053 | 3.9049 | 51.5544 | 4.0969 | 68.7391 | 4.0969 | 124.4257 | 1.3766 | 94.2278 | 5.2703 | 120.9909 | 6.7541 | 133.9831 | 12.9738 | 178.3439 | 11.1593 | 239.7776 | 7.0384 | 284.4942 | 9.0908 | 416.0118 | 6.557 | 708.8984 | 1.959 | 628.7368 | 5.2578 | 952.1407 | 1.9208 | 2661.6758 | 0.2575 | 1299.4691 | 2.196 | 1695.458 | 2.2115 | 31.0189 | 5.3605 | 36.9692 | 7.6425 | 46.9301 | 8.6943 | 58.0158 | 9.8437 | 73.0353 | 10.0531 | 92.6604 | 10.409 | 120.9809 | 9.8106 | 153.2883 | 10.06 | 194.7036 | 9.9144 | 245.2269 | 9.921 | 303.1396 | 10.2093 | 369.1292 | 11.2101 | 515.5435 | 11.8485 | 824.8697 | 11.8485 | 30.4386 | 0.9692 | 37.3835 | 1.2313 | 43.7431 | 1.5186 | 51.5544 | 1.6136 | 68.7391 | 1.6136 | 130.4327 | 0.5119 | 240.5265 | 0.2385 | 372.1465 | 0.151 | 544.5544 | 0.1118 | 616.988 | 0.1924 | 1032.3123 | 0.1237 | 1294.8005 | 0.1229 | 1401.5111 | 0.1497 | 1419.7541 | 0.1979 | 1937.3528 | 0.1397 | 43.7431 | 1.4451 | 51.5544 | 1.5348 | 68.7391 | 1.5348 | 85.9239 | 1.5348 | 111.7011 | 1.5348 | 137.4783 | 1.5348 | 689.085 | 0.1067 | 435.5712 | 0.3966 | 2220.2456 | 0.0741 | 828.188 | 0.3046 | 1111.8306 | 0.2471 | 777.0204 | 0.7324 | 772.175 | 1.0675 | 971.9969 | 0.7855 | 1379.7999 | 0.4418 | 2327.7989 | 0.2287 | 2654.402 | 0.2375 | 2302.1315 | 0.4042
29.3225 | 2.2417 | 38.1311 | 2.9204 | 46.2114 | 3.6526 | 52.5854 | 3.8271 | 70.1139 | 3.8271 | 132.7826 | 1.1903 | 97.1946 | 4.6694 | 123.6821 | 6.1388 | 136.553 | 11.4803 | 181.9466 | 9.9317 | 245.8479 | 6.3018 | 289.9509 | 8.2438 | 425.2645 | 5.8612 | 765.64 | 1.5697 | 643.3652 | 4.7413 | 991.9897 | 1.7051 | 3089.3336 | 0.188 | 1388.1287 | 1.8021 | 1740.1213 | 2.0422 | 31.6392 | 5.0584 | 37.7085 | 7.1776 | 47.8687 | 8.1295 | 59.1761 | 9.1955 | 74.496 | 9.3911 | 94.5136 | 9.7236 | 123.4005 | 9.1645 | 156.354 | 9.3975 | 198.5977 | 9.2615 | 250.1314 | 9.2677 | 309.2024 | 9.537 | 376.5118 | 10.4719 | 525.8544 | 11.0822 | 841.3671 | 11.0822 | 31.0474 | 0.9175 | 38.1311 | 1.16 | 44.6179 | 1.4233 | 52.5854 | 1.5097 | 70.1139 | 1.5097 | 138.8596 | 0.4429 | 265.8048 | 0.1947 | 410.0392 | 0.1253 | 606.1844 | 0.0917 | 693.2979 | 0.1529 | 1132.323 | 0.104 | 1442.7264 | 0.1003 | 1551.9461 | 0.1231 | 1541.3619 | 0.168 | 2098.9763 | 0.1199 | 44.6179 | 1.3551 | 52.5854 | 1.4367 | 70.1139 | 1.4367 | 87.6424 | 1.4367 | 113.9351 | 1.4367 | 140.2278 | 1.4367 | 783.453 | 0.0946 | 464.6663 | 0.3475 | 2534.8578 | 0.0694 | 876.8044 | 0.2734 | 1198.6328 | 0.218 | 812.7365 | 0.6553 | 794.7147 | 0.9835 | 1018.7354 | 0.6975 | 1482.8301 | 0.3796 | 2517.4343 | 0.2018 | 2867.6019 | 0.2095 | 2531.5968 | 0.333
29.909 | 2.1078 | 38.8938 | 2.7503 | 47.1357 | 3.4225 | 53.6371 | 3.5817 | 71.5162 | 3.5817 | 142.4099 | 1.0216 | 100.8581 | 4.0774 | 126.5588 | 5.5829 | 139.033 | 10.3133 | 185.4369 | 8.9581 | 251.0657 | 5.7706 | 295.5133 | 7.5163 | 433.8559 | 5.3254 | 826.9236 | 1.2743 | 657.0187 | 4.3349 | 1036.6107 | 1.5074 | 3511.1889 | 0.144 | 1497.7304 | 1.4555 | 1796.7006 | 1.8568 | 32.272 | 4.7783 | 38.4627 | 6.7503 | 48.8261 | 7.6148 | 60.3597 | 8.6059 | 75.986 | 8.7889 | 96.4038 | 9.1001 | 125.8685 | 8.5769 | 159.4811 | 8.7949 | 202.5696 | 8.6677 | 255.134 | 8.6734 | 315.3864 | 8.9255 | 384.042 | 9.8004 | 536.3715 | 10.3849 | 858.1944 | 10.3849 | 31.6683 | 0.8694 | 38.8938 | 1.0943 | 45.5103 | 1.3362 | 53.6371 | 1.4151 | 71.5162 | 1.4151 | 150.2899 | 0.371 | 290.5 | 0.1633 | 454.5549 | 0.1033 | 679.7245 | 0.0745 | 775.8073 | 0.1232 | 1239.5955 | 0.088 | 1627.7437 | 0.0805 | 1697.2062 | 0.1041 | 1699.7022 | 0.1389 | 2299.5112 | 0.1011 | 45.5103 | 1.273 | 53.6371 | 1.3474 | 71.5162 | 1.3474 | 89.3953 | 1.3474 | 116.2138 | 1.3474 | 143.0324 | 1.3474 | 879.6591 | 0.0861 | 494.6718 | 0.3072 | 2799.0114 | 0.0666 | 936.5608 | 0.2424 | 1286.7244 | 0.1951 | 845.6626 | 0.5959 | 811.865 | 0.927 | 1065.4962 | 0.6252 | 1580.3035 | 0.3339 | 2748.2264 | 0.1768 | 3051.7895 | 0.1903 | 2734.9561 | 0.2868
30.5071 | 1.9881 | 39.6716 | 2.5931 | 48.0784 | 3.212 | 54.7099 | 3.3577 | 72.9465 | 3.3577 | 152.4308 | 0.8835 | 104.7645 | 3.5772 | 130.1526 | 5.0023 | 141.4173 | 9.3803 | 189.3719 | 8.0504 | 255.6254 | 5.3675 | 301.1812 | 6.8852 | 440.4131 | 4.9723 | 898.487 | 1.0292 | 675.6755 | 3.8704 | 1082.1577 | 1.3415 | 4087.587 | 0.1053 | 1596.7276 | 1.227 | 1864.4291 | 1.6691 | 32.9175 | 4.518 | 39.232 | 6.3566 | 49.8026 | 7.1442 | 61.5669 | 8.0677 | 77.5057 | 8.2393 | 98.3319 | 8.531 | 128.3859 | 8.0405 | 162.6707 | 8.2449 | 206.621 | 8.1256 | 260.2367 | 8.131 | 321.6942 | 8.3673 | 391.7228 | 9.1875 | 547.0989 | 9.748 | 875.3583 | 9.748 | 32.3017 | 0.8245 | 39.6716 | 1.0335 | 46.4205 | 1.2565 | 54.7099 | 1.3288 | 72.9465 | 1.3288 | 159.8084 | 0.3246 | 322.2528 | 0.1335 | 498.6836 | 0.0871 | 755.0794 | 0.0621 | 859.0292 | 0.1018 | 1368.3729 | 0.0737 | 1808.0559 | 0.0668 | 1850.2777 | 0.0888 | 1858.7742 | 0.1172 | 2547.3721 | 0.0838 | 46.4205 | 1.1979 | 54.7099 | 1.266 | 72.9465 | 1.266 | 91.1832 | 1.266 | 118.5381 | 1.266 | 145.893 | 1.266 | 983.5655 | 0.0796 | 518.4404 | 0.281 | 3061.8028 | 0.0645 | 1001.3164 | 0.2172 | 1374.1056 | 0.1768 | 889.1687 | 0.5305 | 843.0134 | 0.8376 | 1135.1565 | 0.5391 | 1746.8433 | 0.2754 | 2990.7931 | 0.1569 | 3324.6316 | 0.1678 | 3004.4251 | 0.2413
31.1173 | 1.8844 | 40.4651 | 2.4476 | 49.04 | 3.0188 | 55.8041 | 3.1526 | 74.4055 | 3.1526 | 163.3198 | 0.7644 | 109.2583 | 3.1207 | 135.736 | 4.2852 | 143.8417 | 8.5778 | 193.1969 | 7.315 | 260.5285 | 4.9859 | 308.1886 | 6.2253 | 447.0693 | 4.6544 | 986.055 | 0.8188 | 693.473 | 3.5026 | 1128.575 | 1.201 | 4772.8977 | 0.0767 | 1693.7684 | 1.0544 | 1932.769 | 1.5094 | 33.5758 | 4.2757 | 40.0166 | 5.9929 | 50.7986 | 6.7126 | 62.7982 | 7.5749 | 79.0558 | 7.736 | 100.2986 | 8.0099 | 130.9536 | 7.5493 | 165.9242 | 7.7413 | 210.7534 | 7.6292 | 265.4415 | 7.6343 | 328.1281 | 7.8562 | 399.5573 | 8.6263 | 558.0409 | 9.1644 | 892.8654 | 9.1644 | 32.9477 | 0.7826 | 40.4651 | 0.9772 | 47.3489 | 1.1832 | 55.8041 | 1.2496 | 74.4055 | 1.2496 | 173.1429 | 0.2737 | 355.009 | 0.1112 | 558.6068 | 0.0711 | 837.9153 | 0.0536 | 943.393 | 0.0857 | 1535.8838 | 0.0604 | 2039.9232 | 0.0555 | 2017.155 | 0.076 | 2013.9789 | 0.1009 | 2829.5131 | 0.0695 | 47.3489 | 1.1288 | 55.8041 | 1.1914 | 74.4055 | 1.1914 | 93.0068 | 1.1914 | 120.9089 | 1.1914 | 148.8109 | 1.1914 | 1110.1228 | 0.0741 | 559.4516 | 0.2443 | 3314.5011 | 0.063 | 1080.5346 | 0.1928 | 1473.5555 | 0.1601 | 929.8479 | 0.4799 | 848.2637 | 0.824 | 1211.039 | 0.4665 | 1889.0739 | 0.2389 | 3234.4401 | 0.1414 | 3551.9565 | 0.1531 | 3182.0089 | 0.2196
31.7396 | 1.7875 | 41.2744 | 2.3126 | 50.0208 | 2.841 | 56.9202 | 2.9642 | 75.8936 | 2.9642 | 177.4536 | 0.6441 | 114.287 | 2.7171 | 141.1338 | 3.7448 | 146.3071 | 7.8804 | 197.6921 | 6.592 | 266.8568 | 4.5586 | 314.4146 | 5.727 | 454.7336 | 4.3304 | 1077.8381 | 0.6631 | 711.7396 | 3.1838 | 1184.065 | 1.0618 | 5629.1247 | 0.0548 | 1782.3835 | 0.9284 | 2029.8321 | 1.3219 | 34.2473 | 4.0497 | 40.8169 | 5.6562 | 51.8146 | 6.3157 | 64.0542 | 7.1222 | 80.6369 | 7.2737 | 102.3045 | 7.5312 | 133.5727 | 7.0982 | 169.2426 | 7.2786 | 214.9685 | 7.1733 | 270.7503 | 7.1781 | 334.6906 | 7.3867 | 407.5484 | 8.1108 | 569.2017 | 8.628 | 910.7228 | 8.628 | 33.6067 | 0.7434 | 41.2744 | 0.925 | 48.2959 | 1.1157 | 56.9202 | 1.1769 | 75.8936 | 1.1769 | 184.73 | 0.2392 | 405.1837 | 0.0871 | 616.6767 | 0.06 | 929.8378 | 0.0469 | 1041.1756 | 0.0718 | 1690.1578 | 0.053 | 2256.4871 | 0.0487 | 2249.9985 | 0.0628 | 2199.9683 | 0.0858 | 3123.5267 | 0.059 | 48.2959 | 1.0653 | 56.9202 | 1.1229 | 75.8936 | 1.1229 | 94.867 | 1.1229 | 123.327 | 1.1229 | 151.7871 | 1.1229 | 1267.4284 | 0.0694 | 599.3169 | 0.218 | 3550.8086 | 0.0618 | 1151.517 | 0.1754 | 1613.5498 | 0.1418 | 988.989 | 0.42 | 881.68 | 0.7458 | 1267.9488 | 0.4225 | 2028.0131 | 0.2128 | 3538.3468 | 0.1266 | 3840 | 0.1383 | 3470.0706 | 0.1917
32.3744 | 1.6967 | 42.0999 | 2.1871 | 51.0212 | 2.677 | 58.0586 | 2.7907 | 77.4114 | 2.7907 | 194.3596 | 0.5356 | 120.0261 | 2.3546 | 146.3071 | 3.3272 | 149.1139 | 7.2017 | 202.0895 | 5.9987 | 271.432 | 4.2874 | 320.1258 | 5.3283 | 461.6065 | 4.0721 | 1188.8115 | 0.5295 | 733.4153 | 2.8656 | 1243.5234 | 0.9395 | 6410.6092 | 0.0441 | 1930.8349 | 0.7649 | 2161.8321 | 1.1215 | 34.9323 | 3.8387 | 41.6333 | 5.3439 | 52.8509 | 5.9497 | 65.3353 | 6.7053 | 82.2496 | 6.8479 | 104.3506 | 7.0904 | 136.2441 | 6.6827 | 172.6275 | 6.8526 | 219.2679 | 6.7534 | 276.1653 | 6.7579 | 341.3844 | 6.9543 | 415.6994 | 7.636 | 580.5858 | 8.1338 | 928.9372 | 8.1338 | 34.2788 | 0.7067 | 42.0999 | 0.8763 | 49.2618 | 1.0533 | 58.0586 | 1.1099 | 77.4114 | 1.1099 | 194.8396 | 0.2146 | 451.0413 | 0.0719 | 688.6242 | 0.0517 | 1043.1936 | 0.041 | 1149.8456 | 0.0606 | 1873.5229 | 0.0465 | 2503.8417 | 0.0429 | 2501.8974 | 0.0539 | 2420.9229 | 0.0723 | 3484.1593 | 0.051 | 49.2618 | 1.0066 | 58.0586 | 1.0598 | 77.4114 | 1.0598 | 96.7643 | 1.0598 | 125.7936 | 1.0598 | 154.8229 | 1.0598 | 1399.5062 | 0.0666 | 643.3617 | 0.1951 | 3799.9973 | 0.0608 | 1245.213 | 0.157 | 1720.7313 | 0.1309 | 1055.1936 | 0.3671 | 892.4607 | 0.7233 | 1379.7999 | 0.3547 | 2209.2177 | 0.1865 | 3794.5263 | 0.1169 | 4097.6842 | 0.1277 | 3788.162 | 0.1685
33.0219 | 1.6115 | 42.9419 | 2.0702 | 52.0416 | 2.5253 | 59.2197 | 2.6305 | 78.9597 | 2.6305 | 214.8015 | 0.4387 | 125.8018 | 2.0651 | 151.974 | 2.953 | 152.1262 | 6.5814 | 207.2061 | 5.4179 | 280.5392 | 3.8232 | 325.6137 | 4.9887 | 469.5209 | 3.8064 | 1340.3752 | 0.4051 | 752.7346 | 2.6251 | 1309.9069 | 0.8274 | 7644.2506 | 0.0339 | 2083.299 | 0.6398 | 2281.7715 | 0.9786 | 35.6309 | 3.6412 | 42.4659 | 5.0536 | 53.9079 | 5.6113 | 66.642 | 6.3204 | 83.8946 | 6.4548 | 106.4376 | 6.6834 | 138.969 | 6.2991 | 176.08 | 6.4592 | 223.6532 | 6.3658 | 281.6886 | 6.37 | 348.2121 | 6.5551 | 424.0134 | 7.1977 | 592.1975 | 7.6771 | 947.516 | 7.6771 | 34.9644 | 0.6723 | 42.9419 | 0.831 | 50.2471 | 0.9956 | 59.2197 | 1.048 | 78.9597 | 1.048 | 211.3172 | 0.1823 | 502.6105 | 0.0598 | 779.4442 | 0.0444 | 1162.1053 | 0.0365 | 1267.7164 | 0.053 | 2058.9868 | 0.0416 | 2753.6842 | 0.0386 | 2796.5073 | 0.0468 | 2666.8426 | 0.0612 | 3830.2201 | 0.0453 | 50.2471 | 0.9523 | 59.2197 | 1.0015 | 78.9597 | 1.0015 | 98.6996 | 1.0015 | 128.3095 | 1.0015 | 157.9193 | 1.0015 | 1530.9009 | 0.0645 | 687.0528 | 0.1768 | 4041.2928 | 0.06 | 1349.3447 | 0.1412 | 1849.8088 | 0.1202 | 1119.9633 | 0.3258 | 929.9069 | 0.6535 | 1503.0861 | 0.2998 | 2394.0874 | 0.1659 | 4092.6316 | 0.1079 | 4395.7895 | 0.1178 | 4122.4795 | 0.15
33.6824 | 1.5315 | 43.8007 | 1.9612 | 53.0824 | 2.3848 | 60.4041 | 2.4822 | 80.5389 | 2.4822 | 244.1327 | 0.341 | 132.1201 | 1.8107 | 156.916 | 2.6807 | 156.4458 | 5.8423 | 211.8147 | 4.9738 | 287.3532 | 3.5291 | 332.8568 | 4.5945 | 479.006 | 3.5256 | 1487.2815 | 0.3229 | 773.3355 | 2.4041 | 1367.4533 | 0.7465 | 8740.3897 | 0.0283 | 2279.4927 | 0.5207 | 2427.7218 | 0.8405 | 36.3435 | 3.4562 | 43.3153 | 4.7832 | 54.9861 | 5.2978 | 67.9748 | 5.9642 | 85.5725 | 6.0911 | 108.5664 | 6.3067 | 141.7484 | 5.9441 | 179.6017 | 6.0952 | 228.1263 | 6.007 | 287.3224 | 6.011 | 355.1764 | 6.1857 | 432.4937 | 6.792 | 604.0414 | 7.2542 | 966.4663 | 7.2542 | 35.6637 | 0.6399 | 43.8007 | 0.7887 | 51.252 | 0.942 | 60.4041 | 0.9906 | 80.5389 | 0.9906 | 224.7784 | 0.1614 | 562.9996 | 0.0513 | 858.6816 | 0.0397 | 1304.161 | 0.0326 | 1394.2929 | 0.047 | 2223.1579 | 0.0382 | 2988.1536 | 0.0355 | 3039.2256 | 0.0424 | 2904.3173 | 0.0543 | 4272.4456 | 0.0399 | 51.252 | 0.902 | 60.4041 | 0.9476 | 80.5389 | 0.9476 | 100.6736 | 0.9476 | 130.8756 | 0.9476 | 161.0777 | 0.9476 | 1657.251 | 0.063 | 736.7778 | 0.1601 | 4244.4288 | 0.0595 | 1502.3798 | 0.1238 | 2023.2869 | 0.1091 | 1193.6883 | 0.2881 | 964.8597 | 0.5982 | 1593.5535 | 0.2685 | 2567.4897 | 0.1507 | 4547.3684 | 0.0974 | 4822.9885 | 0.1068 | 4495.68 | 0.1342
34.356 | 1.4563 | 44.6767 | 1.8593 | 54.1441 | 2.2542 | 61.6122 | 2.3448 | 82.1496 | 2.3448 | 264.7303 | 0.2913 | 138.4783 | 1.6033 | 162.1805 | 2.4337 | 161.857 | 5.1019 | 218.702 | 4.4178 | 299.0803 | 3.1046 | 339.9208 | 4.2592 | 490.1507 | 3.2388 | 1703.9616 | 0.2413 | 796.0906 | 2.1943 | 1434.6927 | 0.6668 | 10236.4416 | 0.0233 | 2588.1782 | 0.3924 | 2554.753 | 0.7439 | 37.0704 | 3.2828 | 44.1816 | 4.531 | 56.0858 | 5.0069 | 69.3343 | 5.6339 | 87.284 | 5.7537 | 110.7377 | 5.9574 | 144.5834 | 5.6149 | 183.1937 | 5.7576 | 232.6888 | 5.6743 | 293.0688 | 5.6781 | 362.2799 | 5.8431 | 441.1435 | 6.4159 | 616.1222 | 6.8617 | 985.7956 | 6.8617 | 36.3769 | 0.6095 | 44.6767 | 0.7491 | 52.277 | 0.8922 | 61.6122 | 0.9374 | 82.1496 | 0.9374 | 241.9352 | 0.1399 | 632.6157 | 0.0444 | 950.9113 | 0.0357 | 1417.4157 | 0.0303 | 1550.4091 | 0.0414 | 2412.4325 | 0.0352 | 3291.6591 | 0.0323 | 3330.6149 | 0.0383 | 3156.3648 | 0.0488 | 4780.6302 | 0.0355 | 52.277 | 0.8552 | 61.6122 | 0.8976 | 82.1496 | 0.8976 | 102.687 | 0.8976 | 133.4932 | 0.8976 | 164.2993 | 0.8976 | 1775.4038 | 0.0618 | 801.7223 | 0.143 | 4471.7517 | 0.0591 | 1628.0175 | 0.1132 | 2190.1824 | 0.1009 | 1289.6701 | 0.2497 | 976.6844 | 0.5813 | 1716.1233 | 0.2352 | 2744.8441 | 0.1382 | 5046.5169 | 0.0892 | 5204.931 | 0.0992 | 4992.6457 | 0.1186
35.0431 | 1.3855 | 45.5702 | 1.7639 | 55.227 | 2.1327 | 62.8445 | 2.217 | 83.7926 | 2.217 | 289.3718 | 0.2453 | 146.894 | 1.3832 | 166.9525 | 2.2407 | 167.9574 | 4.444 | 226.9455 | 3.8804 | 308.1886 | 2.8307 | 347.135 | 3.958 | 500.0527 | 3.016 | 1879.4021 | 0.1963 | 822.7996 | 1.9847 | 1500.7316 | 0.6008 | 11529.9638 | 0.0205 | 2995.0272 | 0.286 | 2672.3358 | 0.6691 | 37.8118 | 3.1198 | 45.0652 | 4.2954 | 57.2075 | 4.7362 | 70.721 | 5.3269 | 89.0297 | 5.4402 | 112.9525 | 5.6328 | 147.475 | 5.309 | 186.8576 | 5.4439 | 237.3426 | 5.3652 | 298.9302 | 5.3687 | 369.5255 | 5.5247 | 449.9664 | 6.0663 | 628.4447 | 6.4967 | 1005.5115 | 6.4967 | 37.1045 | 0.5809 | 45.5702 | 0.712 | 53.3226 | 0.8458 | 62.8445 | 0.8879 | 83.7926 | 0.8879 | 258.8696 | 0.123 | 722.7789 | 0.0382 | 1048.6717 | 0.0325 | 1535.7019 | 0.0284 | 1724.1196 | 0.0369 | 2814.0187 | 0.0305 | 3729.2706 | 0.0291 | 3684.2799 | 0.0345 | 3426.719 | 0.0441 | 5405.2153 | 0.0316 | 53.3226 | 0.8117 | 62.8445 | 0.8512 | 83.7926 | 0.8512 | 104.7408 | 0.8512 | 136.163 | 0.8512 | 167.5853 | 0.8512 | 1899.9987 | 0.0608 | 858.8504 | 0.1312 | 4618.7661 | 0.0588 | 1758.6503 | 0.1046 | 2405.7135 | 0.0927 | 1371.6965 | 0.2249 | 1018.3947 | 0.5279 | 1855.8518 | 0.2073 | 2937.5131 | 0.1272 | 5507.3684 | 0.0834 | 5717.7044 | 0.0913 | 5540.4379 | 0.1062
35.744 | 1.3188 | 46.4816 | 1.6746 | 56.3315 | 2.0195 | 64.1014 | 2.0981 | 85.4685 | 2.0981 | 314.1 | 0.2096 | 155.5099 | 1.2049 | 172.7271 | 2.0388 | 175.3371 | 3.8232 | 234.0919 | 3.4987 | 321.7299 | 2.4918 | 353.7933 | 3.7108 | 510.1536 | 2.8146 | 2068.7707 | 0.1606 | 847.0098 | 1.8219 | 1574.5293 | 0.5384 |  |  | 3390.4269 | 0.2197 | 2834.7486 | 0.5838 | 38.568 | 2.9666 | 45.9665 | 4.0749 | 58.3517 | 4.484 | 72.1354 | 5.0412 | 90.8103 | 5.1484 | 115.2115 | 5.3307 | 150.4245 | 5.0242 | 190.5947 | 5.1519 | 242.0895 | 5.0774 | 304.9088 | 5.0807 | 376.916 | 5.2284 | 458.9657 | 5.7409 | 641.0136 | 6.1567 | 1025.6217 | 6.1567 | 37.8466 | 0.5539 | 46.4816 | 0.6773 | 54.389 | 0.8025 | 64.1014 | 0.8418 | 85.4685 | 0.8418 | 278.5768 | 0.1071 | 797.0769 | 0.0346 | 1135.012 | 0.0303 | 1730.9932 | 0.0261 | 1965.6556 | 0.0325 | 3213.4737 | 0.0275 | 4185.6909 | 0.0267 | 4062.7978 | 0.0315 | 3666.4411 | 0.0408 | 6130.5115 | 0.0285 | 54.389 | 0.7711 | 64.1014 | 0.8079 | 85.4685 | 0.8079 | 106.8356 | 0.8079 | 138.8863 | 0.8079 | 170.937 | 0.8079 | 2020.6464 | 0.06 | 930.6644 | 0.1194 | 5052.6316 | 0.0582 | 1868.3237 | 0.0987 | 2706.6068 | 0.0845 | 1454.3717 | 0.2049 | 1022.6059 | 0.523 | 1967.5513 | 0.1894 | 3180.0061 | 0.1162 | 6014.2343 | 0.0786 | 6307.2798 | 0.0846 | 6235.8993 | 0.095
36.4589 | 1.2559 | 47.4113 | 1.5907 | 57.4581 | 1.9138 | 65.3834 | 1.9872 | 87.1778 | 1.9872 | 337.2119 | 0.183 | 165.623 | 1.0389 | 178.165 | 1.8745 | 183.5917 | 3.2863 | 242.4298 | 3.1276 | 334.1907 | 2.2353 | 363.4763 | 3.3953 | 520.9804 | 2.6229 | 2286.34 | 0.1305 | 885.1103 | 1.6068 | 1650.2946 | 0.4843 |  |  | 3849.5424 | 0.1683 | 3004.031 | 0.5117 | 39.3394 | 2.8224 | 46.8858 | 3.8683 | 59.5187 | 4.2487 | 73.5781 | 4.7747 | 92.6265 | 4.8762 | 117.5157 | 5.0489 | 153.433 | 4.7586 | 194.4066 | 4.8796 | 246.9313 | 4.809 | 311.007 | 4.8121 | 384.4543 | 4.952 | 468.145 | 5.4374 | 653.8339 | 5.8394 | 1046.1342 | 5.8394 | 38.6035 | 0.5285 | 47.4113 | 0.6446 | 55.4768 | 0.7621 | 65.3834 | 0.7988 | 87.1778 | 0.7988 | 300.4143 | 0.0932 | 908.7865 | 0.0307 | 1262.1676 | 0.0279 | 1961.3012 | 0.0242 | 2192.8987 | 0.0296 | 3617.6842 | 0.0254 | 4663.8892 | 0.0249 | 4466.2424 | 0.0291 | 3988.7757 | 0.0372 | 7084.5969 | 0.0257 | 55.4768 | 0.7332 | 65.3834 | 0.7676 | 87.1778 | 0.7676 | 108.9723 | 0.7676 | 141.664 | 0.7676 | 174.3557 | 0.7676 | 2122.2144 | 0.0595 | 1011.644 | 0.1091 | 5180.5349 | 0.058 | 1982.7688 | 0.0936 | 3013.54 | 0.0785 | 1548.4911 | 0.1861 | 1079.2081 | 0.4639 | 2096.8886 | 0.1724 | 3482.2666 | 0.1056 | 6690.1794 | 0.0739 | 6849.5394 | 0.0799 | 7036.034 | 0.0861
37.188 | 1.1965 | 48.3595 | 1.512 | 58.6073 | 1.815 | 66.6911 | 1.8836 | 88.9214 | 1.8836 | 358.4231 | 0.163 | 175.3371 | 0.9116 | 185.0657 | 1.695 | 191.8496 | 2.8653 | 249.5628 | 2.8598 | 345.7489 | 2.034 | 372.6769 | 3.1353 | 532.0373 | 2.449 | 2572.6939 | 0.1024 | 922.1537 | 1.4349 | 1752.3375 | 0.4237 |  |  | 4388.3581 | 0.1283 | 3237.9961 | 0.4327 | 40.1262 | 2.6866 | 47.8235 | 3.6745 | 60.7091 | 4.0286 | 75.0497 | 4.5258 | 94.479 | 4.622 | 119.8661 | 4.7857 | 156.5017 | 4.5105 | 198.2947 | 4.6252 | 251.8699 | 4.5583 | 317.2271 | 4.5613 | 392.1434 | 4.6939 | 477.5079 | 5.154 | 666.9105 | 5.5427 | 1067.0569 | 5.5427 | 39.3756 | 0.5044 | 48.3595 | 0.614 | 56.5863 | 0.7242 | 66.6911 | 0.7586 | 88.9214 | 0.7586 | 328.5625 | 0.0792 | 1017.9759 | 0.028 | 1378.946 | 0.0262 | 2236.1735 | 0.0226 | 2542.2983 | 0.0265 | 3956.6279 | 0.0241 | 5367.0215 | 0.023 | 4945.6371 | 0.027 | 4285.6138 | 0.0346 | 7812.6195 | 0.0242 | 56.5863 | 0.6978 | 66.6911 | 0.7299 | 88.9214 | 0.7299 | 111.1518 | 0.7299 | 144.4973 | 0.7299 | 177.8428 | 0.7299 | 2235.8764 | 0.0591 | 1095.0912 | 0.1009 | 5532.5356 | 0.0577 | 2141.8661 | 0.0879 | 3401.0809 | 0.0732 | 1662.5432 | 0.1678 | 1091.0014 | 0.4531 | 2206.9137 | 0.1604 | 3715.0484 | 0.0992 | 7434.3269 | 0.0701 | 7540.0613 | 0.0753 | 7975.2202 | 0.0789
37.9318 | 1.1404 | 49.3267 | 1.4379 | 59.7794 | 1.7224 | 68.0249 | 1.7867 | 90.6998 | 1.7867 | 394.9318 | 0.1356 | 190.7025 | 0.7555 | 192.4265 | 1.5324 | 198.8826 | 2.5731 | 257.4206 | 2.6064 | 358.4231 | 1.8453 | 384.0272 | 2.8579 | 544.9605 | 2.2691 | 2935.7245 | 0.0782 | 960.7477 | 1.2856 | 1853.2689 | 0.3746 |  |  | 5232.8468 | 0.0894 | 3600.0707 | 0.3429 | 40.9287 | 2.5585 | 48.78 | 3.4925 | 61.9233 | 3.8227 | 76.5507 | 4.2929 | 96.3686 | 4.3843 | 122.2634 | 4.5395 | 159.6317 | 4.2785 | 202.2606 | 4.3872 | 256.9073 | 4.3238 | 323.5717 | 4.3266 | 399.9863 | 4.4524 | 487.0581 | 4.8888 | 680.2487 | 5.265 | 1088.398 | 5.265 | 40.1631 | 0.4817 | 49.3267 | 0.5851 | 57.7181 | 0.6887 | 68.0249 | 0.7209 | 90.6998 | 0.7209 | 360.4335 | 0.0672 | 1137.7374 | 0.0259 | 1508.0984 | 0.0247 | 2541.6202 | 0.0214 | 2792.0397 | 0.0249 | 4435.1242 | 0.0227 | 6208.3635 | 0.0216 | 5419.8073 | 0.0254 | 4667.236 | 0.032 | 8705.5761 | 0.0229 | 57.7181 | 0.6646 | 68.0249 | 0.6947 | 90.6998 | 0.6947 | 113.3748 | 0.6947 | 147.3872 | 0.6947 | 181.3997 | 0.6947 | 2309.3831 | 0.0588 | 1202.8568 | 0.0927 | 6064.6141 | 0.0572 | 2308.9091 | 0.0831 | 3767.0744 | 0.0696 | 1786.8632 | 0.1519 | 1143.6513 | 0.4097 | 2356.899 | 0.1468 | 4030.1305 | 0.0923 | 8235.4065 | 0.0671 | 8248.3675 | 0.0718 | 9030.337 | 0.0734
38.6904 | 1.0874 | 50.3132 | 1.3682 | 60.975 | 1.6356 | 69.3854 | 1.6959 | 92.5138 | 1.6959 | 425.6903 | 0.1177 | 213.73 | 0.5899 | 200.68 | 1.378 | 206.7915 | 2.2993 | 266.0575 | 2.3682 | 371.1896 | 1.6824 | 398.1042 | 2.5667 | 560.4348 | 2.0812 | 3250.9683 | 0.0635 | 994.9699 | 1.1732 | 2021.7287 | 0.3101 |  |  | 5900.0165 | 0.07 | 3888.2365 | 0.2904 | 41.7473 | 2.4375 | 49.7556 | 3.3213 | 63.1617 | 3.6297 | 78.0817 | 4.0748 | 98.2959 | 4.1615 | 124.7086 | 4.3088 | 162.8243 | 4.0611 | 206.3058 | 4.1644 | 262.0454 | 4.1041 | 330.0431 | 4.1068 | 407.986 | 4.2262 | 496.7993 | 4.6404 | 693.8537 | 5.0046 | 1110.166 | 5.0046 | 40.9663 | 0.4602 | 50.3132 | 0.5578 | 58.8724 | 0.6553 | 69.3854 | 0.6856 | 92.5138 | 0.6856 | 384.0596 | 0.0604 | 1228.4301 | 0.0247 | 1733.86 | 0.0229 | 2829.2685 | 0.0206 | 3203.3765 | 0.0231 | 4997.9894 | 0.0215 | 6939.265 | 0.0207 | 5976.6316 | 0.024 | 5019.7834 | 0.03 | 9751.199 | 0.0217 | 58.8724 | 0.6334 | 69.3854 | 0.6617 | 92.5138 | 0.6617 | 115.6423 | 0.6617 | 150.335 | 0.6617 | 185.0277 | 0.6617 | 2422.9349 | 0.0585 | 1353.3029 | 0.0845 | 7645.5148 | 0.0564 | 2486.3848 | 0.079 | 4113.8082 | 0.0671 | 1944.7155 | 0.1361 | 1144.6873 | 0.4089 | 2470.2326 | 0.1382 | 4394.8093 | 0.0861 | 9393.4797 | 0.064 | 8985.6081 | 0.069 | 10066.1487 | 0.0696
39.4642 | 1.0372 | 51.3195 | 1.3025 | 62.1945 | 1.5542 | 70.7731 | 1.6108 | 94.3641 | 1.6108 | 458.8453 | 0.1022 | 233.6239 | 0.4886 | 210.5475 | 1.2238 | 215.0161 | 2.0621 | 273.6129 | 2.1879 | 386.3382 | 1.5174 | 411.4598 | 2.3332 | 578.6591 | 1.8912 | 3621.7354 | 0.0512 | 1033.5061 | 1.0645 | 2218.7672 | 0.2542 |  |  | 6786.6341 | 0.0527 | 4233.1816 | 0.2423 | 42.5822 | 2.3233 | 50.7507 | 3.1601 | 64.4249 | 3.4485 | 79.6433 | 3.8703 | 100.2619 | 3.9526 | 127.2028 | 4.0925 | 166.0808 | 3.8572 | 210.432 | 3.9553 | 267.2863 | 3.8981 | 336.6439 | 3.9006 | 416.1457 | 4.014 | 506.7353 | 4.4075 | 707.7308 | 4.7602 | 1132.3693 | 4.7602 | 41.7857 | 0.4398 | 51.3195 | 0.5322 | 60.0499 | 0.624 | 70.7731 | 0.6524 | 94.3641 | 0.6524 | 404.5763 | 0.0562 | 1436.7269 | 0.0227 | 1995.4934 | 0.0215 | 3343.9621 | 0.016 | 3622.1285 | 0.0218 | 5614.9551 | 0.0206 | 8201.639 | 0.016 | 6590.6627 | 0.0228 | 5552.7542 | 0.0277 | 10820.5955 | 0.0209 | 60.0499 | 0.6042 | 70.7731 | 0.6307 | 94.3641 | 0.6307 | 117.9551 | 0.6307 | 153.3417 | 0.6307 | 188.7282 | 0.6307 | 4170.0086 | 0.0562 | 1506.7695 | 0.0785 | 9628.4675 | 0.0559 | 2716.8869 | 0.0749 | 4535.5069 | 0.0648 | 2092.32 | 0.1246 | 1188.5369 | 0.3782 | 2660.2328 | 0.1262 | 4742.7304 | 0.0816 | 10201.248 | 0.0625 | 9809.2042 | 0.0665 | 11457.5535 | 0.066
40.2535 | 0.9896 | 52.3459 | 1.2405 | 63.4384 | 1.4776 | 72.1885 | 1.5308 | 96.2514 | 1.5308 | 499.5525 | 0.0871 | 256.3935 | 0.4027 | 223.7909 | 1.0562 | 226.0396 | 1.8016 | 285.349 | 1.9492 | 399.3003 | 1.3959 | 425.6903 | 2.1207 | 601.6721 | 1.6893 | 3978.6968 | 0.0441 | 1075.6838 | 0.963 | 2418.0288 | 0.2119 |  |  | 7583.3472 | 0.044 | 4617.9658 | 0.2016 | 43.4339 | 2.2152 | 51.7657 | 3.0083 | 65.7134 | 3.2782 | 81.2362 | 3.6781 | 102.2671 | 3.7564 | 129.7469 | 3.8894 | 169.4024 | 3.6658 | 214.6406 | 3.7589 | 272.6321 | 3.7046 | 343.3768 | 3.707 | 424.4686 | 3.8148 | 516.87 | 4.1887 | 721.8854 | 4.5304 | 1155.0167 | 4.5304 | 42.6214 | 0.4205 | 52.3459 | 0.5079 | 61.2509 | 0.5945 | 72.1885 | 0.6213 | 96.2514 | 0.6213 | 444.769 | 0.0496 | 1810.2336 | 0.0207 | 2277.5596 | 0.0205 | 4299.3799 | 0.016 | 4121.2861 | 0.0208 | 6636.4139 | 0.016 | 10544.9645 | 0.016 | 7351.4314 | 0.0217 | 6012.6316 | 0.0262 | 11969.8439 | 0.0202 | 61.2509 | 0.5767 | 72.1885 | 0.6017 | 96.2514 | 0.6017 | 120.3142 | 0.6017 | 156.4085 | 0.6017 | 192.5028 | 0.6017 | 5057.5882 | 0.0558 | 1700.54 | 0.0732 |  |  | 2928.7741 | 0.072 | 5018.7133 | 0.0628 | 2260.5585 | 0.1142 | 1204.4382 | 0.368 | 2838.0632 | 0.1172 | 5022.9393 | 0.0785 | 11419.0959 | 0.0608 | 10630.3124 | 0.0647
41.0586 | 0.9446 | 53.3928 | 1.182 | 64.7072 | 1.4056 | 73.6323 | 1.4556 | 98.1764 | 1.4556 | 546.5978 | 0.0736 | 277.1922 | 0.3432 | 237.1543 | 0.9212 | 235.2646 | 1.6222 | 299.6795 | 1.7106 | 412.2846 | 1.289 | 444.3948 | 1.886 | 621.8584 | 1.5399 | 4383.9673 | 0.038 | 1118.4596 | 0.8749 | 2696.5016 | 0.1686 |  |  | 8593.0499 | 0.0364 | 5017.6118 | 0.1695 | 44.3026 | 2.113 | 52.8011 | 2.865 | 67.0277 | 3.1181 | 82.8609 | 3.4975 | 104.3124 | 3.5719 | 132.3418 | 3.6984 | 172.7905 | 3.4857 | 218.9334 | 3.5744 | 278.0847 | 3.5226 | 350.2444 | 3.525 | 432.958 | 3.6274 | 527.2074 | 3.983 | 736.3231 | 4.3142 | 1178.117 | 4.3142 | 43.4738 | 0.4022 | 53.3928 | 0.485 | 62.4759 | 0.5668 | 73.6323 | 0.592 | 98.1764 | 0.592 | 473.4306 | 0.0459 | 2139.5468 | 0.016 | 2691.8876 | 0.016 | 6210.2154 | 0.014 | 4871.0203 | 0.016 | 8532.5322 | 0.016 |  |  | 8006.1272 | 0.021 | 6633.8304 | 0.0247 |  |  | 62.4759 | 0.5508 | 73.6323 | 0.5743 | 98.1764 | 0.5743 | 122.7205 | 0.5743 | 159.5367 | 0.5743 | 196.3528 | 0.5743 | 6064.6141 | 0.0556 | 1883.5372 | 0.0696 |  |  | 3196.9516 | 0.0691 | 5548.1331 | 0.0612 | 2462.8305 | 0.1045 | 1214.3636 | 0.3619 | 3087.1579 | 0.1072 | 5506.1154 | 0.0744 |  |  | 12023.9798 | 0.0623
41.8798 | 0.9019 | 54.4607 | 1.1267 | 66.0013 | 1.3377 | 75.105 | 1.3849 | 100.1399 | 1.3849 | 612.6001 | 0.0595 | 306.3456 | 0.2802 | 249.5628 | 0.8186 | 247.3274 | 1.4278 | 313.473 | 1.5226 | 428.6804 | 1.1717 | 461.1452 | 1.7097 | 640.1561 | 1.4223 | 4733.4063 | 0.034 | 1174.6277 | 0.7774 | 2941.6047 | 0.1407 |  |  | 9776.2368 | 0.0304 | 5301.309 | 0.1512 | 45.1886 | 2.0162 | 53.8571 | 2.7298 | 68.3683 | 2.9673 | 84.5181 | 3.3275 | 106.3987 | 3.3983 | 134.9886 | 3.5186 | 176.2463 | 3.3163 | 223.3121 | 3.4006 | 283.6464 | 3.3514 | 357.2493 | 3.3536 | 441.6172 | 3.4511 | 537.7515 | 3.7894 | 751.0496 | 4.1105 | 1201.6793 | 4.1105 | 44.3433 | 0.3849 | 54.4607 | 0.4633 | 63.7254 | 0.5406 | 75.105 | 0.5644 | 100.1399 | 0.5644 | 509.7418 | 0.0421 | 2750.8459 | 0.016 | 3460.9984 | 0.016 |  |  | 6262.7404 | 0.016 |  |  |  |  | 8728.2048 | 0.0204 | 7187.0744 | 0.0236 |  |  | 63.7254 | 0.5265 | 75.105 | 0.5486 | 100.1399 | 0.5486 | 125.1749 | 0.5486 | 162.7274 | 0.5486 | 200.2799 | 0.5486 | 7645.5148 | 0.0553 | 2071.0515 | 0.0669 |  |  | 3496.9728 | 0.0666 | 5962.1699 | 0.0602 | 2674.8015 | 0.0967 | 1286.3384 | 0.3227 | 3334.7368 | 0.0995 | 5954.4293 | 0.0714
42.7174 | 0.8614 | 55.5499 | 1.0744 | 67.3214 | 1.2737 | 76.6071 | 1.3182 | 102.1427 | 1.3182 | 662.959 | 0.0522 | 327.2466 | 0.2455 | 260.5285 | 0.742 | 259.4881 | 1.267 | 330.8659 | 1.3291 | 443.9502 | 1.077 | 477.571 | 1.5613 | 664.2862 | 1.2882 | 5117.3861 | 0.0305 | 1226.2383 | 0.7021 | 3202.5701 | 0.1181 |  |  | 11055.7864 | 0.0259 | 5634.7604 | 0.1332 | 46.0924 | 1.9245 | 54.9342 | 2.602 | 69.7356 | 2.8251 | 86.2085 | 3.1673 | 108.5267 | 3.2347 | 137.6884 | 3.3492 | 179.7712 | 3.1567 | 227.7783 | 3.2369 | 289.3193 | 3.1901 | 364.3942 | 3.1922 | 450.4495 | 3.285 | 548.5065 | 3.607 | 766.0706 | 3.9184 | 1225.7129 | 3.9184 | 45.2302 | 0.3684 | 55.5499 | 0.4428 | 64.9999 | 0.5159 | 76.6071 | 0.5383 | 102.1427 | 0.5383 | 571.9579 | 0.0371 | 3973.4441 | 0.016 | 4999.2199 | 0.014 |  |  | 9046.1805 | 0.016 |  |  |  |  | 10316.0183 | 0.016 | 7900.6878 | 0.0225 |  |  | 64.9999 | 0.5035 | 76.6071 | 0.5244 | 102.1427 | 0.5244 | 127.6784 | 0.5244 | 165.982 | 0.5244 | 204.2855 | 0.5244 | 9628.4675 | 0.0552 | 2267.7534 | 0.0648 |  |  | 3882.4472 | 0.0642 | 6821.7893 | 0.059 | 2920.2361 | 0.0897 | 1318.1425 | 0.3077 | 3623.1481 | 0.0924 | 6486.4613 | 0.0687
43.5717 | 0.823 | 56.6609 | 1.0249 | 68.6678 | 1.2134 | 78.1392 | 1.2553 | 104.1856 | 1.2553 | 716.0236 | 0.0465 | 354.856 | 0.2089 | 270.0781 | 0.684 | 271.7032 | 1.1327 | 351.3256 | 1.1474 | 466.2451 | 0.9589 | 491.1323 | 1.4538 | 685.2017 | 1.1877 | 5672.5794 | 0.0267 | 1273.7361 | 0.6424 | 3476.252 | 0.0998 |  |  |  |  | 6085.7725 | 0.1137 | 47.0142 | 1.8375 | 56.0329 | 2.4812 | 71.1303 | 2.6909 | 87.9326 | 3.0163 | 110.6972 | 3.0804 | 140.4422 | 3.1895 | 183.3667 | 3.0061 | 232.3339 | 3.0825 | 295.1057 | 3.0379 | 371.6821 | 3.0399 | 459.4585 | 3.1283 | 559.4767 | 3.4349 | 781.392 | 3.737 | 1250.2272 | 3.737 | 46.1348 | 0.3528 | 56.6609 | 0.4233 | 66.2999 | 0.4925 | 78.1392 | 0.5137 | 104.1856 | 0.5137 | 616.0542 | 0.0344 | [14 empty] | 8680.4211 | 0.0216 |  |  | 66.2999 | 0.4818 | 78.1392 | 0.5015 | 104.1856 | 0.5015 | 130.232 | 0.5015 | 169.3016 | 0.5015 | 208.3712 | 0.5015 |  |  | 2514.4098 | 0.0628 |  |  | 4266.6765 | 0.0624 | 7521.3747 | 0.0583 | 3155.0451 | 0.0845 | 1348.227 | 0.2946 | 3889.628 | 0.0873 | 7237.7017 | 0.0658
44.4431 | 0.7864 | 57.7941 | 0.978 | 70.0411 | 1.1563 | 79.702 | 1.196 | 106.2693 | 1.196 | 722.5263 | 0.0459 | 378.6883 | 0.1837 | 281.1005 | 0.6255 | 287.0664 | 0.9934 | 371.5608 | 1.0037 | 495.5719 | 0.8321 | 509.6445 | 1.3251 | 714.593 | 1.0665 | 6138.8867 | 0.0243 | 1356.5598 | 0.5558 | 3838.0153 | 0.0815 |  |  |  |  | 6429.8728 | 0.1015 | 47.9545 | 1.755 | 57.1536 | 2.3668 | 72.553 | 2.5643 | 89.6913 | 2.8737 | 112.9111 | 2.9348 | 143.251 | 3.0387 | 187.034 | 2.864 | 236.9806 | 2.9368 | 301.0078 | 2.8943 | 379.1158 | 2.8962 | 468.6477 | 2.9804 | 570.6662 | 3.2725 | 797.0198 | 3.5657 | 1275.2317 | 3.5657 | 47.0574 | 0.3379 | 57.7941 | 0.4049 | 67.6259 | 0.4704 | 79.702 | 0.4905 | 106.2693 | 0.4905 | 655.7538 | 0.0325 | [14 empty] | 9372.6316 | 0.021 |  |  | 67.6259 | 0.4613 | 79.702 | 0.4799 | 106.2693 | 0.4799 | 132.8366 | 0.4799 | 172.6876 | 0.4799 | 212.5386 | 0.4799 |  |  | 2805.3928 | 0.061 |  |  | 4651.5244 | 0.0611 | 8032.1512 | 0.0579 | 3448.1482 | 0.0795 | 1426.4357 | 0.2651 | 4158.3117 | 0.083 | 7802.5354 | 0.0641
45.332 | 0.7517 | 58.95 | 0.9336 | 71.442 | 1.1024 | 81.296 | 1.1399 | 108.3947 | 1.1399 | 783.1579 | 0.0409 | 408.9988 | 0.1578 | 297.2918 | 0.5525 | 301.1812 | 0.8878 | 393.7491 | 0.8762 | 526.7428 | 0.724 | 536.3102 | 1.1693 | 743.0127 | 0.9671 | 6643.5335 | 0.0222 | 1423.2657 | 0.4986 | 4233.1816 | 0.0667 |  |  |  |  | 6916.8111 | 0.0874 | 48.9136 | 1.6767 | 58.2966 | 2.2585 | 74.004 | 2.4445 | 91.4851 | 2.739 | 115.1694 | 2.7972 | 146.1161 | 2.8962 | 190.7747 | 2.7297 | 241.7202 | 2.7991 | 307.028 | 2.7586 | 386.6981 | 2.7605 | 478.0206 | 2.8407 | 582.0795 | 3.1191 | 812.9602 | 3.4036 | 1300.7364 | 3.4036 | 47.9986 | 0.3237 | 58.95 | 0.3874 | 68.9784 | 0.4495 | 81.296 | 0.4685 | 108.3947 | 0.4685 | 722.402 | 0.0298 | [14 empty] | 10343.7555 | 0.0203 |  |  | 68.9784 | 0.4419 | 81.296 | 0.4595 | 108.3947 | 0.4595 | 135.4934 | 0.4595 | 176.1414 | 0.4595 | 216.7894 | 0.4595 |  |  | 3055.8639 | 0.0599 |  |  | 5002.564 | 0.0601 | 8731.0474 | 0.0574 | 3760.612 | 0.0754 | 1443.7244 | 0.2593 | 4506.2824 | 0.0787 | 8526.3512 | 0.0625
46.2386 | 0.7187 | 60.129 | 0.8915 | 72.8708 | 1.0514 | 82.9219 | 1.0869 | 110.5626 | 1.0869 | 838.3215 | 0.0372 | 441.7359 | 0.1357 | 308.8055 | 0.5084 | 317.5748 | 0.7857 | 422.2988 | 0.7462 | 557.6391 | 0.6369 | 567.7678 | 1.0199 | 773.3355 | 0.8765 | 7153.7987 | 0.0205 | 1502.2323 | 0.4419 | 4787.2371 | 0.052 |  |  |  |  | 7373.9591 | 0.0767 | 49.8919 | 1.6023 | 59.4626 | 2.1559 | 75.4841 | 2.3313 | 93.3148 | 2.6116 | 117.4728 | 2.6671 | 149.0384 | 2.7616 | 194.5902 | 2.6028 | 246.5546 | 2.669 | 313.1685 | 2.6303 | 394.432 | 2.6321 | 487.581 | 2.7086 | 593.7211 | 2.9741 | 829.2194 | 3.2502 | 1326.7511 | 3.2502 | 48.9586 | 0.3103 | 60.129 | 0.3708 | 70.358 | 0.4297 | 82.9219 | 0.4477 | 110.5626 | 0.4477 | 775.3839 | 0.0282 | [18 empty] | 70.358 | 0.4236 | 82.9219 | 0.4402 | 110.5626 | 0.4402 | 138.2032 | 0.4402 | 179.6642 | 0.4402 | 221.1252 | 0.4402 |  |  | 3445.252 | 0.0589 |  |  | 5436.284 | 0.0593 | 10009.2207 | 0.0568 | 4201.1722 | 0.0711 | 1510.7581 | 0.2391 | 4924.316 | 0.0746 | 9424.898 | 0.0609
47.1634 | 0.6873 | 61.3315 | 0.8515 | 74.3282 | 1.0032 | 84.5804 | 1.0368 | 112.7738 | 1.0368 | 907.2354 | 0.0335 | 478.527 | 0.1161 | 323.9897 | 0.458 | 333.8572 | 0.7014 | 445.2841 | 0.6621 | 593.9011 | 0.5539 | 604.0831 | 0.8819 | 802.4844 | 0.8014 | 7657.1823 | 0.016 | 1603.1192 | 0.3829 | 5290.7156 | 0.0443 |  |  |  |  | 7988.1064 | 0.0652 | 50.8897 | 1.5315 | 60.6518 | 2.0586 | 76.9938 | 2.2241 | 95.1811 | 2.4911 | 119.8222 | 2.544 | 152.0191 | 2.6341 | 198.482 | 2.4827 | 251.4857 | 2.5458 | 319.4319 | 2.5089 | 402.3207 | 2.5106 | 497.3326 | 2.5836 | 605.5955 | 2.8368 | 845.8038 | 3.105 | 1353.2861 | 3.105 | 49.9377 | 0.2974 | 61.3315 | 0.3551 | 71.7652 | 0.411 | 84.5804 | 0.428 | 112.7738 | 0.428 | 841.8341 | 0.0266 | [18 empty] | 71.7652 | 0.4062 | 84.5804 | 0.422 | 112.7738 | 0.422 | 140.9673 | 0.422 | 183.2575 | 0.422 | 225.5477 | 0.422 |  |  | 3760.6878 | 0.0583 |  |  | 5769.2837 | 0.0588 | 11272.8657 | 0.0564 | 4562.7597 | 0.0685 | 1598.7522 | 0.2179 | 5443.2637 | 0.0709 | 10192.2846 | 0.0599
48.1067 | 0.6574 | 62.5582 | 0.8135 | 75.8148 | 0.9574 | 86.272 | 0.9893 | 115.0293 | 0.9893 | 990.6907 | 0.03 | 518.3826 | 0.0994 | 340.9424 | 0.4102 | 347.4818 | 0.6412 | 475.6646 | 0.5718 | 623.1034 | 0.4986 | 633.1531 | 0.7914 | 841.1018 | 0.7167 | 7851.0215 | 0.016 | 1695.458 | 0.3389 | 5886.3966 | 0.0377 |  |  |  |  | 8541.6505 | 0.0569 | 51.9075 | 1.4643 | 61.8649 | 1.9662 | 78.5337 | 2.1226 | 97.0847 | 2.3769 | 122.2187 | 2.4275 | 155.0595 | 2.5134 | 202.4516 | 2.3689 | 256.5154 | 2.4291 | 325.8205 | 2.394 | 410.3671 | 2.3956 | 507.2793 | 2.4652 | 617.7074 | 2.7069 | 862.7199 | 2.9672 | 1380.3518 | 2.9672 | 50.9365 | 0.2852 | 62.5582 | 0.3401 | 73.2005 | 0.3932 | 86.272 | 0.4093 | 115.0293 | 0.4093 | 891.2842 | 0.0256 | [18 empty] | 73.2005 | 0.3898 | 86.272 | 0.4047 | 115.0293 | 0.4047 | 143.7866 | 0.4047 | 186.9226 | 0.4047 | 230.0586 | 0.4047 |  |  | 4016.0761 | 0.0579 |  |  | 6154.6954 | 0.0584 |  |  | 5023.2536 | 0.066 | 1606.7621 | 0.2161 | 5960.6471 | 0.0681 | 11149.4208 | 0.0591
49.0688 | 0.629 | 63.8093 | 0.7775 | 77.3311 | 0.9141 | 87.9974 | 0.9442 | 117.3299 | 0.9442 | 1064.6501 | 0.0275 | 553.7497 | 0.0875 | 366.7621 | 0.351 | 365.2982 | 0.5738 | 495.0761 | 0.5236 | 657.0187 | 0.4444 | 677.0283 | 0.6799 | 881.5766 | 0.642 | 8240.4572 | 0.016 | 1778.8264 | 0.3055 | 6511.9832 | 0.0326 |  |  |  |  | 9206.9083 | 0.0495 | 52.9457 | 1.4003 | 63.1022 | 1.8785 | 80.1043 | 2.0263 | 99.0264 | 2.2688 | 124.663 | 2.317 | 158.1607 | 2.3991 | 206.5006 | 2.2611 | 261.6457 | 2.3186 | 332.337 | 2.2851 | 418.5744 | 2.2866 | 517.4249 | 2.353 | 630.0616 | 2.5837 | 879.9743 | 2.8366 | 1407.9589 | 2.8366 | 51.9552 | 0.2736 | 63.8093 | 0.3258 | 74.6645 | 0.3763 | 87.9974 | 0.3916 | 117.3299 | 0.3916 | 941.8105 | 0.0247 | [18 empty] | 74.6645 | 0.3742 | 87.9974 | 0.3884 | 117.3299 | 0.3884 | 146.6624 | 0.3884 | 190.6611 | 0.3884 | 234.6598 | 0.3884 |  |  | 4365.5242 | 0.0574 |  |  | 6867.0356 | 0.0577 |  |  | 5559.1983 | 0.0638 | 1699.968 | 0.1978 | 6452.7006 | 0.066
50.0502 | 0.6019 | 65.0855 | 0.7432 | 78.8777 | 0.8729 | 89.7574 | 0.9016 | 119.6765 | 0.9016 | 1163.7423 | 0.0248 | 606.5053 | 0.0734 | 394.1426 | 0.3013 | 385.9513 | 0.5085 | 514.7667 | 0.4809 | 693.473 | 0.3957 | 709.6075 | 0.6121 | 925.8497 | 0.5735 | 9270.5144 | 0.016 | 1866.2966 | 0.2756 | 7160.9634 | 0.0287 |  |  |  |  | 9943.8518 | 0.0438 | 54.0046 | 1.3395 | 64.3642 | 1.7953 | 81.7064 | 1.935 | 101.007 | 2.1662 | 127.1563 | 2.2123 | 161.3239 | 2.2906 | 210.6306 | 2.1589 | 266.8786 | 2.2138 | 338.9837 | 2.1818 | 426.9459 | 2.1832 | 527.7734 | 2.2467 | 642.6628 | 2.4669 | 897.5738 | 2.7126 | 1436.118 | 2.7126 | 52.9943 | 0.2625 | 65.0855 | 0.3122 | 76.1578 | 0.3602 | 89.7574 | 0.3748 | 119.6765 | 0.3748 | 990.3158 | 0.024 | [18 empty] | 76.1578 | 0.3594 | 89.7574 | 0.3728 | 119.6765 | 0.3728 | 149.5956 | 0.3728 | 194.4743 | 0.3728 | 239.353 | 0.3728 |  |  | 8589.4737 | 0.0556 |  |  | 8021.6377 | 0.057 |  |  | 5987.3977 | 0.0624 | 1742.3269 | 0.1905 | 7021.922 | 0.0641
51.0512 | 0.5761 | 66.3872 | 0.7106 | 80.4553 | 0.8339 | 91.5525 | 0.8611 | 122.07 | 0.8611 | 1235.7019 | 0.0233 | 648.533 | 0.0645 | 447.0693 | 0.2314 | 413.9364 | 0.4368 | 536.8471 | 0.439 | 735.6196 | 0.3488 | 748.2316 | 0.5444 | 994.9699 | 0.4872 | 10300.5716 | 0.016 | 1969.8402 | 0.2457 | 7874.6173 | 0.0254 |  |  |  |  | 10675.5264 | 0.0393 | 55.0847 | 1.2815 | 65.6515 | 1.7161 | 83.3405 | 1.8484 | 103.0271 | 2.069 | 129.6994 | 2.113 | 164.5504 | 2.1878 | 214.8433 | 2.062 | 272.2162 | 2.1144 | 345.7634 | 2.0838 | 435.4848 | 2.0852 | 538.3288 | 2.1458 | 655.5161 | 2.3561 | 915.5253 | 2.5948 | 1464.8404 | 2.5948 | 54.0542 | 0.2519 | 66.3872 | 0.2993 | 77.6809 | 0.345 | 91.5525 | 0.3588 | 122.07 | 0.3588 | 1040.8421 | 0.0234 | [18 empty] | 77.6809 | 0.3454 | 91.5525 | 0.3581 | 122.07 | 0.3581 | 152.5875 | 0.3581 | 198.3638 | 0.3581 | 244.1401 | 0.3581 | [6 empty] | 9749.2234 | 0.0563 |  |  | 6640.0734 | 0.0608 | 1834.6216 | 0.1764 | 7617.4676 | 0.0626
52.0722 | 0.5515 | 67.715 | 0.6796 | 82.0644 | 0.7968 | 93.3836 | 0.8226 | 124.5114 | 0.8226 | 1309.5006 | 0.0219 | 694.1666 | 0.0566 | 490.6409 | 0.1907 | 462.0678 | 0.3451 | 567.7678 | 0.3892 | 804.0906 | 0.289 | 792.9126 | 0.4796 | 1064.9816 | 0.4188 | 11536.6401 | 0.016 | 2087.4675 | 0.2173 | 8564.6552 | 0.023 |  |  |  |  | 11392.4615 | 0.0357 | 56.1864 | 1.2263 | 66.9645 | 1.6408 | 85.0074 | 1.7661 | 105.0876 | 1.9766 | 132.2934 | 2.0186 | 167.8414 | 2.0901 | 219.1401 | 1.9699 | 277.6605 | 2.02 | 352.6786 | 1.9908 | 444.1945 | 1.9921 | 549.0954 | 2.05 | 668.6264 | 2.251 | 933.8358 | 2.4829 | 1494.1372 | 2.4829 | 55.1353 | 0.2418 | 67.715 | 0.287 | 79.2345 | 0.3305 | 93.3836 | 0.3437 | 124.5114 | 0.3437 | 1111.5789 | 0.0226 | [18 empty] | 79.2345 | 0.332 | 93.3836 | 0.3441 | 124.5114 | 0.3441 | 155.6393 | 0.3441 | 202.3311 | 0.3441 | 249.0229 | 0.3441 | [6 empty] | 10742.2939 | 0.0561 |  |  | 7411.8023 | 0.0596 | 1904.5072 | 0.1672 | 8420.2317 | 0.061
53.1137 | 0.528 | 69.0693 | 0.6501 | 83.7056 | 0.7616 | 95.2512 | 0.7861 | 127.0017 | 0.7861 | 1339.968 | 0.0214 | 761.8217 | 0.0487 | 539.5382 | 0.1568 | 509.6445 | 0.2806 | 603.4795 | 0.3418 | 895.7959 | 0.2305 | 841.1018 | 0.4221 | 1153.6744 | 0.3514 |  |  | 2225.4366 | 0.1899 | 9231.7036 | 0.0212 | [6 empty] | 57.3101 | 1.1737 | 68.3038 | 1.5692 | 86.7075 | 1.688 | 107.1894 | 1.8889 | 134.9393 | 1.9291 | 171.1982 | 1.9973 | 223.5229 | 1.8825 | 283.2137 | 1.9304 | 359.7322 | 1.9024 | 453.0784 | 1.9037 | 560.0773 | 1.959 | 681.9989 | 2.1511 | 952.5125 | 2.3764 | 1524.02 | 2.3764 | 56.238 | 0.2321 | 69.0693 | 0.2753 | 80.8192 | 0.3167 | 95.2512 | 0.3292 | 127.0017 | 0.3292 | 1187.3684 | 0.022 | [18 empty] | 80.8192 | 0.3194 | 95.2512 | 0.3309 | 127.0017 | 0.3309 | 158.7521 | 0.3309 | 206.3777 | 0.3309 | 254.0033 | 0.3309 | [10 empty] | 8440.5625 | 0.0585 | 1945.1035 | 0.1623 | 9048.9741 | 0.0601
54.1759 | 0.5056 | 70.4507 | 0.622 | 85.3798 | 0.7281 | 97.1563 | 0.7514 | 129.5417 | 0.7514 | 1406.4347 | 0.0204 | 839.4211 | 0.0421 | 589.7582 | 0.1306 | 583.8902 | 0.2112 | 648.533 | 0.2935 | 988.0292 | 0.1881 | 890.437 | 0.3736 | 1237.3208 | 0.3021 |  |  | 2382.0359 | 0.1648 | 9627.6985 | 0.0203 | [6 empty] | 58.4563 | 1.1236 | 69.6699 | 1.501 | 88.4416 | 1.6137 | 109.3332 | 1.8055 | 137.6381 | 1.8439 | 174.6222 | 1.9092 | 227.9934 | 1.7994 | 288.878 | 1.8452 | 366.9269 | 1.8185 | 462.14 | 1.8197 | 571.2789 | 1.8726 | 695.6389 | 2.0561 | 971.5627 | 2.2751 | 1554.5004 | 2.2751 | 57.3628 | 0.2229 | 70.4507 | 0.2641 | 82.4356 | 0.3036 | 97.1563 | 0.3155 | 129.5417 | 0.3155 | 1273.2632 | 0.0214 | [18 empty] | 82.4356 | 0.3073 | 97.1563 | 0.3182 | 129.5417 | 0.3182 | 161.9271 | 0.3182 | 210.5053 | 0.3182 | 259.0834 | 0.3182 | [10 empty] | 9028.4989 | 0.0581 | 2073.4724 | 0.1488 | 9836.9512 | 0.0593
55.2595 | 0.4842 | 71.8597 | 0.5952 | 87.0874 | 0.6963 | 99.0994 | 0.7184 | 132.1325 | 0.7184 | 1582.239 | 0.016 | 908.1428 | 0.0376 | 649.1821 | 0.1074 | 674.3249 | 0.1568 | 687.9473 | 0.2593 | 1109.5525 | 0.1481 | 962.6718 | 0.3165 | 1312.5302 | 0.2662 |  |  | 2536.9233 | 0.1446 | 10105.2632 | 0.016 | [6 empty] | 59.6254 | 1.0758 | 71.0633 | 1.4362 | 90.2105 | 1.543 | 111.5199 | 1.7262 | 140.3908 | 1.763 | 178.1147 | 1.8254 | 232.5533 | 1.7204 | 294.6555 | 1.7642 | 374.2654 | 1.7386 | 471.3828 | 1.7398 | 582.7045 | 1.7903 | 709.5517 | 1.9658 | 990.994 | 2.1787 | 1585.5904 | 2.1787 | 58.51 | 0.2141 | 71.8597 | 0.2534 | 84.0843 | 0.2911 | 99.0994 | 0.3024 | 132.1325 | 0.3024 | 1354.1053 | 0.0209 | [18 empty] | 84.0843 | 0.2958 | 99.0994 | 0.3063 | 132.1325 | 0.3063 | 165.1657 | 0.3063 | 214.7154 | 0.3063 | 264.2651 | 0.3063 | [10 empty] | 9795.3216 | 0.0576 | 2077.3683 | 0.1484 | 11022.1521 | 0.0584
56.3647 | 0.4639 | 73.2969 | 0.5697 | 88.8291 | 0.666 | 101.0814 | 0.6871 | 134.7752 | 0.6871 | 1758.0434 | 0.016 | 973.0176 | 0.0342 | 720.3321 | 0.0869 | 733.4153 | 0.132 | 737.0913 | 0.2245 | 1225.0156 | 0.1209 | 1016.0854 | 0.2824 | 1407.6925 | 0.2294 |  |  | 2718.1551 | 0.1254 | 11368.4211 | 0.016 | [6 empty] | 60.8179 | 1.0301 | 72.4845 | 1.3743 | 92.0147 | 1.4758 | 113.7503 | 1.6508 | 143.1986 | 1.6859 | 181.6769 | 1.7456 | 237.2043 | 1.6453 | 300.5487 | 1.6871 | 381.7507 | 1.6627 | 480.8105 | 1.6638 | 594.3585 | 1.7121 | 723.7427 | 1.88 | 1010.8139 | 2.0869 | 1617.3022 | 2.0869 | 59.6802 | 0.2057 | 73.2969 | 0.2433 | 85.766 | 0.2791 | 101.0814 | 0.29 | 134.7752 | 0.29 | 1437.3686 | 0.0205 | [18 empty] | 85.766 | 0.2849 | 101.0814 | 0.2948 | 134.7752 | 0.2948 | 168.469 | 0.2948 | 219.0097 | 0.2948 | 269.5504 | 0.2948 | [10 empty] | 10817.7752 | 0.0571 | 2209.3794 | 0.1371 | 11552.163 | 0.0581
57.4919 | 0.4444 | 74.7628 | 0.5454 | 90.6057 | 0.6371 | 103.103 | 0.6572 | 137.4707 | 0.6572 | 1969.0086 | 0.016 | 1052.9987 | 0.0308 | 787.3814 | 0.0725 | 796.8865 | 0.1114 | 800.0801 | 0.1894 | 1329.7041 | 0.1023 | 1076.761 | 0.2501 | 1497.7304 | 0.2013 |  |  | 2874.721 | 0.1117 | [8 empty] | 62.0343 | 0.9866 | 73.9342 | 1.3154 | 93.855 | 1.4118 | 116.0253 | 1.5791 | 146.0626 | 1.6127 | 185.3105 | 1.6697 | 241.9484 | 1.5737 | 306.5596 | 1.6138 | 389.3857 | 1.5904 | 490.4267 | 1.5915 | 606.2457 | 1.6377 | 738.2176 | 1.7982 | 1031.0301 | 1.9994 | 1649.6482 | 1.9994 | 60.8738 | 0.1977 | 74.7628 | 0.2336 | 87.4813 | 0.2678 | 103.103 | 0.2781 | 137.4707 | 0.2781 | 1698.8511 | 0.016 | [18 empty] | 87.4813 | 0.2745 | 103.103 | 0.284 | 137.4707 | 0.284 | 171.8384 | 0.284 | 223.3899 | 0.284 | 274.9414 | 0.284 | [10 empty] | 12072.4679 | 0.0567 | 2303.0227 | 0.1303
58.6418 | 0.4258 | 76.2581 | 0.5222 | 92.4178 | 0.6096 | 105.1651 | 0.6288 | 140.2201 | 0.6288 | 2679.9613 | 0.016 | 1132.7394 | 0.0281 | 865.8511 | 0.0598 | 849.5542 | 0.0978 | 877.1803 | 0.1566 | 1440.4507 | 0.0869 | 1141.058 | 0.2216 | 1625.7287 | 0.1696 |  |  | 3055.5304 | 0.0986 | [8 empty] | 63.275 | 0.9451 | 75.4129 | 1.2593 | 95.7321 | 1.3508 | 118.3458 | 1.5107 | 148.9839 | 1.5429 | 189.0167 | 1.5975 | 246.7874 | 1.5057 | 312.6908 | 1.5439 | 397.1734 | 1.5216 | 500.2352 | 1.5226 | 618.3706 | 1.5668 | 752.9819 | 1.7204 | 1051.6507 | 1.916 | 1682.6412 | 1.916 | 62.0913 | 0.19 | 76.2581 | 0.2243 | 89.231 | 0.257 | 105.1651 | 0.2668 | 140.2201 | 0.2668 | 2184.2372 | 0.016 | [18 empty] | 89.231 | 0.2647 | 105.1651 | 0.2736 | 140.2201 | 0.2736 | 175.2751 | 0.2736 | 227.8577 | 0.2736 | 280.4402 | 0.2736 | [12 empty] | 2444.8947 | 0.1214
59.8146 | 0.408 | 77.7832 | 0.5001 | 94.2661 | 0.5834 | 107.2684 | 0.6017 | 143.0245 | 0.6017 |  |  | 1210.0244 | 0.026 | 942.6667 | 0.0507 | 912.0661 | 0.0846 | 962.6718 | 0.1294 | 1582.4216 | 0.0718 | 1211.6099 | 0.1957 | 1740.1213 | 0.1472 |  |  | 3228.292 | 0.0881 | [8 empty] | 64.5405 | 0.9054 | 76.9212 | 1.2057 | 97.6467 | 1.2927 | 120.7127 | 1.4457 | 151.9635 | 1.4764 | 192.797 | 1.5287 | 251.7231 | 1.4408 | 318.9446 | 1.4774 | 405.1169 | 1.456 | 510.2399 | 1.457 | 630.738 | 1.4993 | 768.0416 | 1.6463 | 1072.6837 | 1.8364 | 1716.294 | 1.8364 | 63.3331 | 0.1826 | 77.7832 | 0.2154 | 91.0156 | 0.2466 | 107.2684 | 0.256 | 143.0245 | 0.256 | 3155.0093 | 0.014 | [18 empty] | 91.0156 | 0.2552 | 107.2684 | 0.2638 | 143.0245 | 0.2638 | 178.7806 | 0.2638 | 232.4148 | 0.2638 | 286.049 | 0.2638 | [12 empty] | 2502.3361 | 0.1183
61.0109 | 0.3911 | 79.3389 | 0.479 | 96.1515 | 0.5585 | 109.4137 | 0.5759 | 145.885 | 0.5759 |  |  | 1291.2909 | 0.0241 | 1030.4103 | 0.0441 | 1001.9595 | 0.0699 | 1105.1229 | 0.0977 | 1688.6885 | 0.063 | 1315.1535 | 0.1652 | 1885.0489 | 0.1248 |  |  | 3431.3553 | 0.0778 | [8 empty] | 65.8313 | 0.8675 | 78.4596 | 1.1546 | 99.5997 | 1.2374 | 123.1269 | 1.3836 | 155.0028 | 1.4131 | 196.653 | 1.4631 | 256.7576 | 1.379 | 325.3235 | 1.414 | 413.2192 | 1.3936 | 520.4447 | 1.3945 | 643.3528 | 1.435 | 783.4024 | 1.5757 | 1094.1374 | 1.7605 | 1750.6199 | 1.7605 | 64.5998 | 0.1756 | 79.3389 | 0.207 | 92.8359 | 0.2368 | 109.4137 | 0.2457 | 145.885 | 0.2457 | [20 empty] | 92.8359 | 0.2462 | 109.4137 | 0.2544 | 145.885 | 0.2544 | 182.3562 | 0.2544 | 237.0631 | 0.2544 | 291.77 | 0.2544 | [12 empty] | 2655.1367 | 0.1109
62.2311 | 0.3748 | 80.9257 | 0.4588 | 98.0745 | 0.5347 | 111.602 | 0.5513 | 148.8027 | 0.5513 |  |  | 1357.5006 | 0.0228 | 1111.5789 | 0.0392 | 1060.7298 | 0.0623 | 1209.1978 | 0.0813 | 1814.7638 | 0.0544 | 1440.4507 | 0.137 | 2011.6467 | 0.1092 |  |  | 3628.994 | 0.0694 | [8 empty] | 67.1479 | 0.8314 | 80.0288 | 1.1059 | 101.5917 | 1.1846 | 125.5895 | 1.3245 | 158.1029 | 1.3527 | 200.586 | 1.4006 | 261.8927 | 1.3201 | 331.83 | 1.3536 | 421.4836 | 1.334 | 530.8536 | 1.3349 | 656.2199 | 1.3737 | 799.0704 | 1.5084 | 1116.0202 | 1.688 | 1785.6323 | 1.688 | 65.8918 | 0.1689 | 80.9257 | 0.1989 | 94.6926 | 0.2273 | 111.602 | 0.2359 | 148.8027 | 0.2359 | [20 empty] | 94.6926 | 0.2379 | 111.602 | 0.2455 | 148.8027 | 0.2455 | 186.0034 | 0.2455 | 241.8044 | 0.2455 | 297.6054 | 0.2455 | [12 empty] | 2796.0923 | 0.1052
63.4758 | 0.3593 | 82.5442 | 0.4396 | 100.036 | 0.512 | 113.8341 | 0.5278 | 151.7787 | 0.5278 |  |  | 1411.4829 | 0.0219 | 1197.9891 | 0.0352 | 1129.6977 | 0.0549 | 1323.068 | 0.0678 | 1985.6691 | 0.0467 | 1595.1269 | 0.1112 | 2161.8321 | 0.0942 |  |  | 3834.1804 | 0.062 | [8 empty] | 68.4909 | 0.7968 | 81.6294 | 1.0593 | 103.6235 | 1.1343 | 128.1013 | 1.2682 | 161.2649 | 1.2951 | 204.5977 | 1.341 | 267.1306 | 1.2639 | 338.4666 | 1.296 | 429.9133 | 1.2773 | 541.4707 | 1.2781 | 669.3443 | 1.3153 | 815.0519 | 1.4442 | 1138.3406 | 1.6189 | 1821.3449 | 1.6189 | 67.2096 | 0.1624 | 82.5442 | 0.1911 | 96.5865 | 0.2183 | 113.8341 | 0.2265 | 151.7787 | 0.2265 | [20 empty] | 96.5865 | 0.2303 | 113.8341 | 0.2372 | 151.7787 | 0.2372 | 189.7234 | 0.2372 | 246.6405 | 0.2372 | 303.5575 | 0.2372 | [12 empty] | 2932.0391 | 0.1005
64.7453 | 0.3445 | 84.1951 | 0.4212 | 102.0367 | 0.4903 | 116.1107 | 0.5054 | 154.8143 | 0.5054 |  |  | 1451.5705 | 0.0213 | 1312.1179 | 0.031 | 1193.5801 | 0.0497 | 1443.3297 | 0.0568 | 2159.6645 | 0.041 | 1738.3761 | 0.0933 | 2339.5402 | 0.0801 |  |  | 4055.0178 | 0.0554 | [8 empty] | 69.8607 | 0.7637 | 83.262 | 1.0149 | 105.696 | 1.0863 | 130.6633 | 1.2144 | 164.4902 | 1.2402 | 208.6897 | 1.2841 | 272.4732 | 1.2103 | 345.2359 | 1.2411 | 438.5116 | 1.2231 | 552.3001 | 1.2239 | 682.7311 | 1.2595 | 831.3529 | 1.383 | 1161.1074 | 1.5528 | 1857.7718 | 1.5528 | 68.5538 | 0.1563 | 84.1951 | 0.1837 | 98.5182 | 0.2097 | 116.1107 | 0.2175 | 154.8143 | 0.2175 | [20 empty] | 98.5182 | 0.2229 | 116.1107 | 0.2296 | 154.8143 | 0.2296 | 193.5179 | 0.2296 | 251.5733 | 0.2296 | 309.6286 | 0.2296 | [12 empty] | 3056.3584 | 0.0967
66.0402 | 0.3303 | 85.879 | 0.4037 | 104.0774 | 0.4697 | 118.433 | 0.4841 | 157.9106 | 0.4841 |  |  | 1477.9352 | 0.0209 | 1469.0931 | 0.0267 | 1253.5165 | 0.046 | 1576.0967 | 0.0485 | 2410.1053 | 0.0349 | 1900.1886 | 0.0779 | 2575.2728 | 0.0659 |  |  | 4297.1641 | 0.0498 | [8 empty] | 71.2579 | 0.7321 | 84.9272 | 0.9725 | 107.8099 | 1.0405 | 133.2765 | 1.1631 | 167.78 | 1.1878 | 212.8635 | 1.2299 | 277.9227 | 1.1592 | 352.1406 | 1.1886 | 447.2818 | 1.1714 | 563.3461 | 1.1722 | 696.3858 | 1.2063 | 847.9799 | 1.3245 | 1184.3295 | 1.4897 | 1894.9273 | 1.4897 | 69.9249 | 0.1504 | 85.879 | 0.1766 | 100.4886 | 0.2015 | 118.433 | 0.209 | 157.9106 | 0.209 | [20 empty] | 100.4886 | 0.2159 | 118.433 | 0.2223 | 157.9106 | 0.2223 | 197.3883 | 0.2223 | 256.6047 | 0.2223 | 315.8212 | 0.2223 | [12 empty] | 3141.2392 | 0.0944
67.361 | 0.3168 | 87.5965 | 0.3869 | 106.159 | 0.4499 | 120.8016 | 0.4637 | 161.0688 | 0.4637 |  |  | 1551.2455 | 0.016 | 1575.6126 | 0.0245 | 1349.0526 | 0.041 | 1768.4211 | 0.0405 | 2569.3238 | 0.0319 | 2068.7707 | 0.0656 | 2863.2384 | 0.0531 |  |  | 4517.4791 | 0.046 | [8 empty] | 72.683 | 0.7019 | 86.6257 | 0.9319 | 109.9661 | 0.9967 | 135.9421 | 1.1141 | 171.1356 | 1.1378 | 217.1208 | 1.1781 | 283.4811 | 1.1104 | 359.1835 | 1.1386 | 456.2274 | 1.1221 | 574.613 | 1.1229 | 710.3135 | 1.1555 | 864.9395 | 1.2688 | 1208.0161 | 1.4293 | 1932.8258 | 1.4293 | 71.3234 | 0.1447 | 87.5965 | 0.1699 | 102.4983 | 0.1937 | 120.8016 | 0.2008 | 161.0688 | 0.2008 | [20 empty] | 102.4983 | 0.2092 | 120.8016 | 0.2153 | 161.0688 | 0.2153 | 201.336 | 0.2153 | 261.7368 | 0.2153 | 322.1376 | 0.2153 | [12 empty] | 3381.1758 | 0.0888
68.7082 | 0.3038 | 89.3485 | 0.3708 | 108.2822 | 0.4311 | 123.2176 | 0.4442 | 164.2902 | 0.4442 |  |  | 1745.1512 | 0.016 | 1666.368 | 0.023 | 1408.6636 | 0.0385 | 1955.3684 | 0.0349 | 2816.9229 | 0.0282 | 2297.8004 | 0.053 | 3218.6213 | 0.0439 |  |  | 4758.6028 | 0.0424 | [8 empty] | 74.1367 | 0.673 | 88.3583 | 0.8932 | 112.1654 | 0.955 | 138.6609 | 1.0674 | 174.5583 | 1.0901 | 221.4632 | 1.1287 | 289.1507 | 1.0638 | 366.3671 | 1.0908 | 465.352 | 1.075 | 586.1053 | 1.0757 | 724.5198 | 1.107 | 882.2383 | 1.2155 | 1232.1764 | 1.3716 | 1971.4823 | 1.3716 | 72.7499 | 0.1393 | 89.3485 | 0.1634 | 104.5483 | 0.1862 | 123.2176 | 0.193 | 164.2902 | 0.193 | [20 empty] | 104.5483 | 0.2028 | 123.2176 | 0.2086 | 164.2902 | 0.2086 | 205.3627 | 0.2086 | 266.9716 | 0.2086 | 328.5804 | 0.2086 | [12 empty] | 3397.1429 | 0.0885
70.0824 | 0.2914 | 91.1354 | 0.3555 | 110.4478 | 0.4131 | 125.682 | 0.4256 | 167.576 | 0.4256 |  |  | 1939.0568 | 0.016 | 1743.0669 | 0.0219 | 1512.3133 | 0.0347 | 2148.2274 | 0.0306 | 3057.6404 | 0.0254 | 2496.6619 | 0.0463 | 3738.9474 | 0.0351 |  |  | 5012.5986 | 0.0392 | [8 empty] | 75.6194 | 0.6454 | 90.1254 | 0.8562 | 114.4087 | 0.9151 | 141.4341 | 1.0227 | 178.0495 | 1.0445 | 225.8924 | 1.0814 | 294.9338 | 1.0193 | 373.6945 | 1.0452 | 474.659 | 1.03 | 597.8274 | 1.0307 | 739.0101 | 1.0607 | 899.8831 | 1.1647 | 1256.82 | 1.3165 | 2010.912 | 1.3165 | 74.2049 | 0.1341 | 91.1354 | 0.1572 | 106.6393 | 0.179 | 125.682 | 0.1855 | 167.576 | 0.1855 | [20 empty] | 106.6393 | 0.1967 | 125.682 | 0.2023 | 167.576 | 0.2023 | 209.47 | 0.2023 | 272.311 | 0.2023 | 335.152 | 0.2023 | [12 empty] | 3633.5986 | 0.0841
71.484 | 0.2795 | 92.9582 | 0.3409 | 112.6568 | 0.3959 | 128.1956 | 0.4079 | 170.9275 | 0.4079 |  |  | 2171.7437 | 0.016 | 1817.8257 | 0.0209 | 1593.0341 | 0.0322 | 2320.1785 | 0.0277 | 3292.4867 | 0.0233 | 2789.7519 | 0.039 | 4029.504 | 0.0316 |  |  | 5294.3697 | 0.0361 | [8 empty] | 77.1318 | 0.619 | 91.9279 | 0.8208 | 116.6969 | 0.877 | 144.2628 | 0.98 | 181.6105 | 1.0009 | 230.4103 | 1.0363 | 300.8324 | 0.9767 | 381.1684 | 1.0016 | 484.1522 | 0.9871 | 609.7839 | 0.9877 | 753.7904 | 1.0164 | 917.8808 | 1.1161 | 1281.9564 | 1.2637 | 2051.1302 | 1.2637 | 75.689 | 0.1291 | 92.9582 | 0.1512 | 108.7721 | 0.1721 | 128.1956 | 0.1783 | 170.9275 | 0.1783 | [20 empty] | 108.7721 | 0.1908 | 128.1956 | 0.1962 | 170.9275 | 0.1962 | 213.6594 | 0.1962 | 277.7572 | 0.1962 | 341.855 | 0.1962 | [12 empty] | 3708.5841 | 0.0829
72.9137 | 0.2681 | 94.8173 | 0.3268 | 114.9099 | 0.3795 | 130.7596 | 0.3909 | 174.3461 | 0.3909 |  |  | 2955.8982 | 0.016 | 1869.4535 | 0.0203 | 1703.4341 | 0.0294 | 2490.8968 | 0.0253 | 3581.0122 | 0.0212 | 3077.0526 | 0.0338 | 4321.6775 | 0.0287 |  |  | 5604.9145 | 0.0333 | [8 empty] | 78.6745 | 0.5937 | 93.7665 | 0.7869 | 119.0308 | 0.8406 | 147.1481 | 0.9393 | 185.2427 | 0.9593 | 235.0185 | 0.9932 | 306.8491 | 0.9361 | 388.7917 | 0.9599 | 493.8352 | 0.946 | 621.9796 | 0.9467 | 768.8662 | 0.9742 | 936.2384 | 1.0697 | 1307.5955 | 1.2132 | 2092.1528 | 1.2132 | 77.2027 | 0.1243 | 94.8173 | 0.1455 | 110.9475 | 0.1655 | 130.7596 | 0.1715 | 174.3461 | 0.1715 | [20 empty] | 110.9475 | 0.1852 | 130.7596 | 0.1903 | 174.3461 | 0.1903 | 217.9326 | 0.1903 | 283.3124 | 0.1903 | 348.6921 | 0.1903 | [12 empty] | 3940.1781 | 0.0795
74.372 | 0.2572 | 96.7137 | 0.3134 | 117.2081 | 0.3638 | 133.3747 | 0.3747 | 177.833 | 0.3747 |  |  |  |  | 1897.6977 | 0.016 | 1799.7474 | 0.0274 | 2687.5857 | 0.0232 | 3840.6568 | 0.016 | 3295.7811 | 0.0308 | 4602.7048 | 0.0265 |  |  | 5892.288 | 0.0311 | [8 empty] | 80.248 | 0.5694 | 95.6418 | 0.7545 | 121.4114 | 0.8057 | 150.091 | 0.9003 | 188.9476 | 0.9195 | 239.7189 | 0.952 | 312.9861 | 0.8973 | 396.5676 | 0.9201 | 503.7119 | 0.9068 | 634.4192 | 0.9074 | 784.2435 | 0.9338 | 954.9632 | 1.0253 | 1333.7474 | 1.1649 | 2133.9959 | 1.1649 | 78.7468 | 0.1198 | 96.7137 | 0.1401 | 113.1664 | 0.1592 | 133.3747 | 0.1649 | 177.833 | 0.1649 | [20 empty] | 113.1664 | 0.1799 | 133.3747 | 0.1847 | 177.833 | 0.1847 | 222.2912 | 0.1847 | 288.9786 | 0.1847 | 355.666 | 0.1847 | [12 empty] | 3998.1615 | 0.0788
75.8594 | 0.2468 | 98.6479 | 0.3006 | 119.5523 | 0.3487 | 136.0422 | 0.3592 | 181.3896 | 0.3592 |  |  |  |  | 1991.8296 | 0.016 | 1912.9465 | 0.0254 | 2791.68 | 0.0222 | 3957.6253 | 0.016 | 3573.8577 | 0.0276 | 4971.1124 | 0.0241 |  |  | 6206.7941 | 0.029 | [8 empty] | 81.8529 | 0.5462 | 97.5547 | 0.7236 | 123.8397 | 0.7724 | 153.0929 | 0.8631 | 192.7265 | 0.8814 | 244.5132 | 0.9126 | 319.2458 | 0.8602 | 404.4989 | 0.882 | 513.7862 | 0.8693 | 647.1076 | 0.8699 | 799.9284 | 0.8951 | 974.0624 | 0.9829 | 1360.4224 | 1.1186 | 2176.6758 | 1.1186 | 80.3217 | 0.1154 | 98.6479 | 0.1349 | 115.4298 | 0.1532 | 136.0422 | 0.1587 | 181.3896 | 0.1587 | [20 empty] | 115.4298 | 0.1747 | 136.0422 | 0.1794 | 181.3896 | 0.1794 | 226.7371 | 0.1794 | 294.7582 | 0.1794 | 362.7793 | 0.1794 | [12 empty] | 4221.6457 | 0.0762
77.3766 | 0.2368 | 100.6209 | 0.2883 | 121.9433 | 0.3344 | 138.7631 | 0.3444 | 185.0174 | 0.3444 |  |  |  |  | 2240.8083 | 0.016 | 2004.9954 | 0.024 | 2905.6168 | 0.0213 | 4009.4147 | 0.016 | 3829.1571 | 0.0254 | 5241.6909 | 0.0227 |  |  | 6485.9924 | 0.0274 | [8 empty] | 83.49 | 0.524 | 99.5057 | 0.6939 | 126.3165 | 0.7406 | 156.1547 | 0.8275 | 196.581 | 0.8451 | 249.4035 | 0.875 | 325.6307 | 0.8247 | 412.5889 | 0.8456 | 524.0619 | 0.8334 | 660.0497 | 0.834 | 815.9269 | 0.8582 | 993.5437 | 0.9423 | 1387.6308 | 1.0743 | 2220.2093 | 1.0743 | 81.9282 | 0.1112 | 100.6209 | 0.1298 | 117.7384 | 0.1474 | 138.7631 | 0.1527 | 185.0174 | 0.1527 | [20 empty] | 117.7384 | 0.1698 | 138.7631 | 0.1743 | 185.0174 | 0.1743 | 231.2718 | 0.1743 | 300.6533 | 0.1743 | 370.0349 | 0.1743 | [12 empty] | 4351.0515 | 0.0749
78.9241 | 0.2272 | 102.6333 | 0.2765 | 124.3822 | 0.3206 | 141.5383 | 0.3302 | 188.7178 | 0.3302 |  |  |  |  | 2489.7869 | 0.016 | 2082.6543 | 0.023 | 3012.1162 | 0.0205 | 4208.2945 | 0.016 | 4185.5798 | 0.0229 | 5571.3853 | 0.0213 |  |  | 6859.5638 | 0.0255 | [8 empty] | 85.1598 | 0.5028 | 101.4959 | 0.6656 | 128.8428 | 0.7102 | 159.2778 | 0.7934 | 200.5127 | 0.8103 | 254.3916 | 0.839 | 332.1433 | 0.7907 | 420.8407 | 0.8108 | 534.5431 | 0.7991 | 673.2507 | 0.7996 | 832.2455 | 0.8229 | 1013.4145 | 0.9035 | 1415.3834 | 1.0318 | 2264.6135 | 1.0318 | 83.5667 | 0.1071 | 102.6333 | 0.125 | 120.0931 | 0.1419 | 141.5383 | 0.1469 | 188.7178 | 0.1469 | [20 empty] | 120.0931 | 0.1651 | 141.5383 | 0.1694 | 188.7178 | 0.1694 | 235.8972 | 0.1694 | 306.6664 | 0.1694 | 377.4356 | 0.1694 | [12 empty] | 4614.6017 | 0.0726
80.5026 | 0.218 | 104.686 | 0.2653 | 126.8698 | 0.3075 | 144.3691 | 0.3166 | 192.4921 | 0.3166 |  |  |  |  | 2788.5614 | 0.016 | 2161.1621 | 0.0221 | 3122.5364 | 0.016 | 4734.3313 | 0.016 | 4400.1752 | 0.0216 | 5939.6109 | 0.016 |  |  | 7132.3756 | 0.0244 | [8 empty] | 86.863 | 0.4824 | 103.5258 | 0.6384 | 131.4196 | 0.681 | 162.4634 | 0.7608 | 204.5229 | 0.777 | 259.4794 | 0.8045 | 338.7862 | 0.7583 | 429.2575 | 0.7775 | 545.234 | 0.7663 | 686.7157 | 0.7668 | 848.8904 | 0.7891 | 1033.6828 | 0.8664 | 1443.6911 | 0.9912 | 2309.9058 | 0.9912 | 85.2381 | 0.1032 | 104.686 | 0.1204 | 122.495 | 0.1366 | 144.3691 | 0.1414 | 192.4921 | 0.1414 | [20 empty] | 122.495 | 0.1606 | 144.3691 | 0.1647 | 192.4921 | 0.1647 | 240.6152 | 0.1647 | 312.7997 | 0.1647 | 384.9843 | 0.1647 | [12 empty] | 4779.7976 | 0.0713
82.1127 | 0.2092 | 106.7797 | 0.2545 | 129.4072 | 0.2949 | 147.2565 | 0.3037 | 196.342 | 0.3037 |  |  |  |  | 3795.4312 | 0.014 | 2231.4341 | 0.0213 | 3166.5549 | 0.016 | 5260.3682 | 0.016 | 4621.1571 | 0.0205 | 6169.6674 | 0.016 |  |  | 7475.6008 | 0.0231 | [8 empty] | 88.6002 | 0.4629 | 105.5963 | 0.6124 | 134.048 | 0.6532 | 165.7126 | 0.7296 | 208.6134 | 0.7452 | 264.669 | 0.7716 | 345.5619 | 0.7272 | 437.8426 | 0.7457 | 556.1387 | 0.7349 | 700.45 | 0.7354 | 865.8682 | 0.7567 | 1054.3565 | 0.8309 | 1472.5649 | 0.9522 | 2356.1039 | 0.9522 | 86.9428 | 0.0995 | 106.7797 | 0.116 | 124.9449 | 0.1315 | 147.2565 | 0.1361 | 196.342 | 0.1361 | [20 empty] | 124.9449 | 0.1563 | 147.2565 | 0.1602 | 196.342 | 0.1602 | 245.4275 | 0.1602 | 319.0557 | 0.1602 | 392.684 | 0.1602 | [12 empty] | 4851.1931 | 0.0708
83.7549 | 0.2008 | 108.9153 | 0.2442 | 131.9954 | 0.2829 | 150.2016 | 0.2913 | 200.2688 | 0.2913 | [6 empty] | 2285.6387 | 0.0208 | 3323.6262 | 0.016 | 5891.6123 | 0.016 | 4780.9718 | 0.016 | 6262.9086 | 0.016 |  |  | 7772.9078 | 0.0221 | [8 empty] | 90.3722 | 0.4442 | 107.7082 | 0.5875 | 136.729 | 0.6265 | 169.0269 | 0.6998 | 212.7856 | 0.7147 | 269.9624 | 0.74 | 352.4731 | 0.6975 | 446.5995 | 0.7152 | 567.2615 | 0.7048 | 714.459 | 0.7053 | 883.1855 | 0.7258 | 1075.4436 | 0.797 | 1502.0162 | 0.9149 | 2403.2259 | 0.9149 | 88.6817 | 0.096 | 108.9153 | 0.1118 | 127.4438 | 0.1266 | 150.2016 | 0.131 | 200.2688 | 0.131 | [20 empty] | 127.4438 | 0.1522 | 150.2016 | 0.1559 | 200.2688 | 0.1559 | 250.336 | 0.1559 | 325.4368 | 0.1559 | 400.5377 | 0.1559 | [12 empty] | 5094.8257 | 0.0692
85.43 | 0.1927 | 111.0936 | 0.2343 | 134.6353 | 0.2713 | 153.2057 | 0.2794 | 204.2742 | 0.2794 | [6 empty] | 2313.2261 | 0.0205 | 3739.0795 | 0.016 | 8018.9052 | 0.014 | 4906.9137 | 0.016 | 6573.5689 | 0.016 |  |  | 8090.1221 | 0.0211 | [8 empty] | 92.1797 | 0.4263 | 109.8624 | 0.5637 | 139.4636 | 0.6009 | 172.4074 | 0.6713 | 217.0413 | 0.6855 | 275.3616 | 0.7098 | 359.5226 | 0.669 | 455.5315 | 0.686 | 578.6067 | 0.6761 | 728.7482 | 0.6765 | 900.8492 | 0.6962 | 1096.9525 | 0.7644 | 1532.0565 | 0.8791 | 2451.2905 | 0.8791 | 90.4553 | 0.0925 | 111.0936 | 0.1077 | 129.9927 | 0.122 | 153.2057 | 0.1262 | 204.2742 | 0.1262 | [20 empty] | 129.9927 | 0.1482 | 153.2057 | 0.1518 | 204.2742 | 0.1518 | 255.3428 | 0.1518 | 331.9456 | 0.1518 | 408.5484 | 0.1518 | [12 empty] | 5223.4489 | 0.0685
87.1386 | 0.185 | 113.3155 | 0.2248 | 137.328 | 0.2603 | 156.2698 | 0.268 | 208.3597 | 0.268 | [6 empty] | 2427.9695 | 0.016 | 4154.5327 | 0.016 |  |  | 4981.0661 | 0.016 | 7395.265 | 0.016 |  |  | 8386.6712 | 0.0204 | [8 empty] | 94.0233 | 0.4092 | 112.0596 | 0.5409 | 142.2528 | 0.5765 | 175.8556 | 0.6439 | 221.3822 | 0.6576 | 280.8689 | 0.6809 | 366.7131 | 0.6418 | 464.6421 | 0.6581 | 590.1788 | 0.6485 | 743.3232 | 0.649 | 918.8662 | 0.6678 | 1118.8915 | 0.7333 | 1562.6977 | 0.8447 | 2500.3163 | 0.8447 | 92.2644 | 0.0892 | 113.3155 | 0.1038 | 132.5925 | 0.1175 | 156.2698 | 0.1215 | 208.3597 | 0.1215 | [20 empty] | 132.5925 | 0.1444 | 156.2698 | 0.1479 | 208.3597 | 0.1479 | 260.4496 | 0.1479 | 338.5845 | 0.1479 | 416.7194 | 0.1479 | [12 empty] | 5720.2125 | 0.066
88.8814 | 0.1776 | 115.5818 | 0.2158 | 140.0745 | 0.2497 | 159.3952 | 0.2571 | 212.5269 | 0.2571 | [6 empty] | 2731.4657 | 0.016 | 4653.0767 | 0.016 |  |  | 5228.1429 | 0.016 | 8216.9612 | 0.016 |  |  | 8598.9827 | 0.016 | [8 empty] | 95.9037 | 0.3927 | 114.3008 | 0.519 | 145.0979 | 0.5531 | 179.3727 | 0.6178 | 225.8098 | 0.6309 | 286.4862 | 0.6532 | 374.0473 | 0.6157 | 473.9349 | 0.6313 | 601.9824 | 0.6222 | 758.1897 | 0.6226 | 937.2436 | 0.6407 | 1141.2694 | 0.7035 | 1593.9516 | 0.8118 | 2550.3226 | 0.8118 | 94.1097 | 0.0861 | 115.5818 | 0.1001 | 135.2444 | 0.1132 | 159.3952 | 0.1171 | 212.5269 | 0.1171 | [20 empty] | 135.2444 | 0.1408 | 159.3952 | 0.1441 | 212.5269 | 0.1441 | 265.6586 | 0.1441 | 345.3562 | 0.1441 | 425.0538 | 0.1441 | [12 empty] | 6173.3083 | 0.0643
90.659 | 0.1705 | 117.8934 | 0.2071 | 142.876 | 0.2396 | 162.5831 | 0.2467 | 216.7774 | 0.2467 | [6 empty] | 3034.9619 | 0.016 | 6333.1697 | 0.014 |  |  | 5881.6608 | 0.016 | 9202.9965 | 0.016 |  |  | 8816.6703 | 0.016 | [8 empty] | 97.8218 | 0.377 | 116.5868 | 0.4981 | 147.9999 | 0.5307 | 182.9601 | 0.5927 | 230.326 | 0.6053 | 292.216 | 0.6267 | 381.5283 | 0.5907 | 483.4136 | 0.6057 | 614.022 | 0.5969 | 773.3534 | 0.5973 | 955.9884 | 0.6147 | 1164.0948 | 0.675 | 1625.8307 | 0.7803 | 2601.3291 | 0.7803 | 95.9919 | 0.0831 | 117.8934 | 0.0965 | 137.9493 | 0.1091 | 162.5831 | 0.1128 | 216.7774 | 0.1128 | [20 empty] | 137.9493 | 0.1373 | 162.5831 | 0.1405 | 216.7774 | 0.1405 | 270.9718 | 0.1405 | 352.2633 | 0.1405 | 433.5548 | 0.1405 | [12 empty] | 6859.964 | 0.0624
92.4722 | 0.1637 | 120.2513 | 0.1987 | 145.7335 | 0.2299 | 165.8347 | 0.2367 | 221.113 | 0.2367 | [6 empty] | 3399.1573 | 0.016 |  |  |  |  | 6535.1786 | 0.016 |  |  |  |  | 9254.0054 | 0.016 | [8 empty] | 99.7782 | 0.3618 | 118.9186 | 0.478 | 150.9599 | 0.5092 | 186.6193 | 0.5687 | 234.9325 | 0.5808 | 298.0603 | 0.6013 | 389.1588 | 0.5668 | 493.0819 | 0.5812 | 626.3025 | 0.5728 | 788.8205 | 0.5731 | 975.1082 | 0.5898 | 1187.3766 | 0.6476 | 1658.3473 | 0.75 | 2653.3556 | 0.75 | 97.9117 | 0.0801 | 120.2513 | 0.093 | 140.7083 | 0.1051 | 165.8347 | 0.1087 | 221.113 | 0.1087 | [20 empty] | 140.7083 | 0.1339 | 165.8347 | 0.137 | 221.113 | 0.137 | 276.3912 | 0.137 | 359.3086 | 0.137 | 442.2259 | 0.137 | [12 empty] | 7622.9972 | 0.0608
94.3216 | 0.1571 | 122.6563 | 0.1907 | 148.6482 | 0.2206 | 169.1514 | 0.2271 | 225.5352 | 0.2271 | [6 empty] | 4626.4959 | 0.016 |  |  |  |  | 7319.4001 | 0.016 |  |  |  |  | 10410.756 | 0.016 | [8 empty] | 101.7738 | 0.3474 | 121.2969 | 0.4588 | 153.9791 | 0.4886 | 190.3517 | 0.5457 | 239.6312 | 0.5573 | 304.0215 | 0.577 | 396.942 | 0.5439 | 502.9436 | 0.5577 | 638.8285 | 0.5496 | 804.5969 | 0.55 | 994.6104 | 0.566 | 1211.1242 | 0.6214 | 1691.5142 | 0.7209 | 2706.4227 | 0.7209 | 99.87 | 0.0774 | 122.6563 | 0.0897 | 143.5224 | 0.1013 | 169.1514 | 0.1048 | 225.5352 | 0.1048 | [20 empty] | 143.5224 | 0.1307 | 169.1514 | 0.1336 | 225.5352 | 0.1336 | 281.919 | 0.1336 | 366.4947 | 0.1336 | 451.0705 | 0.1336 | [12 empty] | 8559.8208 | 0.0595
96.2081 | 0.1509 | 125.1094 | 0.1831 | 151.6212 | 0.2117 | 172.5344 | 0.2179 | 230.0459 | 0.2179 | [12 empty] | 9962.2263 | 0.014 |  |  |  |  | 11567.5067 | 0.016 | [8 empty] | 103.8093 | 0.3335 | 123.7229 | 0.4403 | 157.0586 | 0.4689 | 194.1588 | 0.5237 | 244.4238 | 0.5348 | 310.1019 | 0.5537 | 404.8808 | 0.5219 | 513.0024 | 0.5352 | 651.6051 | 0.5274 | 820.6889 | 0.5278 | 1014.5026 | 0.5431 | 1235.3467 | 0.5963 | 1725.3445 | 0.6931 | 2760.5512 | 0.6931 | 101.8674 | 0.0747 | 125.1094 | 0.0866 | 146.3929 | 0.0977 | 172.5344 | 0.101 | 230.0459 | 0.101 | [20 empty] | 146.3929 | 0.1277 | 172.5344 | 0.1305 | 230.0459 | 0.1305 | 287.5574 | 0.1305 | 373.8246 | 0.1305 | 460.0919 | 0.1305 | [12 empty] | 9325.0671 | 0.0588
98.1322 | 0.1448 | 127.6116 | 0.1758 | 154.6536 | 0.2032 | 175.9851 | 0.2092 | 234.6469 | 0.2092 | [28 empty] | 105.8855 | 0.3201 | 126.1973 | 0.4227 | 160.1998 | 0.45 | 198.0419 | 0.5026 | 249.3123 | 0.5132 | 316.304 | 0.5314 | 412.9785 | 0.5009 | 523.2625 | 0.5136 | 664.6372 | 0.5062 | 837.1026 | 0.5065 | 1034.7926 | 0.5212 | 1260.0536 | 0.5723 | 1759.8514 | 0.6663 | 2815.7622 | 0.6663 | 103.9047 | 0.0721 | 127.6116 | 0.0835 | 149.3207 | 0.0942 | 175.9851 | 0.0973 | 234.6469 | 0.0973 | [20 empty] | 149.3207 | 0.1247 | 175.9851 | 0.1274 | 234.6469 | 0.1274 | 293.3086 | 0.1274 | 381.3011 | 0.1274 | 469.2937 | 0.1274 | [12 empty] | 10042.7055 | 0.0582
100.0949 | 0.1391 | 130.1639 | 0.1687 | 157.7467 | 0.195 | 179.5048 | 0.2007 | 239.3398 | 0.2007 | [28 empty] | 108.0032 | 0.3074 | 128.7213 | 0.4057 | 163.4038 | 0.4319 | 202.0028 | 0.4823 | 254.2985 | 0.4926 | 322.63 | 0.51 | 421.238 | 0.4807 | 533.7277 | 0.4929 | 677.93 | 0.4858 | 853.8447 | 0.4861 | 1055.4885 | 0.5002 | 1285.2547 | 0.5493 | 1795.0484 | 0.6407 | 2872.0775 | 0.6407 | 105.9828 | 0.0696 | 130.1639 | 0.0806 | 152.3071 | 0.0908 | 179.5048 | 0.0939 | 239.3398 | 0.0939 | [20 empty] | 152.3071 | 0.1219 | 179.5048 | 0.1245 | 239.3398 | 0.1245 | 299.1747 | 0.1245 | 388.9272 | 0.1245 | 478.6796 | 0.1245 | [12 empty] | 10804.2846 | 0.0578
102.0968 | 0.1335 | 132.7671 | 0.162 | 160.9016 | 0.1872 | 183.0949 | 0.1927 | 244.1266 | 0.1927 | [28 empty] | 110.1632 | 0.2951 | 131.2957 | 0.3895 | 166.6719 | 0.4146 | 206.0428 | 0.4629 | 259.3845 | 0.4728 | 329.0826 | 0.4895 | 429.6628 | 0.4614 | 544.4023 | 0.4731 | 691.4886 | 0.4663 | 870.9216 | 0.4666 | 1076.5982 | 0.4801 | 1310.9598 | 0.5272 | 1830.9494 | 0.616 | 2929.519 | 0.616 | 108.1025 | 0.0672 | 132.7671 | 0.0778 | 155.3533 | 0.0876 | 183.0949 | 0.0905 | 244.1266 | 0.0905 | [20 empty] | 155.3533 | 0.1192 | 183.0949 | 0.1217 | 244.1266 | 0.1217 | 305.1582 | 0.1217 | 396.7057 | 0.1217 | 488.2532 | 0.1217 | [12 empty] | 11931.0558 | 0.0573
104.1387 | 0.1282 | 135.4225 | 0.1555 | 164.1196 | 0.1797 | 186.7568 | 0.1849 | 249.0091 | 0.1849 | [28 empty] | 112.3665 | 0.2834 | 133.9216 | 0.3739 | 170.0053 | 0.3979 | 210.1637 | 0.4444 | 264.5722 | 0.4538 | 335.6643 | 0.4699 | 438.256 | 0.4429 | 555.2903 | 0.4541 | 705.3183 | 0.4475 | 888.34 | 0.4478 | 1098.1302 | 0.4609 | 1337.179 | 0.506 | 1867.5684 | 0.5923 | 2988.1094 | 0.5923 | 110.2645 | 0.065 | 135.4225 | 0.0751 | 158.4603 | 0.0845 | 186.7568 | 0.0873 | 249.0091 | 0.0873 | [20 empty] | 158.4603 | 0.1166 | 186.7568 | 0.119 | 249.0091 | 0.119 | 311.2614 | 0.119 | 404.6398 | 0.119 | 498.0182 | 0.119
106.2215 | 0.1231 | 138.1309 | 0.1493 | 167.402 | 0.1725 | 190.492 | 0.1775 | 253.9893 | 0.1775 | [28 empty] | 114.6138 | 0.2721 | 136.6001 | 0.359 | 173.4054 | 0.382 | 214.367 | 0.4265 | 269.8636 | 0.4356 | 342.3776 | 0.451 | 447.0212 | 0.4251 | 566.3961 | 0.4359 | 719.4247 | 0.4296 | 906.1068 | 0.4299 | 1120.0928 | 0.4424 | 1363.9225 | 0.4858 | 1904.9197 | 0.5696 | 3047.8716 | 0.5696 | 112.4698 | 0.0629 | 138.1309 | 0.0725 | 161.6296 | 0.0815 | 190.492 | 0.0842 | 253.9893 | 0.0842 | [20 empty] | 161.6296 | 0.1141 | 190.492 | 0.1164 | 253.9893 | 0.1164 | 317.4866 | 0.1164 | 412.7326 | 0.1164 | 507.9786 | 0.1164
108.3459 | 0.1183 | 140.8935 | 0.1434 | 170.7501 | 0.1656 | 194.3018 | 0.1704 | 259.0691 | 0.1704 | [28 empty] | 116.9061 | 0.2613 | 139.3321 | 0.3447 | 176.8735 | 0.3667 | 218.6543 | 0.4095 | 275.2609 | 0.4182 | 349.2251 | 0.433 | 455.9616 | 0.4081 | 577.7241 | 0.4185 | 733.8132 | 0.4124 | 924.229 | 0.4127 | 1142.4947 | 0.4247 | 1391.201 | 0.4663 | 1943.0181 | 0.5478 | 3108.829 | 0.5478 | 114.7192 | 0.0608 | 140.8935 | 0.07 | 164.8621 | 0.0787 | 194.3018 | 0.0813 | 259.0691 | 0.0813 | [20 empty] | 164.8621 | 0.1117 | 194.3018 | 0.1139 | 259.0691 | 0.1139 | 323.8364 | 0.1139 | 420.9873 | 0.1139 | 518.1382 | 0.1139
110.5128 | 0.1136 | 143.7114 | 0.1377 | 174.1651 | 0.159 | 198.1878 | 0.1636 | 264.2505 | 0.1636 | [28 empty] | 119.2442 | 0.2509 | 142.1187 | 0.3309 | 180.411 | 0.3521 | 223.0274 | 0.3931 | 280.7661 | 0.4015 | 356.2096 | 0.4157 | 465.0808 | 0.3918 | 589.2785 | 0.4017 | 748.4894 | 0.3959 | 942.7135 | 0.3962 | 1165.3446 | 0.4077 | 1419.025 | 0.4477 | 1981.8785 | 0.5269 | 3171.0056 | 0.5269 | 117.0136 | 0.059 | 143.7114 | 0.0676 | 168.1594 | 0.076 | 198.1878 | 0.0784 | 264.2505 | 0.0784 | [20 empty] | 168.1594 | 0.1094 | 198.1878 | 0.1115 | 264.2505 | 0.1115 | 330.3131 | 0.1115 | 429.407 | 0.1115 | 528.5009 | 0.1115
112.7231 | 0.1091 | 146.5856 | 0.1322 | 177.6484 | 0.1526 | 202.1516 | 0.1571 | 269.5355 | 0.1571 | [28 empty] | 121.6291 | 0.241 | 144.9611 | 0.3178 | 184.0192 | 0.338 | 227.4879 | 0.3774 | 286.3814 | 0.3854 | 363.3338 | 0.3991 | 474.3824 | 0.3761 | 601.0641 | 0.3857 | 763.4592 | 0.3801 | 961.5678 | 0.3804 | 1188.6514 | 0.3914 | 1447.4055 | 0.4298 | 2021.5161 | 0.5067 | 3234.4257 | 0.5067 | 119.3539 | 0.0575 | 146.5856 | 0.0653 | 171.5226 | 0.0733 | 202.1516 | 0.0757 | 269.5355 | 0.0757 | [20 empty] | 171.5226 | 0.1072 | 202.1516 | 0.1092 | 269.5355 | 0.1092 | 336.9193 | 0.1092 | 437.9951 | 0.1092 | 539.071 | 0.1092
114.9775 | 0.1048 | 149.5174 | 0.1269 | 181.2013 | 0.1466 | 206.1946 | 0.1508 | 274.9262 | 0.1508 | [28 empty] | 124.0617 | 0.2314 | 147.8603 | 0.3051 | 187.6996 | 0.3245 | 232.0377 | 0.3623 | 292.1091 | 0.37 | 370.6005 | 0.3831 | 483.8701 | 0.3611 | 613.0854 | 0.3703 | 778.7284 | 0.3649 | 980.7992 | 0.3652 | 1212.4245 | 0.3758 | 1476.3536 | 0.4126 | 2061.9464 | 0.4874 | 3299.1142 | 0.4874 | 121.7409 | 0.0559 | 149.5174 | 0.0632 | 174.953 | 0.0708 | 206.1946 | 0.0731 | 274.9262 | 0.0731 | [20 empty] | 174.953 | 0.1051 | 206.1946 | 0.107 | 274.9262 | 0.107 | 343.6577 | 0.107 | 446.7551 | 0.107 | 549.8524 | 0.107
117.2771 | 0.1006 | 152.5077 | 0.1219 | 184.8254 | 0.1407 | 210.3185 | 0.1448 | 280.4247 | 0.1448 | [28 empty] | 126.5429 | 0.2223 | 150.8175 | 0.293 | 191.4536 | 0.3116 | 236.6785 | 0.3479 | 297.9513 | 0.3553 | 378.0125 | 0.3679 | 493.5475 | 0.3467 | 625.3471 | 0.3555 | 794.303 | 0.3504 | 1000.4152 | 0.3506 | 1236.673 | 0.3608 | 1505.8807 | 0.3962 | 2103.1853 | 0.4688 | 3365.0965 | 0.4688 | 124.1757 | 0.0545 | 152.5077 | 0.0611 | 178.4521 | 0.0684 | 210.3185 | 0.0706 | 280.4247 | 0.0706 | [20 empty] | 178.4521 | 0.1031 | 210.3185 | 0.1049 | 280.4247 | 0.1049 | 350.5309 | 0.1049 | 455.6902 | 0.1049 | 560.8494 | 0.1049
119.6226 | 0.0966 | 155.5579 | 0.1171 | 188.5219 | 0.1351 | 214.5249 | 0.139 | 286.0332 | 0.139 | [28 empty] | 129.0738 | 0.2135 | 153.8339 | 0.2814 | 195.2827 | 0.2992 | 241.412 | 0.334 | 303.9103 | 0.3412 | 385.5728 | 0.3532 | 503.4184 | 0.3329 | 637.854 | 0.3414 | 810.189 | 0.3364 | 1020.4235 | 0.3367 | 1261.4064 | 0.3465 | 1535.9983 | 0.3804 | 2145.249 | 0.451 | 3432.3984 | 0.451 | 126.6593 | 0.0531 | 155.5579 | 0.0593 | 182.0211 | 0.0661 | 214.5249 | 0.0682 | 286.0332 | 0.0682 | [20 empty] | 182.0211 | 0.1011 | 214.5249 | 0.1029 | 286.0332 | 0.1029 | 357.5415 | 0.1029 | 464.804 | 0.1029 | 572.0664 | 0.1029
122.0151 | 0.0928 | 158.669 | 0.1124 | 192.2923 | 0.1298 | 218.8154 | 0.1335 | 291.7539 | 0.1335 | [28 empty] | 131.6553 | 0.205 | 156.9105 | 0.2702 | 199.1883 | 0.2873 | 246.2403 | 0.3208 | 309.9885 | 0.3276 | 393.2842 | 0.3392 | 513.4868 | 0.3197 | 650.6111 | 0.3278 | 826.3928 | 0.3231 | 1040.8319 | 0.3233 | 1286.6346 | 0.3327 | 1566.7183 | 0.3653 | 2188.154 | 0.4339 | 3501.0464 | 0.4339 | 129.1925 | 0.0517 | 158.669 | 0.0577 | 185.6616 | 0.0639 | 218.8154 | 0.0659 | 291.7539 | 0.0659 | [20 empty] | 185.6616 | 0.0993 | 218.8154 | 0.101 | 291.7539 | 0.101 | 364.6923 | 0.101 | 474.1 | 0.101 | 583.5077 | 0.101
124.4554 | 0.0892 | 161.8424 | 0.108 | 196.1382 | 0.1246 | 223.1917 | 0.1282 | 297.5889 | 0.1282 | [28 empty] | 134.2884 | 0.1969 | 160.0487 | 0.2595 | 203.1721 | 0.2759 | 251.1651 | 0.308 | 316.1883 | 0.3146 | 401.1499 | 0.3257 | 523.7565 | 0.307 | 663.6233 | 0.3148 | 842.9207 | 0.3102 | 1061.6486 | 0.3104 | 1312.3672 | 0.3195 | 1598.0526 | 0.3508 | 2231.9171 | 0.4174 | 3571.0673 | 0.4174 | 131.7763 | 0.0504 | 161.8424 | 0.0562 | 189.3748 | 0.0618 | 223.1917 | 0.0637 | 297.5889 | 0.0637 | [20 empty] | 189.3748 | 0.0975 | 223.1917 | 0.0991 | 297.5889 | 0.0991 | 371.9862 | 0.0991 | 483.582 | 0.0991 | 595.1779 | 0.0991
126.9445 | 0.0856 | 165.0792 | 0.1037 | 200.0609 | 0.1197 | 227.6555 | 0.1231 | 303.5407 | 0.1231 | [28 empty] | 136.9741 | 0.1891 | 163.2497 | 0.2492 | 207.2355 | 0.2649 | 256.1884 | 0.2958 | 322.512 | 0.3021 | 409.1729 | 0.3128 | 534.2317 | 0.2948 | 676.8958 | 0.3023 | 859.7791 | 0.2979 | 1082.8815 | 0.2981 | 1338.6146 | 0.3068 | 1630.0137 | 0.3368 | 2276.5554 | 0.4015 | 3642.4887 | 0.4015 | 134.4118 | 0.0491 | 165.0792 | 0.0547 | 193.1623 | 0.0598 | 227.6555 | 0.0616 | 303.5407 | 0.0616 | [20 empty] | 193.1623 | 0.0958 | 227.6555 | 0.0973 | 303.5407 | 0.0973 | 379.4259 | 0.0973 | 493.2537 | 0.0973 | 607.0814 | 0.0973
129.4834 | 0.0823 | 168.3808 | 0.0996 | 204.0622 | 0.1149 | 232.2087 | 0.1182 | 309.6115 | 0.1182 | [28 empty] | 139.7136 | 0.1817 | 166.5147 | 0.2394 | 211.3802 | 0.2544 | 261.3121 | 0.2841 | 328.9623 | 0.2901 | 417.3564 | 0.3004 | 544.9163 | 0.2831 | 690.4337 | 0.2903 | 876.9747 | 0.2861 | 1104.5392 | 0.2863 | 1365.3869 | 0.2946 | 1662.614 | 0.3235 | 2322.0865 | 0.3863 | 3715.3385 | 0.3863 | 137.1001 | 0.0479 | 168.3808 | 0.0533 | 197.0255 | 0.0582 | 232.2087 | 0.0597 | 309.6115 | 0.0597 | [20 empty] | 197.0255 | 0.0941 | 232.2087 | 0.0956 | 309.6115 | 0.0956 | 387.0144 | 0.0956 | 503.1187 | 0.0956 | 619.2231 | 0.0956
132.0731 | 0.079 | 171.7484 | 0.0957 | 208.1434 | 0.1104 | 236.8528 | 0.1135 | 315.8038 | 0.1135 | [28 empty] | 142.5079 | 0.1745 | 169.845 | 0.2299 | 215.6078 | 0.2444 | 266.5384 | 0.2728 | 335.5415 | 0.2786 | 425.7035 | 0.2885 | 555.8146 | 0.2719 | 704.2424 | 0.2788 | 894.5142 | 0.2748 | 1126.6299 | 0.2749 | 1392.6946 | 0.2829 | 1695.8662 | 0.3107 | 2368.5283 | 0.3717 | 3789.6452 | 0.3717 | 139.8421 | 0.0468 | 171.7484 | 0.0519 | 200.966 | 0.0567 | 236.8528 | 0.0581 | 315.8038 | 0.0581 | [20 empty] | 200.966 | 0.0925 | 236.8528 | 0.094 | 315.8038 | 0.094 | 394.7547 | 0.094 | 513.1811 | 0.094 | 631.6075 | 0.094
134.7145 | 0.0759 | 175.1834 | 0.0919 | 212.3063 | 0.106 | 241.5899 | 0.109 | 322.1198 | 0.109 | [28 empty] | 145.3581 | 0.1676 | 173.2419 | 0.2208 | 219.92 | 0.2347 | 271.8691 | 0.262 | 342.2523 | 0.2676 | 434.2176 | 0.277 | 566.9309 | 0.2611 | 718.3273 | 0.2677 | 912.4045 | 0.2639 | 1149.1625 | 0.264 | 1420.5485 | 0.2717 | 1729.7836 | 0.2984 | 2415.8988 | 0.3576 | 3865.4381 | 0.3576 | 142.6389 | 0.0457 | 175.1834 | 0.0506 | 204.9854 | 0.0552 | 241.5899 | 0.0565 | 322.1198 | 0.0565 | [20 empty] | 204.9854 | 0.091 | 241.5899 | 0.0924 | 322.1198 | 0.0924 | 402.6498 | 0.0924 | 523.4447 | 0.0924 | 644.2397 | 0.0924
137.4088 | 0.0729 | 178.6871 | 0.0883 | 216.5524 | 0.1018 | 246.4217 | 0.1047 | 328.5622 | 0.1047 | [28 empty] | 148.2652 | 0.161 | 176.7067 | 0.2121 | 224.3184 | 0.2254 | 277.3065 | 0.2516 | 349.0974 | 0.257 | 442.9019 | 0.2661 | 578.2695 | 0.2508 | 732.6938 | 0.2572 | 930.6525 | 0.2534 | 1172.1458 | 0.2536 | 1448.9595 | 0.261 | 1764.3792 | 0.2866 | 2464.2168 | 0.3441 | 3942.7469 | 0.3441 | 145.4917 | 0.0446 | 178.6871 | 0.0493 | 209.0851 | 0.0537 | 246.4217 | 0.055 | 328.5622 | 0.055 | [20 empty] | 209.0851 | 0.0896 | 246.4217 | 0.0909 | 328.5622 | 0.0909 | 410.7028 | 0.0909 | 533.9136 | 0.0909 | 657.1245 | 0.0909
140.157 | 0.0701 | 182.2608 | 0.0848 | 220.8834 | 0.0978 | 251.3501 | 0.1006 | 335.1335 | 0.1006 | [28 empty] | 151.2305 | 0.1547 | 180.2409 | 0.2037 | 228.8048 | 0.2165 | 282.8527 | 0.2417 | 356.0793 | 0.2468 | 451.7599 | 0.2556 | 589.8349 | 0.2409 | 747.3477 | 0.247 | 949.2656 | 0.2434 | 1195.5887 | 0.2436 | 1477.9387 | 0.2507 | 1799.6668 | 0.2752 | 2513.5011 | 0.3311 | 4021.6018 | 0.3311 | 148.4015 | 0.0436 | 182.2608 | 0.0481 | 213.2668 | 0.0524 | 251.3501 | 0.0536 | 335.1335 | 0.0536 | [20 empty] | 213.2668 | 0.0882 | 251.3501 | 0.0894 | 335.1335 | 0.0894 | 418.9169 | 0.0894 | 544.5919 | 0.0894 | 670.267 | 0.0894
142.9601 | 0.0673 | 185.906 | 0.0814 | 225.3011 | 0.0939 | 256.3771 | 0.0966 | 341.8362 | 0.0966 | [28 empty] | 154.2551 | 0.1486 | 183.8457 | 0.1957 | 233.3809 | 0.2079 | 288.5097 | 0.2321 | 363.2009 | 0.2371 | 460.7951 | 0.2455 | 601.6316 | 0.2313 | 762.2946 | 0.2372 | 968.2509 | 0.2338 | 1219.5005 | 0.2339 | 1507.4974 | 0.2407 | 1835.6602 | 0.2643 | 2563.7712 | 0.3186 | 4102.0339 | 0.3186 | 151.3695 | 0.0426 | 185.906 | 0.047 | 217.5321 | 0.051 | 256.3771 | 0.0522 | 341.8362 | 0.0522 | [20 empty] | 217.5321 | 0.0868 | 256.3771 | 0.088 | 341.8362 | 0.088 | 427.2952 | 0.088 | 555.4838 | 0.088 | 683.6723 | 0.088
145.8193 | 0.0647 | 189.6242 | 0.0782 | 229.8071 | 0.0902 | 261.5047 | 0.0928 | 348.6729 | 0.0928 | [28 empty] | 157.3402 | 0.1428 | 187.5226 | 0.188 | 238.0485 | 0.1997 | 294.2799 | 0.223 | 370.4649 | 0.2277 | 470.011 | 0.2358 | 613.6643 | 0.2222 | 777.5405 | 0.2279 | 987.6159 | 0.2246 | 1243.8905 | 0.2247 | 1537.6474 | 0.2312 | 1872.3734 | 0.2539 | 2615.0466 | 0.3066 | 4184.0745 | 0.3066 | 154.3969 | 0.0416 | 189.6242 | 0.0458 | 221.8827 | 0.0497 | 261.5047 | 0.0509 | 348.6729 | 0.0509 | [20 empty] | 221.8827 | 0.0855 | 261.5047 | 0.0867 | 348.6729 | 0.0867 | 435.8411 | 0.0867 | 566.5934 | 0.0867 | 697.3458 | 0.0867
148.7357 | 0.0621 | 193.4166 | 0.0752 | 234.4033 | 0.0867 | 266.7348 | 0.0891 | 355.6463 | 0.0891 | [28 empty] | 160.487 | 0.1372 | 191.2731 | 0.1806 | 242.8095 | 0.1919 | 300.1655 | 0.2142 | 377.8742 | 0.2187 | 479.4113 | 0.2265 | 625.9376 | 0.2134 | 793.0913 | 0.2189 | 1007.3682 | 0.2157 | 1268.7683 | 0.2158 | 1568.4003 | 0.2221 | 1909.8208 | 0.2439 | 2667.3475 | 0.2951 | 4267.756 | 0.2951 | 157.4849 | 0.0407 | 193.4166 | 0.0448 | 226.3204 | 0.0485 | 266.7348 | 0.0496 | 355.6463 | 0.0496 | [20 empty] | 226.3204 | 0.0843 | 266.7348 | 0.0854 | 355.6463 | 0.0854 | 444.5579 | 0.0854 | 577.9253 | 0.0854 | 711.2927 | 0.0854
151.7104 | 0.0597 | 197.285 | 0.0722 | 239.0913 | 0.0832 | 272.0694 | 0.0856 | 362.7593 | 0.0856 | [28 empty] | 163.6968 | 0.1318 | 195.0985 | 0.1735 | 247.6656 | 0.1843 | 306.1688 | 0.2057 | 385.4317 | 0.2101 | 488.9995 | 0.2175 | 638.4563 | 0.205 | 808.9532 | 0.2102 | 1027.5156 | 0.2072 | 1294.1437 | 0.2073 | 1599.7684 | 0.2134 | 1948.0172 | 0.2343 | 2720.6945 | 0.284 | 4353.1112 | 0.284 | 160.6346 | 0.0398 | 197.285 | 0.0437 | 230.8468 | 0.0473 | 272.0694 | 0.0484 | 362.7593 | 0.0484 | [20 empty] | 230.8468 | 0.0831 | 272.0694 | 0.0842 | 362.7593 | 0.0842 | 453.4491 | 0.0842 | 589.4838 | 0.0842 | 725.5185 | 0.0842
154.7446 | 0.0573 | 201.2307 | 0.0694 | 243.8732 | 0.08 | 277.5108 | 0.0822 | 370.0144 | 0.0822 | [28 empty] | 166.9707 | 0.1266 | 199.0005 | 0.1666 | 252.619 | 0.177 | 312.2922 | 0.1976 | 393.1404 | 0.2018 | 498.7795 | 0.209 | 651.2254 | 0.1969 | 825.1322 | 0.202 | 1048.0659 | 0.199 | 1320.0265 | 0.1992 | 1631.7637 | 0.2049 | 1986.9776 | 0.225 | 2775.1084 | 0.2733 | 4440.1734 | 0.2733 | 163.8473 | 0.039 | 201.2307 | 0.0427 | 235.4637 | 0.0462 | 277.5108 | 0.0472 | 370.0144 | 0.0472 | [20 empty] | 235.4637 | 0.0819 | 277.5108 | 0.083 | 370.0144 | 0.083 | 462.5181 | 0.083 | 601.2735 | 0.083 | 740.0289 | 0.083
157.8395 | 0.0551 | 205.2553 | 0.0666 | 248.7506 | 0.0768 | 283.0611 | 0.079 | 377.4147 | 0.079 | [28 empty] | 170.3101 | 0.1216 | 202.9805 | 0.1601 | 257.6713 | 0.1701 | 318.538 | 0.1898 | 401.0032 | 0.1939 | 508.7551 | 0.2007 | 664.2499 | 0.1892 | 841.6349 | 0.194 | 1069.0272 | 0.1912 | 1346.4271 | 0.1913 | 1664.399 | 0.1969 | 2026.7171 | 0.2162 | 2830.6105 | 0.263 | 4528.9768 | 0.263 | 167.1242 | 0.0381 | 205.2553 | 0.0418 | 240.173 | 0.0451 | 283.0611 | 0.0461 | 377.4147 | 0.0461 | [20 empty] | 240.173 | 0.0809 | 283.0611 | 0.0818 | 377.4147 | 0.0818 | 471.7684 | 0.0818 | 613.2989 | 0.0818 | 754.8295 | 0.0818
160.9963 | 0.0529 | 209.3604 | 0.064 | 253.7256 | 0.0738 | 288.7223 | 0.0759 | 384.963 | 0.0759 | [28 empty] | 173.7163 | 0.1168 | 207.0401 | 0.1538 | 262.8248 | 0.1634 | 324.9088 | 0.1824 | 409.0232 | 0.1862 | 518.9302 | 0.1928 | 677.5349 | 0.1817 | 858.4676 | 0.1864 | 1090.4078 | 0.1837 | 1373.3556 | 0.1838 | 1697.687 | 0.1891 | 2067.2515 | 0.2077 | 2887.2227 | 0.2532 | 4619.5564 | 0.2532 | 170.4667 | 0.0373 | 209.3604 | 0.0408 | 244.9765 | 0.0441 | 288.7223 | 0.045 | 384.963 | 0.045 | [20 empty] | 244.9765 | 0.0798 | 288.7223 | 0.0808 | 384.963 | 0.0808 | 481.2038 | 0.0808 | 625.5649 | 0.0808 | 769.9261 | 0.0808
164.2163 | 0.0511 | 213.5476 | 0.0615 | 258.8001 | 0.0709 | 294.4967 | 0.0729 | 392.6623 | 0.0729 | [28 empty] | 177.1907 | 0.1123 | 211.1809 | 0.1478 | 268.0813 | 0.1569 | 331.407 | 0.1752 | 417.2037 | 0.1789 | 529.3088 | 0.1852 | 691.0856 | 0.1746 | 875.6369 | 0.179 | 1112.2159 | 0.1764 | 1400.8227 | 0.1766 | 1731.6407 | 0.1817 | 2108.5965 | 0.1995 | 2944.9672 | 0.2436 | 4711.9475 | 0.2436 | 173.876 | 0.0366 | 213.5476 | 0.0399 | 249.876 | 0.043 | 294.4967 | 0.044 | 392.6623 | 0.044 | [20 empty] | 249.876 | 0.0788 | 294.4967 | 0.0797 | 392.6623 | 0.0797 | 490.8279 | 0.0797 | 638.0762 | 0.0797 | 785.3246 | 0.0797
167.5006 | 0.0495 | 217.8186 | 0.0591 | 263.9762 | 0.0681 | 300.3867 | 0.07 | 400.5155 | 0.07 | [28 empty] | 180.7345 | 0.1079 | 215.4045 | 0.142 | 273.4429 | 0.1508 | 338.0351 | 0.1683 | 425.5478 | 0.1719 | 539.8949 | 0.178 | 704.9073 | 0.1677 | 893.1497 | 0.172 | 1134.4603 | 0.1695 | 1428.8392 | 0.1696 | 1766.2735 | 0.1745 | 2150.7684 | 0.1916 | 3003.8665 | 0.2345 | 4806.1865 | 0.2345 | 177.3536 | 0.0359 | 217.8186 | 0.0391 | 254.8735 | 0.0421 | 300.3867 | 0.043 | 400.5155 | 0.043 | [20 empty] | 254.8735 | 0.0778 | 300.3867 | 0.0787 | 400.5155 | 0.0787 | 500.6444 | 0.0787 | 650.8378 | 0.0787 | 801.0311 | 0.0787
170.8506 | 0.048 | 222.1749 | 0.0568 | 269.2557 | 0.0654 | 306.3944 | 0.0673 | 408.5258 | 0.0673 | [28 empty] | 184.3492 | 0.1036 | 219.7126 | 0.1364 | 278.9117 | 0.1448 | 344.7958 | 0.1617 | 434.0587 | 0.1651 | 550.6928 | 0.171 | 719.0055 | 0.1611 | 911.0126 | 0.1652 | 1157.1495 | 0.1628 | 1457.416 | 0.1629 | 1801.599 | 0.1677 | 2193.7838 | 0.1841 | 3063.9439 | 0.2257 | 4902.3102 | 0.2257 | 180.9006 | 0.0352 | 222.1749 | 0.0383 | 259.971 | 0.0411 | 306.3944 | 0.042 | 408.5258 | 0.042 | [20 empty] | 259.971 | 0.0769 | 306.3944 | 0.0777 | 408.5258 | 0.0777 | 510.6573 | 0.0777 | 663.8545 | 0.0777 | 817.0517 | 0.0777
174.2676 | 0.0465 | 226.6184 | 0.0545 | 274.6408 | 0.0629 | 312.5223 | 0.0646 | 416.6964 | 0.0646 | [28 empty] | 188.0361 | 0.0996 | 224.1069 | 0.131 | 284.49 | 0.1392 | 351.6917 | 0.1553 | 442.7399 | 0.1586 | 561.7067 | 0.1642 | 733.3856 | 0.1548 | 929.2329 | 0.1587 | 1180.2925 | 0.1564 | 1486.5643 | 0.1565 | 1837.631 | 0.1611 | 2237.6595 | 0.1769 | 3125.2227 | 0.2173 | 5000.3564 | 0.2173 | 184.5186 | 0.0345 | 226.6184 | 0.0375 | 265.1704 | 0.0402 | 312.5223 | 0.0411 | 416.6964 | 0.0411 | [20 empty] | 265.1704 | 0.076 | 312.5223 | 0.0768 | 416.6964 | 0.0768 | 520.8705 | 0.0768 | 677.1316 | 0.0768 | 833.3927 | 0.0768
177.7529 | 0.0451 | 231.1508 | 0.0524 | 280.1336 | 0.0604 | 318.7727 | 0.0621 | 425.0303 | 0.0621 | [28 empty] | 191.7969 | 0.0957 | 228.589 | 0.1259 | 290.1798 | 0.1337 | 358.7256 | 0.1492 | 451.5947 | 0.1524 | 572.9408 | 0.1578 | 748.0533 | 0.1487 | 947.8176 | 0.1525 | 1203.8983 | 0.1503 | 1516.2956 | 0.1504 | 1874.3836 | 0.1548 | 2282.4127 | 0.1699 | 3187.7272 | 0.2091 | 5100.3635 | 0.2091 | 188.209 | 0.0338 | 231.1508 | 0.0367 | 270.4738 | 0.0394 | 318.7727 | 0.0402 | 425.0303 | 0.0402 | [20 empty] | 270.4738 | 0.0751 | 318.7727 | 0.0759 | 425.0303 | 0.0759 | 531.2879 | 0.0759 | 690.6742 | 0.0759 | 850.0606 | 0.0759
181.308 | 0.0437 | 235.7738 | 0.0507 | 285.7363 | 0.058 | 325.1482 | 0.0597 | 433.5309 | 0.0597 | [28 empty] | 195.6328 | 0.0919 | 233.1608 | 0.121 | 295.9834 | 0.1284 | 365.9001 | 0.1434 | 460.6266 | 0.1464 | 584.3997 | 0.1516 | 763.0144 | 0.1429 | 966.7739 | 0.1465 | 1227.9763 | 0.1444 | 1546.6215 | 0.1445 | 1911.8713 | 0.1487 | 2328.0609 | 0.1633 | 3251.4817 | 0.2013 | 5202.3708 | 0.2013 | 191.9732 | 0.0332 | 235.7738 | 0.036 | 275.8833 | 0.0385 | 325.1482 | 0.0393 | 433.5309 | 0.0393 | [20 empty] | 275.8833 | 0.0743 | 325.1482 | 0.075 | 433.5309 | 0.075 | 541.9136 | 0.075 | 704.4877 | 0.075 | 867.0618 | 0.075
184.9342 | 0.0424 | 240.4893 | 0.0491 | 291.451 | 0.0557 | 331.6511 | 0.0573 | 442.2015 | 0.0573 | [28 empty] | 199.5455 | 0.0883 | 237.824 | 0.1162 | 301.903 | 0.1234 | 373.2181 | 0.1377 | 469.8391 | 0.1407 | 596.0876 | 0.1457 | 778.2747 | 0.1373 | 986.1094 | 0.1408 | 1252.5358 | 0.1387 | 1577.5539 | 0.1388 | 1950.1087 | 0.1429 | 2374.6221 | 0.1569 | 3316.5114 | 0.1938 | 5306.4182 | 0.1938 | 195.8126 | 0.0326 | 240.4893 | 0.0353 | 281.401 | 0.0377 | 331.6511 | 0.0385 | 442.2015 | 0.0385 | [20 empty] | 281.401 | 0.0735 | 331.6511 | 0.0742 | 442.2015 | 0.0742 | 552.7519 | 0.0742 | 718.5775 | 0.0742 | 884.403 | 0.0742
188.6329 | 0.0411 | 245.2991 | 0.0476 | 297.28 | 0.0536 | 338.2842 | 0.0551 | 451.0455 | 0.0551 | [28 empty] | 203.5364 | 0.0849 | 242.5805 | 0.1117 | 307.9411 | 0.1186 | 380.6824 | 0.1323 | 479.2359 | 0.1352 | 608.0094 | 0.1399 | 793.8402 | 0.1319 | 1005.8316 | 0.1352 | 1277.5865 | 0.1333 | 1609.105 | 0.1334 | 1989.1109 | 0.1373 | 2422.1146 | 0.1507 | 3382.8416 | 0.1865 | 5412.5466 | 0.1865 | 199.7289 | 0.032 | 245.2991 | 0.0346 | 287.029 | 0.037 | 338.2842 | 0.0377 | 451.0455 | 0.0377 | [20 empty] | 287.029 | 0.0727 | 338.2842 | 0.0734 | 451.0455 | 0.0734 | 563.8069 | 0.0734 | 732.949 | 0.0734 | 902.0911 | 0.0734
192.4055 | 0.0399 | 250.2051 | 0.0461 | 303.2256 | 0.0516 | 345.0498 | 0.0529 | 460.0665 | 0.0529 | [28 empty] | 207.6071 | 0.0816 | 247.4321 | 0.1073 | 314.0999 | 0.1139 | 388.2961 | 0.1272 | 488.8206 | 0.1299 | 620.1696 | 0.1345 | 809.717 | 0.1267 | 1025.9482 | 0.1299 | 1303.1382 | 0.1281 | 1641.2871 | 0.1281 | 2028.8931 | 0.1319 | 2470.5569 | 0.1448 | 3450.4984 | 0.1795 | 5520.7975 | 0.1795 | 203.7235 | 0.0315 | 250.2051 | 0.0339 | 292.7696 | 0.0362 | 345.0498 | 0.0369 | 460.0665 | 0.0369 | [20 empty] | 292.7696 | 0.072 | 345.0498 | 0.0727 | 460.0665 | 0.0727 | 575.0831 | 0.0727 | 747.608 | 0.0727 | 920.1329 | 0.0727
196.2536 | 0.0387 | 255.2092 | 0.0447 | 309.2901 | 0.05 | 351.9508 | 0.0511 | 469.2678 | 0.0511 | [28 empty] | 211.7592 | 0.0784 | 252.3807 | 0.1031 | 320.3819 | 0.1095 | 396.062 | 0.1222 | 498.597 | 0.1248 | 632.573 | 0.1292 | 825.9113 | 0.1218 | 1046.4672 | 0.1249 | 1329.201 | 0.123 | 1674.1128 | 0.1231 | 2069.4709 | 0.1267 | 2519.968 | 0.1391 | 3519.5084 | 0.1728 | 5631.2135 | 0.1728 | 207.7979 | 0.0309 | 255.2092 | 0.0333 | 298.625 | 0.0355 | 351.9508 | 0.0361 | 469.2678 | 0.0361 | [20 empty] | 298.625 | 0.0713 | 351.9508 | 0.0719 | 469.2678 | 0.0719 | 586.5847 | 0.0719 | 762.5602 | 0.0719 | 938.5356 | 0.0719
200.1787 | 0.0376 | 260.3133 | 0.0434 | 315.4759 | 0.0484 | 358.9899 | 0.0495 | 478.6531 | 0.0495 | [28 empty] | 215.9944 | 0.0753 | 257.4284 | 0.0991 | 326.7896 | 0.1052 | 403.9833 | 0.1174 | 508.569 | 0.1199 | 645.2244 | 0.1241 | 842.4295 | 0.117 | 1067.3965 | 0.12 | 1355.785 | 0.1182 | 1707.5951 | 0.1183 | 2110.8604 | 0.1217 | 2570.3674 | 0.1337 | 3589.8986 | 0.1664 | 5743.8377 | 0.1664 | 211.9539 | 0.0304 | 260.3133 | 0.0327 | 304.5975 | 0.0348 | 358.9899 | 0.0354 | 478.6531 | 0.0354 | [20 empty] | 304.5975 | 0.0706 | 358.9899 | 0.0712 | 478.6531 | 0.0712 | 598.3164 | 0.0712 | 777.8114 | 0.0712 | 957.3063 | 0.0712
204.1823 | 0.0365 | 265.5196 | 0.0421 | 321.7855 | 0.0469 | 366.1697 | 0.048 | 488.2262 | 0.048 | [28 empty] | 220.3143 | 0.0724 | 262.5769 | 0.0952 | 333.3253 | 0.1011 | 412.0629 | 0.1128 | 518.7403 | 0.1152 | 658.1289 | 0.1193 | 859.2781 | 0.1124 | 1088.7444 | 0.1153 | 1382.9007 | 0.1136 | 1741.747 | 0.1137 | 2153.0776 | 0.117 | 2621.7747 | 0.1284 | 3661.6965 | 0.1602 | 5858.7145 | 0.1602 | 216.193 | 0.0299 | 265.5196 | 0.0321 | 310.6894 | 0.0341 | 366.1697 | 0.0347 | 488.2262 | 0.0347 | [20 empty] | 310.6894 | 0.07 | 366.1697 | 0.0706 | 488.2262 | 0.0706 | 610.2828 | 0.0706 | 793.3676 | 0.0706 | 976.4524 | 0.0706
208.2659 | 0.0355 | 270.83 | 0.0408 | 328.2212 | 0.0455 | 373.493 | 0.0465 | 497.9907 | 0.0465 | [28 empty] | 224.7206 | 0.0695 | 267.8285 | 0.0915 | 339.9919 | 0.0971 | 420.3042 | 0.1084 | 529.1152 | 0.1107 | 671.2915 | 0.1146 | 876.4637 | 0.108 | 1110.5193 | 0.1107 | 1410.5587 | 0.1091 | 1776.5819 | 0.1092 | 2196.1391 | 0.1124 | 2674.2102 | 0.1234 | 3734.9305 | 0.1542 | 5975.8888 | 0.1542 | 220.5168 | 0.0294 | 270.83 | 0.0315 | 316.9032 | 0.0335 | 373.493 | 0.0341 | 497.9907 | 0.0341 | [20 empty] | 316.9032 | 0.0693 | 373.493 | 0.0699 | 497.9907 | 0.0699 | 622.4884 | 0.0699 | 809.2349 | 0.0699 | 995.9815 | 0.0699
212.4312 | 0.0345 | 276.2466 | 0.0396 | 334.7856 | 0.0441 | 380.9629 | 0.0451 | 507.9505 | 0.0451 | [28 empty] | 229.215 | 0.0668 | 273.185 | 0.0879 | 346.7917 | 0.0933 | 428.7103 | 0.1041 | 539.6975 | 0.1063 | 684.7173 | 0.1101 | 893.993 | 0.1038 | 1132.7297 | 0.1064 | 1438.7699 | 0.1049 | 1812.1136 | 0.1049 | 2240.0619 | 0.108 | 2727.6944 | 0.1186 | 3809.6291 | 0.1484 | 6095.4065 | 0.1484 | 224.9272 | 0.029 | 276.2466 | 0.031 | 323.2413 | 0.0329 | 380.9629 | 0.0334 | 507.9505 | 0.0334 | [20 empty] | 323.2413 | 0.0688 | 380.9629 | 0.0693 | 507.9505 | 0.0693 | 634.9382 | 0.0693 | 825.4196 | 0.0693 | 1015.9011 | 0.0693
216.6799 | 0.0335 | 281.7715 | 0.0384 | 341.4813 | 0.0428 | 388.5822 | 0.0437 | 518.1096 | 0.0437 | [28 empty] | 233.7993 | 0.0642 | 278.6487 | 0.0845 | 353.7275 | 0.0896 | 437.2845 | 0.1001 | 550.4914 | 0.1022 | 698.4117 | 0.1058 | 911.8728 | 0.0997 | 1155.3843 | 0.1023 | 1467.5453 | 0.1008 | 1848.3558 | 0.1008 | 2284.8631 | 0.1038 | 2782.2483 | 0.1139 | 3885.8217 | 0.1429 | 6217.3147 | 0.1429 | 229.4257 | 0.0285 | 281.7715 | 0.0305 | 329.7061 | 0.0323 | 388.5822 | 0.0328 | 518.1096 | 0.0328 | [20 empty] | 329.7061 | 0.0682 | 388.5822 | 0.0687 | 518.1096 | 0.0687 | 647.6369 | 0.0687 | 841.928 | 0.0687 | 1036.2191 | 0.0687
221.0135 | 0.0326 | 287.407 | 0.0373 | 348.3109 | 0.0415 | 396.3538 | 0.0424 | 528.4717 | 0.0424 | [28 empty] | 238.4753 | 0.0617 | 284.2217 | 0.0812 | 360.8021 | 0.0861 | 446.0302 | 0.0961 | 561.5012 | 0.0982 | 712.3799 | 0.1017 | 930.1103 | 0.0958 | 1178.492 | 0.0983 | 1496.8962 | 0.0968 | 1885.323 | 0.0969 | 2330.5604 | 0.0997 | 2837.8933 | 0.1095 | 3963.5381 | 0.1376 | 6341.661 | 0.1376 | 234.0142 | 0.0281 | 287.407 | 0.03 | 336.3002 | 0.0317 | 396.3538 | 0.0322 | 528.4717 | 0.0322 | [20 empty] | 336.3002 | 0.0676 | 396.3538 | 0.0681 | 528.4717 | 0.0681 | 660.5897 | 0.0681 | 858.7666 | 0.0681 | 1056.9435 | 0.0681
225.4337 | 0.0317 | 293.1551 | 0.0363 | 355.2771 | 0.0402 | 404.2809 | 0.0411 | 539.0412 | 0.0411 | [28 empty] | 243.2448 | 0.0593 | 289.9061 | 0.078 | 368.0181 | 0.0828 | 454.9508 | 0.0924 | 572.7313 | 0.0943 | 726.6275 | 0.0977 | 948.7125 | 0.0921 | 1202.0618 | 0.0944 | 1526.8341 | 0.093 | 1923.0294 | 0.0931 | 2377.1716 | 0.0958 | 2894.6511 | 0.1052 | 4042.8089 | 0.1325 | 6468.4942 | 0.1325 | 238.6945 | 0.0277 | 293.1551 | 0.0295 | 343.0262 | 0.0312 | 404.2809 | 0.0317 | 539.0412 | 0.0317 | [20 empty] | 343.0262 | 0.0671 | 404.2809 | 0.0676 | 539.0412 | 0.0676 | 673.8015 | 0.0676 | 875.9419 | 0.0676 | 1078.0824 | 0.0676
229.9424 | 0.0309 | 299.0182 | 0.0352 | 362.3827 | 0.0391 | 412.3665 | 0.0399 | 549.822 | 0.0399 | [28 empty] | 248.1097 | 0.057 | 295.7043 | 0.0749 | 375.3785 | 0.0795 | 464.0498 | 0.0888 | 584.1859 | 0.0907 | 741.1601 | 0.0939 | 967.6867 | 0.0885 | 1226.1031 | 0.0907 | 1557.3708 | 0.0894 | 1961.49 | 0.0895 | 2424.715 | 0.0921 | 2952.5442 | 0.1011 | 4123.665 | 0.1275 | 6597.8641 | 0.1275 | 243.4684 | 0.0273 | 299.0182 | 0.029 | 349.8867 | 0.0307 | 412.3665 | 0.0311 | 549.822 | 0.0311 | [20 empty] | 349.8867 | 0.0666 | 412.3665 | 0.067 | 549.822 | 0.067 | 687.2775 | 0.067 | 893.4608 | 0.067 | 1099.644 | 0.067
234.5412 | 0.0301 | 304.9986 | 0.0343 | 369.6303 | 0.0379 | 420.6138 | 0.0387 | 560.8184 | 0.0387 | [28 empty] | 253.0719 | 0.0548 | 301.6184 | 0.072 | 382.886 | 0.0764 | 473.3308 | 0.0853 | 595.8696 | 0.0871 | 755.9833 | 0.0902 | 987.0405 | 0.085 | 1250.6251 | 0.0872 | 1588.5182 | 0.0859 | 2000.7198 | 0.086 | 2473.2093 | 0.0885 | 3011.5951 | 0.0971 | 4206.1383 | 0.1228 | 6729.8214 | 0.1228 | 248.3378 | 0.0269 | 304.9986 | 0.0286 | 356.8845 | 0.0301 | 420.6138 | 0.0306 | 560.8184 | 0.0306 | [20 empty] | 356.8845 | 0.0661 | 420.6138 | 0.0665 | 560.8184 | 0.0665 | 701.0231 | 0.0665 | 911.33 | 0.0665 | 1121.6369 | 0.0665
239.2321 | 0.0293 | 311.0985 | 0.0333 | 377.0229 | 0.0368 | 429.0261 | 0.0376 | 572.0348 | 0.0376 | [28 empty] | 258.1333 | 0.0526 | 307.6507 | 0.0692 | 390.5438 | 0.0734 | 482.7974 | 0.082 | 607.787 | 0.0837 | 771.1029 | 0.0867 | 1006.7813 | 0.0817 | 1275.6376 | 0.0838 | 1620.2886 | 0.0826 | 2040.7342 | 0.0826 | 2522.6735 | 0.085 | 3071.827 | 0.0933 | 4290.2611 | 0.1182 | 6864.4178 | 0.1182 | 253.3045 | 0.0265 | 311.0985 | 0.0282 | 364.0222 | 0.0297 | 429.0261 | 0.0301 | 572.0348 | 0.0301 | [20 empty] | 364.0222 | 0.0656 | 429.0261 | 0.066 | 572.0348 | 0.066 | 715.0435 | 0.066 | 929.5566 | 0.066 | 1144.0696 | 0.066
244.0167 | 0.0285 | 317.3205 | 0.0324 | 384.5634 | 0.0358 | 437.6066 | 0.0365 | 583.4755 | 0.0365 | [28 empty] | 263.296 | 0.0509 | 313.8037 | 0.0665 | 398.3546 | 0.0706 | 492.4533 | 0.0788 | 619.9427 | 0.0804 | 786.525 | 0.0833 | 1026.9169 | 0.0785 | 1301.1504 | 0.0805 | 1652.6944 | 0.0793 | 2081.5489 | 0.0794 | 2573.127 | 0.0817 | 3133.2635 | 0.0897 | 4376.0663 | 0.1138 | 7001.7061 | 0.1138 | 258.3706 | 0.0262 | 317.3205 | 0.0277 | 371.3026 | 0.0292 | 437.6066 | 0.0296 | 583.4755 | 0.0296 | [20 empty] | 371.3026 | 0.0652 | 437.6066 | 0.0656 | 583.4755 | 0.0656 | 729.3444 | 0.0656 | 948.1477 | 0.0656 | 1166.951 | 0.0656
248.897 | 0.0278 | 323.6669 | 0.0315 | 392.2547 | 0.0348 | 446.3588 | 0.0355 | 595.145 | 0.0355 | [28 empty] | 268.5619 | 0.0493 | 320.0798 | 0.0639 | 406.3217 | 0.0678 | 502.3024 | 0.0757 | 632.3416 | 0.0773 | 802.2555 | 0.08 | 1047.4552 | 0.0754 | 1327.1734 | 0.0774 | 1685.7483 | 0.0762 | 2123.1799 | 0.0763 | 2624.5895 | 0.0785 | 3195.9288 | 0.0862 | 4463.5877 | 0.1096 | 7141.7403 | 0.1096 | 263.538 | 0.0258 | 323.6669 | 0.0273 | 378.7287 | 0.0287 | 446.3588 | 0.0291 | 595.145 | 0.0291 | [20 empty] | 378.7287 | 0.0647 | 446.3588 | 0.0651 | 595.145 | 0.0651 | 743.9313 | 0.0651 | 967.1107 | 0.0651 | 1190.29 | 0.0651
253.875 | 0.0271 | 330.1403 | 0.0307 | 400.0998 | 0.0338 | 455.2859 | 0.0345 | 607.0479 | 0.0345 | [28 empty] | 273.9332 | 0.0478 | 326.4814 | 0.0614 | 414.4482 | 0.0652 | 512.3484 | 0.0727 | 644.9884 | 0.0743 | 818.3006 | 0.0769 | 1068.4043 | 0.0725 | 1353.7169 | 0.0743 | 1719.4632 | 0.0733 | 2165.6435 | 0.0733 | 2677.0813 | 0.0754 | 3259.8473 | 0.0828 | 4552.8594 | 0.1055 | 7284.5751 | 0.1055 | 268.8088 | 0.0255 | 330.1403 | 0.027 | 386.3032 | 0.0283 | 455.2859 | 0.0287 | 607.0479 | 0.0287 | [20 empty] | 386.3032 | 0.0643 | 455.2859 | 0.0647 | 607.0479 | 0.0647 | 758.8099 | 0.0647 | 986.4529 | 0.0647 | 1214.0958 | 0.0647
258.9525 | 0.0265 | 336.7431 | 0.0299 | 408.1018 | 0.0329 | 464.3917 | 0.0335 | 619.1889 | 0.0335 | [28 empty] | 279.4118 | 0.0463 | 333.011 | 0.059 | 422.7371 | 0.0626 | 522.5954 | 0.0699 | 657.8882 | 0.0714 | 834.6666 | 0.0739 | 1089.7724 | 0.0697 | 1380.7912 | 0.0714 | 1753.8525 | 0.0704 | 2208.9563 | 0.0704 | 2730.623 | 0.0725 | 3325.0443 | 0.0796 | 4643.9166 | 0.1016 | 7430.2666 | 0.1016 | 274.185 | 0.0252 | 336.7431 | 0.0266 | 394.0293 | 0.0279 | 464.3917 | 0.0283 | 619.1889 | 0.0283 | [20 empty] | 394.0293 | 0.0639 | 464.3917 | 0.0643 | 619.1889 | 0.0643 | 773.9861 | 0.0643 | 1006.1819 | 0.0643 | 1238.3778 | 0.0643
264.1315 | 0.0258 | 343.4779 | 0.0291 | 416.2638 | 0.032 | 473.6795 | 0.0326 | 631.5727 | 0.0326 | [28 empty] | 285.0001 | 0.0449 | 339.6713 | 0.0567 | 431.1919 | 0.0602 | 533.0473 | 0.0672 | 671.0459 | 0.0686 | 851.3599 | 0.071 | 1111.5679 | 0.0669 | 1408.407 | 0.0686 | 1788.9296 | 0.0676 | 2253.1355 | 0.0677 | 2785.2354 | 0.0697 | 3391.5452 | 0.0765 | 4736.7949 | 0.0978 | 7578.8719 | 0.0978 | 279.6687 | 0.0249 | 343.4779 | 0.0262 | 401.9099 | 0.0275 | 473.6795 | 0.0278 | 631.5727 | 0.0278 | [20 empty] | 401.9099 | 0.0635 | 473.6795 | 0.0639 | 631.5727 | 0.0639 | 789.4658 | 0.0639 | 1026.3056 | 0.0639 | 1263.1453 | 0.0639
269.4142 | 0.0252 | 350.3475 | 0.0284 | 424.5891 | 0.0311 | 483.1531 | 0.0317 | 644.2041 | 0.0317 | [28 empty] | 290.7001 | 0.0436 | 346.4647 | 0.0545 | 439.8157 | 0.0578 | 543.7083 | 0.0645 | 684.4669 | 0.0659 | 868.3871 | 0.0683 | 1133.7992 | 0.0643 | 1436.5752 | 0.066 | 1824.7081 | 0.065 | 2298.1982 | 0.0651 | 2840.9401 | 0.0669 | 3459.3761 | 0.0735 | 4831.5308 | 0.0942 | 7730.4493 | 0.0942 | 285.2621 | 0.0246 | 350.3475 | 0.0259 | 409.9481 | 0.0271 | 483.1531 | 0.0274 | 644.2041 | 0.0274 | [20 empty] | 409.9481 | 0.0631 | 483.1531 | 0.0635 | 644.2041 | 0.0635 | 805.2551 | 0.0635 | 1046.8317 | 0.0635 | 1288.4082 | 0.0635
274.8024 | 0.0246 | 357.3544 | 0.0276 | 433.0809 | 0.0303 | 492.8161 | 0.0309 | 657.0882 | 0.0309 | [28 empty] | 296.5141 | 0.0422 | 353.394 | 0.0524 | 448.612 | 0.0556 | 554.5824 | 0.062 | 698.1562 | 0.0633 | 885.7549 | 0.0656 | 1156.4752 | 0.0618 | 1465.3067 | 0.0634 | 1861.2023 | 0.0625 | 2344.1621 | 0.0625 | 2897.7589 | 0.0643 | 3528.5636 | 0.0706 | 4928.1615 | 0.0907 | 7885.0583 | 0.0907 | 290.9673 | 0.0243 | 357.3544 | 0.0256 | 418.147 | 0.0267 | 492.8161 | 0.0271 | 657.0882 | 0.0271 | [20 empty] | 418.147 | 0.0628 | 492.8161 | 0.0631 | 657.0882 | 0.0631 | 821.3602 | 0.0631 | 1067.7683 | 0.0631 | 1314.1764 | 0.0631
280.2985 | 0.024 | 364.5015 | 0.027 | 441.7425 | 0.0295 | 502.6725 | 0.0301 | 670.23 | 0.0301 | [28 empty] | 302.4443 | 0.041 | 360.4619 | 0.0507 | 457.5843 | 0.0534 | 565.6741 | 0.0596 | 712.1193 | 0.0609 | 903.47 | 0.063 | 1179.6047 | 0.0594 | 1494.6128 | 0.0609 | 1898.4264 | 0.06 | 2391.0454 | 0.0601 | 2955.7141 | 0.0618 | 3599.1349 | 0.0679 | 5026.7247 | 0.0873 | 8042.7595 | 0.0873 | 296.7866 | 0.024 | 364.5015 | 0.0252 | 426.51 | 0.0264 | 502.6725 | 0.0267 | 670.23 | 0.0267 | [20 empty] | 426.51 | 0.0624 | 502.6725 | 0.0628 | 670.23 | 0.0628 | 837.7874 | 0.0628 | 1089.1237 | 0.0628 | 1340.4599 | 0.0628
285.9045 | 0.0235 | 371.7915 | 0.0263 | 450.5773 | 0.0288 | 512.7259 | 0.0293 | 683.6346 | 0.0293 | [28 empty] | 308.4932 | 0.0398 | 367.6711 | 0.0492 | 466.736 | 0.0515 | 576.9876 | 0.0573 | 726.3617 | 0.0585 | 921.5394 | 0.0606 | 1203.1968 | 0.0571 | 1524.5051 | 0.0585 | 1936.3949 | 0.0577 | 2438.8663 | 0.0577 | 3014.8284 | 0.0594 | 3671.1176 | 0.0652 | 5127.2592 | 0.0841 | 8203.6147 | 0.0841 | 302.7224 | 0.0238 | 371.7915 | 0.0249 | 435.0402 | 0.026 | 512.7259 | 0.0263 | 683.6346 | 0.0263 | [20 empty] | 435.0402 | 0.0621 | 512.7259 | 0.0624 | 683.6346 | 0.0624 | 854.5432 | 0.0624 | 1110.9062 | 0.0624 | 1367.2691 | 0.0624
291.6226 | 0.023 | 379.2274 | 0.0257 | 459.5889 | 0.028 | 522.9804 | 0.0285 | 697.3072 | 0.0285 | [28 empty] | 314.6631 | 0.0386 | 375.0245 | 0.0476 | 476.0707 | 0.0499 | 588.5273 | 0.0551 | 740.889 | 0.0562 | 939.9702 | 0.0582 | 1227.2608 | 0.0549 | 1554.9952 | 0.0563 | 1975.1228 | 0.0554 | 2487.6436 | 0.0555 | 3075.125 | 0.0571 | 3744.5399 | 0.0627 | 5229.8044 | 0.0809 | 8367.687 | 0.0809 | 308.7768 | 0.0235 | 379.2274 | 0.0246 | 443.741 | 0.0257 | 522.9804 | 0.026 | 697.3072 | 0.026 | [20 empty] | 443.741 | 0.0618 | 522.9804 | 0.0621 | 697.3072 | 0.0621 | 871.6341 | 0.0621 | 1133.1243 | 0.0621 | 1394.6145 | 0.0621
297.455 | 0.0225 | 386.8119 | 0.0251 | 468.7806 | 0.0273 | 533.44 | 0.0278 | 711.2534 | 0.0278 | [28 empty] | 320.9564 | 0.0375 | 382.525 | 0.0462 | 485.5921 | 0.0484 | 600.2979 | 0.0529 | 755.7067 | 0.054 | 958.7696 | 0.0559 | 1251.806 | 0.0527 | 1586.0951 | 0.0541 | 2014.6252 | 0.0533 | 2537.3965 | 0.0533 | 3136.6275 | 0.0549 | 3819.4307 | 0.0602 | 5334.4004 | 0.0779 | 8535.0407 | 0.0779 | 314.9524 | 0.0233 | 386.8119 | 0.0244 | 452.6158 | 0.0253 | 533.44 | 0.0256 | 711.2534 | 0.0256 | [20 empty] | 452.6158 | 0.0615 | 533.44 | 0.0618 | 711.2534 | 0.0618 | 889.0667 | 0.0618 | 1155.7868 | 0.0618 | 1422.5068 | 0.0618
303.4041 | 0.022 | 394.5482 | 0.0245 | 478.1563 | 0.0267 | 544.1088 | 0.0271 | 725.4785 | 0.0271 | [28 empty] | 327.3755 | 0.0364 | 390.1755 | 0.0448 | 495.3039 | 0.0469 | 612.3038 | 0.0512 | 770.8209 | 0.052 | 977.945 | 0.0538 | 1276.8421 | 0.051 | 1617.817 | 0.0521 | 2054.9177 | 0.0514 | 2588.1444 | 0.0515 | 3199.36 | 0.0527 | 3895.8193 | 0.0579 | 5441.0885 | 0.075 | 8705.7415 | 0.075 | 321.2514 | 0.0231 | 394.5482 | 0.0241 | 461.6681 | 0.025 | 544.1088 | 0.0253 | 725.4785 | 0.0253 | [20 empty] | 461.6681 | 0.0612 | 544.1088 | 0.0615 | 725.4785 | 0.0615 | 906.8481 | 0.0615 | 1178.9025 | 0.0615 | 1450.9569 | 0.0615
309.4722 | 0.0215 | 402.4391 | 0.0239 | 487.7194 | 0.026 | 554.991 | 0.0265 | 739.988 | 0.0265 | [28 empty] | 333.923 | 0.0354 | 397.979 | 0.0434 | 505.21 | 0.0454 | 624.5499 | 0.0495 | 786.2373 | 0.0504 | 997.5039 | 0.0518 | 1302.3789 | 0.0494 | 1650.1733 | 0.0504 | 2096.0161 | 0.0498 | 2639.9073 | 0.0499 | 3263.3472 | 0.051 | 3973.7357 | 0.0556 | 5549.9102 | 0.0723 | 8879.8564 | 0.0723 | 327.6764 | 0.0228 | 402.4391 | 0.0238 | 470.9015 | 0.0247 | 554.991 | 0.025 | 739.988 | 0.025 | [20 empty] | 470.9015 | 0.0609 | 554.991 | 0.0612 | 739.988 | 0.0612 | 924.985 | 0.0612 | 1202.4805 | 0.0612 | 1479.9761 | 0.0612
315.6616 | 0.0211 | 410.4879 | 0.0234 | 497.4738 | 0.0254 | 566.0908 | 0.0258 | 754.7878 | 0.0258 | [28 empty] | 340.6014 | 0.0344 | 405.9386 | 0.0421 | 515.3142 | 0.0441 | 637.0409 | 0.048 | 801.962 | 0.0488 | 1017.4539 | 0.0502 | 1328.4265 | 0.0479 | 1683.1768 | 0.0488 | 2137.9364 | 0.0483 | 2692.7054 | 0.0483 | 3328.6142 | 0.0494 | 4053.2104 | 0.0535 | 5660.9084 | 0.0696 | 9057.4535 | 0.0696 | 334.23 | 0.0226 | 410.4879 | 0.0236 | 480.3195 | 0.0245 | 566.0908 | 0.0247 | 754.7878 | 0.0247 | [20 empty] | 480.3195 | 0.0607 | 566.0908 | 0.0609 | 754.7878 | 0.0609 | 943.4847 | 0.0609 | 1226.5302 | 0.0609 | 1509.5756 | 0.0609
321.9749 | 0.0206 | 418.6977 | 0.0228 | 507.4232 | 0.0248 | 577.4127 | 0.0252 | 769.8835 | 0.0252 | [28 empty] | 347.4135 | 0.0335 | 414.0574 | 0.0408 | 525.6205 | 0.0427 | 649.7817 | 0.0465 | 818.0013 | 0.0473 | 1037.803 | 0.0486 | 1354.995 | 0.0464 | 1716.8403 | 0.0473 | 2180.6951 | 0.0468 | 2746.5595 | 0.0468 | 3395.1864 | 0.0479 | 4134.2746 | 0.0516 | 5774.1266 | 0.067 | 9238.6026 | 0.067 | 340.9146 | 0.0224 | 418.6977 | 0.0233 | 489.9259 | 0.0242 | 577.4127 | 0.0244 | 769.8835 | 0.0244 | [20 empty] | 489.9259 | 0.0604 | 577.4127 | 0.0606 | 769.8835 | 0.0606 | 962.3544 | 0.0606 | 1251.0608 | 0.0606 | 1539.7671 | 0.0606
328.4144 | 0.0202 | 427.0716 | 0.0223 | 517.5717 | 0.0242 | 588.9609 | 0.0246 | 785.2812 | 0.0246 | [28 empty] | 354.3617 | 0.0326 | 422.3385 | 0.0396 | 536.1329 | 0.0415 | 662.7773 | 0.0451 | 834.3613 | 0.0459 | 1058.5591 | 0.0471 | 1382.0949 | 0.045 | 1751.1771 | 0.0459 | 2224.309 | 0.0454 | 2801.4907 | 0.0454 | 3463.0902 | 0.0464 | 4216.9601 | 0.05 | 5889.6091 | 0.0645 | 9423.3746 | 0.0645 | 347.7329 | 0.0222 | 427.0716 | 0.0231 | 499.7244 | 0.0239 | 588.9609 | 0.0242 | 785.2812 | 0.0242 | [20 empty] | 499.7244 | 0.0601 | 588.9609 | 0.0604 | 785.2812 | 0.0604 | 981.6015 | 0.0604 | 1276.082 | 0.0604 | 1570.5624 | 0.0604
332.0867 | 0.016 | 435.6131 | 0.0219 | 527.9231 | 0.0237 | 600.7401 | 0.024 | 800.9868 | 0.024 | [28 empty] | 361.449 | 0.0317 | 430.7853 | 0.0385 | 546.8556 | 0.0402 | 676.0329 | 0.0437 | 851.0485 | 0.0445 | 1079.7303 | 0.0457 | 1409.7368 | 0.0436 | 1786.2007 | 0.0445 | 2268.7952 | 0.044 | 2857.5206 | 0.044 | 3532.352 | 0.045 | 4301.2993 | 0.0484 | 6007.4013 | 0.0621 | 9611.8421 | 0.0621 | 354.6875 | 0.022 | 435.6131 | 0.0229 | 509.7189 | 0.0237 | 600.7401 | 0.0239 | 800.9868 | 0.0239 | [20 empty] | 509.7189 | 0.0599 | 600.7401 | 0.0601 | 800.9868 | 0.0601 | 1001.2336 | 0.0601 | 1301.6036 | 0.0601 | 1601.9737 | 0.0601
338.7284 | 0.016 | 444.3253 | 0.0214 | 538.4816 | 0.0231 | 612.7549 | 0.0235 | 817.0066 | 0.0235 | [28 empty] | 368.678 | 0.0308 | 439.401 | 0.0374 | 557.7927 | 0.0391 | 689.5536 | 0.0424 | 868.0695 | 0.0431 | 1101.3249 | 0.0443 | 1437.9316 | 0.0423 | 1821.9247 | 0.0431 | 2314.1711 | 0.0427 | 2914.671 | 0.0427 | 3602.999 | 0.0436 | 4387.3253 | 0.0469 | 6127.5493 | 0.0598 | 9804.0789 | 0.0598 | 361.7813 | 0.0218 | 444.3253 | 0.0227 | 519.9133 | 0.0234 | 612.7549 | 0.0236 | 817.0066 | 0.0236 | [20 empty] | 519.9133 | 0.0597 | 612.7549 | 0.0599 | 817.0066 | 0.0599 | 1021.2582 | 0.0599 | 1327.6357 | 0.0599 | 1634.0132 | 0.0599
345.503 | 0.016 | 453.2118 | 0.021 | 549.2512 | 0.0226 | 625.01 | 0.023 | 833.3467 | 0.023 | [28 empty] | 376.0515 | 0.03 | 448.189 | 0.0363 | 568.9485 | 0.0379 | 703.3446 | 0.0412 | 885.4309 | 0.0418 | 1123.3514 | 0.043 | 1466.6902 | 0.0411 | 1858.3632 | 0.0418 | 2360.4546 | 0.0414 | 2972.9644 | 0.0414 | 3675.059 | 0.0423 | 4475.0718 | 0.0455 | 6250.1003 | 0.0576 | 10000.1605 | 0.0576 | 369.0169 | 0.0217 | 453.2118 | 0.0224 | 530.3115 | 0.0232 | 625.01 | 0.0234 | 833.3467 | 0.0234 | [20 empty] | 530.3115 | 0.0595 | 625.01 | 0.0597 | 833.3467 | 0.0597 | 1041.6834 | 0.0597 | 1354.1884 | 0.0597 | 1666.6934 | 0.0597
352.413 | 0.016 | 462.2761 | 0.0205 | 560.2363 | 0.0221 | 637.5102 | 0.0225 | 850.0136 | 0.0225 | [28 empty] | 383.5726 | 0.0292 | 457.1528 | 0.0353 | 580.3275 | 0.0368 | 717.4115 | 0.04 | 903.1395 | 0.0406 | 1145.8184 | 0.0417 | 1496.024 | 0.0399 | 1895.5304 | 0.0406 | 2407.6636 | 0.0402 | 3032.4237 | 0.0402 | 3748.5602 | 0.0411 | 4564.5733 | 0.0441 | 6375.1023 | 0.0555 | 10200.1637 | 0.0555 | 376.3972 | 0.0215 | 462.2761 | 0.0222 | 540.9178 | 0.0229 | 637.5102 | 0.0232 | 850.0136 | 0.0232 | [20 empty] | 540.9178 | 0.0594 | 637.5102 | 0.0595 | 850.0136 | 0.0595 | 1062.5171 | 0.0595 | 1381.2722 | 0.0595 | 1700.0273 | 0.0595
359.4613 | 0.016 | 471.5216 | 0.0201 | 571.441 | 0.0217 | 650.2604 | 0.022 | 867.0139 | 0.022 | [28 empty] | 391.244 | 0.0285 | 466.2958 | 0.0343 | 591.934 | 0.0358 | 731.7597 | 0.0388 | 921.2023 | 0.0394 | 1168.7348 | 0.0404 | 1525.9445 | 0.0387 | 1933.441 | 0.0394 | 2455.8169 | 0.039 | 3093.0721 | 0.039 | 3823.5314 | 0.0399 | 4655.8647 | 0.0428 | 6502.6044 | 0.0537 | 10404.167 | 0.0537 | 383.9252 | 0.0213 | 471.5216 | 0.022 | 551.7361 | 0.0227 | 650.2604 | 0.0229 | 867.0139 | 0.0229 | [20 empty] | 551.7361 | 0.0592 | 650.2604 | 0.0594 | 867.0139 | 0.0594 | 1083.7674 | 0.0594 | 1408.8976 | 0.0594 | 1734.0278 | 0.0594
366.6505 | 0.016 | 474.4096 | 0.016 | 582.8698 | 0.0212 | 663.2656 | 0.0215 | 884.3542 | 0.0215 | [28 empty] | 399.0689 | 0.0278 | 475.6218 | 0.0334 | 603.7727 | 0.0348 | 746.3949 | 0.0377 | 939.6263 | 0.0383 | 1192.1095 | 0.0393 | 1556.4634 | 0.0376 | 1972.1099 | 0.0383 | 2504.9333 | 0.0379 | 3154.9336 | 0.0379 | 3900.002 | 0.0387 | 4748.982 | 0.0415 | 6632.6565 | 0.0521 | 10612.2503 | 0.0521 | 391.6037 | 0.0212 | 480.952 | 0.0219 | 562.7709 | 0.0225 | 663.2656 | 0.0227 | 884.3542 | 0.0227 | [20 empty] | 562.7709 | 0.059 | 663.2656 | 0.0592 | 884.3542 | 0.0592 | 1105.4427 | 0.0592 | 1437.0756 | 0.0592 | 1768.7084 | 0.0592
373.9835 | 0.016 | 483.8977 | 0.016 | 594.5272 | 0.0208 | 676.531 | 0.0211 | 902.0413 | 0.0211 | [28 empty] | 407.0503 | 0.0271 | 485.1342 | 0.0325 | 615.8482 | 0.0338 | 761.3228 | 0.0366 | 958.4189 | 0.0372 | 1215.9516 | 0.0381 | 1587.5927 | 0.0365 | 2011.5521 | 0.0372 | 2555.0319 | 0.0368 | 3218.0323 | 0.0368 | 3978.002 | 0.0376 | 4843.9617 | 0.0403 | 6765.3096 | 0.0505 | 10824.4953 | 0.0505 | 399.4357 | 0.021 | 490.571 | 0.0217 | 574.0263 | 0.0223 | 676.531 | 0.0225 | 902.0413 | 0.0225 | [20 empty] | 574.0263 | 0.0589 | 676.531 | 0.059 | 902.0413 | 0.059 | 1127.5516 | 0.059 | 1465.8171 | 0.059 | 1804.0826 | 0.059
381.4632 | 0.016 | 493.5757 | 0.016 | 606.4178 | 0.0203 | 690.0616 | 0.0206 | 920.0821 | 0.0206 | [28 empty] | 415.1913 | 0.0264 | 494.8369 | 0.0316 | 628.1651 | 0.0329 | 776.5493 | 0.0356 | 977.5872 | 0.0361 | 1240.2707 | 0.037 | 1619.3445 | 0.0355 | 2051.7831 | 0.0361 | 2606.1326 | 0.0357 | 3282.3929 | 0.0358 | 4057.5621 | 0.0365 | 4940.8409 | 0.0391 | 6900.6158 | 0.049 | 11040.9853 | 0.049 | 407.4245 | 0.0209 | 500.3825 | 0.0215 | 585.5068 | 0.0221 | 690.0616 | 0.0223 | 920.0821 | 0.0223 | [20 empty] | 585.5068 | 0.0587 | 690.0616 | 0.0589 | 920.0821 | 0.0589 | 1150.1026 | 0.0589 | 1495.1334 | 0.0589 | 1840.1642 | 0.0589
389.0925 | 0.016 | 503.4472 | 0.016 | 616.7324 | 0.016 | 703.8628 | 0.0202 | 938.4837 | 0.0202 | [28 empty] | 423.4951 | 0.0258 | 504.7336 | 0.0307 | 640.7284 | 0.032 | 792.0803 | 0.0346 | 997.139 | 0.0351 | 1265.0761 | 0.036 | 1651.7314 | 0.0345 | 2092.8188 | 0.0351 | 2658.2552 | 0.0347 | 3348.0408 | 0.0348 | 4138.7133 | 0.0355 | 5039.6577 | 0.038 | 7038.6281 | 0.0476 | 11261.805 | 0.0476 | 415.5729 | 0.0207 | 510.3901 | 0.0213 | 597.2169 | 0.0219 | 703.8628 | 0.0221 | 938.4837 | 0.0221 | [20 empty] | 597.2169 | 0.0586 | 703.8628 | 0.0587 | 938.4837 | 0.0587 | 1173.1047 | 0.0587 | 1525.0361 | 0.0587 | 1876.9675 | 0.0587
396.8743 | 0.016 | 513.5162 | 0.016 | 629.0671 | 0.016 | 711.6143 | 0.016 | 948.8191 | 0.016 | [28 empty] | 431.965 | 0.0252 | 514.8283 | 0.0299 | 653.543 | 0.0312 | 807.9219 | 0.0336 | 1017.0818 | 0.0341 | 1290.3776 | 0.035 | 1684.766 | 0.0335 | 2134.6751 | 0.0341 | 2711.4203 | 0.0338 | 3415.0016 | 0.0338 | 4221.4876 | 0.0345 | 5140.4509 | 0.0369 | 7179.4007 | 0.0462 | 11487.0411 | 0.0462 | 423.8844 | 0.0206 | 520.5979 | 0.0212 | 609.1613 | 0.0217 | 717.9401 | 0.0219 | 957.2534 | 0.0219 | [20 empty] | 609.1613 | 0.0584 | 717.9401 | 0.0586 | 957.2534 | 0.0586 | 1196.5668 | 0.0586 | 1555.5368 | 0.0586 | 1914.5068 | 0.0586
404.8118 | 0.016 | 523.7865 | 0.016 | 641.6484 | 0.016 | 725.8466 | 0.016 | 967.7955 | 0.016 | [28 empty] | 440.6043 | 0.0246 | 525.1249 | 0.0292 | 666.6139 | 0.0303 | 824.0803 | 0.0327 | 1037.4234 | 0.0332 | 1316.1852 | 0.034 | 1718.4613 | 0.0326 | 2177.3686 | 0.0332 | 2765.6487 | 0.0328 | 3483.3016 | 0.0329 | 4305.9173 | 0.0335 | 5243.2599 | 0.0358 | 7322.9887 | 0.0448 | 11716.7819 | 0.0448 | 432.3621 | 0.0204 | 531.0099 | 0.021 | 621.3445 | 0.0216 | 732.2989 | 0.0217 | 976.3985 | 0.0217 | [20 empty] | 621.3445 | 0.0583 | 732.2989 | 0.0584 | 976.3985 | 0.0584 | 1220.4981 | 0.0584 | 1586.6475 | 0.0584 | 1952.797 | 0.0584
412.9081 | 0.016 | 534.2622 | 0.016 | 654.4814 | 0.016 | 740.3635 | 0.016 | 987.1514 | 0.016 | [28 empty] | 449.4164 | 0.024 | 535.6274 | 0.0284 | 679.9462 | 0.0295 | 840.5619 | 0.0318 | 1058.1719 | 0.0323 | 1342.5089 | 0.0331 | 1752.8306 | 0.0317 | 2220.916 | 0.0323 | 2820.9617 | 0.032 | 3552.9676 | 0.032 | 4392.0357 | 0.0326 | 5348.1251 | 0.0348 | 7469.4484 | 0.0436 | 11951.1175 | 0.0436 | 441.0093 | 0.0203 | 541.6301 | 0.0209 | 633.7714 | 0.0214 | 746.9448 | 0.0215 | 995.9265 | 0.0215 | [20 empty] | 633.7714 | 0.0582 | 746.9448 | 0.0583 | 995.9265 | 0.0583 | 1244.9081 | 0.0583 | 1618.3805 | 0.0583 | 1991.8529 | 0.0583
421.1662 | 0.016 | 544.9475 | 0.016 | 667.571 | 0.016 | 755.1708 | 0.016 | 1006.8944 | 0.016 | [28 empty] | 458.4047 | 0.0235 | 546.3399 | 0.0277 | 693.5451 | 0.0288 | 857.3732 | 0.031 | 1079.3353 | 0.0314 | 1369.359 | 0.0322 | 1787.8872 | 0.0309 | 2265.3343 | 0.0314 | 2877.3809 | 0.0311 | 3624.027 | 0.0311 | 4479.8764 | 0.0317 | 5455.0876 | 0.0339 | 7618.8374 | 0.0423 |  |  | 449.8295 | 0.0202 | 552.4627 | 0.0207 | 646.4468 | 0.0212 | 761.8837 | 0.0214 | 1015.845 | 0.0214 | [20 empty] | 646.4468 | 0.0581 | 761.8837 | 0.0582 | 1015.845 | 0.0582 | 1269.8062 | 0.0582 | 1650.7481 | 0.0582 | 2031.69 | 0.0582
429.5895 | 0.016 | 555.8464 | 0.016 | 680.9224 | 0.016 | 770.2742 | 0.016 | 1027.0323 | 0.016 | [28 empty] | 467.5728 | 0.0229 | 557.2667 | 0.027 | 707.416 | 0.028 | 874.5206 | 0.0301 | 1100.922 | 0.0306 | 1396.7462 | 0.0313 | 1823.6449 | 0.0301 | 2310.641 | 0.0306 | 2934.9285 | 0.0303 | 3696.5075 | 0.0303 | 4569.4739 | 0.0309 | 5564.1893 | 0.0329 | 7771.2142 | 0.0411 |  |  | 458.8261 | 0.0201 | 563.5119 | 0.0206 | 659.3757 | 0.0211 | 777.1214 | 0.0212 | 1036.1619 | 0.0212 | [20 empty] | 659.3757 | 0.0579 | 777.1214 | 0.058 | 1036.1619 | 0.058 | 1295.2024 | 0.058 | 1683.7631 | 0.058 | 2072.3238 | 0.058
438.1813 | 0.016 | 566.9633 | 0.016 | 694.5409 | 0.016 | 785.6797 | 0.016 | 1047.573 | 0.016 | [28 empty] | 476.9243 | 0.0224 | 568.412 | 0.0264 | 721.5643 | 0.0273 | 892.011 | 0.0294 | 1122.9404 | 0.0298 | 1424.6812 | 0.0305 | 1860.1178 | 0.0293 | 2356.8538 | 0.0298 | 2993.6271 | 0.0295 | 3770.4377 | 0.0295 | 4660.8634 | 0.0301 | 5675.4731 | 0.032 | 7926.6384 | 0.04 |  |  | 464.7819 | 0.016 | 574.7822 | 0.0205 | 672.5633 | 0.0209 | 792.6638 | 0.0211 | 1056.8851 | 0.0211 | [20 empty] | 672.5633 | 0.0578 | 792.6638 | 0.0579 | 1056.8851 | 0.0579 | 1321.1064 | 0.0579 | 1717.4383 | 0.0579 | 2113.7703 | 0.0579
446.945 | 0.016 | 578.3026 | 0.016 | 708.4317 | 0.016 | 801.3933 | 0.016 | 1068.5244 | 0.016 | [28 empty] | 486.4627 | 0.022 | 579.7803 | 0.0257 | 735.9956 | 0.0267 | 909.8513 | 0.0286 | 1145.3993 | 0.029 | 1453.1748 | 0.0297 | 1897.3202 | 0.0285 | 2403.9909 | 0.029 | 3053.4997 | 0.0287 | 3845.8464 | 0.0288 | 4754.0807 | 0.0293 | 5788.9826 | 0.0312 | 8085.1712 | 0.0389 |  |  | 474.0776 | 0.016 | 586.2778 | 0.0203 | 686.0145 | 0.0208 | 808.5171 | 0.0209 | 1078.0228 | 0.0209 | [20 empty] | 686.0145 | 0.0577 | 808.5171 | 0.0578 | 1078.0228 | 0.0578 | 1347.5285 | 0.0578 | 1751.7871 | 0.0578 | 2156.0457 | 0.0578
455.8839 | 0.016 | 589.8686 | 0.016 | 722.6003 | 0.016 | 817.4212 | 0.016 | 1089.8949 | 0.016 | [28 empty] | 496.192 | 0.0215 | 591.3759 | 0.0251 | 750.7155 | 0.026 | 928.0483 | 0.0279 | 1168.3072 | 0.0283 | 1482.2383 | 0.0289 | 1935.2666 | 0.0278 | 2452.0707 | 0.0283 | 3114.5697 | 0.028 | 3922.7634 | 0.028 | 4849.1623 | 0.0285 | 5904.7622 | 0.0304 | 8246.8746 | 0.0378 |  |  | 483.5591 | 0.016 | 598.0034 | 0.0202 | 699.7348 | 0.0206 | 824.6875 | 0.0208 | 1099.5833 | 0.0208 | [20 empty] | 699.7348 | 0.0576 | 824.6875 | 0.0577 | 1099.5833 | 0.0577 | 1374.4791 | 0.0577 | 1786.8228 | 0.0577 | 2199.1666 | 0.0577
465.0015 | 0.016 | 601.666 | 0.016 | 737.0523 | 0.016 | 833.7696 | 0.016 | 1111.6928 | 0.016 | [28 empty] | 506.1158 | 0.021 | 603.2034 | 0.0245 | 765.7298 | 0.0254 | 946.6093 | 0.0272 | 1191.6734 | 0.0276 | 1511.883 | 0.0282 | 1973.9719 | 0.0271 | 2501.1121 | 0.0276 | 3176.861 | 0.0273 | 4001.2186 | 0.0273 | 4946.1455 | 0.0278 | 6022.8575 | 0.0296 | 8411.8121 | 0.0368 |  |  | 493.2303 | 0.016 | 609.9634 | 0.0201 | 713.7295 | 0.0205 | 841.1812 | 0.0206 | 1121.575 | 0.0206 | [20 empty] | 713.7295 | 0.0575 | 841.1812 | 0.0576 | 1121.575 | 0.0576 | 1401.9687 | 0.0576 | 1822.5593 | 0.0576 | 2243.1499 | 0.0576
474.3016 | 0.016 | 613.6993 | 0.016 | 751.7934 | 0.016 | 850.445 | 0.016 | 1133.9267 | 0.016 | [28 empty] | 516.2382 | 0.0206 | 615.2675 | 0.024 | 781.0444 | 0.0248 | 965.5414 | 0.0265 | 1215.5069 | 0.0269 | 1542.1207 | 0.0275 | 2013.4514 | 0.0265 | 2551.1344 | 0.0269 | 3240.3983 | 0.0266 | 4081.243 | 0.0266 | 5045.0684 | 0.0271 | 6143.3146 | 0.0288 | 8580.0484 | 0.0358 |  |  | 503.0949 | 0.016 | 619.7093 | 0.016 | 728.0041 | 0.0204 | 858.0048 | 0.0205 | 1144.0065 | 0.0205 | [20 empty] | 728.0041 | 0.0574 | 858.0048 | 0.0575 | 1144.0065 | 0.0575 | 1430.0081 | 0.0575 | 1859.0105 | 0.0575 | 2288.0129 | 0.0575
483.7876 | 0.016 | 625.9733 | 0.016 | 766.8292 | 0.016 | 867.4539 | 0.016 | 1156.6052 | 0.016 | [28 empty] | 526.5629 | 0.0202 | 627.5728 | 0.0234 | 796.6653 | 0.0242 | 984.8523 | 0.0259 | 1239.817 | 0.0262 | 1572.9631 | 0.0268 | 2053.7204 | 0.0258 | 2602.1571 | 0.0262 | 3305.2062 | 0.026 | 4162.8679 | 0.026 | 5145.9698 | 0.0265 | 6266.1809 | 0.0281 | 8751.6493 | 0.0348 |  |  | 513.1568 | 0.016 | 632.1034 | 0.016 | 742.5642 | 0.0203 | 875.1649 | 0.0204 | 1166.8866 | 0.0204 | [20 empty] | 742.5642 | 0.0573 | 875.1649 | 0.0574 | 1166.8866 | 0.0574 | 1458.6082 | 0.0574 | 1896.1907 | 0.0574 | 2333.7732 | 0.0574
493.4633 | 0.016 | 638.4928 | 0.016 | 782.1658 | 0.016 | 884.803 | 0.016 | 1179.7373 | 0.016 | [28 empty] | 531.9078 | 0.016 | 640.1243 | 0.0229 | 812.5986 | 0.0237 | 1004.5493 | 0.0253 | 1264.6133 | 0.0256 | 1604.4224 | 0.0261 | 2094.7948 | 0.0252 | 2654.2002 | 0.0256 | 3371.3104 | 0.0254 | 4246.1252 | 0.0254 | 5248.8892 | 0.0258 | 6391.5045 | 0.0274 | 8926.6823 | 0.0339 |  |  | 523.42 | 0.016 | 644.7455 | 0.016 | 757.4155 | 0.0201 | 892.6682 | 0.0202 | 1190.2243 | 0.0202 | [20 empty] | 757.4155 | 0.0572 | 892.6682 | 0.0573 | 1190.2243 | 0.0573 | 1487.7804 | 0.0573 | 1934.1145 | 0.0573 | 2380.4486 | 0.0573
503.3326 | 0.016 | 651.2626 | 0.016 | 797.8091 | 0.016 | 902.499 | 0.016 | 1203.332 | 0.016 | [28 empty] | 542.5459 | 0.016 | 652.9268 | 0.0224 | 828.8506 | 0.0231 | 1024.6403 | 0.0247 | 1289.9056 | 0.025 | 1636.5108 | 0.0255 | 2136.6907 | 0.0246 | 2707.2842 | 0.025 | 3438.7366 | 0.0248 | 4331.0477 | 0.0248 | 5353.867 | 0.0252 | 6519.3346 | 0.0267 | 9105.216 | 0.033 |  |  | 533.8884 | 0.016 | 657.6404 | 0.016 | 772.5638 | 0.02 | 910.5216 | 0.0201 | 1214.0288 | 0.0201 | [20 empty] | 772.5638 | 0.0571 | 910.5216 | 0.0572 | 1214.0288 | 0.0572 | 1517.536 | 0.0572 | 1972.7968 | 0.0572 | 2428.0576 | 0.0572
513.3993 | 0.016 | 664.2879 | 0.016 | 813.7653 | 0.016 | 920.549 | 0.016 | 1227.3987 | 0.016 | [28 empty] | 553.3968 | 0.016 | 665.9853 | 0.0219 | 845.4276 | 0.0226 | 1045.1331 | 0.0241 | 1315.7037 | 0.0244 | 1669.241 | 0.0249 | 2179.4245 | 0.024 | 2761.4299 | 0.0244 | 3507.5113 | 0.0242 | 4417.6687 | 0.0242 | 5460.9443 | 0.0246 | 6649.7213 | 0.0261 | 9287.3203 | 0.0322 |  |  | 544.5661 | 0.016 | 670.7932 | 0.016 | 774.6366 | 0.016 | 928.732 | 0.02 | 1238.3094 | 0.02 | [20 empty] | 788.0151 | 0.0571 | 928.732 | 0.0571 | 1238.3094 | 0.0571 | 1547.8867 | 0.0571 | 2012.2527 | 0.0571 | 2476.6187 | 0.0571
523.6672 | 0.016 | 677.5737 | 0.016 | 830.0406 | 0.016 | 938.96 | 0.016 | 1251.9467 | 0.016 | [28 empty] | 564.4648 | 0.016 | 679.305 | 0.0214 | 862.3361 | 0.0221 | 1066.0358 | 0.0235 | 1342.0178 | 0.0238 | 1702.6259 | 0.0243 | 2223.013 | 0.0235 | 2816.6585 | 0.0238 | 3577.6615 | 0.0236 | 4506.0221 | 0.0237 | 5570.1632 | 0.0241 | 6782.7158 | 0.0254 | 9473.0667 | 0.0313 |  |  | 555.4575 | 0.016 | 684.2091 | 0.016 | 790.1293 | 0.016 | 929.5639 | 0.016 | 1239.4185 | 0.016 | [20 empty] | 803.7754 | 0.057 | 947.3067 | 0.0571 | 1263.0756 | 0.0571 | 1578.8445 | 0.0571 | 2052.4978 | 0.0571 | 2526.1511 | 0.0571
534.1406 | 0.016 | 691.1251 | 0.016 | 846.6414 | 0.016 | 957.7392 | 0.016 | 1276.9856 | 0.016 | [28 empty] | 575.7541 | 0.016 | 692.8911 | 0.021 | 879.5829 | 0.0217 | 1087.3565 | 0.023 | 1368.8581 | 0.0233 | 1736.6784 | 0.0238 | 2267.4732 | 0.023 | 2872.9917 | 0.0233 | 3649.2148 | 0.0231 | 4596.1425 | 0.0231 | 5681.5665 | 0.0235 | 6918.3701 | 0.0248 | 9662.528 | 0.0306 |  |  | 566.5666 | 0.016 | 697.8933 | 0.016 | 805.9319 | 0.016 | 948.1552 | 0.016 | 1264.2069 | 0.016 | [20 empty] | 819.8509 | 0.0569 | 966.2528 | 0.057 | 1288.3371 | 0.057 | 1610.4213 | 0.057 | 2093.5477 | 0.057 | 2576.6741 | 0.057
544.8234 | 0.016 | 704.9476 | 0.016 | 863.5743 | 0.016 | 976.894 | 0.016 | 1302.5253 | 0.016 | [28 empty] | 587.2692 | 0.016 | 706.7489 | 0.0206 | 897.1745 | 0.0212 | 1109.1036 | 0.0225 | 1396.2353 | 0.0228 | 1771.4119 | 0.0232 | 2312.8227 | 0.0225 | 2930.4515 | 0.0228 | 3722.1991 | 0.0226 | 4688.0654 | 0.0226 | 5795.1978 | 0.023 | 7056.7375 | 0.0243 | 9855.7786 | 0.0298 |  |  | 577.8979 | 0.016 | 711.8511 | 0.016 | 822.0505 | 0.016 | 967.1183 | 0.016 | 1289.491 | 0.016 | [20 empty] | 836.2479 | 0.0568 | 985.5779 | 0.0569 | 1314.1038 | 0.0569 | 1642.6298 | 0.0569 | 2135.4187 | 0.0569 | 2628.2076 | 0.0569
555.7199 | 0.016 | 719.0466 | 0.016 | 880.8458 | 0.016 | 996.4319 | 0.016 | 1328.5758 | 0.016 | [28 empty] | 599.0145 | 0.016 | 720.8839 | 0.0202 | 915.118 | 0.0208 | 1131.2857 | 0.022 | 1424.16 | 0.0223 | 1806.8402 | 0.0227 | 2359.0792 | 0.022 | 2989.0605 | 0.0223 | 3796.643 | 0.0221 | 4781.8267 | 0.0221 | 5911.1018 | 0.0225 | 7197.8722 | 0.0237 | 10052.8942 | 0.0291 |  |  | 589.4559 | 0.016 | 726.0882 | 0.016 | 838.4915 | 0.016 | 986.4606 | 0.016 | 1315.2809 | 0.016 | [20 empty] | 852.9728 | 0.0568 | 1005.2894 | 0.0568 | 1340.3859 | 0.0568 | 1675.4824 | 0.0568 | 2178.1271 | 0.0568 | 2680.7718 | 0.0568
566.8343 | 0.016 | 733.4275 | 0.016 | 898.4627 | 0.016 | 1016.3605 | 0.016 | 1355.1473 | 0.016 | [28 empty] | 610.9948 | 0.016 | 726.6581 | 0.02 | 933.4204 | 0.0204 | 1153.9114 | 0.0216 | 1452.6432 | 0.0218 | 1842.977 | 0.0222 | 2406.2607 | 0.0215 | 3048.8417 | 0.0218 | 3872.5759 | 0.0216 | 4877.4632 | 0.0217 | 6029.3238 | 0.022 | 7341.8297 | 0.0232 | 10253.9521 | 0.0284 |  |  | 601.245 | 0.016 | 740.6099 | 0.016 | 855.2614 | 0.016 | 1006.1899 | 0.016 | 1341.5865 | 0.016 | [20 empty] | 870.0323 | 0.0567 | 1025.3952 | 0.0567 | 1367.1936 | 0.0567 | 1708.992 | 0.0567 | 2221.6896 | 0.0567 | 2734.3872 | 0.0567
578.171 | 0.016 | 748.0961 | 0.016 | 916.4319 | 0.016 | 1036.6877 | 0.016 | 1382.2503 | 0.016 | [28 empty] | 623.2147 | 0.016 | 741.1913 | 0.016 | 950.0724 | 0.016 | 1176.9896 | 0.0211 | 1481.6961 | 0.0213 | 1879.8365 | 0.0218 | 2454.386 | 0.0211 | 3109.8186 | 0.0214 | 3950.0274 | 0.0212 | 4975.0125 | 0.0212 | 6149.9103 | 0.0215 | 7488.6663 | 0.0227 | 10459.0311 | 0.0277 |  |  | 613.2699 | 0.016 | 755.4221 | 0.016 | 872.3666 | 0.016 | 1026.3137 | 0.016 | 1368.4182 | 0.016 | [20 empty] | 887.4329 | 0.0566 | 1045.9031 | 0.0567 | 1394.5375 | 0.0567 | 1743.1718 | 0.0567 | 2266.1234 | 0.0567 | 2789.075 | 0.0567
589.7344 | 0.016 | 763.058 | 0.016 | 934.7606 | 0.016 | 1057.4215 | 0.016 | 1409.8953 | 0.016 | [28 empty] | 635.679 | 0.016 | 756.0151 | 0.016 | 969.0738 | 0.016 | 1200.5294 | 0.0207 | 1511.33 | 0.0209 | 1917.4333 | 0.0213 | 2503.4737 | 0.0206 | 3172.015 | 0.0209 | 4029.028 | 0.0208 | 5074.5127 | 0.0208 | 6272.9085 | 0.0211 | 7638.4396 | 0.0222 | 10668.2117 | 0.027 |  |  | 625.5353 | 0.016 | 770.5306 | 0.016 | 889.8139 | 0.016 | 1046.8399 | 0.016 | 1395.7866 | 0.016 | [20 empty] | 905.1816 | 0.0566 | 1066.8212 | 0.0566 | 1422.4282 | 0.0566 | 1778.0353 | 0.0566 | 2311.4459 | 0.0566 | 2844.8565 | 0.0566
601.5291 | 0.016 | 778.3192 | 0.016 | 953.4558 | 0.016 | 1078.5699 | 0.016 | 1438.0932 | 0.016 | [28 empty] | 648.3926 | 0.016 | 771.1354 | 0.016 | 988.4553 | 0.016 | 1224.54 | 0.0203 | 1541.5566 | 0.0205 | 1955.7819 | 0.0209 | 2553.5432 | 0.0202 | 3235.4552 | 0.0205 | 4109.6085 | 0.0203 | 5176.003 | 0.0203 | 6398.3667 | 0.0206 | 7791.2084 | 0.0217 | 10881.5759 | 0.0264 |  |  | 638.046 | 0.016 | 785.9412 | 0.016 | 907.6102 | 0.016 | 1067.7767 | 0.016 | 1423.7023 | 0.016 | [20 empty] | 923.2852 | 0.0565 | 1088.1576 | 0.0566 | 1450.8768 | 0.0566 | 1813.596 | 0.0566 | 2357.6748 | 0.0566 | 2901.7536 | 0.0566
613.5596 | 0.016 | 793.8855 | 0.016 | 972.5249 | 0.016 | 1100.1413 | 0.016 | 1466.855 | 0.016 | [28 empty] | 661.3605 | 0.016 | 786.5581 | 0.016 | 1008.2244 | 0.016 | 1240.6508 | 0.02 | 1572.3877 | 0.0201 | 1994.8976 | 0.0204 | 2582.7827 | 0.016 | 3300.1644 | 0.0201 | 4178.5889 | 0.02 | 5264.6212 | 0.016 | 6526.334 | 0.0202 | 7947.0325 | 0.0212 | 11099.2075 | 0.0258 |  |  | 650.8069 | 0.016 | 801.66 | 0.016 | 925.7624 | 0.016 | 1089.1323 | 0.016 | 1452.1763 | 0.016 | [20 empty] | 941.7509 | 0.0564 | 1109.9207 | 0.0565 | 1479.8943 | 0.0565 | 1849.8679 | 0.0565 | 2404.8283 | 0.0565 | 2959.7887 | 0.0565
625.8308 | 0.016 | 809.7632 | 0.016 | 991.9754 | 0.016 | 1122.1441 | 0.016 | 1496.1921 | 0.016 | [28 empty] | 674.5877 | 0.016 | 802.2893 | 0.016 | 1028.3889 | 0.016 | 1265.4638 | 0.016 | 1578.3494 | 0.016 | 2034.7955 | 0.02 | 2634.4384 | 0.016 | 3313.8049 | 0.016 | 4262.1607 | 0.016 | 5369.9136 | 0.016 | 6601.7392 | 0.016 | 8105.9732 | 0.0208 | 11321.1916 | 0.0252 |  |  | 663.8231 | 0.016 | 817.6932 | 0.016 | 944.2777 | 0.016 | 1110.9149 | 0.016 | 1481.2199 | 0.016 | [20 empty] | 960.586 | 0.0564 | 1132.1192 | 0.0564 | 1509.4922 | 0.0564 | 1886.8653 | 0.0564 | 2452.9249 | 0.0564 | 3018.9844 | 0.0564
638.3475 | 0.016 | 825.9585 | 0.016 | 1011.8149 | 0.016 | 1144.587 | 0.016 | 1526.116 | 0.016 | [28 empty] | 688.0794 | 0.016 | 818.3351 | 0.016 | 1048.9567 | 0.016 | 1290.7731 | 0.016 | 1609.9164 | 0.016 | 2037.5732 | 0.02 | 2687.1272 | 0.016 | 3380.081 | 0.016 | 4347.4039 | 0.016 | 5477.3119 | 0.016 | 6733.774 | 0.016 | 8268.0927 | 0.0204 | 11547.6155 | 0.0246 |  |  | 677.0995 | 0.016 | 834.0471 | 0.016 | 963.1632 | 0.016 | 1133.1332 | 0.016 | 1510.8443 | 0.016 | [20 empty] | 979.7977 | 0.0563 | 1154.7615 | 0.0564 | 1539.6821 | 0.0564 | 1924.6026 | 0.0564 | 2501.9833 | 0.0564 | 3079.3641 | 0.0564
651.1144 | 0.016 | 842.4777 | 0.016 | 1032.0512 | 0.016 | 1167.4787 | 0.016 | 1556.6383 | 0.016 | [28 empty] | 701.841 | 0.016 | 834.7018 | 0.016 | 1069.9358 | 0.016 | 1316.5885 | 0.016 | 1642.1147 | 0.016 | 2078.3247 | 0.016 | 2740.8697 | 0.016 | 3447.6826 | 0.016 | 4434.352 | 0.016 | 5586.8581 | 0.016 | 6868.4495 | 0.016 | 8423.3673 | 0.016 | 11778.5678 | 0.0241 |  |  | 690.6415 | 0.016 | 850.728 | 0.016 | 982.4265 | 0.016 | 1155.7959 | 0.016 | 1541.0612 | 0.016 | [20 empty] | 999.3936 | 0.0563 | 1177.8568 | 0.0563 | 1570.4757 | 0.0563 | 1963.0946 | 0.0563 | 2552.023 | 0.0563 | 3140.9514 | 0.0563
664.1367 | 0.016 | 859.3272 | 0.016 | 1052.6922 | 0.016 | 1190.8283 | 0.016 | 1587.7711 | 0.016 | [28 empty] | 715.8778 | 0.016 | 851.3958 | 0.016 | 1091.3345 | 0.016 | 1342.9203 | 0.016 | 1674.957 | 0.016 | 2119.8912 | 0.016 | 2795.6871 | 0.016 | 3516.6363 | 0.016 | 4523.039 | 0.016 | 5698.5953 | 0.016 | 7005.8185 | 0.016 | 8591.8347 | 0.016 | 12014.1391 | 0.0236 |  |  | 704.4544 | 0.016 | 867.7426 | 0.016 | 1002.075 | 0.016 | 1178.9118 | 0.016 | 1571.8824 | 0.016 | [20 empty] | 1019.3815 | 0.0562 | 1201.4139 | 0.0563 | 1601.8852 | 0.0563 | 2002.3565 | 0.0563 | 2603.0635 | 0.0563 | 3203.7704 | 0.0563
664.1734 | 0.016 | 876.5138 | 0.016 | 1073.7461 | 0.016 | 1214.6449 | 0.016 | 1619.5265 | 0.016 | [28 empty] | 730.1954 | 0.016 | 868.4238 | 0.016 | 1113.1612 | 0.016 | 1369.7787 | 0.016 | 1708.4561 | 0.016 | 2162.289 | 0.016 | 2851.6009 | 0.016 | 3586.969 | 0.016 | 4613.4998 | 0.016 | 5812.5672 | 0.016 | 7145.9348 | 0.016 | 8763.6714 | 0.016 |  |  |  |  | 718.5434 | 0.016 | 885.0974 | 0.016 | 1022.1165 | 0.016 | 1202.49 | 0.016 | 1603.32 | 0.016 | [20 empty] | 1039.7691 | 0.0562 | 1225.4422 | 0.0562 | 1633.9229 | 0.0562 | 2042.4036 | 0.0562 | 2655.1247 | 0.0562 | 3267.8458 | 0.0562
677.4568 | 0.014 | 894.0441 | 0.016 | 1095.221 | 0.016 | 1238.9378 | 0.016 | 1651.917 | 0.016 | [28 empty] | 744.7993 | 0.016 | 885.7922 | 0.016 | 1135.4244 | 0.016 | 1397.1743 | 0.016 | 1742.6253 | 0.016 | 2205.5348 | 0.016 | 2908.6329 | 0.016 | 3658.7084 | 0.016 | 4705.7698 | 0.016 | 5928.8185 | 0.016 | 7288.8535 | 0.016 | 8938.9448 | 0.016 |  |  |  |  | 732.9143 | 0.016 | 902.7994 | 0.016 | 1042.5588 | 0.016 | 1226.5398 | 0.016 | 1635.3864 | 0.016 | [20 empty] | 1060.5645 | 0.0561 | 1249.951 | 0.0562 | 1666.6014 | 0.0562 | 2083.2517 | 0.0562 | 2708.2272 | 0.0562 | 3333.2028 | 0.0562
691.006 | 0.014 | 911.9249 | 0.016 | 1117.1254 | 0.016 | 1263.7165 | 0.016 | 1684.9554 | 0.016 | [28 empty] | 759.6953 | 0.016 | 903.5081 | 0.016 | 1158.1329 | 0.016 | 1425.1178 | 0.016 | 1777.4778 | 0.016 | 2249.6455 | 0.016 | 2966.8055 | 0.016 | 3731.8825 | 0.016 | 4799.8852 | 0.016 | 6047.3949 | 0.016 | 7434.6306 | 0.016 | 9117.7237 | 0.016 |  |  |  |  | 747.5726 | 0.016 | 920.8554 | 0.016 | 1063.41 | 0.016 | 1251.0706 | 0.016 | 1668.0942 | 0.016 | [20 empty] | 1081.7758 | 0.0561 | 1274.9501 | 0.0561 | 1699.9334 | 0.0561 | 2124.9168 | 0.0561 | 2762.3918 | 0.0561 | 3399.8668 | 0.0561
704.8261 | 0.014 | 930.1634 | 0.016 | 1139.4679 | 0.016 | 1288.9909 | 0.016 | 1718.6545 | 0.016 | [28 empty] | 774.8892 | 0.016 | 921.5782 | 0.016 | 1181.2956 | 0.016 | 1453.6201 | 0.016 | 1813.0273 | 0.016 | 2294.6384 | 0.016 | 3026.1416 | 0.016 | 3806.5202 | 0.016 | 4895.8829 | 0.016 | 6168.3428 | 0.016 | 7583.3232 | 0.016 | 9300.0782 | 0.016 |  |  |  |  | 762.5241 | 0.016 | 939.2725 | 0.016 | 1084.6782 | 0.016 | 1276.092 | 0.016 | 1701.456 | 0.016 | [20 empty] | 1103.4113 | 0.056 | 1300.4491 | 0.0561 | 1733.9321 | 0.0561 | 2167.4151 | 0.0561 | 2817.6396 | 0.0561 | 3467.8641 | 0.0561
718.9226 | 0.014 | 948.7667 | 0.016 | 1162.2573 | 0.016 | 1314.7707 | 0.016 | 1753.0276 | 0.016 | [28 empty] | 790.387 | 0.016 | 940.0098 | 0.016 | 1204.9215 | 0.016 | 1482.6925 | 0.016 | 1849.2879 | 0.016 | 2340.5311 | 0.016 | 3086.6645 | 0.016 | 3882.6506 | 0.016 | 4993.8006 | 0.016 | 6291.7096 | 0.016 | 7734.9897 | 0.016 | 9486.0797 | 0.016 |  |  |  |  | 777.7745 | 0.016 | 958.0579 | 0.016 | 1106.3718 | 0.016 | 1301.6139 | 0.016 | 1735.4852 | 0.016 | [20 empty] | 1125.4795 | 0.056 | 1326.458 | 0.056 | 1768.6107 | 0.056 | 2210.7634 | 0.056 | 2873.9924 | 0.056 | 3537.2214 | 0.056
733.3011 | 0.014 | 948.8191 | 0.014 | 1185.5024 | 0.016 | 1341.0661 | 0.016 | 1788.0881 | 0.016 | [28 empty] | 806.1947 | 0.016 | 958.81 | 0.016 | 1229.0199 | 0.016 | 1512.3464 | 0.016 | 1886.2736 | 0.016 | 2387.3417 | 0.016 | 3148.3978 | 0.016 | 3960.3036 | 0.016 | 5093.6766 | 0.016 | 6417.5438 | 0.016 | 7889.6895 | 0.016 | 9675.8013 | 0.016 |  |  |  |  | 793.33 | 0.016 | 977.2191 | 0.016 | 1128.4992 | 0.016 | 1327.6461 | 0.016 | 1770.1949 | 0.016 | [20 empty] | 1147.9891 | 0.056 | 1352.9872 | 0.056 | 1803.9829 | 0.056 | 2254.9787 | 0.056 | 2931.4723 | 0.056 | 3607.9659 | 0.056
747.9671 | 0.014 | 967.7955 | 0.014 | 1209.2125 | 0.016 | 1367.8874 | 0.016 | 1823.8499 | 0.016 | [28 empty] | 822.3186 | 0.016 | 977.9862 | 0.016 | 1253.6003 | 0.016 | 1542.5933 | 0.016 | 1923.9991 | 0.016 | 2435.0886 | 0.016 | 3211.3657 | 0.016 | 4039.5097 | 0.016 | 5195.5501 | 0.016 | 6545.8947 | 0.016 | 8047.4832 | 0.016 | 9869.3173 | 0.016 |  |  |  |  | 809.1966 | 0.016 | 996.7635 | 0.016 | 1151.0692 | 0.016 | 1354.1991 | 0.016 | 1805.5988 | 0.016 | [20 empty] | 1170.9489 | 0.0559 | 1380.0469 | 0.056 | 1840.0626 | 0.056 | 2300.0782 | 0.056 | 2990.1017 | 0.056 | 3680.1252 | 0.056
762.9264 | 0.014 | 987.1514 | 0.014 | 1233.3967 | 0.016 | 1395.2452 | 0.016 | 1860.3269 | 0.016 | [28 empty] | 838.765 | 0.016 | 997.5459 | 0.016 | 1278.6723 | 0.016 | 1573.4452 | 0.016 | 1962.4791 | 0.016 | 2483.7904 | 0.016 | 3275.593 | 0.016 | 4120.2999 | 0.016 | 5299.4611 | 0.016 | 6676.8126 | 0.016 | 8208.4329 | 0.016 | 10066.7037 | 0.016 |  |  |  |  | 825.3806 | 0.016 | 1016.6987 | 0.016 | 1174.0906 | 0.016 | 1381.2831 | 0.016 | 1841.7107 | 0.016 | [20 empty] | 1194.3679 | 0.0559 | 1407.6479 | 0.0559 | 1876.8638 | 0.0559 | 2346.0798 | 0.0559 | 3049.9037 | 0.0559 | 3753.7277 | 0.0559
778.185 | 0.014 | 1006.8944 | 0.014 | 1233.4648 | 0.014 | 1423.1501 | 0.016 | 1897.5334 | 0.016 | [28 empty] | 855.5403 | 0.016 | 1017.4968 | 0.016 | 1304.2458 | 0.016 | 1604.9141 | 0.016 | 2001.7287 | 0.016 | 2533.4662 | 0.016 | 3341.1049 | 0.016 | 4202.7059 | 0.016 | 5405.4504 | 0.016 | 6810.3489 | 0.016 | 8372.6016 | 0.016 | 10268.0378 | 0.016 |  |  |  |  | 841.8882 | 0.016 | 1037.0327 | 0.016 | 1197.5724 | 0.016 | 1408.9087 | 0.016 | 1878.545 | 0.016 | [20 empty] | 1218.2553 | 0.0559 | 1435.8008 | 0.0559 | 1914.4011 | 0.0559 | 2393.0014 | 0.0559 | 3110.9018 | 0.0559 | 3828.8022 | 0.0559
793.7487 | 0.014 | 1027.0323 | 0.014 | 1258.1341 | 0.014 | 1423.2286 | 0.016 | 1897.6382 | 0.016 | [28 empty] | 872.6511 | 0.016 | 1037.8468 | 0.016 | 1330.3307 | 0.016 | 1637.0123 | 0.016 | 2041.7632 | 0.016 | 2584.1355 | 0.016 | 3407.927 | 0.016 | 4286.76 | 0.016 | 5513.5594 | 0.016 | 6946.5558 | 0.016 | 8540.0536 | 0.016 | 10473.3985 | 0.016 |  |  |  |  | 858.7259 | 0.016 | 1057.7734 | 0.016 | 1221.5239 | 0.016 | 1437.0869 | 0.016 | 1916.1158 | 0.016 | [20 empty] | 1242.6204 | 0.0558 | 1464.5169 | 0.0559 | 1952.6891 | 0.0559 | 2440.8614 | 0.0559 | 3173.1199 | 0.0559 | 3905.3783 | 0.0559
809.6236 | 0.014 | 1047.573 | 0.014 | 1283.2968 | 0.014 | 1451.6932 | 0.014 | 1935.591 | 0.014 | [28 empty] | 890.1041 | 0.016 | 1058.6037 | 0.016 | 1356.9373 | 0.016 | 1669.7526 | 0.016 | 2082.5985 | 0.016 | 2635.8182 | 0.016 | 3476.0855 | 0.016 | 4372.4952 | 0.016 | 5623.8305 | 0.016 | 7085.487 | 0.016 | 8710.8547 | 0.016 | 10682.8665 | 0.016 |  |  |  |  | 875.9004 | 0.016 | 1078.9288 | 0.016 | 1245.9543 | 0.016 | 1465.8286 | 0.016 | 1954.4382 | 0.016 | [20 empty] | 1267.4728 | 0.0558 | 1493.8072 | 0.0558 | 1991.7429 | 0.0558 | 2489.6787 | 0.0558 | 3236.5822 | 0.0558 | 3983.4858 | 0.0558
825.8161 | 0.014 | 1068.5244 | 0.014 | 1308.9627 | 0.014 | 1480.7271 | 0.014 | 1974.3028 | 0.014 | [28 empty] | 907.9062 | 0.016 | 1079.7758 | 0.016 | 1384.076 | 0.016 | 1703.1476 | 0.016 | 2124.2505 | 0.016 | 2688.5346 | 0.016 | 3545.6072 | 0.016 | 4459.9451 | 0.016 | 5736.3072 | 0.016 | 7227.1967 | 0.016 | 8885.0718 | 0.016 | 10896.5238 | 0.016 |  |  |  |  | 893.4185 | 0.016 | 1100.5074 | 0.016 | 1270.8734 | 0.016 | 1495.1452 | 0.016 | 1993.5269 | 0.016 | [20 empty] | 1292.8222 | 0.0558 | 1523.6833 | 0.0558 | 2031.5778 | 0.0558 | 2539.4722 | 0.0558 | 3301.3139 | 0.0558 | 4063.1556 | 0.0558
842.3324 | 0.014 | 1089.8949 | 0.014 | 1335.142 | 0.014 | 1510.3416 | 0.014 | 2013.7888 | 0.014 | [28 empty] | 926.0643 | 0.016 | 1101.3713 | 0.016 | 1411.7576 | 0.016 | 1737.2106 | 0.016 | 2166.7355 | 0.016 | 2742.3053 | 0.016 | 3616.5194 | 0.016 | 4549.144 | 0.016 | 5851.0333 | 0.016 | 7371.7406 | 0.016 | 9062.7732 | 0.016 | 11114.4543 | 0.016 |  |  |  |  | 911.2868 | 0.016 | 1122.5176 | 0.016 | 1296.2909 | 0.016 | 1525.0481 | 0.016 | 2033.3975 | 0.016 | [20 empty] | 1318.6787 | 0.0557 | 1554.157 | 0.0558 | 2072.2093 | 0.0558 | 2590.2617 | 0.0558 | 3367.3402 | 0.0558 | 4144.4187 | 0.0558
859.1791 | 0.014 | 1111.6928 | 0.014 | 1361.8448 | 0.014 | 1540.5485 | 0.014 | 2054.0646 | 0.014 | [28 empty] | 944.5856 | 0.016 | 1123.3987 | 0.016 | 1439.9927 | 0.016 | 1771.9548 | 0.016 | 2210.0702 | 0.016 | 2797.1514 | 0.016 | 3688.8498 | 0.016 | 4640.1269 | 0.016 | 5968.054 | 0.016 | 7519.1754 | 0.016 | 9244.0287 | 0.016 | 11336.7434 | 0.016 |  |  |  |  | 929.5126 | 0.016 | 1144.9679 | 0.016 | 1322.2167 | 0.016 | 1555.5491 | 0.016 | 2074.0654 | 0.016 | [20 empty] | 1345.0522 | 0.0557 | 1585.2401 | 0.0557 | 2113.6535 | 0.0557 | 2642.0669 | 0.0557 | 3434.687 | 0.0557 | 4227.307 | 0.0557
876.3627 | 0.014 | 1133.9267 | 0.014 | 1389.0817 | 0.014 | 1571.3594 | 0.014 | 2095.1459 | 0.014 | [28 empty] | 963.4773 | 0.016 | 1145.8667 | 0.016 | 1468.7926 | 0.016 | 1807.3939 | 0.016 | 2254.2716 | 0.016 | 2853.0944 | 0.016 | 3762.6268 | 0.016 | 4732.9294 | 0.016 | 6087.415 | 0.016 | 7669.559 | 0.016 | 9428.9092 | 0.016 | 11563.4782 | 0.016 |  |  |  |  | 929.5639 | 0.014 | 1167.8673 | 0.016 | 1348.661 | 0.016 | 1586.66 | 0.016 | 2115.5467 | 0.016 | [20 empty] | 1371.9533 | 0.0557 | 1616.9449 | 0.0557 | 2155.9266 | 0.0557 | 2694.9082 | 0.0557 | 3503.3807 | 0.0557 | 4311.8532 | 0.0557
893.8899 | 0.014 | 1156.6052 | 0.014 | 1416.8634 | 0.014 | 1602.7866 | 0.014 | 2137.0488 | 0.014 | [28 empty] | 982.7468 | 0.016 | 1168.784 | 0.016 | 1498.1684 | 0.016 | 1843.5418 | 0.016 | 2299.357 | 0.016 | 2910.1563 | 0.016 | 3837.8793 | 0.016 | 4827.588 | 0.016 | 6209.1633 | 0.016 | 7822.9501 | 0.016 | 9617.4874 | 0.016 | 11794.7478 | 0.016 |  |  |  |  | 948.1552 | 0.014 | 1191.2246 | 0.016 | 1375.6343 | 0.016 | 1618.3932 | 0.016 | 2157.8577 | 0.016 | [20 empty] | 1399.3924 | 0.0557 | 1649.2838 | 0.0557 | 2199.0451 | 0.0557 | 2748.8064 | 0.0557 | 3573.4483 | 0.0557 | 4398.0903 | 0.0557
911.7677 | 0.014 | 1179.7373 | 0.014 | 1445.2006 | 0.014 | 1634.8424 | 0.014 | 2179.7898 | 0.014 | [28 empty] | 1002.4018 | 0.016 | 1192.1597 | 0.016 | 1528.1318 | 0.016 | 1880.4126 | 0.016 | 2345.3442 | 0.016 | 2968.3594 | 0.016 | 3914.6369 | 0.016 | 4924.1397 | 0.016 | 6333.3466 | 0.016 | 7979.4091 | 0.016 | 9809.8372 | 0.016 | 12030.6428 | 0.016 |  |  |  |  | 967.1183 | 0.014 | 1215.0491 | 0.016 | 1403.1469 | 0.016 | 1650.7611 | 0.016 | 2201.0148 | 0.016 | [20 empty] | 1427.3802 | 0.0556 | 1682.2695 | 0.0556 | 2243.026 | 0.0556 | 2803.7825 | 0.0556 | 3644.9173 | 0.0556 | 4486.0521 | 0.0556
930.0031 | 0.014 | 1203.332 | 0.014 | 1474.1047 | 0.014 | 1667.5392 | 0.014 | 2223.3856 | 0.014 | [28 empty] | 1022.4498 | 0.016 | 1216.0029 | 0.016 | 1558.6944 | 0.016 | 1918.0209 | 0.016 | 2392.251 | 0.016 | 3027.7266 | 0.016 | 3992.9296 | 0.016 | 5022.6225 | 0.016 | 6460.0135 | 0.016 | 8138.9973 | 0.016 | 10006.0339 | 0.016 | [6 empty] | 986.4606 | 0.014 | 1239.3501 | 0.016 | 1431.2099 | 0.016 | 1683.7763 | 0.016 | 2245.0351 | 0.016 | [20 empty] | 1455.9278 | 0.0556 | 1715.9149 | 0.0556 | 2287.8865 | 0.0556 | 2859.8582 | 0.0556 | 3717.8156 | 0.0556 | 4575.7731 | 0.0556
948.6031 | 0.014 | 1227.3987 | 0.014 | 1503.5867 | 0.014 | 1700.89 | 0.014 | 2267.8533 | 0.014 | [28 empty] | 1042.8988 | 0.016 | 1240.323 | 0.016 | 1589.8683 | 0.016 | 1956.3813 | 0.016 | 2440.0961 | 0.016 | 3088.2811 | 0.016 | 4072.7882 | 0.016 | 5123.075 | 0.016 | 6589.2138 | 0.016 | 8301.7773 | 0.016 | 10206.1546 | 0.016 | [6 empty] | 1006.1899 | 0.014 | 1239.4185 | 0.014 | 1459.8341 | 0.016 | 1717.4519 | 0.016 | 2289.9358 | 0.016 | [20 empty] | 1485.0464 | 0.0556 | 1750.2332 | 0.0556 | 2333.6443 | 0.0556 | 2917.0553 | 0.0556 | 3792.172 | 0.0556 | 4667.2886 | 0.0556
967.5752 | 0.014 | 1251.9467 | 0.014 | 1533.6585 | 0.014 | 1734.9078 | 0.014 | 2313.2104 | 0.014 | [28 empty] | 1063.7568 | 0.016 | 1265.1294 | 0.016 | 1621.6657 | 0.016 | 1995.5089 | 0.016 | 2488.898 | 0.016 | 3150.0467 | 0.016 | 4154.244 | 0.016 | 5225.5365 | 0.016 | 6720.9981 | 0.016 | 8467.8128 | 0.016 | 10410.2777 | 0.016 | [6 empty] | 1026.3137 | 0.014 | 1264.2069 | 0.014 | 1489.0308 | 0.016 | 1751.8009 | 0.016 | 2335.7345 | 0.016 | [20 empty] | 1514.7473 | 0.0556 | 1785.2379 | 0.0556 | 2380.3172 | 0.0556 | 2975.3965 | 0.0556 | 3868.0154 | 0.0556 | 4760.6343 | 0.0556
986.9267 | 0.014 | 1276.9856 | 0.014 | 1564.3316 | 0.014 | 1769.6059 | 0.014 | 2359.4746 | 0.014 | [28 empty] | 1063.8155 | 0.014 | 1290.432 | 0.016 | 1654.099 | 0.016 | 2035.4191 | 0.016 | 2538.6759 | 0.016 | 3213.0477 | 0.016 | 4237.3289 | 0.016 | 5330.0472 | 0.016 | 6855.4181 | 0.016 | 8637.1691 | 0.016 | 10618.4832 | 0.016 | [6 empty] | 1046.8399 | 0.014 | 1289.491 | 0.014 | 1518.8114 | 0.016 | 1786.8369 | 0.016 | 2382.4492 | 0.016 | [20 empty] | 1545.0422 | 0.0555 | 1820.9426 | 0.0556 | 2427.9235 | 0.0556 | 3034.9044 | 0.0556 | 3945.3757 | 0.0556 | 4855.847 | 0.0556
1006.6652 | 0.014 | 1302.5253 | 0.014 | 1595.6183 | 0.014 | 1804.9981 | 0.014 | 2406.6641 | 0.014 | [28 empty] | 1085.0918 | 0.014 | 1316.2407 | 0.016 | 1687.181 | 0.016 | 2076.1275 | 0.016 | 2589.4495 | 0.016 | 3277.3086 | 0.016 | 4322.0754 | 0.016 | 5436.6482 | 0.016 | 6992.5264 | 0.016 | 8809.9124 | 0.016 | 10830.8529 | 0.016 | [6 empty] | 1067.7767 | 0.014 | 1315.2809 | 0.014 | 1549.1876 | 0.016 | 1822.5737 | 0.016 | 2430.0982 | 0.016 | [20 empty] | 1575.9431 | 0.0555 | 1857.3615 | 0.0555 | 2476.482 | 0.0555 | 3095.6025 | 0.0555 | 4024.2832 | 0.0555 | 4952.964 | 0.0555
1026.7985 | 0.014 | 1328.5758 | 0.014 | 1627.5306 | 0.014 | 1841.098 | 0.014 | 2454.7974 | 0.014 | [28 empty] | 1106.7937 | 0.014 | 1342.5655 | 0.016 | 1720.9246 | 0.016 | 2117.65 | 0.016 | 2641.2385 | 0.016 | 3342.8548 | 0.016 | 4408.5169 | 0.016 | 5545.3811 | 0.016 | 7132.3769 | 0.016 | 8986.1107 | 0.016 | 11047.47 | 0.016 | [6 empty] | 1089.1323 | 0.014 | 1341.5865 | 0.014 | 1549.2732 | 0.014 | 1859.0251 | 0.016 | 2478.7002 | 0.016 | [20 empty] | 1607.4619 | 0.0555 | 1894.5087 | 0.0555 | 2526.0116 | 0.0555 | 3157.5145 | 0.0555 | 4104.7689 | 0.0555 | 5052.0232 | 0.0555
1047.3345 | 0.014 | 1355.1473 | 0.014 | 1660.0813 | 0.014 | 1877.92 | 0.014 | 2503.8933 | 0.014 | [28 empty] | 1128.9296 | 0.014 | 1369.4168 | 0.016 | 1755.3431 | 0.016 | 2160.003 | 0.016 | 2694.0632 | 0.016 | 3409.7119 | 0.016 | 4496.6873 | 0.016 | 5656.2887 | 0.016 | 7275.0245 | 0.016 | 9165.8329 | 0.016 | 11268.4194 | 0.016 | [6 empty] | 1110.9149 | 0.014 | 1368.4182 | 0.014 | 1580.2586 | 0.014 | 1859.1278 | 0.014 | 2478.8371 | 0.014 | [20 empty] | 1639.6112 | 0.0555 | 1932.3989 | 0.0555 | 2576.5318 | 0.0555 | 3220.6648 | 0.0555 | 4186.8643 | 0.0555 | 5153.0637 | 0.0555
1068.2812 | 0.014 | 1382.2503 | 0.014 | 1693.2829 | 0.014 | 1915.4784 | 0.014 | 2553.9712 | 0.014 | [28 empty] | 1151.5081 | 0.014 | 1396.8051 | 0.016 | 1790.4499 | 0.016 | 2203.2031 | 0.016 | 2747.9445 | 0.016 | 3477.9061 | 0.016 | 4586.621 | 0.016 | 5769.4145 | 0.016 | 7420.525 | 0.016 | 9349.1496 | 0.016 | 11493.7877 | 0.016 | [6 empty] | 1133.1332 | 0.014 | 1395.7866 | 0.014 | 1611.8638 | 0.014 | 1896.3103 | 0.014 | 2528.4138 | 0.014 | [20 empty] | 1672.4034 | 0.0555 | 1971.0469 | 0.0555 | 2628.0625 | 0.0555 | 3285.0781 | 0.0555 | 4270.6015 | 0.0555 | 5256.125 | 0.0555
1089.6468 | 0.014 | 1409.8953 | 0.014 | 1727.1485 | 0.014 | 1953.7879 | 0.014 | 2605.0506 | 0.014 | [28 empty] | 1174.5383 | 0.014 | 1424.7412 | 0.016 | 1826.2589 | 0.016 | 2247.2671 | 0.016 | 2802.9034 | 0.016 | 3547.4643 | 0.016 | 4678.3535 | 0.016 | 5884.8028 | 0.016 | 7568.9355 | 0.016 | 9536.1326 | 0.016 | 11723.6635 | 0.016 | [6 empty] | 1155.7959 | 0.014 | 1423.7023 | 0.014 | 1644.1011 | 0.014 | 1934.2366 | 0.014 | 2578.9821 | 0.014 | [20 empty] | 1705.8515 | 0.0554 | 2010.4678 | 0.0555 | 2680.6237 | 0.0555 | 3350.7797 | 0.0555 | 4356.0136 | 0.0555 | 5361.2475 | 0.0555
1111.4397 | 0.014 | 1438.0932 | 0.014 | 1761.6915 | 0.014 | 1992.8637 | 0.014 | 2657.1516 | 0.014 | [28 empty] | 1198.0291 | 0.014 | 1453.236 | 0.016 | 1862.7841 | 0.016 | 2292.2125 | 0.016 | 2858.9614 | 0.016 | 3618.4135 | 0.016 | 4771.9205 | 0.016 | 6002.4989 | 0.016 | 7720.3142 | 0.016 | 9726.8552 | 0.016 | 11958.1368 | 0.016 | [6 empty] | 1178.9118 | 0.014 | 1452.1763 | 0.014 | 1676.9831 | 0.014 | 1972.9213 | 0.014 | 2630.5617 | 0.014 | [20 empty] | 1739.9685 | 0.0554 | 2050.6772 | 0.0554 | 2734.2362 | 0.0554 | 3417.7953 | 0.0554 | 4443.1338 | 0.0554 | 5468.4724 | 0.0554
1133.6685 | 0.014 | 1466.855 | 0.014 | 1796.9253 | 0.014 | 2032.721 | 0.014 | 2710.2946 | 0.014 | [28 empty] | 1221.9897 | 0.014 | 1453.3163 | 0.014 | 1900.0398 | 0.016 | 2338.0567 | 0.016 | 2916.1407 | 0.016 | 3690.7818 | 0.016 | 4867.3589 | 0.016 | 6122.5488 | 0.016 | 7874.7205 | 0.016 | 9921.3923 | 0.016 | [8 empty] | 1202.49 | 0.014 | 1481.2199 | 0.014 | 1710.5228 | 0.014 | 2012.3797 | 0.014 | 2683.173 | 0.014 | [20 empty] | 1774.7679 | 0.0554 | 2091.6907 | 0.0554 | 2788.9209 | 0.0554 | 3486.1512 | 0.0554 | 4531.9965 | 0.0554 | 5577.8419 | 0.0554
1156.3419 | 0.014 | 1496.1921 | 0.014 | 1832.8639 | 0.014 | 2073.3754 | 0.014 | 2764.5005 | 0.014 | [28 empty] | 1246.4294 | 0.014 | 1482.3826 | 0.014 | 1900.1447 | 0.014 | 2384.8179 | 0.016 | 2974.4635 | 0.016 | 3764.5974 | 0.016 | 4964.7061 | 0.016 | 6244.9998 | 0.016 | 8032.2149 | 0.016 | 10119.8202 | 0.016 | [8 empty] | 1226.5398 | 0.014 | 1510.8443 | 0.014 | 1744.7332 | 0.014 | 2052.6273 | 0.014 | 2736.8364 | 0.014 | [20 empty] | 1810.2632 | 0.0554 | 2133.5245 | 0.0554 | 2844.6994 | 0.0554 | 3555.8742 | 0.0554 | 4622.6365 | 0.0554 | 5689.3987 | 0.0554
1179.4688 | 0.014 | 1526.116 | 0.014 | 1869.5211 | 0.014 | 2114.8429 | 0.014 | 2819.7905 | 0.014 | [28 empty] | 1271.358 | 0.014 | 1512.0303 | 0.014 | 1938.1476 | 0.014 | 2432.5142 | 0.016 | 3033.9528 | 0.016 | 3839.8894 | 0.016 | 5064.0002 | 0.016 | 6369.8998 | 0.016 | 8192.8592 | 0.016 | 10322.2166 | 0.016 | [8 empty] | 1251.0706 | 0.014 | 1541.0612 | 0.014 | 1779.6279 | 0.014 | 2093.6799 | 0.014 | 2791.5731 | 0.014 | [20 empty] | 1846.4685 | 0.0554 | 2176.195 | 0.0554 | 2901.5933 | 0.0554 | 3626.9917 | 0.0554 | 4715.0892 | 0.0554 | 5803.1867 | 0.0554
1203.0581 | 0.014 | 1556.6383 | 0.014 | 1906.9116 | 0.014 | 2157.1398 | 0.014 | 2876.1864 | 0.014 | [28 empty] | 1296.7852 | 0.014 | 1542.2709 | 0.014 | 1976.9106 | 0.014 | 2481.1645 | 0.016 | 3094.6318 | 0.016 | 3916.6872 | 0.016 | 5165.2802 | 0.016 | 6497.2978 | 0.016 | 8356.7164 | 0.016 | 10528.6609 | 0.016 | [8 empty] | 1276.092 | 0.014 | 1571.8824 | 0.014 | 1815.2204 | 0.014 | 2135.5535 | 0.014 | 2847.4046 | 0.014 | [20 empty] | 1883.3979 | 0.0554 | 2219.7189 | 0.0554 | 2959.6252 | 0.0554 | 3699.5315 | 0.0554 | 4809.391 | 0.0554 | 5919.2504 | 0.0554
1227.1193 | 0.014 | 1587.7711 | 0.014 | 1945.0498 | 0.014 | 2200.2826 | 0.014 | 2933.7101 | 0.014 | [28 empty] | 1322.7209 | 0.014 | 1573.1163 | 0.014 | 2016.4488 | 0.014 | 2481.3015 | 0.014 | 3156.5244 | 0.016 | 3995.0209 | 0.016 | 5165.5655 | 0.016 | 6627.2438 | 0.016 | 8357.1779 | 0.016 | 10529.2424 | 0.014 | [8 empty] | 1301.6139 | 0.014 | 1603.32 | 0.014 | 1851.5248 | 0.014 | 2178.2645 | 0.014 | 2904.3527 | 0.014 | [20 empty] | 1921.0658 | 0.0553 | 2264.1133 | 0.0554 | 3018.8177 | 0.0554 | 3773.5221 | 0.0554 | 4905.5788 | 0.0554 | 6037.6354 | 0.0554
1251.6617 | 0.014 | 1619.5265 | 0.014 | 1983.9508 | 0.014 | 2244.2882 | 0.014 | 2992.3843 | 0.014 | [28 empty] | 1349.1753 | 0.014 | 1604.5786 | 0.014 | 2056.7778 | 0.014 | 2530.9276 | 0.014 | 3156.6988 | 0.014 | 4074.9213 | 0.016 | 5268.8768 | 0.014 | 6627.6098 | 0.016 | 8524.3214 | 0.014 | 10739.8272 | 0.014 | [8 empty] | 1327.6461 | 0.014 | 1635.3864 | 0.014 | 1888.5553 | 0.014 | 2221.8298 | 0.014 | 2962.4397 | 0.014 | [20 empty] | 1959.4871 | 0.0553 | 2309.3956 | 0.0553 | 3079.1941 | 0.0553 | 3848.9926 | 0.0553 | 5003.6904 | 0.0553 | 6158.3881 | 0.0553
1276.6949 | 0.014 | 1651.917 | 0.014 | 2023.6298 | 0.014 | 2289.174 | 0.014 | 3052.232 | 0.014 | [28 empty] | 1376.1588 | 0.014 | 1636.6702 | 0.014 | 2097.9133 | 0.014 | 2581.5461 | 0.014 | 3219.8328 | 0.014 | 4075.1464 | 0.014 | 5374.2543 | 0.014 | 6760.162 | 0.014 | 8694.8079 | 0.014 | 10954.6238 | 0.014 | [8 empty] | 1354.1991 | 0.014 | 1668.0942 | 0.014 | 1926.3264 | 0.014 | 2266.2664 | 0.014 | 3021.6885 | 0.014 | [20 empty] | 1998.6769 | 0.0553 | 2355.5835 | 0.0553 | 3140.7779 | 0.0553 | 3925.9724 | 0.0553 | 5103.7642 | 0.0553 | 6281.5559 | 0.0553
1302.2288 | 0.014 | 1684.9554 | 0.014 | 2064.1024 | 0.014 | 2334.9575 | 0.014 | 3113.2766 | 0.014 | [28 empty] | 1403.682 | 0.014 | 1669.4036 | 0.014 | 2139.8716 | 0.014 | 2633.177 | 0.014 | 3284.2294 | 0.014 | 4156.6493 | 0.014 | 5481.7394 | 0.014 | 6895.3652 | 0.014 | 8868.704 | 0.014 | 11173.7162 | 0.014 | [8 empty] | 1381.2831 | 0.014 | 1701.456 | 0.014 | 1964.853 | 0.014 | 2311.5917 | 0.014 | 3082.1223 | 0.014 | [20 empty] | 2038.6504 | 0.0553 | 2402.6951 | 0.0553 | 3203.5935 | 0.0553 | 4004.4919 | 0.0553 | 5205.8394 | 0.0553 | 6407.187 | 0.0553
1328.2734 | 0.014 | 1718.6545 | 0.014 | 2105.3844 | 0.014 | 2381.6566 | 0.014 | 3175.5421 | 0.014 | [28 empty] | 1431.7556 | 0.014 | 1702.7917 | 0.014 | 2182.669 | 0.014 | 2685.8406 | 0.014 | 3349.914 | 0.014 | 4239.7823 | 0.014 | 5591.3742 | 0.014 | 7033.2725 | 0.014 | 9046.0781 | 0.014 | 11397.1905 | 0.014 | [8 empty] | 1408.9087 | 0.014 | 1735.4852 | 0.014 | 2004.15 | 0.014 | 2357.8236 | 0.014 | 3143.7648 | 0.014 | [20 empty] | 2079.4234 | 0.0553 | 2450.749 | 0.0553 | 3267.6654 | 0.0553 | 4084.5817 | 0.0553 | 5309.9562 | 0.0553 | 6535.3308 | 0.0553
1354.8389 | 0.014 | 1753.0276 | 0.014 | 2147.4921 | 0.014 | 2429.2897 | 0.014 | 3239.053 | 0.014 | [28 empty] | 1460.3908 | 0.014 | 1736.8475 | 0.014 | 2226.3224 | 0.014 | 2739.5574 | 0.014 | 3416.9123 | 0.014 | 4324.578 | 0.014 | 5703.2017 | 0.014 | 7173.938 | 0.014 | 9226.9997 | 0.014 | 11625.1344 | 0.014 | [8 empty] | 1437.0869 | 0.014 | 1770.1949 | 0.014 | 2044.233 | 0.014 | 2404.98 | 0.014 | 3206.6401 | 0.014 | [20 empty] | 2121.0119 | 0.0553 | 2499.764 | 0.0553 | 3333.0187 | 0.0553 | 4166.2734 | 0.0553 | 5416.1554 | 0.0553 | 6666.0374 | 0.0553
1381.9356 | 0.014 | 1788.0881 | 0.014 | 2190.442 | 0.014 | 2477.8755 | 0.014 | 3303.834 | 0.014 | [28 empty] | 1489.5986 | 0.014 | 1771.5845 | 0.014 | 2270.8489 | 0.014 | 2794.3485 | 0.014 | 3485.2505 | 0.014 | 4411.0695 | 0.014 | 5817.2657 | 0.014 | 7317.4167 | 0.014 | 9411.5397 | 0.014 | 11857.637 | 0.014 | [8 empty] | 1465.8286 | 0.014 | 1805.5988 | 0.014 | 2085.1177 | 0.014 | 2453.0796 | 0.014 | 3270.7729 | 0.014 | [20 empty] | 2163.4321 | 0.0553 | 2549.7593 | 0.0553 | 3399.6791 | 0.0553 | 4249.5988 | 0.0553 | 5524.4785 | 0.0553 | 6799.3581 | 0.0553
1409.5743 | 0.014 | 1823.8499 | 0.014 | 2234.2508 | 0.014 | 2527.433 | 0.014 | 3369.9107 | 0.014 | [28 empty] | 1519.3905 | 0.014 | 1807.0161 | 0.014 | 2316.2658 | 0.014 | 2850.2355 | 0.014 | 3554.9555 | 0.014 | 4499.2909 | 0.014 | 5933.6111 | 0.014 | 7463.7651 | 0.014 | 9599.7704 | 0.014 | 12094.7898 | 0.014 | [8 empty] | 1495.1452 | 0.014 | 1841.7107 | 0.014 | 2126.82 | 0.014 | 2502.1412 | 0.014 | 3336.1883 | 0.014 | [20 empty] | 2206.7008 | 0.0553 | 2600.7545 | 0.0553 | 3467.6726 | 0.0553 | 4334.5908 | 0.0553 | 5634.968 | 0.0553 | 6935.3453 | 0.0553
1437.7658 | 0.014 | 1860.3269 | 0.014 | 2278.9358 | 0.014 | 2577.9817 | 0.014 | 3437.3089 | 0.014 | [28 empty] | 1549.7784 | 0.014 | 1843.1565 | 0.014 | 2362.5912 | 0.014 | 2907.2402 | 0.014 | 3626.0546 | 0.014 | 4589.2767 | 0.014 | 6052.2833 | 0.014 | 7613.0404 | 0.014 | 9791.7659 | 0.014 | [10 empty] | 1525.0481 | 0.014 | 1878.545 | 0.014 | 2169.3565 | 0.014 | 2552.1841 | 0.014 | 3402.9121 | 0.014 | [20 empty] | 2250.8348 | 0.0553 | 2652.7696 | 0.0553 | 3537.0261 | 0.0553 | 4421.2826 | 0.0553 | 5747.6674 | 0.0553 | 7074.0522 | 0.0553
1466.5211 | 0.014 | 1897.5334 | 0.014 | 2324.5145 | 0.014 | 2629.5413 | 0.014 | 3506.0551 | 0.014 | [28 empty] | 1580.7739 | 0.014 | 1880.0196 | 0.014 | 2409.843 | 0.014 | 2965.385 | 0.014 | 3698.5757 | 0.014 | 4681.0623 | 0.014 | 6173.3289 | 0.014 | 7765.3012 | 0.014 | 9987.6012 | 0.014 | [10 empty] | 1555.5491 | 0.014 | 1916.1158 | 0.014 | 2212.7436 | 0.014 | 2603.2277 | 0.014 | 3470.9703 | 0.014 | [20 empty] | 2295.8515 | 0.0552 | 2705.825 | 0.0553 | 3607.7666 | 0.0553 | 4509.7083 | 0.0553 | 5862.6207 | 0.0553 | 7215.5332 | 0.0553
1495.8516 | 0.014 | 1935.4841 | 0.014 | 2371.0048 | 0.014 | 2682.1322 | 0.014 | 3576.1762 | 0.014 | [28 empty] | 1612.3894 | 0.014 | 1917.62 | 0.014 | 2458.0398 | 0.014 | 3024.6927 | 0.014 | 3772.5472 | 0.014 | 4774.6835 | 0.014 | 6296.7955 | 0.014 | 7920.6072 | 0.014 | 10187.3532 | 0.014 | [10 empty] | 1586.66 | 0.014 | 1954.4382 | 0.014 | 2256.9985 | 0.014 | 2655.2923 | 0.014 | 3540.3897 | 0.014 | [20 empty] | 2341.7685 | 0.0552 | 2759.9415 | 0.0552 | 3679.9219 | 0.0552 | 4599.9024 | 0.0552 | 5979.8732 | 0.0552 | 7359.8439 | 0.0552
1525.7686 | 0.014 | 1974.1938 | 0.014 | 2418.4249 | 0.014 | 2735.7748 | 0.014 | 3647.6997 | 0.014 | [28 empty] | 1644.6372 | 0.014 | 1955.9724 | 0.014 | 2507.2006 | 0.014 | 3085.1866 | 0.014 | 3847.9982 | 0.014 | 4870.1772 | 0.014 | 6422.7314 | 0.014 | 8079.0193 | 0.014 | 10391.1003 | 0.014 | [10 empty] | 1618.3932 | 0.014 | 1993.5269 | 0.014 | 2302.1384 | 0.014 | 2708.3981 | 0.014 | 3611.1975 | 0.014 | [20 empty] | 2388.6039 | 0.0552 | 2815.1403 | 0.0552 | 3753.5204 | 0.0552 | 4691.9005 | 0.0552 | 6099.4706 | 0.0552 | 7507.0408 | 0.0552
1556.284 | 0.014 | 2013.6776 | 0.014 | 2466.7934 | 0.014 | 2790.4903 | 0.014 | 3720.6537 | 0.014 | [28 empty] | 1677.5299 | 0.014 | 1995.0918 | 0.014 | 2557.3446 | 0.014 | 3146.8903 | 0.014 | 3924.9582 | 0.014 | 4967.5807 | 0.014 | 6551.1861 | 0.014 | 8240.5997 | 0.014 | 10598.9223 | 0.014 | [10 empty] | 1650.7611 | 0.014 | 2033.3975 | 0.014 | 2348.1812 | 0.014 | 2762.5661 | 0.014 | 3683.4215 | 0.014 | [20 empty] | 2436.376 | 0.0552 | 2871.4431 | 0.0552 | 3828.5908 | 0.0552 | 4785.7385 | 0.0552 | 6221.46 | 0.0552 | 7657.1816 | 0.0552
1587.4097 | 0.014 | 2053.9512 | 0.014 | 2516.1293 | 0.014 | 2846.3001 | 0.014 | 3795.0668 | 0.014 | [28 empty] | 1711.0805 | 0.014 | 2034.9937 | 0.014 | 2608.4915 | 0.014 | 3209.8281 | 0.014 | 4003.4573 | 0.014 | 5066.9323 | 0.014 | 6682.2098 | 0.014 | 8405.4117 | 0.014 | 10810.9007 | 0.014 | [10 empty] | 1683.7763 | 0.014 | 2074.0654 | 0.014 | 2395.1448 | 0.014 | 2817.8174 | 0.014 | 3757.0899 | 0.014 | [20 empty] | 2485.1035 | 0.0552 | 2928.872 | 0.0552 | 3905.1626 | 0.0552 | 4881.4533 | 0.0552 | 6345.8892 | 0.0552 | 7810.3252 | 0.0552
1619.1578 | 0.014 | 2095.0302 | 0.014 | 2566.4519 | 0.014 | 2903.2261 | 0.014 | 3870.9681 | 0.014 | [28 empty] | 1745.3021 | 0.014 | 2075.6935 | 0.014 | 2660.6614 | 0.014 | 3274.0247 | 0.014 | 4083.5265 | 0.014 | 5168.271 | 0.014 | 6815.854 | 0.014 | 8573.5199 | 0.014 | 11027.1187 | 0.014 | [10 empty] | 1717.4519 | 0.014 | 2115.5467 | 0.014 | 2443.0477 | 0.014 | 2874.1738 | 0.014 | 3832.2317 | 0.014 | [20 empty] | 2534.8055 | 0.0552 | 2987.4494 | 0.0552 | 3983.2659 | 0.0552 | 4979.0823 | 0.0552 | 6472.807 | 0.0552 | 7966.5317 | 0.0552
1651.541 | 0.014 | 2136.9308 | 0.014 | 2617.7809 | 0.014 | 2961.2906 | 0.014 | 3948.3875 | 0.014 | [28 empty] | 1780.2082 | 0.014 | 2117.2074 | 0.014 | 2713.8746 | 0.014 | 3339.5052 | 0.014 | 4165.197 | 0.014 | 5271.6364 | 0.014 | 6952.1711 | 0.014 | 8744.9903 | 0.014 | 11247.6611 | 0.014 | [10 empty] | 1751.8009 | 0.014 | 2157.8577 | 0.014 | 2491.9087 | 0.014 | 2931.6573 | 0.014 | 3908.8763 | 0.014 | [20 empty] | 2585.5017 | 0.0552 | 3047.1984 | 0.0552 | 4062.9312 | 0.0552 | 5078.664 | 0.0552 | 6602.2632 | 0.0552 | 8125.8624 | 0.0552
1684.5718 | 0.014 | 2179.6694 | 0.014 | 2670.1365 | 0.014 | 3020.5164 | 0.014 | 4027.3553 | 0.014 | [28 empty] | 1815.8123 | 0.014 | 2159.5516 | 0.014 | 2768.1521 | 0.014 | 3406.2953 | 0.014 | 4248.5009 | 0.014 | 5377.0691 | 0.014 | 7091.2145 | 0.014 | 8919.8901 | 0.014 | 11472.6143 | 0.014 | [10 empty] | 1786.8369 | 0.014 | 2201.0148 | 0.014 | 2541.7468 | 0.014 | 2990.2904 | 0.014 | 3987.0539 | 0.014 | [20 empty] | 2637.2117 | 0.0552 | 3108.1424 | 0.0552 | 4144.1898 | 0.0552 | 5180.2373 | 0.0552 | 6734.3084 | 0.0552 | 8288.3796 | 0.0552
1718.2633 | 0.014 | 2223.2628 | 0.014 | 2723.5393 | 0.014 | 3080.9268 | 0.014 | 4107.9024 | 0.014 | [28 empty] | 1852.1286 | 0.014 | 2202.7426 | 0.014 | 2823.5151 | 0.014 | 3474.4212 | 0.014 | 4333.471 | 0.014 | 5484.6105 | 0.014 | 7233.0388 | 0.014 | 9098.288 | 0.014 | 11702.0666 | 0.014 | [10 empty] | 1822.5737 | 0.014 | 2245.0351 | 0.014 | 2592.5818 | 0.014 | 3050.0962 | 0.014 | 4066.7949 | 0.014 | [20 empty] | 2689.9559 | 0.0552 | 3170.3052 | 0.0552 | 4227.0736 | 0.0552 | 5283.842 | 0.0552 | 6868.9946 | 0.0552 | 8454.1472 | 0.0552
1752.6285 | 0.014 | 2267.7281 | 0.014 | 2778.0101 | 0.014 | 3142.5453 | 0.014 | 4190.0604 | 0.014 | [28 empty] | 1889.1712 | 0.014 | 2246.7974 | 0.014 | 2879.9854 | 0.014 | 3543.9096 | 0.014 | 4420.1404 | 0.014 | 5594.3027 | 0.014 | 7377.6995 | 0.014 | 9280.2537 | 0.014 | 11936.1079 | 0.014 | [10 empty] | 1859.0251 | 0.014 | 2289.9358 | 0.014 | 2644.4334 | 0.014 | 3111.0981 | 0.014 | 4148.1308 | 0.014 | [20 empty] | 2743.755 | 0.0552 | 3233.7113 | 0.0552 | 4311.6151 | 0.0552 | 5389.5188 | 0.0552 | 7006.3745 | 0.0552 | 8623.2301 | 0.0552
1787.6811 | 0.014 | 2313.0826 | 0.014 | 2833.5703 | 0.014 | 3205.3962 | 0.014 | 4273.8616 | 0.014 | [28 empty] | 1926.9546 | 0.014 | 2291.7334 | 0.014 | 2937.5851 | 0.014 | 3614.7878 | 0.014 | 4508.5432 | 0.014 | 5706.1888 | 0.014 | 7525.2535 | 0.014 | 9465.8588 | 0.014 | [12 empty] | 1896.2056 | 0.014 | 2335.7345 | 0.014 | 2697.3221 | 0.014 | 3173.3201 | 0.014 | 4231.0935 | 0.014 | [20 empty] | 2798.6301 | 0.0552 | 3298.3855 | 0.0552 | 4397.8474 | 0.0552 | 5497.3092 | 0.0552 | 7146.502 | 0.0552 | 8795.6947 | 0.0552
1823.4347 | 0.014 | 2359.3443 | 0.014 | 2890.2417 | 0.014 | 3269.5041 | 0.014 | 4359.3389 | 0.014 | [28 empty] | 1965.4937 | 0.014 | 2337.5681 | 0.014 | 2996.3368 | 0.014 | 3687.0835 | 0.014 | 4598.714 | 0.014 | 5820.3125 | 0.014 | 7675.7586 | 0.014 | 9655.176 | 0.014 | [12 empty] | 1934.1297 | 0.014 | 2382.4492 | 0.014 | 2751.2685 | 0.014 | 3236.7865 | 0.014 | 4315.7153 | 0.014 | [20 empty] | 2854.6027 | 0.0552 | 3364.3532 | 0.0552 | 4485.8043 | 0.0552 | 5607.2554 | 0.0552 | 7289.432 | 0.0552 | 8971.6086 | 0.0552
1859.9034 | 0.014 | 2406.5312 | 0.014 | 2948.0465 | 0.014 | 3334.8942 | 0.014 | 4446.5256 | 0.014 | [28 empty] | 2004.8036 | 0.014 | 2384.3194 | 0.014 | 3056.2636 | 0.014 | 3760.8252 | 0.014 | 4690.6883 | 0.014 | 5936.7188 | 0.014 | 7829.2738 | 0.014 | 9848.2795 | 0.014 | [12 empty] | 1972.8123 | 0.014 | 2430.0982 | 0.014 | 2806.2939 | 0.014 | 3301.5222 | 0.014 | 4402.0296 | 0.014 | [20 empty] | 2911.6948 | 0.0552 | 3431.6403 | 0.0552 | 4575.5204 | 0.0552 | 5719.4005 | 0.0552 | 7435.2207 | 0.0552 | 9151.0408 | 0.0552
1897.1015 | 0.014 | 2454.6618 | 0.014 | 3007.0074 | 0.014 | 3401.5921 | 0.014 | 4535.4561 | 0.014 | [28 empty] | 2044.8996 | 0.014 | 2432.0058 | 0.014 | 3117.3889 | 0.014 | 3836.0417 | 0.014 | 4784.5021 | 0.014 | 6055.4532 | 0.014 | 7985.8593 | 0.014 | 10045.2451 | 0.014 | [12 empty] | 2012.2686 | 0.014 | 2478.7002 | 0.014 | 2862.4198 | 0.014 | 3367.5527 | 0.014 | 4490.0702 | 0.014 | [20 empty] | 2969.9287 | 0.0551 | 3500.2731 | 0.0552 | 4667.0308 | 0.0552 | 5833.7885 | 0.0552 | 7583.9251 | 0.0552 | 9334.0616 | 0.0552
1935.0435 | 0.014 | 2503.755 | 0.014 | 3067.1476 | 0.014 | 3469.6239 | 0.014 | 4626.1653 | 0.014 | [28 empty] | 2085.7976 | 0.014 | 2480.6459 | 0.014 | 3179.7366 | 0.014 | 3912.7626 | 0.014 | 4880.1921 | 0.014 | 6176.5622 | 0.014 | 8145.5764 | 0.014 | 10246.15 | 0.014 | [12 empty] | 2052.514 | 0.014 | 2528.2742 | 0.014 | 2919.6682 | 0.014 | 3434.9037 | 0.014 | 4579.8716 | 0.014 | [20 empty] | 3029.3273 | 0.0551 | 3570.2786 | 0.0551 | 4760.3714 | 0.0551 | 5950.4643 | 0.0551 | 7735.6036 | 0.0551 | 9520.7429 | 0.0551
1973.7444 | 0.014 | 2553.8301 | 0.014 | 3128.4905 | 0.014 | 3539.0164 | 0.014 | 4718.6886 | 0.014 | [28 empty] | 2127.5136 | 0.014 | 2530.2588 | 0.014 | 3243.3314 | 0.014 | 3991.0178 | 0.014 | 4977.796 | 0.014 | 6300.0935 | 0.014 | 8308.488 | 0.014 | 10451.073 | 0.014 | [12 empty] | 2093.5642 | 0.014 | 2578.8397 | 0.014 | 2978.0615 | 0.014 | 3503.6018 | 0.014 | 4671.4691 | 0.014 | [20 empty] | 3089.9138 | 0.0551 | 3641.6841 | 0.0551 | 4855.5789 | 0.0551 | 6069.4736 | 0.0551 | 7890.3156 | 0.0551 | 9711.1577 | 0.0551
2013.2193 | 0.014 | 2604.9067 | 0.014 | 3191.0603 | 0.014 | 3609.7968 | 0.014 | 4813.0623 | 0.014 | [28 empty] | 2170.0638 | 0.014 | 2580.864 | 0.014 | 3308.198 | 0.014 | 4070.8382 | 0.014 | 5077.3519 | 0.014 | 6426.0953 | 0.014 | 8474.6577 | 0.014 | 10660.0944 | 0.014 | [12 empty] | 2135.4355 | 0.014 | 2630.4164 | 0.014 | 3037.6228 | 0.014 | 3573.6738 | 0.014 | 4764.8984 | 0.014 | [20 empty] | 3151.7121 | 0.0551 | 3714.5178 | 0.0551 | 4952.6904 | 0.0551 | 6190.863 | 0.0551 | 8048.122 | 0.0551 | 9905.3809 | 0.0551
2053.4836 | 0.014 | 2657.0049 | 0.014 | 3254.8815 | 0.014 | 3681.9927 | 0.014 | 4909.3236 | 0.014 | [28 empty] | 2213.4651 | 0.014 | 2632.4813 | 0.014 | 3374.362 | 0.014 | 4152.2549 | 0.014 | 5178.8989 | 0.014 | 6554.6173 | 0.014 | 8644.1509 | 0.014 | 10873.2963 | 0.014 | [12 empty] | 2178.1442 | 0.014 | 2683.0248 | 0.014 | 3098.3752 | 0.014 | 3645.1473 | 0.014 | 4860.1964 | 0.014 | [20 empty] | 3214.7463 | 0.0551 | 3788.8082 | 0.0551 | 5051.7442 | 0.0551 | 6314.6803 | 0.0551 | 8209.0844 | 0.0551 | 10103.4885 | 0.0551
2094.5533 | 0.014 | 2710.145 | 0.014 | 3319.9792 | 0.014 | 3755.6325 | 0.014 | 5007.5101 | 0.014 | [28 empty] | 2257.7344 | 0.014 | 2685.1309 | 0.014 | 3441.8492 | 0.014 | 4235.3 | 0.014 | 5282.4769 | 0.014 | 6685.7096 | 0.014 | 8817.0339 | 0.014 | 11090.7622 | 0.014 | [12 empty] | 2221.7071 | 0.014 | 2736.6853 | 0.014 | 3160.3427 | 0.014 | 3718.0503 | 0.014 | 4957.4003 | 0.014 | [20 empty] | 3279.0413 | 0.0551 | 3864.5843 | 0.0551 | 5152.7791 | 0.0551 | 6440.9739 | 0.0551 | 8373.2661 | 0.0551 | 10305.5583 | 0.0551
2136.4444 | 0.014 | 2764.3479 | 0.014 | 3386.3788 | 0.014 | 3830.7452 | 0.014 | 5107.6603 | 0.014 | [28 empty] | 2302.8891 | 0.014 | 2738.8335 | 0.014 | 3510.6862 | 0.014 | 4320.006 | 0.014 | 5388.1264 | 0.014 | 6819.4238 | 0.014 | 8993.3746 | 0.014 | 11312.5775 | 0.014 | [12 empty] | 2266.1413 | 0.014 | 2791.419 | 0.014 | 3223.5496 | 0.014 | 3792.4113 | 0.014 | 5056.5483 | 0.014 | [20 empty] | 3344.6221 | 0.0551 | 3941.876 | 0.0551 | 5255.8347 | 0.0551 | 6569.7934 | 0.0551 | 8540.7314 | 0.0551 | 10511.6694 | 0.0551
2179.1733 | 0.014 | 2819.6348 | 0.014 | 3454.1063 | 0.014 | 3907.3601 | 0.014 | 5209.8135 | 0.014 | [28 empty] | 2348.9469 | 0.014 | 2793.6102 | 0.014 | 3580.8999 | 0.014 | 4406.4061 | 0.014 | 5495.889 | 0.014 | 6955.8123 | 0.014 | 9173.2421 | 0.014 | 11538.829 | 0.014 | [12 empty] | 2311.4641 | 0.014 | 2847.2474 | 0.014 | 3288.0206 | 0.014 | 3868.2595 | 0.014 | 5157.6793 | 0.014 | [20 empty] | 3411.5145 | 0.0551 | 4020.7136 | 0.0551 | 5360.9514 | 0.0551 | 6701.1893 | 0.0551 | 8711.546 | 0.0551 | 10721.9028 | 0.0551
2222.7567 | 0.014 | 2876.0275 | 0.014 | 3523.1885 | 0.014 | 3985.5073 | 0.014 | 5314.0097 | 0.014 | [28 empty] | 2395.9258 | 0.014 | 2849.4824 | 0.014 | 3652.5179 | 0.014 | 4494.5343 | 0.014 | 5605.8068 | 0.014 | 7094.9285 | 0.014 | 9356.7069 | 0.014 | 11769.6056 | 0.014 | [12 empty] | 2357.6934 | 0.014 | 2904.1923 | 0.014 | 3353.781 | 0.014 | 3945.6247 | 0.014 | 5260.8329 | 0.014 | [20 empty] | 3479.7448 | 0.0551 | 4101.1278 | 0.0551 | 5468.1704 | 0.0551 | 6835.213 | 0.0551 | 8885.777 | 0.0551 | 10936.3409 | 0.0551
2267.2119 | 0.014 | 2933.5481 | 0.014 | 3593.6522 | 0.014 | 4065.2174 | 0.014 | 5420.2899 | 0.014 | [28 empty] | 2443.8443 | 0.014 | 2906.4721 | 0.014 | 3725.5683 | 0.014 | 4584.425 | 0.014 | 5717.9229 | 0.014 | 7236.8271 | 0.014 | 9543.841 | 0.014 | 12004.9977 | 0.014 | [12 empty] | 2404.8472 | 0.014 | 2962.2762 | 0.014 | 3420.8566 | 0.014 | 4024.5372 | 0.014 | 5366.0496 | 0.014 | [20 empty] | 3549.3397 | 0.0551 | 4183.1504 | 0.0551 | 5577.5338 | 0.0551 | 6971.9173 | 0.0551 | 9063.4925 | 0.0551 | 11155.0677 | 0.0551
2312.5561 | 0.014 | 2992.219 | 0.014 | 3665.5253 | 0.014 | 4146.5218 | 0.014 | 5528.6957 | 0.014 | [28 empty] | 2492.7212 | 0.014 | 2964.6015 | 0.014 | 3800.0796 | 0.014 | 4676.1135 | 0.014 | 5832.2814 | 0.014 | 7381.5636 | 0.014 | 9734.7179 | 0.014 | [14 empty] | 2452.9442 | 0.014 | 3021.5217 | 0.014 | 3489.2737 | 0.014 | 4105.0279 | 0.014 | 5473.3705 | 0.014 | [20 empty] | 3620.3265 | 0.0551 | 4266.8134 | 0.0551 | 5689.0845 | 0.0551 | 7111.3556 | 0.0551 | 9244.7623 | 0.0551 | 11378.169 | 0.0551
2358.8072 | 0.014 | 3052.0634 | 0.014 | 3738.8358 | 0.014 | 4229.4522 | 0.014 | 5639.2696 | 0.014 | [28 empty] | 2542.5757 | 0.014 | 3023.8935 | 0.014 | 3876.0812 | 0.014 | 4769.6357 | 0.014 | 5948.927 | 0.014 | 7529.1949 | 0.014 | 9929.4122 | 0.014 | [14 empty] | 2502.0031 | 0.014 | 3081.9521 | 0.014 | 3559.0592 | 0.014 | 4187.1285 | 0.014 | 5582.838 | 0.014 | [20 empty] | 3692.733 | 0.0551 | 4352.1497 | 0.0551 | 5802.8662 | 0.0551 | 7253.5828 | 0.0551 | 9429.6576 | 0.0551 | 11605.7324 | 0.0551
2405.9834 | 0.014 | 3113.1047 | 0.014 | 3813.6125 | 0.014 | 4314.0413 | 0.014 | 5752.055 | 0.014 | [28 empty] | 2593.4272 | 0.014 | 3084.3714 | 0.014 | 3953.6028 | 0.014 | 4865.0284 | 0.014 | 6067.9055 | 0.014 | 7679.7788 | 0.014 | 10128.0005 | 0.014 | [14 empty] | 2552.0431 | 0.014 | 3143.5912 | 0.014 | 3630.2404 | 0.014 | 4270.871 | 0.014 | 5694.4947 | 0.014 | [20 empty] | 3766.5877 | 0.0551 | 4439.1927 | 0.0551 | 5918.9235 | 0.0551 | 7398.6544 | 0.0551 | 9618.2507 | 0.0551 | 11837.8471 | 0.0551
2454.103 | 0.014 | 3175.3668 | 0.014 | 3889.8847 | 0.014 | 4400.3221 | 0.014 | 5867.0961 | 0.014 | [28 empty] | 2645.2957 | 0.014 | 3146.0588 | 0.014 | 4032.6749 | 0.014 | 4962.329 | 0.014 | 6189.2636 | 0.014 | 7833.3744 | 0.014 | 10330.5605 | 0.014 | [14 empty] | 2603.084 | 0.014 | 3206.463 | 0.014 | 3702.8452 | 0.014 | 4356.2885 | 0.014 | 5808.3846 | 0.014 | [20 empty] | 3841.9195 | 0.0551 | 4527.9765 | 0.0551 | 6037.302 | 0.0551 | 7546.6275 | 0.0551 | 9810.6158 | 0.0551 | 12074.604 | 0.0551
2503.1851 | 0.014 | 3238.8741 | 0.014 | 3967.6824 | 0.014 | 4488.3285 | 0.014 | 5984.4381 | 0.014 | [28 empty] | 2698.2016 | 0.014 | 3208.98 | 0.014 | 4113.3284 | 0.014 | 5061.5756 | 0.014 | 6313.0489 | 0.014 | 7990.0419 | 0.014 | 10537.1717 | 0.014 | [14 empty] | 2655.1457 | 0.014 | 3270.5922 | 0.014 | 3776.9021 | 0.014 | 4443.4142 | 0.014 | 5924.5523 | 0.014 | [20 empty] | 3918.7578 | 0.0551 | 4618.536 | 0.0551 | 6158.048 | 0.0551 | 7697.5601 | 0.0551 | 10006.8281 | 0.0551
2553.2488 | 0.014 | 3303.6516 | 0.014 | 4047.0361 | 0.014 | 4578.0951 | 0.014 | 6104.1268 | 0.014 | [28 empty] | 2752.1657 | 0.014 | 3273.1596 | 0.014 | 4195.595 | 0.014 | 5162.8071 | 0.014 | 6439.3099 | 0.014 | 8149.8427 | 0.014 | 10747.9151 | 0.014 | [14 empty] | 2708.2486 | 0.014 | 3336.0041 | 0.014 | 3852.4401 | 0.014 | 4532.2825 | 0.014 | 6043.0433 | 0.014 | [20 empty] | 3997.133 | 0.0551 | 4710.9068 | 0.0551 | 6281.209 | 0.0551 | 7851.5113 | 0.0551 | 10206.9646 | 0.0551
2604.3138 | 0.014 | 3369.7246 | 0.014 | 4127.9768 | 0.014 | 4669.657 | 0.014 | 6226.2094 | 0.014 | [28 empty] | 2807.209 | 0.014 | 3338.6228 | 0.014 | 4279.5069 | 0.014 | 5266.0632 | 0.014 | 6568.0961 | 0.014 | 8312.8395 | 0.014 | 10962.8734 | 0.014 | [14 empty] | 2762.4135 | 0.014 | 3402.7242 | 0.014 | 3929.4889 | 0.014 | 4622.9282 | 0.014 | 6163.9042 | 0.014 | [20 empty] | 4077.0757 | 0.0551 | 4805.1249 | 0.0551 | 6406.8332 | 0.0551 | 8008.5415 | 0.0551 | 10411.1039 | 0.0551
2656.4001 | 0.014 | 3437.1191 | 0.014 | 4210.5363 | 0.014 | 4763.0502 | 0.014 | 6350.7335 | 0.014 | [28 empty] | 2863.3532 | 0.014 | 3405.3953 | 0.014 | 4365.097 | 0.014 | 5371.3845 | 0.014 | 6699.458 | 0.014 | 8479.0963 | 0.014 | 11182.1309 | 0.014 | [14 empty] | 2817.6618 | 0.014 | 3470.7786 | 0.014 | 4008.0787 | 0.014 | 4715.3867 | 0.014 | 6287.1823 | 0.014 | [20 empty] | 4158.6172 | 0.0551 | 4901.2274 | 0.0551 | 6534.9699 | 0.0551 | 8168.7123 | 0.0551 | 10619.326 | 0.0551
2709.5281 | 0.014 | 3505.8615 | 0.014 | 4294.7471 | 0.014 | 4858.3112 | 0.014 | 6477.7482 | 0.014 | [28 empty] | 2920.6202 | 0.014 | 3473.5032 | 0.014 | 4452.3989 | 0.014 | 5478.8122 | 0.014 | 6833.4472 | 0.014 | 8648.6783 | 0.014 | 11405.7735 | 0.014 | [14 empty] | 2874.0151 | 0.014 | 3540.1942 | 0.014 | 4088.2403 | 0.014 | 4809.6945 | 0.014 | 6412.9259 | 0.014 | [20 empty] | 4241.7895 | 0.0551 | 4999.2519 | 0.0551 | 6665.6692 | 0.0551 | 8332.0866 | 0.0551 | 10831.7125 | 0.0551
2763.7186 | 0.014 | 3575.9787 | 0.014 | 4380.642 | 0.014 | 4955.4774 | 0.014 | 6607.3032 | 0.014 | [28 empty] | 2979.0326 | 0.014 | 3542.9732 | 0.014 | 4541.4469 | 0.014 | 5588.3884 | 0.014 | 6970.1161 | 0.014 | 8821.6518 | 0.014 | 11633.889 | 0.014 | [14 empty] | 2931.4954 | 0.014 | 3610.9981 | 0.014 | 4170.0051 | 0.014 | 4905.8883 | 0.014 | 6541.1845 | 0.014 | [20 empty] | 4326.6253 | 0.0551 | 5099.237 | 0.0551 | 6798.9826 | 0.0551 | 8498.7283 | 0.0551 | 11048.3468 | 0.0551
2818.993 | 0.014 | 3647.4983 | 0.014 | 4468.2548 | 0.014 | 5054.5869 | 0.014 | 6739.4492 | 0.014 | [28 empty] | 3038.6133 | 0.014 | 3613.8327 | 0.014 | 4632.2758 | 0.014 | 5700.1562 | 0.014 | 7109.5184 | 0.014 | 8998.0849 | 0.014 | 11866.5668 | 0.014 | [14 empty] | 2990.1253 | 0.014 | 3683.2181 | 0.014 | 4253.4052 | 0.014 | 5004.0061 | 0.014 | 6672.0082 | 0.014 | [20 empty] | 4413.1578 | 0.0551 | 5201.2217 | 0.0551 | 6934.9623 | 0.0551 | 8668.7029 | 0.0551 | 11269.3137 | 0.0551
2875.3729 | 0.014 | 3720.4483 | 0.014 | 4557.6199 | 0.014 | 5155.6787 | 0.014 | 6874.2382 | 0.014 | [28 empty] | 3099.3855 | 0.014 | 3686.1094 | 0.014 | 4724.9214 | 0.014 | 5814.1593 | 0.014 | 7251.7088 | 0.014 | 9178.0466 | 0.014 | 12103.8981 | 0.014 | [14 empty] | 3049.9278 | 0.014 | 3756.8824 | 0.014 | 4338.4733 | 0.014 | 5104.0862 | 0.014 | 6805.4483 | 0.014 | [20 empty] | 4501.421 | 0.0551 | 5305.2461 | 0.0551 | 7073.6615 | 0.0551 | 8842.0769 | 0.0551 | 11494.7 | 0.0551
2932.8803 | 0.014 | 3794.8572 | 0.014 | 4648.7723 | 0.014 | 5258.7922 | 0.014 | 7011.723 | 0.014 | [28 empty] | 3161.3733 | 0.014 | 3759.8315 | 0.014 | 4819.4198 | 0.014 | 5930.4425 | 0.014 | 7396.743 | 0.014 | 9361.6075 | 0.014 | [16 empty] | 3110.9263 | 0.014 | 3832.0201 | 0.014 | 4425.2428 | 0.014 | 5206.168 | 0.014 | 6941.5573 | 0.014 | [20 empty] | 4591.4494 | 0.0551 | 5411.3511 | 0.0551 | 7215.1348 | 0.0551 | 9018.9185 | 0.0551 | 11724.594 | 0.0551
2991.5379 | 0.014 | 3870.7544 | 0.014 | 4741.7478 | 0.014 | 5363.9681 | 0.014 | 7151.9575 | 0.014 | [28 empty] | 3224.6007 | 0.014 | 3835.0282 | 0.014 | 4915.8082 | 0.014 | 6049.0514 | 0.014 | 7544.6778 | 0.014 | 9548.8396 | 0.014 | [16 empty] | 3173.1448 | 0.014 | 3908.6605 | 0.014 | 4513.7476 | 0.014 | 5310.2913 | 0.014 | 7080.3884 | 0.014 | [20 empty] | 4683.2784 | 0.0551 | 5519.5781 | 0.0551 | 7359.4375 | 0.0551 | 9199.2968 | 0.0551 | 11959.0859 | 0.0551
3051.3687 | 0.014 | 3948.1695 | 0.014 | 4836.5827 | 0.014 | 5471.2475 | 0.014 | 7294.9966 | 0.014 | [28 empty] | 3289.0927 | 0.014 | 3911.7287 | 0.014 | 5014.1244 | 0.014 | 6170.0324 | 0.014 | 7695.5714 | 0.014 | 9739.8164 | 0.014 | [16 empty] | 3236.6077 | 0.014 | 3986.8337 | 0.014 | 4604.0226 | 0.014 | 5416.4971 | 0.014 | 7221.9962 | 0.014 | [20 empty] | 4776.9439 | 0.0551 | 5629.9697 | 0.0551 | 7506.6262 | 0.0551 | 9383.2828 | 0.0551
3112.3961 | 0.014 | 4027.1329 | 0.014 | 4933.3144 | 0.014 | 5580.6724 | 0.014 | 7440.8965 | 0.014 | [28 empty] | 3354.8746 | 0.014 | 3989.9633 | 0.014 | 5114.4068 | 0.014 | 6293.433 | 0.014 | 7849.4828 | 0.014 | 9934.6128 | 0.014 | [16 empty] | 3301.3399 | 0.014 | 4066.5704 | 0.014 | 4696.103 | 0.014 | 5524.8271 | 0.014 | 7366.4361 | 0.014 | [20 empty] | 4872.4828 | 0.0551 | 5742.569 | 0.0551 | 7656.7587 | 0.0551 | 9570.9484 | 0.0551
3174.644 | 0.014 | 4107.6755 | 0.014 | 5031.9807 | 0.014 | 5692.2858 | 0.014 | 7589.7145 | 0.014 | [28 empty] | 3421.9721 | 0.014 | 4069.7626 | 0.014 | 5216.695 | 0.014 | 6419.3017 | 0.014 | 8006.4725 | 0.014 | 10133.305 | 0.014 | [16 empty] | 3367.3667 | 0.014 | 4147.9018 | 0.014 | 4790.0251 | 0.014 | 5635.3236 | 0.014 | 7513.7648 | 0.014 | [20 empty] | 4969.9325 | 0.0551 | 5857.4204 | 0.0551 | 7809.8939 | 0.0551 | 9762.3674 | 0.0551
3238.1369 | 0.014 | 4189.829 | 0.014 | 5132.6203 | 0.014 | 5806.1316 | 0.014 | 7741.5088 | 0.014 | [28 empty] | 3490.4115 | 0.014 | 4151.1578 | 0.014 | 5321.0289 | 0.014 | 6547.6877 | 0.014 | 8166.6019 | 0.014 | 10335.9711 | 0.014 | [16 empty] | 3434.714 | 0.014 | 4230.8598 | 0.014 | 4885.8256 | 0.014 | 5748.0301 | 0.014 | 7664.0401 | 0.014 | [20 empty] | 5069.3311 | 0.055 | 5974.5688 | 0.0551 | 7966.0918 | 0.0551 | 9957.6147 | 0.0551
3302.8996 | 0.014 | 4273.6256 | 0.014 | 5235.2727 | 0.014 | 5922.2542 | 0.014 | 7896.3389 | 0.014 | [28 empty] | 3560.2197 | 0.014 | 4234.181 | 0.014 | 5427.4495 | 0.014 | 6678.6415 | 0.014 | 8329.934 | 0.014 | 10542.6905 | 0.014 | [16 empty] | 3503.4083 | 0.014 | 4315.477 | 0.014 | 4983.5421 | 0.014 | 5862.9907 | 0.014 | 7817.3209 | 0.014 | [20 empty] | 5170.7178 | 0.055 | 6094.0602 | 0.055 | 8125.4136 | 0.055 | 10156.767 | 0.055
3368.9576 | 0.014 | 4359.0981 | 0.014 | 5339.9782 | 0.014 | 6040.6993 | 0.014 | 8054.2657 | 0.014 | [28 empty] | 3631.4241 | 0.014 | 4318.8646 | 0.014 | 5535.9984 | 0.014 | 6812.2143 | 0.014 | 8496.5326 | 0.014 | 10753.5444 | 0.014 | [16 empty] | 3573.4765 | 0.014 | 4401.7865 | 0.014 | 5083.2129 | 0.014 | 5980.2505 | 0.014 | 7973.6674 | 0.014 | [20 empty] | 5274.1321 | 0.055 | 6215.9414 | 0.055 | 8287.9219 | 0.055 | 10359.9024 | 0.055
3436.3367 | 0.014 | 4446.2801 | 0.014 | 5446.7777 | 0.014 | 6161.5133 | 0.014 | 8215.351 | 0.014 | [28 empty] | 3704.0526 | 0.014 | 4405.2419 | 0.014 | 5646.7184 | 0.014 | 6948.4586 | 0.014 | 8666.4633 | 0.014 | 10968.6152 | 0.014 | [16 empty] | 3644.946 | 0.014 | 4489.8223 | 0.014 | 5184.8772 | 0.014 | 6099.8555 | 0.014 | 8133.1407 | 0.014 | [20 empty] | 5379.6148 | 0.055 | 6340.2602 | 0.055 | 8453.6803 | 0.055 | 10567.1004 | 0.055
3505.0635 | 0.014 | 4535.2057 | 0.014 | 5555.7133 | 0.014 | 6284.7435 | 0.014 | 8379.658 | 0.014 | [28 empty] | 3778.1337 | 0.014 | 4493.3467 | 0.014 | 5759.6528 | 0.014 | 7087.4278 | 0.014 | 8839.7926 | 0.014 | 11187.9875 | 0.014 | [16 empty] | 3717.8449 | 0.014 | 4579.6187 | 0.014 | 5288.5747 | 0.014 | 6221.8526 | 0.014 | 8295.8035 | 0.014 | [20 empty] | 5487.207 | 0.055 | 6467.0655 | 0.055 | 8622.7539 | 0.055 | 10778.4424 | 0.055
3575.1647 | 0.014 | 4625.9098 | 0.014 | 5666.8275 | 0.014 | 6410.4384 | 0.014 | 8547.2512 | 0.014 | [28 empty] | 3853.6964 | 0.014 | 4583.2137 | 0.014 | 5874.8458 | 0.014 | 7229.1763 | 0.014 | 9016.5884 | 0.014 | 11411.7473 | 0.014 | [16 empty] | 3792.2018 | 0.014 | 4671.2111 | 0.014 | 5394.3462 | 0.014 | 6346.2897 | 0.014 | 8461.7196 | 0.014 | [20 empty] | 5596.9512 | 0.055 | 6596.4068 | 0.055 | 8795.209 | 0.055 | 10994.0113 | 0.055
3646.668 | 0.014 | 4718.428 | 0.014 | 5780.1641 | 0.014 | 6538.6472 | 0.014 | 8718.1962 | 0.014 | [28 empty] | 3930.7703 | 0.014 | 4674.8779 | 0.014 | 5992.3428 | 0.014 | 7373.7599 | 0.014 | 9196.9202 | 0.014 | 11639.9822 | 0.014 | [16 empty] | 3868.0459 | 0.014 | 4764.6353 | 0.014 | 5502.2332 | 0.014 | 6473.2155 | 0.014 | 8630.954 | 0.014 | [20 empty] | 5708.8902 | 0.055 | 6728.3349 | 0.055 | 8971.1132 | 0.055 | 11213.8915 | 0.055
3719.6014 | 0.014 | 4812.7965 | 0.014 | 5895.7674 | 0.014 | 6669.4201 | 0.014 | 8892.5602 | 0.014 | [28 empty] | 4009.3857 | 0.014 | 4768.3755 | 0.014 | 6112.1896 | 0.014 | 7521.2351 | 0.014 | 9380.8586 | 0.014 | 11872.7819 | 0.014 | [16 empty] | 3945.4068 | 0.014 | 4859.928 | 0.014 | 5612.2778 | 0.014 | 6602.6798 | 0.014 | 8803.5731 | 0.014 | [20 empty] | 5823.068 | 0.055 | 6862.9016 | 0.055 | 9150.5355 | 0.055 | 11438.1693 | 0.055
3793.9934 | 0.014 | 4909.0525 | 0.014 | 6013.6827 | 0.014 | 6802.8085 | 0.014 | 9070.4114 | 0.014 | [28 empty] | 4089.5734 | 0.014 | 4863.743 | 0.014 | 6234.4334 | 0.014 | 7671.6598 | 0.014 | 9568.4757 | 0.014 | 12110.2375 | 0.014 | [16 empty] | 4024.3149 | 0.014 | 4957.1266 | 0.014 | 5724.5234 | 0.014 | 6734.7334 | 0.014 | 8979.6445 | 0.014 | [20 empty] | 5939.5294 | 0.055 | 7000.1596 | 0.055 | 9333.5462 | 0.055 | 11666.9327 | 0.055
3869.8733 | 0.014 | 5007.2335 | 0.014 | 6133.9564 | 0.014 | 6938.8647 | 0.014 | 9251.8196 | 0.014 | [28 empty] | 4171.3649 | 0.014 | 4961.0179 | 0.014 | 6359.1221 | 0.014 | 7825.093 | 0.014 | 9759.8453 | 0.014 | [18 empty] | 4104.8012 | 0.014 | 5056.2691 | 0.014 | 5839.0139 | 0.014 | 6869.4281 | 0.014 | 9159.2374 | 0.014 | [20 empty] | 6058.32 | 0.055 | 7140.1628 | 0.055 | 9520.2171 | 0.055 | 11900.2714 | 0.055
3947.2708 | 0.014 | 5107.3782 | 0.014 | 6256.6355 | 0.014 | 7077.642 | 0.014 | 9436.856 | 0.014 | [28 empty] | 4254.7922 | 0.014 | 5060.2382 | 0.014 | 6486.3045 | 0.014 | 7981.5948 | 0.014 | 9955.0422 | 0.014 | [18 empty] | 4186.8972 | 0.014 | 5157.3945 | 0.014 | 5955.7941 | 0.014 | 7006.8166 | 0.014 | 9342.4222 | 0.014 | [20 empty] | 6179.4864 | 0.055 | 7282.9661 | 0.055 | 9710.6214 | 0.055
4026.2162 | 0.014 | 5209.5258 | 0.014 | 6381.7682 | 0.014 | 7219.1948 | 0.014 | 9625.5931 | 0.014 | [28 empty] | 4339.888 | 0.014 | 5161.443 | 0.014 | 6616.0306 | 0.014 | 8141.2267 | 0.014 | 10154.143 | 0.014 | [18 empty] | 4270.6352 | 0.014 | 5260.5424 | 0.014 | 6074.91 | 0.014 | 7146.953 | 0.014 | 9529.2706 | 0.014 | [20 empty] | 6303.0761 | 0.055 | 7428.6254 | 0.055 | 9904.8339 | 0.055
4106.7405 | 0.014 | 5313.7163 | 0.014 | 6509.4036 | 0.014 | 7363.5787 | 0.014 | 9818.105 | 0.014 | [28 empty] | 4426.6858 | 0.014 | 5264.6719 | 0.014 | 6748.3512 | 0.014 | 8304.0513 | 0.014 | 10357.2259 | 0.014 | [18 empty] | 4356.0479 | 0.014 | 5365.7532 | 0.014 | 6196.4082 | 0.014 | 7289.892 | 0.014 | 9719.856 | 0.014 | [20 empty] | 6429.1376 | 0.055 | 7577.1979 | 0.055 | 10102.9305 | 0.055
4188.8753 | 0.014 | 5419.9906 | 0.014 | 6639.5917 | 0.014 | 7510.8503 | 0.014 | 10014.4671 | 0.014 | [28 empty] | 4515.2195 | 0.014 | 5369.9653 | 0.014 | 6883.3182 | 0.014 | 8470.1323 | 0.014 | 10564.3704 | 0.014 | [18 empty] | 4443.1688 | 0.014 | 5473.0683 | 0.014 | 6320.3364 | 0.014 | 7435.6899 | 0.014 | 9914.2531 | 0.014 | [20 empty] | 6557.7204 | 0.055 | 7728.7419 | 0.055 | 10304.9891 | 0.055
4272.6528 | 0.014 | 5528.3904 | 0.014 | 6772.3835 | 0.014 | 7661.0673 | 0.014 | 10214.7564 | 0.014 | [28 empty] | 4605.5239 | 0.014 | 5477.3646 | 0.014 | 7020.9846 | 0.014 | 8639.5349 | 0.014 | 10775.6578 | 0.014 | [18 empty] | 4532.0322 | 0.014 | 5582.5297 | 0.014 | 6446.7431 | 0.014 | 7584.4037 | 0.014 | 10112.5382 | 0.014 | [20 empty] | 6688.8748 | 0.055 | 7883.3167 | 0.055 | 10511.0889 | 0.055
4358.1059 | 0.014 | 5638.9582 | 0.014 | 6907.8312 | 0.014 | 7814.2886 | 0.014 | 10419.0515 | 0.014 | [28 empty] | 4697.6344 | 0.014 | 5586.9119 | 0.014 | 7161.4043 | 0.014 | 8812.3256 | 0.014 | 10991.171 | 0.014 | [18 empty] | 4622.6729 | 0.014 | 5694.1802 | 0.014 | 6575.678 | 0.014 | 7736.0917 | 0.014 | 10314.789 | 0.014 | [20 empty] | 6822.6523 | 0.055 | 8040.983 | 0.055 | 10721.3107 | 0.055
4445.268 | 0.014 | 5751.7374 | 0.014 | 7045.9878 | 0.014 | 7970.5744 | 0.014 | 10627.4326 | 0.014 | [28 empty] | 4791.587 | 0.014 | 5698.6501 | 0.014 | 7304.6324 | 0.014 | 8988.5721 | 0.014 | 11210.9944 | 0.014 | [18 empty] | 4715.1263 | 0.014 | 5808.0638 | 0.014 | 6707.1915 | 0.014 | 7890.8136 | 0.014 | 10521.0848 | 0.014 | [20 empty] | 6959.1053 | 0.055 | 8201.8027 | 0.055 | 10935.7369 | 0.055
4534.1733 | 0.014 | 5866.7721 | 0.014 | 7186.9075 | 0.014 | 8129.9859 | 0.014 | 10839.9812 | 0.014 | [28 empty] | 4887.4188 | 0.014 | 5812.6231 | 0.014 | 7450.725 | 0.014 | 9168.3436 | 0.014 | 11435.2143 | 0.014 | [18 empty] | 4809.4289 | 0.014 | 5924.2251 | 0.014 | 6841.3354 | 0.014 | 8048.6298 | 0.014 | 10731.5064 | 0.014 | [20 empty] | 7098.2874 | 0.055 | 8365.8387 | 0.055 | 11154.4517 | 0.055
4624.8568 | 0.014 | 5984.1076 | 0.014 | 7330.6457 | 0.014 | 8292.5856 | 0.014 | 11056.7808 | 0.014 | [28 empty] | 4985.1672 | 0.014 | 5928.8756 | 0.014 | 7599.7395 | 0.014 | 9351.7105 | 0.014 | 11663.9185 | 0.014 | [18 empty] | 4905.6174 | 0.014 | 6042.7096 | 0.014 | 6978.1621 | 0.014 | 8209.6024 | 0.014 | 10946.1366 | 0.014 | [20 empty] | 7240.2532 | 0.055 | 8533.1555 | 0.055 | 11377.5407 | 0.055
4717.3539 | 0.014 | 6103.7897 | 0.014 | 7477.2586 | 0.014 | 8458.4373 | 0.014 | 11277.9164 | 0.014 | [28 empty] | 5084.8705 | 0.014 | 6047.4531 | 0.014 | 7751.7343 | 0.014 | 9538.7447 | 0.014 | 11897.1969 | 0.014 | [18 empty] | 5003.7298 | 0.014 | 6163.5638 | 0.014 | 7117.7253 | 0.014 | 8373.7945 | 0.014 | 11165.0593 | 0.014 | [20 empty] | 7385.0582 | 0.055 | 8703.8186 | 0.055 | 11605.0915 | 0.055
4811.701 | 0.014 | 6225.8655 | 0.014 | 7626.8038 | 0.014 | 8627.6061 | 0.014 | 11503.4748 | 0.014 | [28 empty] | 5186.5679 | 0.014 | 6168.4022 | 0.014 | 7906.769 | 0.014 | 9729.5196 | 0.014 | [20 empty] | 5103.8044 | 0.014 | 6286.8351 | 0.014 | 7260.0798 | 0.014 | 8541.2704 | 0.014 | 11388.3605 | 0.014 | [20 empty] | 7532.7594 | 0.055 | 8877.895 | 0.055 | 11837.1933 | 0.055
4907.935 | 0.014 | 6350.3828 | 0.014 | 7779.3399 | 0.014 | 8800.1582 | 0.014 | 11733.5443 | 0.014 | [28 empty] | 5290.2993 | 0.014 | 6291.7702 | 0.014 | 8064.9044 | 0.014 | 9924.1099 | 0.014 | [20 empty] | 5205.8805 | 0.014 | 6412.5718 | 0.014 | 7405.2814 | 0.014 | 8712.0958 | 0.014 | 11616.1277 | 0.014 | [20 empty] | 7683.4146 | 0.055 | 9055.4529 | 0.055 | 12073.9372 | 0.055
5006.0937 | 0.014 | 6477.3905 | 0.014 | 7934.9266 | 0.014 | 8976.1614 | 0.014 | 11968.2152 | 0.014 | [28 empty] | 5396.1052 | 0.014 | 6417.6056 | 0.014 | 8226.2025 | 0.014 | 10122.5921 | 0.014 | [20 empty] | 5309.9981 | 0.014 | 6540.8232 | 0.014 | 7553.387 | 0.014 | 8886.3377 | 0.014 | 11848.4503 | 0.014 | [20 empty] | 7837.0829 | 0.055 | 9236.562 | 0.055
5106.2156 | 0.014 | 6606.9383 | 0.014 | 8093.6252 | 0.014 | 9155.6846 | 0.014 | [30 empty] | 5504.0274 | 0.014 | 6545.9577 | 0.014 | 8390.7265 | 0.014 | 10325.044 | 0.014 | [20 empty] | 5416.198 | 0.014 | 6671.6397 | 0.014 | 7704.4548 | 0.014 | 9064.0644 | 0.014 | 12085.4193 | 0.014 | [20 empty] | 7993.8245 | 0.055 | 9421.2932 | 0.055
5208.3399 | 0.014 | 6739.0771 | 0.014 | 8255.4977 | 0.014 | 9338.7983 | 0.014 | [30 empty] | 5614.1079 | 0.014 | 6676.8769 | 0.014 | 8558.5411 | 0.014 | 10531.5449 | 0.014 | [20 empty] | 5524.522 | 0.014 | 6805.0725 | 0.014 | 7858.5439 | 0.014 | 9245.3457 | 0.014 | [22 empty] | 8153.701 | 0.055 | 9609.7191 | 0.055
5312.5067 | 0.014 | 6873.8586 | 0.014 | 8420.6076 | 0.014 | 9525.5743 | 0.014 | [30 empty] | 5726.3901 | 0.014 | 6810.4144 | 0.014 | 8729.7119 | 0.014 | 10742.1758 | 0.014 | [20 empty] | 5635.0124 | 0.014 | 6941.1739 | 0.014 | 8015.7148 | 0.014 | 9430.2526 | 0.014 | [22 empty] | 8316.775 | 0.055 | 9801.9134 | 0.055
5418.7569 | 0.014 | 7011.3358 | 0.014 | 8589.0198 | 0.014 | 9716.0857 | 0.014 | [30 empty] | 5840.9179 | 0.014 | 6946.6227 | 0.014 | 8904.3061 | 0.014 | 10957.0193 | 0.014 | [20 empty] | 5747.7127 | 0.014 | 7079.9974 | 0.014 | 8176.029 | 0.014 | 9618.8577 | 0.014 | [22 empty] | 8483.1105 | 0.055 | 9997.9517 | 0.055
5527.132 | 0.014 | 7151.5625 | 0.014 | 8760.8002 | 0.014 | 9910.4075 | 0.014 | [30 empty] | 5957.7362 | 0.014 | 7085.5552 | 0.014 | 9082.3922 | 0.014 | 11176.1597 | 0.014 | [20 empty] | 5862.6669 | 0.014 | 7221.5974 | 0.014 | 8339.5496 | 0.014 | 9811.2349 | 0.014 | [22 empty] | 8652.7728 | 0.055 | 10197.9107 | 0.055
5637.6746 | 0.014 | 7294.5937 | 0.014 | 8936.0162 | 0.014 | 10108.6156 | 0.014 | [30 empty] | 6076.8909 | 0.014 | 7227.2663 | 0.014 | 9264.0401 | 0.014 | 11399.6829 | 0.014 | [20 empty] | 5979.9203 | 0.014 | 7366.0293 | 0.014 | 8506.3406 | 0.014 | 10007.4596 | 0.014 | [22 empty] | 8825.8282 | 0.055 | 10401.869 | 0.055
5750.4281 | 0.014 | 7440.4856 | 0.014 | 9114.7365 | 0.014 | 10310.7879 | 0.014 | [30 empty] | 6198.4288 | 0.014 | 7371.8116 | 0.014 | 9449.3209 | 0.014 | 11627.6765 | 0.014 | [20 empty] | 6099.5187 | 0.014 | 7513.3499 | 0.014 | 8676.4674 | 0.014 | 10207.6087 | 0.014 | [22 empty] | 9002.3448 | 0.055 | 10609.9063 | 0.055
5865.4367 | 0.014 | 7589.2953 | 0.014 | 9297.0312 | 0.014 | 10517.0037 | 0.014 | [30 empty] | 6322.3973 | 0.014 | 7519.2478 | 0.014 | 9638.3073 | 0.014 | 11860.23 | 0.014 | [20 empty] | 6221.509 | 0.014 | 7663.6169 | 0.014 | 8849.9968 | 0.014 | 10411.7609 | 0.014 | [22 empty] | 9182.3917 | 0.055 | 10822.1045 | 0.055
5982.7454 | 0.014 | 7741.0812 | 0.014 | 9482.9719 | 0.014 | 10727.3437 | 0.014 | [30 empty] | 6448.8453 | 0.014 | 7669.6328 | 0.014 | 9831.0734 | 0.014 | 12097.4346 | 0.014 | [20 empty] | 6345.9392 | 0.014 | 7816.8892 | 0.014 | 9026.9967 | 0.014 | 10619.9961 | 0.014 | [22 empty] | 9366.0395 | 0.055 | 11038.5466 | 0.055
6102.4003 | 0.014 | 7895.9029 | 0.014 | 9672.6313 | 0.014 | 10941.8906 | 0.014 | [30 empty] | 6577.8222 | 0.014 | 7823.0254 | 0.014 | 10027.6949 | 0.014 | [22 empty] | 6472.858 | 0.014 | 7973.227 | 0.014 | 9207.5367 | 0.014 | 10832.3961 | 0.014 | [22 empty] | 9553.3603 | 0.055 | 11259.3175 | 0.055
6224.4484 | 0.014 | 8053.8209 | 0.014 | 9866.0839 | 0.014 | 11160.7284 | 0.014 | [30 empty] | 6709.3786 | 0.014 | 7979.4859 | 0.014 | 10228.2488 | 0.014 | [22 empty] | 6602.3152 | 0.014 | 8132.6916 | 0.014 | 9391.6874 | 0.014 | 11049.044 | 0.014 | [22 empty] | 9744.4275 | 0.055 | 11484.5038 | 0.055
6348.9373 | 0.014 | 8214.8973 | 0.014 | 10063.4056 | 0.014 | 11383.943 | 0.014 | [30 empty] | 6843.5662 | 0.014 | 8139.0757 | 0.014 | 10432.8138 | 0.014 | [22 empty] | 6734.3615 | 0.014 | 8295.3454 | 0.014 | 9579.5211 | 0.014 | 11270.0249 | 0.014 | [22 empty] | 9939.3161 | 0.055 | 11714.1939 | 0.055
6475.9161 | 0.014 | 8379.1953 | 0.014 | 10264.6737 | 0.014 | 11611.6219 | 0.014 | [30 empty] | 6980.4375 | 0.014 | 8301.8572 | 0.014 | 10641.4701 | 0.014 | [22 empty] | 6869.0487 | 0.014 | 8461.2523 | 0.014 | 9771.1116 | 0.014 | 11495.4254 | 0.014 | [22 empty] | 10138.1024 | 0.055 | 11948.4778 | 0.055
6605.4344 | 0.014 | 8546.7792 | 0.014 | 10469.9672 | 0.014 | 11843.8543 | 0.014 | [30 empty] | 7120.0463 | 0.014 | 8467.8943 | 0.014 | 10854.2995 | 0.014 | [22 empty] | 7006.4297 | 0.014 | 8630.4774 | 0.014 | 9966.5338 | 0.014 | 11725.3339 | 0.014 | [22 empty] | 10340.8644 | 0.055
6737.5431 | 0.014 | 8717.7148 | 0.014 | 10679.3665 | 0.014 | 12080.7314 | 0.014 | [30 empty] | 7262.4472 | 0.014 | 8637.2522 | 0.014 | 11071.3855 | 0.014 | [22 empty] | 7146.5583 | 0.014 | 8803.0869 | 0.014 | 10165.8645 | 0.014 | 11959.8405 | 0.014 | [22 empty] | 10547.6817 | 0.055
6872.2939 | 0.014 | 8892.0691 | 0.014 | 10892.9539 | 0.014 | [32 empty] | 7407.6961 | 0.014 | 8809.9973 | 0.014 | 11292.8132 | 0.014 | [22 empty] | 7289.4894 | 0.014 | 8979.1486 | 0.014 | 10369.1817 | 0.014 | [24 empty] | 10758.6353 | 0.055
7009.7398 | 0.014 | 9069.9105 | 0.014 | 11110.813 | 0.014 | [32 empty] | 7555.8501 | 0.014 | 8986.1972 | 0.014 | 11518.6694 | 0.014 | [22 empty] | 7435.2792 | 0.014 | 9158.7316 | 0.014 | 10576.5654 | 0.014 | [24 empty] | 10973.8081 | 0.055
7149.9346 | 0.014 | 9251.3087 | 0.014 | 11333.0292 | 0.014 | [32 empty] | 7706.9671 | 0.014 | 9165.9211 | 0.014 | 11749.0428 | 0.014 | [22 empty] | 7583.9848 | 0.014 | 9341.9062 | 0.014 | 10788.0967 | 0.014 | [24 empty] | 11193.2842 | 0.055
7292.9333 | 0.014 | 9436.3348 | 0.014 | 11559.6898 | 0.014 | [32 empty] | 7861.1064 | 0.014 | 9349.2396 | 0.014 | 11984.0237 | 0.014 | [22 empty] | 7735.6645 | 0.014 | 9528.7444 | 0.014 | 11003.8586 | 0.014 | [24 empty] | 11417.1499 | 0.055
7438.792 | 0.014 | 9625.0615 | 0.014 | 11790.8836 | 0.014 | [32 empty] | 8018.3285 | 0.014 | 9536.2244 | 0.014 | [24 empty] | 7890.3778 | 0.014 | 9719.3193 | 0.014 | 11223.9358 | 0.014 | [24 empty] | 11645.4929 | 0.055
7587.5678 | 0.014 | 9817.5628 | 0.014 | 12026.7013 | 0.014 | [32 empty] | 8178.6951 | 0.014 | 9726.9488 | 0.014 | [24 empty] | 8048.1854 | 0.014 | 9913.7056 | 0.014 | 11448.4145 | 0.014 | [24 empty] | 11878.4028 | 0.055
7739.3192 | 0.014 | 10013.914 | 0.014 | [34 empty] | 8342.269 | 0.014 | 9921.4878 | 0.014 | [24 empty] | 8209.1491 | 0.014 | 10111.9798 | 0.014 | 11677.3828 | 0.014 | [24 empty] | 12115.9708 | 0.055
7894.1055 | 0.014 | 10214.1923 | 0.014 | [34 empty] | 8509.1144 | 0.014 | 10119.9176 | 0.014 | [24 empty] | 8373.332 | 0.014 | 10314.2193 | 0.014 | 11910.9305 | 0.014
8051.9877 | 0.014 | 10418.4761 | 0.014 | [34 empty] | 8679.2967 | 0.014 | 10322.3159 | 0.014 | [24 empty] | 8540.7987 | 0.014 | 10520.5037 | 0.014
8213.0274 | 0.014 | 10626.8457 | 0.014 | [34 empty] | 8852.8826 | 0.014 | 10528.7622 | 0.014 | [24 empty] | 8711.6147 | 0.014 | 10730.9138 | 0.014
8377.288 | 0.014 | 10839.3826 | 0.014 | [34 empty] | 9029.9403 | 0.014 | 10739.3375 | 0.014 | [24 empty] | 8885.847 | 0.014 | 10945.5321 | 0.014
8544.8337 | 0.014 | 11056.1702 | 0.014 | [34 empty] | 9210.5391 | 0.014 | 10954.1242 | 0.014 | [24 empty] | 9063.5639 | 0.014 | 11164.4427 | 0.014
8715.7304 | 0.014 | 11277.2936 | 0.014 | [34 empty] | 9394.7499 | 0.014 | 11173.2067 | 0.014 | [24 empty] | 9244.8352 | 0.014 | 11387.7316 | 0.014
8890.045 | 0.014 | 11502.8395 | 0.014 | [34 empty] | 9582.6449 | 0.014 | 11396.6709 | 0.014 | [24 empty] | 9429.7319 | 0.014 | 11615.4862 | 0.014
9067.8459 | 0.014 | 11732.8963 | 0.014 | [34 empty] | 9774.2978 | 0.014 | 11624.6043 | 0.014 | [24 empty] | 9618.3265 | 0.014 | 11847.7959 | 0.014
9249.2028 | 0.014 | 11967.5542 | 0.014 | [34 empty] | 9969.7837 | 0.014 | 11857.0964 | 0.014 | [24 empty] | 9810.693 | 0.014 | 12084.7519 | 0.014
9434.1869 | 0.014 | [36 empty] | 10169.1794 | 0.014 | 12094.2383 | 0.014 | [24 empty] | 10006.9069 | 0.014
9622.8706 | 0.014 | [36 empty] | 10372.563 | 0.014 | [26 empty] | 10207.045 | 0.014
9815.328 | 0.014 | [36 empty] | 10580.0142 | 0.014 | [26 empty] | 10411.1859 | 0.014
10011.6346 | 0.014 | [36 empty] | 10791.6145 | 0.014 | [26 empty] | 10619.4097 | 0.014
10211.8673 | 0.014 | [36 empty] | 11007.4468 | 0.014 | [26 empty] | 10831.7979 | 0.014
10416.1046 | 0.014 | [36 empty] | 11227.5957 | 0.014 | [26 empty] | 11048.4338 | 0.014
10624.4267 | 0.014 | [36 empty] | 11452.1477 | 0.014 | [26 empty] | 11269.4025 | 0.014
10836.9153 | 0.014 | [36 empty] | 11681.1906 | 0.014 | [26 empty] | 11494.7905 | 0.014
11053.6536 | 0.014 | [36 empty] | 11914.8144 | 0.014 | [26 empty] | 11724.6863 | 0.014
11274.7266 | 0.014 | [64 empty] | 11959.1801 | 0.014
11500.2212 | 0.014
11730.2256 | 0.014
11964.8301 | 0.014

## Evaluated Points (hidden)
E |  |  | Main |  |  | T |  |  | Tap
Max T Spec | - multiple - |  | Max T Spec | - multiple - |  | Max T Spec | - multiple - |  | Max T Spec | - multiple -
Amp Type | Current | Max of Max T Spec | Amp Type | Current | Max of Max T Spec | Amp Type | Current | Max of Max T Spec | Amp Type | Current | Max of Max T Spec
100E | 223.685 | 416.4039 | 100Main | 111.32 | 531.4604 | 100T | 241.0056 | 764.0825 | 100Tap | 112.8314 | 67.5249
| 225.9334 | 163.3041 |  | 113.52 | 45.6758 |  | 245.8257 | 247.15 |  | 114.6354 | 32.727
| 228.2038 | 100.8088 |  | 114.6 | 31.3999 |  | 248.3 | 182.7372 |  | 115.9 | 23.966
| 229.6 | 81.4788 |  | 115.72 | 23.6632 |  | 250.7422 | 145.052 |  | 117.1555 | 18.8955
| 230.9593 | 68.5961 |  | 118.4 | 14.8048 |  | 253.2 | 119.9196 |  | 119.2 | 14.0086
| 232.2 | 59.9024 |  | 121 | 10.8023 |  | 255.7571 | 101.4498 |  | 121.2739 | 11.0619
| 233.5135 | 52.7815 |  | 121.8 | 9.963 |  | 258.3 | 87.858 |  | 122.3 | 10.0084
| 234.8 | 47.2494 |  | 122.5796 | 9.2579 |  | 260.8722 | 77.2809 |  | 123.4167 | 9.0619
| 236.0963 | 42.7136 |  | 124.8 | 7.6909 |  | 263.5 | 68.7416 |  | 125.8 | 7.5241
| 237.6 | 38.4109 |  | 127.006 | 6.5687 |  | 266.0897 | 61.9307 |  | 128.1995 | 6.4104
| 239.1862 | 34.6996 |  | 130.1 | 5.4357 |  | 268.8 | 56.0593 |  | 131 | 5.4516
| 240.8 | 31.5749 |  | 133.2507 | 4.609 |  | 271.4115 | 51.3244 |  | 133.7897 | 4.733
| 242.3157 | 29.0979 |  | 138.4966 | 3.6572 |  | 274.1 | 47.1814 |  | 141.6723 | 3.4157
| 243.8 | 27.01 |  | 148.06 | 2.6234 |  | 276.8397 | 43.5624 |  | 149.864 | 2.6194
| 245.2406 | 25.2415 |  | 155.3409 | 2.1401 |  | 279.6 | 40.4085 |  | 160.1875 | 1.9994
| 246.7 | 23.6627 |  | 173.1466 | 1.4452 |  | 282.3765 | 37.64 |  | 170.1568 | 1.6104
| 248.2018 | 22.2237 |  | 190.1955 | 1.0812 |  | 285.2 | 35.1656 |  | 183.0191 | 1.2719
| 250 | 20.7059 |  | 205.678 | 0.8692 |  | 288.024 | 32.9758 |  | 193.6011 | 1.0754
| 251.7009 | 19.4411 |  | 224.5188 | 0.6937 |  | 293.7845 | 29.21 |  | 208.8856 | 0.8698
| 253.5 | 18.2536 |  | 242.5434 | 0.5762 |  | 299.6602 | 26.108 |  | 224.4407 | 0.7205
| 255.2495 | 17.2233 |  | 262.194 | 0.4828 |  | 305.6534 | 23.5104 |  | 243.6775 | 0.5873
| 257 | 16.2967 |  | 295.314 | 0.3748 |  | 311.7664 | 21.305 |  | 268.1679 | 0.4685
| 258.8476 | 15.4151 |  | 329.508 | 0.3016 |  | 318.0018 | 19.4107 |  | 290.2449 | 0.3917
| 260.7 | 14.6167 |  | 372.294 | 0.2406 |  | 324.3618 | 17.7671 |  | 316.4359 | 0.3242
| 262.4974 | 13.9126 |  | 408.526 | 0.207 |  | 330.849 | 16.3286 |  | 339.2928 | 0.2795
| 265.3 | 12.9327 |  | 445.484 | 0.1814 |  | 337.466 | 15.06 |  | 365.6994 | 0.2391
| 268.0678 | 12.0833 |  | 497.586 | 0.155 |  | 344.2153 | 13.9338 |  | 401.381 | 0.1979
| 272.3919 | 10.9454 |  | 552.312 | 0.1353 |  | 351.0997 | 12.9279 |  | 440.802 | 0.1643
| 276.7853 | 9.9754 |  | 620.783 | 0.1179 |  | 358.1216 | 12.0248 |  | 485.103 | 0.1365
| 281.5307 | 9.0908 |  | 681.907 | 0.1067 |  | 365.2841 | 11.2101 |  | 538.882 | 0.1118
| 286.9306 | 8.2438 |  | 775.292 | 0.0946 |  | 372.5898 | 10.4719 |  | 599.87 | 0.0917
| 292.435 | 7.5163 |  | 870.496 | 0.0861 |  | 380.0416 | 9.8004 |  | 672.644 | 0.0745
| 298.0439 | 6.8852 |  | 973.32 | 0.0796 |  | 387.6424 | 9.1875 |  | 747.214 | 0.0621
| 304.9783 | 6.2253 |  | 1098.559 | 0.0741 |  | 395.3952 | 8.6263 |  | 829.187 | 0.0536
| 311.1394 | 5.727 |  | 1254.226 | 0.0694 |  | 403.3031 | 8.1108 |  | 920.152 | 0.0469
| 316.7912 | 5.3283 |  | 1384.928 | 0.0666 |  | 411.3692 | 7.636 |  | 1032.327 | 0.041
| 322.2219 | 4.9887 |  | 1514.954 | 0.0645 |  | 419.5966 | 7.1977 |  | 1150 | 0.0365
| 329.3895 | 4.5945 |  | 1639.988 | 0.063 |  | 427.9885 | 6.792 |  | 1290.576 | 0.0326
| 336.38 | 4.2592 |  | 1756.91 | 0.0618 |  | 436.5483 | 6.4159 |  | 1402.651 | 0.0303
| 343.519 | 3.958 |  | 1880.207 | 0.0608 |  | 445.2793 | 6.0663 |  | 1519.705 | 0.0284
| 350.108 | 3.7108 |  | 1999.598 | 0.06 |  | 454.1848 | 5.7409 |  | 1712.962 | 0.0261
| 359.6901 | 3.3953 |  | 2100.108 | 0.0595 |  | 463.2685 | 5.4374 |  | 1940.871 | 0.0242
| 368.7948 | 3.1353 |  | 2212.586 | 0.0591 |  | 472.5339 | 5.154 |  | 2212.88 | 0.0226
| 380.0269 | 2.8579 |  | 2285.327 | 0.0588 |  | 481.9846 | 4.8888 |  | 2515.145 | 0.0214
| 393.9573 | 2.5667 |  | 2397.696 | 0.0585 |  | 491.6243 | 4.6404 |  | 2799.797 | 0.0206
| 407.1738 | 2.3332 |  | 4126.571 | 0.0562 |  | 501.4568 | 4.4075 |  | 3309.1292 | 0.016
| 421.256 | 2.1207 |  | 5004.905 | 0.0558 |  | 511.4859 | 4.1887 |  | 4254.5947 | 0.016
| 439.7657 | 1.886 |  | 6001.441 | 0.0556 |  | 521.7156 | 3.983 |  | 6145.5256 | 0.014
| 456.3416 | 1.7097 |  | 7565.874 | 0.0553 |  | 532.1499 | 3.7894 | 150Tap | 166.9448 | 630.3053
| 472.5963 | 1.5613 |  | 9528.171 | 0.0552 |  | 542.7929 | 3.607 |  | 169.73 | 56.808
| 486.0163 | 1.4538 | 150Main | 166.98 | 531.4604 |  | 553.6488 | 3.4349 |  | 171.8 | 33.7166
| 504.3357 | 1.3251 |  | 168.3 | 101.5883 |  | 564.7218 | 3.2725 |  | 173.8528 | 23.9565
| 530.7236 | 1.1693 |  | 170.83 | 39.5832 |  | 576.0162 | 3.1191 |  | 175.7 | 18.9666
| 561.8536 | 1.0199 |  | 171.8 | 32.0201 |  | 587.5365 | 2.9741 |  | 177.5334 | 15.6923
| 597.7906 | 0.8819 |  | 172.7 | 27.1782 |  | 599.2872 | 2.8368 |  | 180.1 | 12.611
| 626.5578 | 0.7914 |  | 174.9 | 19.8 |  | 611.273 | 2.7069 |  | 182.6847 | 10.5069
| 669.9759 | 0.6799 |  | 177.1 | 15.5346 |  | 623.4985 | 2.5837 |  | 185.4 | 8.9227
| 702.2158 | 0.6121 |  | 178.8 | 13.2988 |  | 635.9684 | 2.4669 |  | 188.1946 | 7.7104
| 740.4375 | 0.5444 |  | 180.4 | 11.7007 |  | 648.6878 | 2.3561 |  | 191.1 | 6.7449
| 784.6531 | 0.4796 |  | 182 | 10.4366 |  | 661.6615 | 2.251 |  | 193.9476 | 5.9988
| 832.3403 | 0.4221 |  | 183.5427 | 9.445 |  | 674.8948 | 2.1511 |  | 196.9 | 5.3742
| 881.1616 | 0.3736 |  | 187.2 | 7.6909 |  | 688.3927 | 2.0561 |  | 199.8931 | 4.8549
| 952.644 | 0.3165 |  | 190.7642 | 6.495 |  | 702.1605 | 1.9658 |  | 209.6996 | 3.6625
| 1005.5012 | 0.2824 |  | 195.3 | 5.4053 |  | 716.2037 | 1.88 |  | 218.845 | 2.9576
| 1065.5447 | 0.2501 |  | 199.9294 | 4.601 |  | 730.5278 | 1.7982 |  | 230.7789 | 2.3437
| 1129.172 | 0.2216 |  | 208.8812 | 3.5493 |  | 745.1384 | 1.7204 |  | 243.6181 | 1.8991
| 1198.989 | 0.1957 |  | 216.4217 | 2.9597 |  | 760.0411 | 1.6463 |  | 257.7069 | 1.5587
| 1301.454 | 0.1652 |  | 226.1116 | 2.4244 |  | 775.242 | 1.5757 |  | 274.3642 | 1.2743
| 1425.446 | 0.137 |  | 236.5 | 2.0182 |  | 790.7468 | 1.5084 |  | 292.611 | 1.0521
| 1578.511 | 0.1112 |  | 248.622 | 1.6773 |  | 806.5617 | 1.4442 |  | 315.3898 | 0.8546
| 1720.268 | 0.0933 |  | 262.9 | 1.3889 |  | 822.693 | 1.383 |  | 336.7705 | 0.7199
| 1880.395 | 0.0779 |  | 281.182 | 1.1283 |  | 839.1468 | 1.3245 |  | 365.6411 | 0.5868
| 2047.221 | 0.0656 |  | 295.6151 | 0.977 |  | 855.9298 | 1.2688 |  | 394.515 | 0.49
| 2273.865 | 0.053 |  | 313.0677 | 0.836 |  | 873.0484 | 1.2155 |  | 424.3415 | 0.4148
| 2470.655 | 0.0463 |  | 333.2835 | 0.7119 |  | 890.5093 | 1.1647 |  | 464.9799 | 0.339
| 2760.692 | 0.039 |  | 350.7581 | 0.6282 |  | 908.3195 | 1.1161 |  | 505.4522 | 0.2836
| 3045 | 0.0338 |  | 366.8456 | 0.5652 |  | 926.4859 | 1.0697 |  | 554.214 | 0.2341
| 3261.45 | 0.0308 |  | 391.3492 | 0.4881 |  | 945.0156 | 1.0253 |  | 610.561 | 0.1924
| 3536.63 | 0.0276 |  | 419.6742 | 0.4195 |  | 963.9159 | 0.9829 |  | 686.076 | 0.1529
| 3789.27 | 0.0254 |  | 431.034 | 0.3966 |  | 983.1942 | 0.9423 |  | 767.726 | 0.1232
| 4141.98 | 0.0229 |  | 459.826 | 0.3475 |  | 1002.8581 | 0.9035 |  | 850.081 | 0.1018
| 4354.34 | 0.0216 |  | 489.519 | 0.3072 |  | 1022.9153 | 0.8664 |  | 933.566 | 0.0857
| 4573.02 | 0.0205 |  | 513.04 | 0.281 |  | 1043.3736 | 0.8309 |  | 1030.33 | 0.0718
| 4731.17 | 0.016 |  | 553.624 | 0.2443 |  | 1064.2411 | 0.797 |  | 1137.868 | 0.0606
| 4855.8 | 0.016 |  | 593.074 | 0.218 |  | 1085.5259 | 0.7644 |  | 1254.511 | 0.053
| 4929.18 | 0.016 |  | 636.66 | 0.1951 |  | 1107.2364 | 0.7333 |  | 1379.769 | 0.047
| 5173.6831 | 0.016 |  | 679.896 | 0.1768 |  | 1129.3811 | 0.7035 |  | 1534.259 | 0.0414
| 5820.3935 | 0.016 |  | 729.103 | 0.1601 |  | 1151.9688 | 0.675 |  | 1706.16 | 0.0369
| 6467.1039 | 0.016 |  | 793.371 | 0.143 |  | 1175.0081 | 0.6476 |  | 1945.18 | 0.0325
| 7243.1563 | 0.016 |  | 849.904 | 0.1312 |  | 1198.5083 | 0.6214 |  | 2170.056 | 0.0296
| 9858.4531 | 0.014 |  | 920.97 | 0.1194 |  | 1222.4785 | 0.5963 |  | 2515.816 | 0.0265
10E | 23.46 | 118.2059 |  | 1001.106 | 0.1091 |  | 1246.928 | 0.5723 |  | 2762.956 | 0.0249
| 23.7 | 77.2201 |  | 1083.684 | 0.1009 |  | 1271.8666 | 0.5493 |  | 3170.008 | 0.0231
| 23.9292 | 57.8469 |  | 1190.327 | 0.0927 |  | 1297.3039 | 0.5272 |  | 3584.398 | 0.0218
| 24.2 | 44.4984 |  | 1339.206 | 0.0845 |  | 1323.25 | 0.506 |  | 4078.356 | 0.0208
| 24.4078 | 37.7402 |  | 1491.074 | 0.0785 |  | 1349.715 | 0.4858 |  | 4820.2805 | 0.016
| 24.7 | 31.034 |  | 1682.826 | 0.0732 |  | 1376.7093 | 0.4663 |  | 6197.5035 | 0.016
| 24.8959 | 27.6966 |  | 1863.917 | 0.0696 |  | 1404.2435 | 0.4477 |  | 8951.9495 | 0.016
| 25.1 | 24.8841 |  | 2049.478 | 0.0669 |  | 1432.3284 | 0.4298 | 15Tap | 18.36 | 43.3984
| 25.3939 | 21.6781 |  | 2244.131 | 0.0648 |  | 1460.9749 | 0.4126 |  | 18.5 | 31.1198
| 25.6 | 19.8628 |  | 2488.218 | 0.0628 |  | 1490.1944 | 0.3962 |  | 18.7272 | 21.2569
| 25.9017 | 17.6722 |  | 2776.17 | 0.061 |  | 1519.9983 | 0.3804 |  | 18.9 | 17.0905
| 26.2 | 15.9144 |  | 3024.032 | 0.0599 |  | 1550.3983 | 0.3653 |  | 19.1017 | 13.8809
| 26.4198 | 14.8162 |  | 3409.364 | 0.0589 |  | 1581.4063 | 0.3508 |  | 19.3 | 11.6981
| 26.9482 | 12.679 |  | 3721.514 | 0.0583 |  | 1613.0344 | 0.3368 |  | 19.4838 | 10.1963
| 27.4871 | 11.021 |  | 3974.242 | 0.0579 |  | 1645.2951 | 0.3235 |  | 19.7 | 8.8458
| 28.0369 | 9.6983 |  | 4320.05 | 0.0574 |  | 1678.201 | 0.3107 |  | 19.8735 | 7.9882
| 28.5976 | 8.6194 |  | 8500 | 0.0556 |  | 1711.765 | 0.2984 |  | 20.2709 | 6.5184
| 29.1696 | 7.7235 | 200Main | 224.2999 | 106.5043 |  | 1746.0003 | 0.2866 |  | 20.6763 | 5.4705
| 29.753 | 6.9682 |  | 231.957 | 22.3834 |  | 1780.9203 | 0.2752 |  | 21.0899 | 4.6862
| 30.348 | 6.3582 |  | 237.5 | 14.1071 |  | 1816.5387 | 0.2643 |  | 21.5117 | 4.0776
| 30.955 | 5.8487 |  | 242.9581 | 10.2841 |  | 1852.8695 | 0.2539 |  | 21.9419 | 3.5921
| 31.5741 | 5.3987 |  | 248.5 | 8.0296 |  | 1889.9269 | 0.2439 |  | 22.3807 | 3.196
| 32.2056 | 4.9985 |  | 254.012 | 6.5687 |  | 1927.7254 | 0.2343 |  | 22.8284 | 2.867
| 32.8497 | 4.6407 |  | 260.3 | 5.4205 |  | 1966.2799 | 0.225 |  | 23.2849 | 2.5896
| 33.5067 | 4.3189 |  | 266.5014 | 4.609 |  | 2005.6055 | 0.2162 |  | 23.7506 | 2.3527
| 34.1768 | 4.0284 |  | 276.9921 | 3.6572 |  | 2045.7176 | 0.2077 |  | 24.2256 | 2.1483
| 34.8603 | 3.7649 |  | 296.1211 | 2.6234 |  | 2086.632 | 0.1995 |  | 24.7101 | 1.9702
| 35.5575 | 3.525 |  | 313.918 | 2.054 |  | 2128.3646 | 0.1916 |  | 25.2043 | 1.8137
| 36.2687 | 3.3058 |  | 346.2943 | 1.4452 |  | 2170.9319 | 0.1841 |  | 25.7084 | 1.6754
| 36.9941 | 3.105 |  | 380.391 | 1.0812 |  | 2214.3505 | 0.1769 |  | 26.2226 | 1.5522
| 37.7339 | 2.9204 |  | 411.356 | 0.8692 |  | 2258.6375 | 0.1699 |  | 26.7471 | 1.4419
| 38.4886 | 2.7503 |  | 449.0387 | 0.6937 |  | 2303.8103 | 0.1633 |  | 27.282 | 1.3428
| 39.2584 | 2.5931 |  | 485.0857 | 0.5762 |  | 2349.8865 | 0.1569 |  | 27.8276 | 1.2531
| 40.0436 | 2.4476 |  | 524.387 | 0.4828 |  | 2396.8842 | 0.1507 |  | 28.3842 | 1.1718
| 40.8444 | 2.3126 |  | 590.627 | 0.3748 |  | 2444.8219 | 0.1448 |  | 28.9519 | 1.0977
| 41.6613 | 2.1871 |  | 659.016 | 0.3016 |  | 2493.7184 | 0.1391 |  | 29.5309 | 1.03
| 42.4945 | 2.0702 |  | 744.589 | 0.2406 |  | 2543.5927 | 0.1337 |  | 30.1215 | 0.9692
| 43.3444 | 1.9612 |  | 817.051 | 0.207 |  | 2594.4646 | 0.1284 |  | 30.724 | 0.9175
| 44.2113 | 1.8593 |  | 890.968 | 0.1814 |  | 2646.3539 | 0.1234 |  | 31.3384 | 0.8694
| 45.0955 | 1.7639 |  | 995.172 | 0.155 |  | 2699.2809 | 0.1186 |  | 31.9652 | 0.8245
| 45.9975 | 1.6746 |  | 1104.625 | 0.1353 |  | 2753.2666 | 0.1139 |  | 32.6045 | 0.7826
| 46.9174 | 1.5907 |  | 1241.566 | 0.1179 |  | 2808.3319 | 0.1095 |  | 33.2566 | 0.7434
| 47.8558 | 1.512 |  | 1363.814 | 0.1067 |  | 2864.4985 | 0.1052 |  | 33.9217 | 0.7067
| 48.8129 | 1.4379 |  | 1550.583 | 0.0946 |  | 2921.7885 | 0.1011 |  | 34.6002 | 0.6723
| 49.7891 | 1.3682 |  | 1740.992 | 0.0861 |  | 2980.2243 | 0.0971 |  | 35.2922 | 0.6399
| 50.7849 | 1.3025 |  | 1946.641 | 0.0796 |  | 3039.8288 | 0.0933 |  | 35.998 | 0.6095
| 51.8006 | 1.2405 |  | 2197.118 | 0.0741 |  | 3100.6253 | 0.0897 |  | 36.718 | 0.5809
| 52.8366 | 1.182 |  | 2508.453 | 0.0694 |  | 3162.6378 | 0.0862 |  | 37.4523 | 0.5539
| 53.8934 | 1.1267 |  | 2769.855 | 0.0666 |  | 3225.8906 | 0.0828 |  | 38.2014 | 0.5285
| 54.9712 | 1.0744 |  | 3029.909 | 0.0645 |  | 3290.4084 | 0.0796 |  | 38.9654 | 0.5044
| 56.0706 | 1.0249 |  | 3279.975 | 0.063 |  | 3356.2166 | 0.0765 |  | 39.7447 | 0.4817
| 57.1921 | 0.978 |  | 3513.821 | 0.0618 |  | 3423.3409 | 0.0735 |  | 40.5396 | 0.4602
| 58.3359 | 0.9336 |  | 3760.414 | 0.0608 |  | 3491.8077 | 0.0706 |  | 41.3504 | 0.4398
| 59.5026 | 0.8915 |  | 3999.196 | 0.06 |  | 3561.6439 | 0.0679 |  | 42.1774 | 0.4205
| 60.6927 | 0.8515 |  | 4200.216 | 0.0595 |  | 3632.8768 | 0.0652 |  | 43.021 | 0.4022
| 61.9065 | 0.8135 |  | 4425.171 | 0.0591 |  | 3705.5343 | 0.0627 |  | 43.8814 | 0.3849
| 63.1447 | 0.7775 |  | 4570.654 | 0.0588 |  | 3779.645 | 0.0602 |  | 44.759 | 0.3684
| 64.4075 | 0.7432 |  | 5000 | 0.0582 |  | 3855.2379 | 0.0579 |  | 45.6542 | 0.3528
| 65.6957 | 0.7106 |  | 5126.571 | 0.058 |  | 3932.3426 | 0.0556 |  | 46.5673 | 0.3379
| 67.0096 | 0.6796 |  | 5474.905 | 0.0577 |  | 4010.9895 | 0.0535 |  | 47.4986 | 0.3237
| 68.3498 | 0.6501 |  | 6001.441 | 0.0572 |  | 4091.2093 | 0.0516 |  | 48.4486 | 0.3103
| 69.7168 | 0.622 |  | 7565.874 | 0.0564 |  | 4173.0335 | 0.05 |  | 49.4176 | 0.2974
| 71.1111 | 0.5952 |  | 9528.171 | 0.0559 |  | 4256.4941 | 0.0484 |  | 50.4059 | 0.2852
| 72.5334 | 0.5697 | 250Main | 281.4812 | 74.554 |  | 4341.624 | 0.0469 |  | 51.414 | 0.2736
| 73.984 | 0.5454 |  | 288.9183 | 24.4888 |  | 4428.4565 | 0.0455 |  | 52.4423 | 0.2625
| 75.4637 | 0.5222 |  | 294.9 | 15.7832 |  | 4517.0256 | 0.0441 |  | 53.4912 | 0.2519
| 76.973 | 0.5001 |  | 300.9127 | 11.5718 |  | 4607.3661 | 0.0428 |  | 54.561 | 0.2418
| 78.5124 | 0.479 |  | 308 | 8.762 |  | 4699.5135 | 0.0415 |  | 55.6522 | 0.2321
| 80.0827 | 0.4588 |  | 315.0444 | 7.0302 |  | 4793.5037 | 0.0403 |  | 56.7652 | 0.2229
| 81.6843 | 0.4396 |  | 318.7 | 6.3672 |  | 4889.3738 | 0.0391 |  | 57.9005 | 0.2141
| 83.318 | 0.4212 |  | 322.3572 | 5.8132 |  | 4987.1613 | 0.038 |  | 59.0586 | 0.2057
| 84.9844 | 0.4037 |  | 326.1 | 5.3335 |  | 5086.9045 | 0.0369 |  | 60.2397 | 0.1977
| 86.6841 | 0.3869 |  | 329.8394 | 4.9234 |  | 5188.6426 | 0.0358 |  | 61.4445 | 0.19
| 88.4178 | 0.3708 |  | 335.3 | 4.421 |  | 5292.4155 | 0.0348 |  | 62.6734 | 0.1826
| 90.1861 | 0.3555 |  | 340.7151 | 4.0094 |  | 5398.2638 | 0.0339 |  | 63.9269 | 0.1756
| 91.9898 | 0.3409 |  | 350.4446 | 3.4255 |  | 5506.229 | 0.0329 |  | 65.2054 | 0.1689
| 93.8296 | 0.3268 |  | 361.9242 | 2.9119 |  | 5616.3536 | 0.032 |  | 66.5095 | 0.1624
| 95.7062 | 0.3134 |  | 376.1648 | 2.4435 |  | 5728.6807 | 0.0312 |  | 67.8397 | 0.1563
| 97.6204 | 0.3006 |  | 393.8308 | 2.0249 |  | 5843.2543 | 0.0304 |  | 69.1965 | 0.1504
| 99.5728 | 0.2883 |  | 414.4811 | 1.6757 |  | 5960.1194 | 0.0296 |  | 70.5804 | 0.1447
| 101.5642 | 0.2765 |  | 440.7887 | 1.3625 |  | 6079.3218 | 0.0288 |  | 71.992 | 0.1393
| 103.5955 | 0.2653 |  | 464.387 | 1.1593 |  | 6200.9082 | 0.0281 |  | 73.4319 | 0.1341
| 105.6674 | 0.2545 |  | 490.7815 | 0.9877 |  | 6324.9264 | 0.0274 |  | 74.9005 | 0.1291
| 107.7808 | 0.2442 |  | 514.9903 | 0.8656 |  | 6451.4249 | 0.0267 |  | 76.3985 | 0.1243
| 109.9364 | 0.2343 |  | 539.0836 | 0.768 |  | 6580.4534 | 0.0261 |  | 77.9265 | 0.1198
| 112.1351 | 0.2248 |  | 564.9886 | 0.6826 |  | 6712.0625 | 0.0254 |  | 79.485 | 0.1154
| 114.3778 | 0.2158 |  | 593.9945 | 0.6048 |  | 6846.3037 | 0.0248 |  | 81.0747 | 0.1112
| 116.6654 | 0.2071 |  | 626.4478 | 0.5345 |  | 6983.2298 | 0.0243 |  | 82.6962 | 0.1071
| 118.9987 | 0.1987 |  | 655.7551 | 0.4824 |  | 7122.8944 | 0.0237 |  | 84.3502 | 0.1032
| 121.3786 | 0.1907 |  | 698.2239 | 0.4211 |  | 7265.3523 | 0.0232 |  | 86.0372 | 0.0995
| 123.8062 | 0.1831 |  | 744.0906 | 0.3689 |  | 7410.6593 | 0.0227 |  | 87.7579 | 0.096
| 126.2823 | 0.1758 |  | 777.916 | 0.3373 |  | 7558.8725 | 0.0222 |  | 89.5131 | 0.0925
| 128.808 | 0.1687 |  | 819.561 | 0.3046 |  | 7710.05 | 0.0217 |  | 91.3033 | 0.0892
| 131.3841 | 0.162 |  | 867.671 | 0.2734 |  | 7864.251 | 0.0212 |  | 93.1294 | 0.0861
| 134.0118 | 0.1555 |  | 926.805 | 0.2424 |  | 8021.536 | 0.0208 |  | 94.992 | 0.0831
| 136.6921 | 0.1493 |  | 990.886 | 0.2172 |  | 8181.9667 | 0.0204 |  | 96.8918 | 0.0801
| 139.4259 | 0.1434 |  | 1069.279 | 0.1928 |  | 8335.6239 | 0.016 |  | 98.8297 | 0.0774
| 142.2144 | 0.1377 |  | 1139.522 | 0.1754 |  | 8502.3364 | 0.016 |  | 100.8062 | 0.0747
| 145.0587 | 0.1322 |  | 1232.242 | 0.157 |  | 8672.3831 | 0.016 |  | 102.8224 | 0.0721
| 147.9599 | 0.1269 |  | 1335.289 | 0.1412 |  | 8845.8308 | 0.016 |  | 104.8788 | 0.0696
| 150.9191 | 0.1219 |  | 1486.73 | 0.1238 |  | 9022.7474 | 0.016 |  | 106.9764 | 0.0672
| 153.9375 | 0.1171 |  | 1611.059 | 0.1132 |  | 9203.2023 | 0.016 |  | 109.1159 | 0.065
| 157.0162 | 0.1124 |  | 1740.331 | 0.1046 |  | 9387.2664 | 0.016 |  | 111.2982 | 0.0629
| 160.1565 | 0.108 |  | 1848.862 | 0.0987 |  | 9575.0117 | 0.016 |  | 113.5242 | 0.0608
| 163.3597 | 0.1037 |  | 1962.115 | 0.0936 |  | 9766.5119 | 0.016 |  | 115.7947 | 0.059
| 166.6269 | 0.0996 |  | 2119.555 | 0.0879 |  | 9961.8422 | 0.016 |  | 118.1106 | 0.0575
| 169.9594 | 0.0957 |  | 2284.858 | 0.0831 |  | 10161.079 | 0.016 |  | 120.4728 | 0.0559
| 173.3586 | 0.0919 |  | 2460.485 | 0.079 |  | 10364.3006 | 0.016 |  | 122.8823 | 0.0545
| 176.8258 | 0.0883 |  | 2688.586 | 0.0749 |  | 10571.5866 | 0.016 |  | 125.3399 | 0.0531
| 180.3623 | 0.0848 |  | 2898.266 | 0.072 |  | 10783.0184 | 0.016 |  | 127.8467 | 0.0517
| 183.9695 | 0.0814 |  | 3163.65 | 0.0691 |  | 10998.6787 | 0.016 |  | 130.4036 | 0.0504
| 187.6489 | 0.0782 |  | 3460.546 | 0.0666 |  | 11218.6523 | 0.016 |  | 133.0117 | 0.0491
| 191.4019 | 0.0752 |  | 3842.005 | 0.0642 |  | 11443.0253 | 0.016 |  | 135.6719 | 0.0479
| 195.2299 | 0.0722 |  | 4222.232 | 0.0624 |  | 11671.8859 | 0.016 |  | 138.3854 | 0.0468
| 199.1345 | 0.0694 |  | 4603.071 | 0.0611 |  | 11905.3236 | 0.016 |  | 141.1531 | 0.0457
| 203.1172 | 0.0666 |  | 4950.454 | 0.0601 | 10T | 23.664 | 272.498 |  | 143.9761 | 0.0446
| 207.1796 | 0.064 |  | 5379.656 | 0.0593 |  | 23.9 | 179.5901 |  | 146.8557 | 0.0436
| 211.3231 | 0.0615 |  | 5709.187 | 0.0588 |  | 24.1373 | 133.3555 |  | 149.7928 | 0.0426
| 215.5496 | 0.0591 |  | 6090.584 | 0.0584 |  | 24.4 | 103.5017 |  | 152.7886 | 0.0416
| 219.8606 | 0.0568 |  | 6795.504 | 0.0577 |  | 24.62 | 87.0045 |  | 155.8444 | 0.0407
| 224.2578 | 0.0545 |  | 7938.079 | 0.057 |  | 24.9 | 72.1924 |  | 158.9613 | 0.0398
| 228.743 | 0.0524 |  | 9647.669 | 0.0563 |  | 25.1124 | 63.8513 |  | 162.1405 | 0.039
| 233.3178 | 0.0507 |  | 10630.395 | 0.0561 |  | 25.4 | 55.1302 |  | 165.3833 | 0.0381
| 237.9842 | 0.0491 | 25Main | 28.56 | 44.1934 |  | 25.6147 | 49.9771 |  | 168.691 | 0.0373
| 242.7439 | 0.0476 |  | 28.8 | 30.8029 |  | 25.9 | 44.3998 |  | 172.0648 | 0.0366
| 247.5987 | 0.0461 |  | 29.1312 | 21.6565 |  | 26.127 | 40.7423 |  | 175.5061 | 0.0359
| 252.5507 | 0.0447 |  | 29.4 | 17.4158 |  | 26.4 | 37.0327 |  | 179.0162 | 0.0352
| 257.6017 | 0.0434 |  | 29.7138 | 14.1488 |  | 26.6495 | 34.1586 |  | 182.5966 | 0.0345
| 262.7538 | 0.0421 |  | 30 | 12.0642 |  | 26.9 | 31.6652 |  | 186.2485 | 0.0338
| 268.0088 | 0.0408 |  | 30.3081 | 10.5447 |  | 27.1825 | 29.2318 |  | 189.9735 | 0.0332
| 273.369 | 0.0396 |  | 30.6 | 9.4117 |  | 27.7261 | 25.4094 |  | 193.7729 | 0.0326
| 278.8364 | 0.0384 |  | 30.9143 | 8.4281 |  | 28.2807 | 22.3601 |  | 197.6484 | 0.032
| 284.4131 | 0.0373 |  | 31.2 | 7.6909 |  | 28.8463 | 19.8731 |  | 201.6014 | 0.0315
| 290.1014 | 0.0363 |  | 31.5325 | 6.9747 |  | 29.4232 | 17.8076 |  | 205.6334 | 0.0309
| 295.9034 | 0.0352 |  | 31.8 | 6.4848 |  | 30.0117 | 16.0696 |  | 209.7461 | 0.0304
| 301.8215 | 0.0343 |  | 32.1632 | 5.9157 |  | 30.6119 | 14.7202 |  | 213.941 | 0.0299
| 307.8579 | 0.0333 |  | 32.5 | 5.4665 |  | 31.2241 | 13.5375 |  | 218.2198 | 0.0294
| 314.0151 | 0.0324 |  | 32.8065 | 5.1104 |  | 31.8486 | 12.4931 |  | 222.5842 | 0.029
| 320.2954 | 0.0315 |  | 33.1 | 4.8079 |  | 32.4856 | 11.5649 |  | 227.0359 | 0.0285
| 326.7013 | 0.0307 |  | 33.4626 | 4.4777 |  | 33.1353 | 10.7351 |  | 231.5766 | 0.0281
| 333.2353 | 0.0299 |  | 34.1318 | 3.968 |  | 33.798 | 9.9894 |  | 236.2081 | 0.0277
| 339.9 | 0.0291 |  | 34.8145 | 3.5488 |  | 34.474 | 9.3161 |  | 240.9323 | 0.0273
| 346.698 | 0.0284 |  | 35.5108 | 3.1982 |  | 35.1635 | 8.7057 |  | 245.7509 | 0.0269
| 353.632 | 0.0276 |  | 36.221 | 2.9009 |  | 35.8667 | 8.15 |  | 250.666 | 0.0265
| 360.7046 | 0.027 |  | 36.9454 | 2.6458 |  | 36.5841 | 7.6425 |  | 255.6793 | 0.0262
| 367.9187 | 0.0263 |  | 37.6843 | 2.4247 |  | 37.3157 | 7.1776 |  | 260.7929 | 0.0258
| 375.2771 | 0.0257 |  | 38.438 | 2.2312 |  | 38.0621 | 6.7503 |  | 266.0087 | 0.0255
| 382.7826 | 0.0251 |  | 39.2068 | 2.0608 |  | 38.8233 | 6.3566 |  | 271.3289 | 0.0252
| 390.4383 | 0.0245 |  | 39.9909 | 1.9095 |  | 39.5998 | 5.9929 |  | 276.7555 | 0.0249
| 398.2471 | 0.0239 |  | 40.7907 | 1.7745 |  | 40.3918 | 5.6562 |  | 282.2906 | 0.0246
| 406.212 | 0.0234 |  | 41.6065 | 1.6534 |  | 41.1996 | 5.3439 |  | 287.9364 | 0.0243
| 414.3362 | 0.0228 |  | 42.4387 | 1.5441 |  | 42.0236 | 5.0536 |  | 293.6951 | 0.024
| 422.623 | 0.0223 |  | 43.2874 | 1.4451 |  | 42.8641 | 4.7832 |  | 299.569 | 0.0238
| 431.0754 | 0.0219 |  | 44.1532 | 1.3551 |  | 43.7213 | 4.531 |  | 305.5604 | 0.0235
| 439.6969 | 0.0214 |  | 45.0362 | 1.273 |  | 44.5958 | 4.2954 |  | 311.6716 | 0.0233
| 448.4909 | 0.021 |  | 45.937 | 1.1979 |  | 45.4877 | 4.0749 |  | 317.905 | 0.0231
| 457.4607 | 0.0205 |  | 46.8557 | 1.1288 |  | 46.3974 | 3.8683 |  | 324.2631 | 0.0228
| 466.6099 | 0.0201 |  | 47.7928 | 1.0653 |  | 47.3254 | 3.6745 |  | 330.7484 | 0.0226
| 469.4678 | 0.016 |  | 48.7487 | 1.0066 |  | 48.2719 | 3.4925 |  | 337.3634 | 0.0224
| 478.8571 | 0.016 |  | 49.7237 | 0.9523 |  | 49.2373 | 3.3213 |  | 344.1106 | 0.0222
| 488.4343 | 0.016 |  | 50.7181 | 0.902 |  | 50.2221 | 3.1601 |  | 350.9928 | 0.022
| 498.203 | 0.016 |  | 51.7325 | 0.8552 |  | 51.2265 | 3.0083 |  | 358.0127 | 0.0218
| 508.167 | 0.016 |  | 52.7671 | 0.8117 |  | 52.2511 | 2.865 |  | 365.173 | 0.0217
| 518.3304 | 0.016 |  | 53.8225 | 0.7711 |  | 53.2961 | 2.7298 |  | 372.4764 | 0.0215
| 528.697 | 0.016 |  | 54.8989 | 0.7332 |  | 54.362 | 2.602 |  | 379.9259 | 0.0213
| 539.2709 | 0.016 |  | 55.9969 | 0.6978 |  | 55.4492 | 2.4812 |  | 387.5245 | 0.0212
| 550.0563 | 0.016 |  | 57.1168 | 0.6646 |  | 56.5582 | 2.3668 |  | 395.275 | 0.021
| 561.0575 | 0.016 |  | 58.2592 | 0.6334 |  | 57.6894 | 2.2585 |  | 403.1805 | 0.0209
| 572.2786 | 0.016 |  | 59.4244 | 0.6042 |  | 58.8432 | 2.1559 |  | 411.2441 | 0.0207
| 583.7242 | 0.016 |  | 60.6129 | 0.5767 |  | 60.02 | 2.0586 |  | 419.4689 | 0.0206
| 595.3987 | 0.016 |  | 61.8251 | 0.5508 |  | 61.2204 | 1.9662 |  | 427.8583 | 0.0204
| 607.3066 | 0.016 |  | 63.0616 | 0.5265 |  | 62.4448 | 1.8785 |  | 436.4155 | 0.0203
| 619.4528 | 0.016 |  | 64.3228 | 0.5035 |  | 63.6937 | 1.7953 |  | 445.1438 | 0.0202
| 631.8418 | 0.016 |  | 65.6093 | 0.4818 |  | 64.9676 | 1.7161 |  | 454.0467 | 0.0201
| 644.4787 | 0.016 |  | 66.9215 | 0.4613 |  | 66.267 | 1.6408 |  | 459.9405 | 0.016
| 657.3682 | 0.016 |  | 68.2599 | 0.4419 |  | 67.5923 | 1.5692 |  | 469.1393 | 0.016
| 670.5156 | 0.016 |  | 69.6251 | 0.4236 |  | 68.9442 | 1.501 |  | 478.5221 | 0.016
| 683.9259 | 0.016 |  | 71.0176 | 0.4062 |  | 70.323 | 1.4362 |  | 488.0925 | 0.016
| 697.6044 | 0.016 |  | 72.438 | 0.3898 |  | 71.7295 | 1.3743 |  | 497.8544 | 0.016
| 711.5565 | 0.016 |  | 73.8867 | 0.3742 |  | 73.1641 | 1.3154 |  | 507.8114 | 0.016
| 725.7876 | 0.016 |  | 75.3645 | 0.3594 |  | 74.6274 | 1.2593 |  | 517.9677 | 0.016
| 740.3034 | 0.016 |  | 76.8718 | 0.3454 |  | 76.1199 | 1.2057 |  | 528.327 | 0.016
| 755.1095 | 0.016 |  | 78.4092 | 0.332 |  | 77.6423 | 1.1546 |  | 538.8936 | 0.016
| 770.2117 | 0.016 |  | 79.9774 | 0.3194 |  | 79.1952 | 1.1059 |  | 549.6714 | 0.016
| 785.6159 | 0.016 |  | 81.5769 | 0.3073 |  | 80.7791 | 1.0593 |  | 560.6649 | 0.016
| 801.3282 | 0.016 |  | 83.2085 | 0.2958 |  | 82.3946 | 1.0149 |  | 571.8782 | 0.016
| 817.3548 | 0.016 |  | 84.8726 | 0.2849 |  | 84.0425 | 0.9725 |  | 583.3157 | 0.016
| 833.7019 | 0.016 |  | 86.5701 | 0.2745 |  | 85.7234 | 0.9319 |  | 594.982 | 0.016
| 850.3759 | 0.016 |  | 88.3015 | 0.2647 |  | 87.4379 | 0.8932 |  | 606.8817 | 0.016
| 867.3834 | 0.016 |  | 90.0675 | 0.2552 |  | 89.1866 | 0.8562 |  | 619.0193 | 0.016
| 884.7311 | 0.016 |  | 91.8689 | 0.2462 |  | 90.9703 | 0.8208 |  | 631.3997 | 0.016
| 902.4257 | 0.016 |  | 93.7062 | 0.2379 |  | 92.7898 | 0.7869 |  | 644.0277 | 0.016
| 920.4742 | 0.016 |  | 95.5804 | 0.2303 |  | 94.6455 | 0.7545 |  | 656.9082 | 0.016
| 938.8837 | 0.016 |  | 97.492 | 0.2229 |  | 96.5385 | 0.7236 |  | 670.0464 | 0.016
| 938.9356 | 0.014 |  | 99.4418 | 0.2159 |  | 98.4692 | 0.6939 |  | 683.4473 | 0.016
| 957.7143 | 0.014 |  | 101.4306 | 0.2092 |  | 100.4386 | 0.6656 |  | 697.1163 | 0.016
| 976.8686 | 0.014 |  | 103.4593 | 0.2028 |  | 102.4474 | 0.6384 |  | 711.0586 | 0.016
| 996.4059 | 0.014 |  | 105.5284 | 0.1967 |  | 104.4963 | 0.6124 |  | 725.2798 | 0.016
| 1016.3341 | 0.014 |  | 107.639 | 0.1908 |  | 106.5863 | 0.5875 |  | 739.7854 | 0.016
| 1036.6607 | 0.014 |  | 109.7918 | 0.1852 |  | 108.718 | 0.5637 |  | 754.5811 | 0.016
| 1057.3939 | 0.014 |  | 111.9876 | 0.1799 |  | 110.8923 | 0.5409 |  | 769.6727 | 0.016
| 1078.5418 | 0.014 |  | 114.2274 | 0.1747 |  | 113.1102 | 0.519 |  | 785.0662 | 0.016
| 1100.1127 | 0.014 |  | 116.5119 | 0.1698 |  | 115.3724 | 0.4981 |  | 800.7675 | 0.016
| 1122.1149 | 0.014 |  | 118.8422 | 0.1651 |  | 117.6798 | 0.478 |  | 816.7828 | 0.016
| 1144.5572 | 0.014 |  | 121.219 | 0.1606 |  | 120.0334 | 0.4588 |  | 833.1185 | 0.016
| 1167.4484 | 0.014 |  | 123.6434 | 0.1563 |  | 122.4341 | 0.4403 |  | 849.7809 | 0.016
| 1190.7973 | 0.014 |  | 126.1163 | 0.1522 |  | 124.8828 | 0.4227 |  | 866.7765 | 0.016
| 1214.6133 | 0.014 |  | 128.6386 | 0.1482 |  | 127.3804 | 0.4057 |  | 884.112 | 0.016
| 1238.9055 | 0.014 |  | 131.2114 | 0.1444 |  | 129.9281 | 0.3895 |  | 901.7943 | 0.016
| 1263.6837 | 0.014 |  | 133.8356 | 0.1408 |  | 132.5266 | 0.3739 |  | 919.8301 | 0.016
| 1288.9573 | 0.014 |  | 136.5123 | 0.1373 |  | 135.1771 | 0.359 |  | 919.8809 | 0.014
| 1314.7365 | 0.014 |  | 139.2425 | 0.1339 |  | 137.8807 | 0.3447 |  | 938.2786 | 0.014
| 1341.0312 | 0.014 |  | 142.0274 | 0.1307 |  | 140.6383 | 0.3309 |  | 957.0441 | 0.014
| 1367.8518 | 0.014 |  | 144.8679 | 0.1277 |  | 143.4511 | 0.3178 |  | 976.185 | 0.014
| 1395.2089 | 0.014 |  | 147.7653 | 0.1247 |  | 146.3201 | 0.3051 |  | 995.7087 | 0.014
| 1423.113 | 0.014 |  | 150.7206 | 0.1219 |  | 149.2465 | 0.293 |  | 1015.6229 | 0.014
| 1451.5753 | 0.014 |  | 153.735 | 0.1192 |  | 152.2314 | 0.2814 |  | 1035.9353 | 0.014
| 1480.6068 | 0.014 |  | 156.8097 | 0.1166 |  | 155.276 | 0.2702 |  | 1056.6541 | 0.014
| 1510.2189 | 0.014 |  | 159.9459 | 0.1141 |  | 158.3816 | 0.2595 |  | 1077.7871 | 0.014
| 1540.4233 | 0.014 |  | 163.1448 | 0.1117 |  | 161.5492 | 0.2492 |  | 1099.3429 | 0.014
| 1571.2318 | 0.014 |  | 166.4077 | 0.1094 |  | 164.7802 | 0.2394 |  | 1121.3297 | 0.014
| 1602.6564 | 0.014 |  | 169.7359 | 0.1072 |  | 168.0758 | 0.2299 |  | 1143.7563 | 0.014
| 1634.7096 | 0.014 |  | 173.1306 | 0.1051 |  | 171.4373 | 0.2208 |  | 1166.6315 | 0.014
| 1667.4037 | 0.014 |  | 176.5932 | 0.1031 |  | 174.8661 | 0.2121 |  | 1189.9641 | 0.014
| 1700.7518 | 0.014 |  | 180.1251 | 0.1011 |  | 178.3634 | 0.2037 |  | 1213.7634 | 0.014
| 1734.7669 | 0.014 |  | 183.7276 | 0.0993 |  | 181.9306 | 0.1957 |  | 1238.0386 | 0.014
| 1769.4622 | 0.014 |  | 187.4021 | 0.0975 |  | 185.5693 | 0.188 |  | 1262.7994 | 0.014
| 1804.8514 | 0.014 |  | 191.1502 | 0.0958 |  | 189.2806 | 0.1806 |  | 1288.0554 | 0.014
| 1840.9485 | 0.014 |  | 194.9732 | 0.0941 |  | 193.0663 | 0.1735 |  | 1313.8165 | 0.014
| 1877.7674 | 0.014 |  | 198.8726 | 0.0925 |  | 196.9276 | 0.1666 |  | 1340.0928 | 0.014
| 1915.3228 | 0.014 |  | 202.8501 | 0.091 |  | 200.8661 | 0.1601 |  | 1366.8947 | 0.014
| 1953.6292 | 0.014 |  | 206.9071 | 0.0896 |  | 204.8835 | 0.1538 |  | 1394.2326 | 0.014
| 1992.7018 | 0.014 |  | 211.0452 | 0.0882 |  | 208.9811 | 0.1478 |  | 1422.1172 | 0.014
| 2032.5559 | 0.014 |  | 215.2661 | 0.0868 |  | 213.1607 | 0.142 |  | 1450.5596 | 0.014
| 2073.207 | 0.014 |  | 219.5715 | 0.0855 |  | 217.424 | 0.1364 |  | 1479.5708 | 0.014
| 2114.6711 | 0.014 |  | 223.9629 | 0.0843 |  | 221.7724 | 0.131 |  | 1509.1622 | 0.014
| 2156.9645 | 0.014 |  | 228.4421 | 0.0831 |  | 226.2079 | 0.1259 |  | 1539.3454 | 0.014
| 2200.1038 | 0.014 |  | 233.011 | 0.0819 |  | 230.732 | 0.121 |  | 1570.1323 | 0.014
| 2244.1059 | 0.014 |  | 237.6712 | 0.0809 |  | 235.3467 | 0.1162 |  | 1601.535 | 0.014
| 2288.988 | 0.014 |  | 242.4246 | 0.0798 |  | 240.0536 | 0.1117 |  | 1633.5657 | 0.014
| 2334.7678 | 0.014 |  | 247.2731 | 0.0788 |  | 244.8547 | 0.1073 |  | 1666.237 | 0.014
| 2381.4631 | 0.014 |  | 252.2186 | 0.0778 |  | 249.7518 | 0.1031 |  | 1699.5617 | 0.014
| 2429.0924 | 0.014 |  | 257.263 | 0.0769 |  | 254.7468 | 0.0991 |  | 1733.553 | 0.014
| 2477.6742 | 0.014 |  | 262.4082 | 0.076 |  | 259.8418 | 0.0952 |  | 1768.224 | 0.014
| 2527.2277 | 0.014 |  | 267.6564 | 0.0751 |  | 265.0386 | 0.0915 |  | 1803.5885 | 0.014
| 2577.7723 | 0.014 |  | 273.0095 | 0.0743 |  | 270.3394 | 0.0879 |  | 1839.6603 | 0.014
| 2629.3277 | 0.014 |  | 278.4697 | 0.0735 |  | 275.7461 | 0.0845 |  | 1876.4535 | 0.014
| 2681.9143 | 0.014 |  | 284.0391 | 0.0727 |  | 281.2611 | 0.0812 |  | 1913.9826 | 0.014
| 2735.5526 | 0.014 |  | 289.7199 | 0.072 |  | 286.8863 | 0.078 |  | 1952.2622 | 0.014
| 2790.2636 | 0.014 |  | 295.5143 | 0.0713 |  | 292.624 | 0.0749 |  | 1991.3075 | 0.014
| 2846.0689 | 0.014 |  | 301.4246 | 0.0706 |  | 298.4765 | 0.072 |  | 2031.1336 | 0.014
| 2902.9903 | 0.014 |  | 307.4531 | 0.07 |  | 304.446 | 0.0692 |  | 2071.7563 | 0.014
| 2961.0501 | 0.014 |  | 313.6021 | 0.0693 |  | 310.5349 | 0.0665 |  | 2113.1914 | 0.014
| 3020.2711 | 0.014 |  | 319.8742 | 0.0688 |  | 316.7456 | 0.0639 |  | 2155.4552 | 0.014
| 3080.6765 | 0.014 |  | 326.2716 | 0.0682 |  | 323.0806 | 0.0614 |  | 2198.5643 | 0.014
| 3142.29 | 0.014 |  | 332.7971 | 0.0676 |  | 329.5422 | 0.059 |  | 2242.5356 | 0.014
| 3205.1358 | 0.014 |  | 339.453 | 0.0671 |  | 336.133 | 0.0567 |  | 2287.3863 | 0.014
| 3269.2386 | 0.014 |  | 346.2421 | 0.0666 |  | 342.8557 | 0.0545 |  | 2333.1341 | 0.014
| 3334.6233 | 0.014 |  | 353.1669 | 0.0661 |  | 349.7128 | 0.0524 |  | 2379.7967 | 0.014
| 3401.3158 | 0.014 |  | 360.2303 | 0.0656 |  | 356.707 | 0.0507 |  | 2427.3927 | 0.014
| 3469.3421 | 0.014 |  | 367.4349 | 0.0652 |  | 363.8412 | 0.0492 |  | 2475.9405 | 0.014
| 3538.7289 | 0.014 |  | 374.7836 | 0.0647 |  | 371.118 | 0.0476 |  | 2525.4593 | 0.014
| 3609.5035 | 0.014 |  | 382.2792 | 0.0643 |  | 378.5404 | 0.0462 |  | 2575.9685 | 0.014
| 3681.6936 | 0.014 |  | 389.9248 | 0.0639 |  | 386.1112 | 0.0448 |  | 2627.4879 | 0.014
| 3755.3275 | 0.014 |  | 397.7233 | 0.0635 |  | 393.8334 | 0.0434 |  | 2680.0377 | 0.014
| 3830.434 | 0.014 |  | 405.6778 | 0.0631 |  | 401.7101 | 0.0421 |  | 2733.6384 | 0.014
| 3907.0427 | 0.014 |  | 413.7913 | 0.0628 |  | 409.7443 | 0.0408 |  | 2788.3112 | 0.014
| 3985.1836 | 0.014 |  | 422.0672 | 0.0624 |  | 417.9392 | 0.0396 |  | 2844.0774 | 0.014
| 4064.8872 | 0.014 |  | 430.5085 | 0.0621 |  | 426.2979 | 0.0385 |  | 2900.9589 | 0.014
| 4146.185 | 0.014 |  | 439.1187 | 0.0618 |  | 434.8239 | 0.0374 |  | 2958.9781 | 0.014
| 4229.1087 | 0.014 |  | 447.901 | 0.0615 |  | 443.5204 | 0.0363 |  | 3018.1577 | 0.014
| 4313.6908 | 0.014 |  | 456.8591 | 0.0612 |  | 452.3908 | 0.0353 |  | 3078.5208 | 0.014
| 4399.9647 | 0.014 |  | 465.9962 | 0.0609 |  | 461.4386 | 0.0343 |  | 3140.0913 | 0.014
| 4487.964 | 0.014 |  | 475.3162 | 0.0607 |  | 470.6674 | 0.0334 |  | 3202.8931 | 0.014
| 4577.7232 | 0.014 |  | 484.8225 | 0.0604 |  | 480.0807 | 0.0325 |  | 3266.9509 | 0.014
| 4669.2777 | 0.014 |  | 494.5189 | 0.0601 |  | 489.6823 | 0.0316 |  | 3332.29 | 0.014
| 4762.6632 | 0.014 |  | 504.4093 | 0.0599 |  | 499.476 | 0.0307 |  | 3398.9358 | 0.014
| 4857.9165 | 0.014 |  | 514.4975 | 0.0597 |  | 509.4655 | 0.0299 |  | 3466.9145 | 0.014
| 4955.0748 | 0.014 |  | 524.7875 | 0.0595 |  | 519.6548 | 0.0292 |  | 3536.2528 | 0.014
| 5054.1763 | 0.014 |  | 535.2832 | 0.0594 |  | 530.0479 | 0.0284 |  | 3606.9778 | 0.014
| 5155.2599 | 0.014 |  | 545.9889 | 0.0592 |  | 540.6489 | 0.0277 |  | 3679.1174 | 0.014
| 5258.3651 | 0.014 |  | 556.9087 | 0.059 |  | 551.4618 | 0.027 |  | 3752.6997 | 0.014
| 5363.5324 | 0.014 |  | 568.0468 | 0.0589 |  | 562.4911 | 0.0264 |  | 3827.7537 | 0.014
| 5470.803 | 0.014 |  | 579.4078 | 0.0587 |  | 573.7409 | 0.0257 |  | 3904.3088 | 0.014
| 5580.2191 | 0.014 |  | 590.9959 | 0.0586 |  | 585.2157 | 0.0251 |  | 3982.395 | 0.014
| 5691.8235 | 0.014 |  | 602.8158 | 0.0584 |  | 596.92 | 0.0245 |  | 4062.0429 | 0.014
| 5805.6599 | 0.014 |  | 614.8722 | 0.0583 |  | 608.8584 | 0.024 |  | 4143.2837 | 0.014
| 5921.7731 | 0.014 |  | 627.1696 | 0.0582 |  | 621.0356 | 0.0234 |  | 4226.1494 | 0.014
| 6040.2086 | 0.014 |  | 639.713 | 0.0581 |  | 633.4563 | 0.0229 |  | 4310.6724 | 0.014
| 6161.0128 | 0.014 |  | 652.5072 | 0.0579 |  | 646.1254 | 0.0224 |  | 4396.8858 | 0.014
| 6284.233 | 0.014 |  | 665.5574 | 0.0578 |  | 659.0479 | 0.0219 |  | 4484.8236 | 0.014
| 6409.9177 | 0.014 |  | 678.8685 | 0.0577 |  | 672.2289 | 0.0214 |  | 4574.52 | 0.014
| 6538.116 | 0.014 |  | 692.4459 | 0.0576 |  | 685.6735 | 0.021 |  | 4666.0104 | 0.014
| 6668.8783 | 0.014 |  | 706.2948 | 0.0575 |  | 699.387 | 0.0206 |  | 4759.3306 | 0.014
| 6802.2559 | 0.014 |  | 720.4207 | 0.0574 |  | 713.3747 | 0.0202 |  | 4854.5172 | 0.014
| 6938.301 | 0.014 |  | 734.8291 | 0.0573 |  | 719.0888 | 0.02 |  | 4951.6076 | 0.014
| 7077.0671 | 0.014 |  | 749.5257 | 0.0572 |  | 733.4706 | 0.016 |  | 5050.6397 | 0.014
| 7218.6084 | 0.014 |  | 764.5162 | 0.0571 |  | 748.14 | 0.016 |  | 5151.6525 | 0.014
| 7362.9806 | 0.014 |  | 779.8066 | 0.0571 |  | 763.1028 | 0.016 |  | 5254.6856 | 0.014
| 7510.2402 | 0.014 |  | 795.4027 | 0.057 |  | 778.3648 | 0.016 |  | 5359.7793 | 0.014
| 7660.445 | 0.014 |  | 811.3108 | 0.0569 |  | 793.9321 | 0.016 |  | 5466.9749 | 0.014
| 7813.6539 | 0.014 |  | 827.537 | 0.0568 |  | 809.8108 | 0.016 |  | 5576.3144 | 0.014
| 7969.927 | 0.014 |  | 844.0877 | 0.0568 |  | 826.007 | 0.016 |  | 5687.8407 | 0.014
| 8129.3255 | 0.014 |  | 860.9695 | 0.0567 |  | 842.5271 | 0.016 |  | 5801.5975 | 0.014
| 8291.912 | 0.014 |  | 878.1888 | 0.0566 |  | 859.3777 | 0.016 |  | 5917.6294 | 0.014
| 8457.7502 | 0.014 |  | 895.7526 | 0.0566 |  | 876.5652 | 0.016 |  | 6035.982 | 0.014
| 8626.9052 | 0.014 |  | 913.6677 | 0.0565 |  | 894.0965 | 0.016 |  | 6156.7017 | 0.014
| 8799.4434 | 0.014 |  | 931.941 | 0.0564 |  | 911.9785 | 0.016 |  | 6279.8357 | 0.014
| 8975.4322 | 0.014 |  | 950.5799 | 0.0564 |  | 930.218 | 0.016 |  | 6405.4324 | 0.014
| 9154.9409 | 0.014 |  | 969.5914 | 0.0563 |  | 948.8224 | 0.016 |  | 6533.5411 | 0.014
| 9338.0397 | 0.014 |  | 988.9833 | 0.0563 |  | 967.7988 | 0.016 |  | 6664.2119 | 0.014
| 9524.8005 | 0.014 |  | 1008.7629 | 0.0562 |  | 987.1548 | 0.016 |  | 6797.4961 | 0.014
| 9715.2965 | 0.014 |  | 1028.9382 | 0.0562 |  | 1006.8979 | 0.016 |  | 6933.446 | 0.014
| 9909.6024 | 0.014 |  | 1049.517 | 0.0561 |  | 1027.0359 | 0.016 |  | 7072.115 | 0.014
| 10107.7945 | 0.014 |  | 1070.5073 | 0.0561 |  | 1047.5766 | 0.016 |  | 7213.5573 | 0.014
| 10309.9503 | 0.014 |  | 1091.9175 | 0.056 |  | 1068.5281 | 0.016 |  | 7357.8284 | 0.014
| 10516.1494 | 0.014 |  | 1113.7558 | 0.056 |  | 1089.8987 | 0.016 |  | 7504.985 | 0.014
| 10726.4724 | 0.014 |  | 1136.0309 | 0.056 |  | 1111.6967 | 0.016 |  | 7655.0847 | 0.014
| 10941.0018 | 0.014 |  | 1158.7515 | 0.0559 |  | 1133.9306 | 0.016 |  | 7808.1864 | 0.014
| 11159.8218 | 0.014 |  | 1181.9266 | 0.0559 |  | 1156.6092 | 0.016 |  | 7964.3501 | 0.014
| 11383.0183 | 0.014 |  | 1205.5651 | 0.0559 |  | 1179.7414 | 0.016 |  | 8123.6371 | 0.014
| 11610.6786 | 0.014 |  | 1229.6764 | 0.0558 |  | 1203.3362 | 0.016 |  | 8286.1098 | 0.014
| 11842.8922 | 0.014 |  | 1254.2699 | 0.0558 |  | 1227.4029 | 0.016 |  | 8451.832 | 0.014
125E | 330 | 115.8085 |  | 1279.3553 | 0.0558 |  | 1251.951 | 0.016 |  | 8620.8687 | 0.014
| 330.3795 | 108.3406 |  | 1304.9424 | 0.0557 |  | 1276.99 | 0.016 |  | 8793.286 | 0.014
| 332 | 84.8939 |  | 1331.0413 | 0.0557 |  | 1302.5298 | 0.016 |  | 8969.1518 | 0.014
| 333.6993 | 69.1274 |  | 1357.6621 | 0.0557 |  | 1328.5804 | 0.016 |  | 9148.5348 | 0.014
| 335.2 | 59.3469 |  | 1384.8153 | 0.0557 |  | 1355.152 | 0.016 |  | 9331.5055 | 0.014
| 336.7166 | 51.8935 |  | 1412.5117 | 0.0556 |  | 1382.2551 | 0.016 |  | 9518.1356 | 0.014
| 338.6 | 44.8612 |  | 1440.7619 | 0.0556 |  | 1409.9002 | 0.016 |  | 9708.4983 | 0.014
| 340.4412 | 39.5878 |  | 1469.5771 | 0.0556 |  | 1438.0982 | 0.016 |  | 9902.6683 | 0.014
| 342.8 | 34.3786 |  | 1498.9687 | 0.0556 |  | 1438.1776 | 0.014 |  | 10100.7217 | 0.014
| 345.2405 | 30.2336 |  | 1528.948 | 0.0555 |  | 1466.9411 | 0.014 |  | 10302.7361 | 0.014
| 347.8 | 26.8178 |  | 1559.527 | 0.0555 |  | 1496.28 | 0.014 |  | 10508.7908 | 0.014
| 350.4578 | 23.983 |  | 1590.7175 | 0.0555 |  | 1526.2056 | 0.014 |  | 10718.9666 | 0.014
| 352.8 | 21.9259 |  | 1622.5319 | 0.0555 |  | 1556.7297 | 0.014 |  | 10933.346 | 0.014
| 355.0437 | 20.2511 |  | 1654.9825 | 0.0555 |  | 1587.8643 | 0.014 |  | 11152.0129 | 0.014
| 357.7 | 18.5609 |  | 1688.0822 | 0.0554 |  | 1619.6215 | 0.014 |  | 11375.0531 | 0.014
| 360.4095 | 17.0947 |  | 1721.8438 | 0.0554 |  | 1652.014 | 0.014 |  | 11602.5542 | 0.014
| 363.7 | 15.5869 |  | 1756.2807 | 0.0554 |  | 1685.0543 | 0.014 |  | 11834.6053 | 0.014
| 366.9556 | 14.3255 |  | 1791.4063 | 0.0554 |  | 1718.7553 | 0.014 | 200Tap | 223.6872 | 159.2083
| 369.4 | 13.4988 |  | 1827.2344 | 0.0554 |  | 1753.1304 | 0.014 |  | 227.8518 | 41.0907
| 371.7571 | 12.7829 |  | 1863.7791 | 0.0554 |  | 1788.1931 | 0.014 |  | 231.3 | 25.3107
| 374.2 | 12.1128 |  | 1901.0547 | 0.0553 |  | 1823.9569 | 0.014 |  | 234.6795 | 18.3234
| 376.6213 | 11.5108 |  | 1939.0758 | 0.0553 |  | 1860.4361 | 0.014 |  | 237.7 | 14.6619
| 379.3 | 10.907 |  | 1977.8573 | 0.0553 |  | 1897.6448 | 0.014 |  | 240.658 | 12.2398
| 381.931 | 10.369 |  | 2017.4145 | 0.0553 |  | 1935.5977 | 0.014 |  | 245.9 | 9.4357
| 384.8 | 9.8362 |  | 2057.7628 | 0.0553 |  | 1974.3096 | 0.014 |  | 251.1641 | 7.6437
| 387.7038 | 9.3464 |  | 2098.918 | 0.0553 |  | 2013.7958 | 0.014 |  | 255.8 | 6.5319
| 393.9573 | 8.4316 |  | 2140.8964 | 0.0553 |  | 2054.0717 | 0.014 |  | 260.4789 | 5.6841
| 398.7126 | 7.8398 |  | 2183.7143 | 0.0553 |  | 2095.1532 | 0.014 |  | 265.2 | 5.0165
| 403.9299 | 7.2727 |  | 2227.3886 | 0.0553 |  | 2137.0562 | 0.014 |  | 269.8696 | 4.487
| 411.6783 | 6.557 |  | 2271.9364 | 0.0552 |  | 2179.7974 | 0.014 |  | 282.7616 | 3.4521
| 420.8347 | 5.8612 |  | 2317.3751 | 0.0552 |  | 2223.3933 | 0.014 |  | 299.2627 | 2.6373
| 429.3366 | 5.3254 |  | 2363.7226 | 0.0552 |  | 2267.8612 | 0.014 |  | 319.3971 | 2.0227
| 435.8255 | 4.9723 |  | 2410.997 | 0.0552 |  | 2313.2184 | 0.014 |  | 337.5042 | 1.6568
| 442.4123 | 4.6544 |  | 2459.217 | 0.0552 |  | 2359.4828 | 0.014 |  | 362.2465 | 1.3137
| 449.9968 | 4.3304 |  | 2508.4013 | 0.0552 |  | 2406.6724 | 0.014 |  | 392.0521 | 1.0375
| 456.7981 | 4.0721 |  | 2558.5694 | 0.0552 |  | 2454.8059 | 0.014 |  | 419.4817 | 0.8603
| 464.6301 | 3.8064 |  | 2609.7407 | 0.0552 |  | 2503.902 | 0.014 |  | 448.8308 | 0.7207
| 474.0164 | 3.5256 |  | 2661.9356 | 0.0552 |  | 2553.98 | 0.014 |  | 482.7372 | 0.6011
| 485.045 | 3.2388 |  | 2715.1743 | 0.0552 |  | 2605.0596 | 0.014 |  | 512.1666 | 0.5216
| 494.8438 | 3.016 |  | 2769.4777 | 0.0552 |  | 2657.1608 | 0.014 |  | 548.0684 | 0.4458
| 504.8395 | 2.8146 |  | 2824.8673 | 0.0552 |  | 2710.304 | 0.014 |  | 587.0238 | 0.3821
| 515.5535 | 2.6229 |  | 2881.3646 | 0.0552 |  | 2764.5101 | 0.014 |  | 652.0657 | 0.3041
| 526.4952 | 2.449 |  | 2938.9919 | 0.0551 |  | 2819.8003 | 0.014 |  | 703.804 | 0.2589
| 539.2838 | 2.2691 |  | 2997.7718 | 0.0551 |  | 2876.1963 | 0.014 |  | 765.686 | 0.2177
| 554.5969 | 2.0812 |  | 3057.7272 | 0.0551 |  | 2933.7202 | 0.014 |  | 846.11 | 0.1782
| 572.6314 | 1.8912 |  | 3118.8818 | 0.0551 |  | 2992.3947 | 0.014 |  | 909.083 | 0.1548
| 595.4047 | 1.6893 |  | 3181.2594 | 0.0551 |  | 3052.2425 | 0.014 |  | 1021.559 | 0.1237
| 615.3807 | 1.5399 |  | 3244.8846 | 0.0551 |  | 3113.2874 | 0.014 |  | 1120.528 | 0.104
| 633.4878 | 1.4223 |  | 3309.7823 | 0.0551 |  | 3175.5531 | 0.014 |  | 1226.683 | 0.088
| 657.3666 | 1.2882 |  | 3375.9779 | 0.0551 |  | 3239.0642 | 0.014 |  | 1354.119 | 0.0737
| 678.0642 | 1.1877 |  | 3443.4975 | 0.0551 |  | 3303.8455 | 0.014 |  | 1519.885 | 0.0604
| 707.1493 | 1.0665 |  | 3512.3674 | 0.0551 |  | 3369.9224 | 0.014 |  | 1672.552 | 0.053
| 735.273 | 0.9671 |  | 3582.6148 | 0.0551 |  | 3437.3209 | 0.014 |  | 1854.007 | 0.0465
| 765.2799 | 0.8765 |  | 3654.2671 | 0.0551 |  | 3506.0673 | 0.014 |  | 2037.539 | 0.0416
| 794.1252 | 0.8014 |  | 3727.3524 | 0.0551 |  | 3576.1886 | 0.014 |  | 2200 | 0.0382
| 832.3403 | 0.7167 |  | 3801.8995 | 0.0551 |  | 3647.7124 | 0.014 |  | 2387.303 | 0.0352
| 872.3935 | 0.642 |  | 3877.9375 | 0.0551 |  | 3720.6666 | 0.014 |  | 2784.706 | 0.0305
| 916.2054 | 0.5735 |  | 3955.4962 | 0.0551 |  | 3795.08 | 0.014 |  | 3180 | 0.0275
| 984.6056 | 0.4872 |  | 4034.6061 | 0.0551 |  | 3870.9816 | 0.014 |  | 3580 | 0.0254
| 1053.888 | 0.4188 |  | 4115.2982 | 0.0551 |  | 3948.4012 | 0.014 |  | 3915.413 | 0.0241
| 1141.657 | 0.3514 |  | 4197.6042 | 0.0551 |  | 4027.3692 | 0.014 |  | 4388.925 | 0.0227
| 1224.432 | 0.3021 |  | 4281.5563 | 0.0551 |  | 4107.9166 | 0.014 |  | 4945.927 | 0.0215
| 1298.858 | 0.2662 |  | 4367.1874 | 0.0551 |  | 4190.0749 | 0.014 |  | 5556.466 | 0.0206
| 1393.029 | 0.2294 |  | 4454.5312 | 0.0551 |  | 4273.8764 | 0.014 |  | 6567.2846 | 0.016
| 1482.129 | 0.2013 |  | 4543.6218 | 0.0551 |  | 4359.354 | 0.014 |  | 8443.6517 | 0.016
| 1608.794 | 0.1696 |  | 4634.4942 | 0.0551 |  | 4446.541 | 0.014 | 20Tap | 23.46 | 45.3051
| 1721.995 | 0.1472 |  | 4727.1841 | 0.0551 |  | 4535.4719 | 0.014 |  | 23.7 | 29.6164
| 1865.413 | 0.1248 |  | 4821.7278 | 0.0551 |  | 4626.1813 | 0.014 |  | 23.9292 | 22.2004
| 1990.692 | 0.1092 |  | 4918.1624 | 0.0551 |  | 4718.7049 | 0.014 |  | 24.2 | 17.0905
| 2139.313 | 0.0942 |  | 5016.5256 | 0.055 |  | 4813.079 | 0.014 |  | 24.4078 | 14.5033
| 2315.17 | 0.0801 |  | 5116.8561 | 0.055 |  | 4909.3406 | 0.014 |  | 24.7 | 11.9359
| 2548.447 | 0.0659 |  | 5219.1932 | 0.055 |  | 5007.5274 | 0.014 |  | 24.8959 | 10.6581
| 2833.413 | 0.0531 |  | 5323.5771 | 0.055 |  | 5107.678 | 0.014 |  | 25.1 | 9.5812
| 3185.094 | 0.0439 |  | 5430.0486 | 0.055 |  | 5209.8315 | 0.014 |  | 25.3939 | 8.3536
| 3700 | 0.0351 |  | 5538.6496 | 0.055 |  | 5314.0282 | 0.014 |  | 25.6 | 7.6584
| 3987.53 | 0.0316 |  | 5649.4226 | 0.055 |  | 5420.3087 | 0.014 |  | 25.9017 | 6.8195
| 4276.66 | 0.0287 |  | 5762.4111 | 0.055 |  | 5528.7149 | 0.014 |  | 26.2 | 6.1462
| 4554.76 | 0.0265 |  | 5877.6593 | 0.055 |  | 5639.2892 | 0.014 |  | 26.4198 | 5.7255
| 4919.33 | 0.0241 |  | 5995.2125 | 0.055 |  | 5752.075 | 0.014 |  | 26.9482 | 4.9067
| 5187.09 | 0.0227 |  | 6115.1167 | 0.055 |  | 5867.1165 | 0.014 |  | 27.4871 | 4.2713
| 5513.35 | 0.0213 |  | 6237.4191 | 0.055 |  | 5984.4588 | 0.014 |  | 28.0369 | 3.7642
| 5877.74 | 0.016 |  | 6362.1674 | 0.055 |  | 6104.148 | 0.014 |  | 28.5976 | 3.3506
| 6105.4 | 0.016 |  | 6489.4108 | 0.055 |  | 6226.2309 | 0.014 |  | 29.1696 | 3.0069
| 6197.67 | 0.016 |  | 6619.199 | 0.055 |  | 6350.7556 | 0.014 |  | 29.753 | 2.717
| 6505.0942 | 0.016 |  | 6751.583 | 0.055 |  | 6477.7707 | 0.014 |  | 30.348 | 2.4828
| 7318.231 | 0.016 |  | 6886.6146 | 0.055 |  | 6607.3261 | 0.014 |  | 30.955 | 2.2872
| 8131.3678 | 0.016 |  | 7024.3469 | 0.055 |  | 6739.4726 | 0.014 |  | 31.5741 | 2.1143
| 9107.1319 | 0.016 |  | 7164.8339 | 0.055 |  | 6874.2621 | 0.014 |  | 32.2056 | 1.9605
13E | 29.58 | 121.916 |  | 7308.1305 | 0.055 |  | 7011.7473 | 0.014 |  | 32.8497 | 1.8228
| 29.9 | 78.0928 |  | 7454.2932 | 0.055 |  | 7151.9822 | 0.014 |  | 33.5067 | 1.6991
| 30.1716 | 60.5897 |  | 7603.379 | 0.055 |  | 7295.0219 | 0.014 |  | 34.1768 | 1.5872
| 30.5 | 47.9726 |  | 7755.4466 | 0.055 |  | 7440.9223 | 0.014 |  | 34.8603 | 1.4857
| 30.775 | 40.7885 |  | 7910.5555 | 0.055 |  | 7589.7408 | 0.014 |  | 35.5575 | 1.3933
| 31.1 | 34.6053 |  | 8068.7666 | 0.055 |  | 7741.5356 | 0.014 |  | 36.2687 | 1.3088
| 31.3905 | 30.439 |  | 8230.142 | 0.055 |  | 7896.3663 | 0.014 |  | 36.9941 | 1.2313
| 31.7 | 26.9497 |  | 8394.7448 | 0.055 |  | 8054.2936 | 0.014 |  | 37.7339 | 1.16
| 32.0183 | 24.0817 |  | 8562.6397 | 0.055 |  | 8215.3795 | 0.014 |  | 38.4886 | 1.0943
| 32.3 | 21.9916 |  | 8733.8925 | 0.055 |  | 8379.6871 | 0.014 |  | 39.2584 | 1.0335
| 32.6587 | 19.783 |  | 8908.5704 | 0.055 |  | 8547.2808 | 0.014 |  | 40.0436 | 0.9772
| 33 | 18.0407 |  | 9086.7418 | 0.055 |  | 8718.2265 | 0.014 |  | 40.8444 | 0.925
| 33.3119 | 16.6845 |  | 9268.4766 | 0.055 |  | 8892.591 | 0.014 |  | 41.6613 | 0.8763
| 33.6 | 15.5919 |  | 9453.8461 | 0.055 |  | 9070.4428 | 0.014 |  | 42.4945 | 0.831
| 33.9781 | 14.3466 |  | 9642.923 | 0.055 |  | 9251.8517 | 0.014 |  | 43.3444 | 0.7887
| 34.3 | 13.4245 |  | 9835.7815 | 0.055 |  | 9436.8887 | 0.014 |  | 44.2113 | 0.7491
| 34.6577 | 12.5212 |  | 10032.4971 | 0.055 |  | 9625.6265 | 0.014 |  | 45.0955 | 0.712
| 35.3508 | 11.0575 |  | 10233.1471 | 0.055 |  | 9818.139 | 0.014 |  | 45.9975 | 0.6773
| 36.0579 | 9.8585 |  | 10437.81 | 0.055 |  | 10014.5018 | 0.014 |  | 46.9174 | 0.6446
| 36.779 | 8.8591 |  | 10646.5662 | 0.055 |  | 10214.7918 | 0.014 |  | 47.8558 | 0.614
| 37.5146 | 8.0138 |  | 10859.4976 | 0.055 |  | 10419.0876 | 0.014 |  | 48.8129 | 0.5851
| 38.2649 | 7.2902 |  | 11076.6875 | 0.055 |  | 10627.4694 | 0.014 |  | 49.7891 | 0.5578
| 39.0302 | 6.6641 |  | 11298.2213 | 0.055 |  | 10840.0188 | 0.014 |  | 50.7849 | 0.5322
| 39.8108 | 6.1175 |  | 11524.1857 | 0.055 |  | 11056.8192 | 0.014 |  | 51.8006 | 0.5079
| 40.607 | 5.6365 |  | 11754.6694 | 0.055 |  | 11277.9555 | 0.014 |  | 52.8366 | 0.485
| 41.4191 | 5.2103 |  | 11989.7628 | 0.055 |  | 11503.5146 | 0.014 |  | 53.8934 | 0.4633
| 42.2475 | 4.8303 | 300Main | 333.883 | 605.9736 |  | 11733.585 | 0.014 |  | 54.9712 | 0.4428
| 43.0925 | 4.4896 |  | 337.7077 | 75.7498 |  | 11968.2566 | 0.014 |  | 56.0706 | 0.4233
| 43.9543 | 4.1827 |  | 343.3595 | 32.7987 | 12T | 30.6408 | 301.2904 |  | 57.1921 | 0.4049
| 44.8334 | 3.9049 |  | 348.3 | 21.8277 |  | 30.9 | 209.118 |  | 58.3359 | 0.3874
| 45.7301 | 3.6526 |  | 353.2078 | 16.3314 |  | 31.2536 | 147.1089 |  | 59.5026 | 0.3708
| 46.6447 | 3.4225 |  | 359.6 | 12.2543 |  | 31.6 | 113.7088 |  | 60.6927 | 0.3551
| 47.5776 | 3.212 |  | 365.9854 | 9.777 |  | 31.8787 | 95.9984 |  | 61.9065 | 0.3401
| 48.5291 | 3.0188 |  | 373.8 | 7.8108 |  | 32.2 | 81.2669 |  | 63.1447 | 0.3258
| 49.4997 | 2.841 |  | 381.5273 | 6.4952 |  | 32.5163 | 70.5108 |  | 64.4075 | 0.3122
| 50.4897 | 2.677 |  | 390.7 | 5.3952 |  | 32.8 | 62.9648 |  | 65.6957 | 0.2993
| 51.4995 | 2.5253 |  | 399.8599 | 4.6009 |  | 33.1666 | 55.2495 |  | 67.0096 | 0.287
| 52.5295 | 2.3848 |  | 417.7635 | 3.5492 |  | 33.5 | 49.6567 |  | 68.3498 | 0.2753
| 53.5801 | 2.2542 |  | 432.8434 | 2.9597 |  | 33.8299 | 45.0948 |  | 69.7168 | 0.2641
| 54.6517 | 2.1327 |  | 452.2243 | 2.4244 |  | 34.2 | 40.8422 |  | 71.1111 | 0.2534
| 55.7447 | 2.0195 |  | 474.2309 | 1.998 |  | 34.5065 | 37.856 |  | 72.5334 | 0.2433
| 56.8596 | 1.9138 |  | 499.4451 | 1.6514 |  | 34.9 | 34.5774 |  | 73.984 | 0.2336
| 57.9968 | 1.815 |  | 524.9706 | 1.396 |  | 35.1966 | 32.4384 |  | 75.4637 | 0.2243
| 59.1567 | 1.7224 |  | 562.3629 | 1.1283 |  | 35.5 | 30.4929 |  | 76.973 | 0.2154
| 60.3399 | 1.6356 |  | 591.2302 | 0.977 |  | 35.9006 | 28.2345 |  | 78.5124 | 0.207
| 61.5467 | 1.5542 |  | 626.1354 | 0.836 |  | 36.6186 | 24.8799 |  | 80.0827 | 0.1989
| 62.7776 | 1.4776 |  | 666.567 | 0.7119 |  | 37.351 | 22.1428 |  | 81.6843 | 0.1911
| 64.0332 | 1.4056 |  | 701.5162 | 0.6282 |  | 38.098 | 19.8687 |  | 83.318 | 0.1837
| 65.3138 | 1.3377 |  | 735.8912 | 0.5613 |  | 38.8599 | 17.9506 |  | 84.9844 | 0.1766
| 66.6201 | 1.2737 |  | 782.6995 | 0.4881 |  | 39.6371 | 16.3123 |  | 86.6841 | 0.1699
| 67.9525 | 1.2134 |  | 839.3473 | 0.4195 |  | 40.4299 | 14.8977 |  | 88.4178 | 0.1634
| 69.3115 | 1.1563 |  | 887.0477 | 0.3739 |  | 41.2385 | 13.6647 |  | 90.1861 | 0.1572
| 70.6978 | 1.1024 |  | 919.652 | 0.3475 |  | 42.0633 | 12.5815 |  | 91.9898 | 0.1512
| 72.1117 | 1.0514 |  | 979.038 | 0.3072 |  | 42.9045 | 11.6228 |  | 93.8296 | 0.1455
| 73.554 | 1.0032 |  | 1026.08 | 0.281 |  | 43.7626 | 10.7691 |  | 95.7062 | 0.1401
| 75.025 | 0.9574 |  | 1100.249 | 0.2471 |  | 44.6379 | 10.0046 |  | 97.6204 | 0.1349
| 76.5255 | 0.9141 |  | 1186.147 | 0.218 |  | 45.5306 | 9.3165 |  | 99.5728 | 0.1298
| 78.0561 | 0.8729 |  | 1273.321 | 0.1951 |  | 46.4412 | 8.6943 |  | 101.5642 | 0.125
| 79.6172 | 0.8339 |  | 1359.792 | 0.1768 |  | 47.3701 | 8.1295 |  | 103.5955 | 0.1204
| 81.2095 | 0.7968 |  | 1458.206 | 0.1601 |  | 48.3175 | 7.6148 |  | 105.6674 | 0.116
| 82.8337 | 0.7616 |  | 1596.742 | 0.1418 |  | 49.2838 | 7.1442 |  | 107.7808 | 0.1118
| 84.4904 | 0.7281 |  | 1702.807 | 0.1309 |  | 50.2695 | 6.7126 |  | 109.9364 | 0.1077
| 86.1802 | 0.6963 |  | 1830.54 | 0.1202 |  | 51.2749 | 6.3157 |  | 112.1351 | 0.1038
| 87.9038 | 0.666 |  | 2002.211 | 0.1091 |  | 52.3004 | 5.9497 |  | 114.3778 | 0.1001
| 89.6619 | 0.6371 |  | 2167.368 | 0.1009 |  | 53.3464 | 5.6113 |  | 116.6654 | 0.0965
| 91.4551 | 0.6096 |  | 2380.654 | 0.0927 |  | 54.4133 | 5.2978 |  | 118.9987 | 0.093
| 93.2842 | 0.5834 |  | 2678.413 | 0.0845 |  | 55.5016 | 5.0069 |  | 121.3786 | 0.0897
| 95.1499 | 0.5585 |  | 2982.149 | 0.0785 |  | 56.6116 | 4.7362 |  | 123.8062 | 0.0866
| 97.0529 | 0.5347 |  | 3365.653 | 0.0732 |  | 57.7438 | 4.484 |  | 126.2823 | 0.0835
| 98.9939 | 0.512 |  | 3727.834 | 0.0696 |  | 58.8987 | 4.2487 |  | 128.808 | 0.0806
| 100.9738 | 0.4903 |  | 4070.956 | 0.0671 |  | 60.0767 | 4.0286 |  | 131.3841 | 0.0778
| 102.9933 | 0.4697 |  | 4488.262 | 0.0648 |  | 61.2782 | 3.8227 |  | 134.0118 | 0.0751
| 105.0532 | 0.4499 |  | 4966.435 | 0.0628 |  | 62.5038 | 3.6297 |  | 136.6921 | 0.0725
| 107.1542 | 0.4311 |  | 5490.34 | 0.0612 |  | 63.7539 | 3.4485 |  | 139.4259 | 0.07
| 109.2973 | 0.4131 |  | 5900.064 | 0.0602 |  | 65.0289 | 3.2782 |  | 142.2144 | 0.0676
| 111.4833 | 0.3959 |  | 6750.729 | 0.059 |  | 66.3295 | 3.1181 |  | 145.0587 | 0.0653
| 113.7129 | 0.3795 |  | 7443.027 | 0.0583 |  | 67.6561 | 2.9673 |  | 147.9599 | 0.0632
| 115.9872 | 0.3638 |  | 7948.483 | 0.0579 |  | 69.0092 | 2.8251 |  | 150.9191 | 0.0611
| 118.3069 | 0.3487 |  | 8640.099 | 0.0574 |  | 70.3894 | 2.6909 |  | 153.9375 | 0.0593
| 120.6731 | 0.3344 |  | 9904.958 | 0.0568 |  | 71.7972 | 2.5643 |  | 157.0162 | 0.0577
| 123.0865 | 0.3206 |  | 11155.44 | 0.0564 |  | 73.2331 | 2.4445 |  | 160.1565 | 0.0562
| 125.5483 | 0.3075 | 30Main | 33.66 | 101.5883 |  | 74.6978 | 2.3313 |  | 163.3597 | 0.0547
| 128.0592 | 0.2949 |  | 34.3332 | 32.8902 |  | 76.1918 | 2.2241 |  | 166.6269 | 0.0533
| 130.6204 | 0.2829 |  | 34.7 | 23.9453 |  | 77.7156 | 2.1226 |  | 169.9594 | 0.0519
| 133.2328 | 0.2713 |  | 35.0199 | 19.3218 |  | 79.2699 | 2.0263 |  | 173.3586 | 0.0506
| 135.8975 | 0.2603 |  | 35.4 | 15.6891 |  | 80.8553 | 1.935 |  | 176.8258 | 0.0493
| 138.6154 | 0.2497 |  | 35.7203 | 13.5272 |  | 82.4724 | 1.8484 |  | 180.3623 | 0.0481
| 141.3877 | 0.2396 |  | 36.1 | 11.6131 |  | 84.1219 | 1.7661 |  | 183.9695 | 0.047
| 144.2155 | 0.2299 |  | 36.4347 | 10.3153 |  | 85.8043 | 1.688 |  | 187.6489 | 0.0458
| 147.0998 | 0.2206 |  | 36.8 | 9.1851 |  | 87.5204 | 1.6137 |  | 191.4019 | 0.0448
| 150.0418 | 0.2117 |  | 37.1634 | 8.2753 |  | 89.2708 | 1.543 |  | 195.2299 | 0.0437
| 153.0426 | 0.2032 |  | 37.5 | 7.5744 |  | 91.0562 | 1.4758 |  | 199.1345 | 0.0427
| 156.1035 | 0.195 |  | 37.9066 | 6.8658 |  | 92.8773 | 1.4118 |  | 203.1172 | 0.0418
| 159.2256 | 0.1872 |  | 38.3 | 6.2911 |  | 94.7349 | 1.3508 |  | 207.1796 | 0.0408
| 162.4101 | 0.1797 |  | 38.6648 | 5.8343 |  | 96.6296 | 1.2927 |  | 211.3231 | 0.0399
| 165.6583 | 0.1725 |  | 39.1 | 5.3652 |  | 98.5622 | 1.2374 |  | 215.5496 | 0.0391
| 168.9714 | 0.1656 |  | 39.4381 | 5.0472 |  | 100.5334 | 1.1846 |  | 219.8606 | 0.0383
| 172.3509 | 0.159 |  | 39.8 | 4.7439 |  | 102.5441 | 1.1343 |  | 224.2578 | 0.0375
| 175.7979 | 0.1526 |  | 40.2268 | 4.4273 |  | 104.595 | 1.0863 |  | 228.743 | 0.0367
| 179.3138 | 0.1466 |  | 41.0314 | 3.9269 |  | 106.6869 | 1.0405 |  | 233.3178 | 0.036
| 182.9001 | 0.1407 |  | 41.852 | 3.5146 |  | 108.8206 | 0.9967 |  | 237.9842 | 0.0353
| 186.5581 | 0.1351 |  | 42.689 | 3.1694 |  | 110.997 | 0.955 |  | 242.7439 | 0.0346
| 190.2893 | 0.1298 |  | 43.5428 | 2.8763 |  | 113.2169 | 0.9151 |  | 247.5987 | 0.0339
| 194.0951 | 0.1246 |  | 44.4137 | 2.6246 |  | 115.4813 | 0.877 |  | 252.5507 | 0.0333
| 197.977 | 0.1197 |  | 45.3019 | 2.4062 |  | 117.7909 | 0.8406 |  | 257.6017 | 0.0327
| 201.9365 | 0.1149 |  | 46.208 | 2.215 |  | 120.1467 | 0.8057 |  | 262.7538 | 0.0321
| 205.9752 | 0.1104 |  | 47.1321 | 2.0464 |  | 122.5497 | 0.7724 |  | 268.0088 | 0.0315
| 210.0947 | 0.106 |  | 48.0748 | 1.8967 |  | 125.0007 | 0.7406 |  | 273.369 | 0.031
| 214.2966 | 0.1018 |  | 49.0363 | 1.7631 |  | 127.5007 | 0.7102 |  | 278.8364 | 0.0305
| 218.5826 | 0.0978 |  | 50.017 | 1.643 |  | 130.0507 | 0.681 |  | 284.4131 | 0.03
| 222.9542 | 0.0939 |  | 51.0173 | 1.5348 |  | 132.6517 | 0.6532 |  | 290.1014 | 0.0295
| 227.4133 | 0.0902 |  | 52.0377 | 1.4367 |  | 135.3047 | 0.6265 |  | 295.9034 | 0.029
| 231.9616 | 0.0867 |  | 53.0784 | 1.3474 |  | 138.0108 | 0.6009 |  | 301.8215 | 0.0286
| 236.6008 | 0.0832 |  | 54.14 | 1.266 |  | 140.771 | 0.5765 |  | 307.8579 | 0.0282
| 241.3328 | 0.08 |  | 55.2228 | 1.1914 |  | 143.5865 | 0.5531 |  | 314.0151 | 0.0277
| 246.1595 | 0.0768 |  | 56.3273 | 1.1229 |  | 146.4582 | 0.5307 |  | 320.2954 | 0.0273
| 251.0827 | 0.0738 |  | 57.4538 | 1.0598 |  | 149.3874 | 0.5092 |  | 326.7013 | 0.027
| 256.1043 | 0.0709 |  | 58.6029 | 1.0015 |  | 152.3751 | 0.4886 |  | 333.2353 | 0.0266
| 261.2264 | 0.0681 |  | 59.7749 | 0.9476 |  | 155.4226 | 0.4689 |  | 339.9 | 0.0262
| 266.4509 | 0.0654 |  | 60.9704 | 0.8976 |  | 158.5311 | 0.45 |  | 346.698 | 0.0259
| 271.7799 | 0.0629 |  | 62.1898 | 0.8512 |  | 161.7017 | 0.4319 |  | 353.632 | 0.0256
| 277.2155 | 0.0604 |  | 63.4336 | 0.8079 |  | 164.9357 | 0.4146 |  | 360.7046 | 0.0252
| 282.7599 | 0.058 |  | 64.7023 | 0.7676 |  | 168.2344 | 0.3979 |  | 367.9187 | 0.0249
| 288.4151 | 0.0557 |  | 65.9964 | 0.7299 |  | 171.5991 | 0.382 |  | 375.2771 | 0.0246
| 294.1834 | 0.0536 |  | 67.3163 | 0.6947 |  | 175.0311 | 0.3667 |  | 382.7826 | 0.0244
| 300.067 | 0.0516 |  | 68.6626 | 0.6617 |  | 178.5317 | 0.3521 |  | 390.4383 | 0.0241
| 306.0684 | 0.05 |  | 70.0359 | 0.6307 |  | 182.1024 | 0.338 |  | 398.2471 | 0.0238
| 312.1897 | 0.0484 |  | 71.4366 | 0.6017 |  | 185.7444 | 0.3245 |  | 406.212 | 0.0236
| 318.4335 | 0.0469 |  | 72.8653 | 0.5743 |  | 189.4593 | 0.3116 |  | 414.3362 | 0.0233
| 324.8022 | 0.0455 |  | 74.3226 | 0.5486 |  | 193.2485 | 0.2992 |  | 422.623 | 0.0231
| 331.2982 | 0.0441 |  | 75.8091 | 0.5244 |  | 197.1134 | 0.2873 |  | 431.0754 | 0.0229
| 337.9242 | 0.0428 |  | 77.3252 | 0.5015 |  | 201.0557 | 0.2759 |  | 439.6969 | 0.0227
| 344.6827 | 0.0415 |  | 78.8718 | 0.4799 |  | 205.0768 | 0.2649 |  | 448.4909 | 0.0224
| 351.5763 | 0.0402 |  | 80.4492 | 0.4595 |  | 209.1784 | 0.2544 |  | 457.4607 | 0.0222
| 358.6079 | 0.0391 |  | 82.0582 | 0.4402 |  | 213.3619 | 0.2444 |  | 466.6099 | 0.022
| 365.78 | 0.0379 |  | 83.6993 | 0.422 |  | 217.6292 | 0.2347 |  | 475.9421 | 0.0219
| 373.0956 | 0.0368 |  | 85.3733 | 0.4047 |  | 221.9818 | 0.2254 |  | 485.4609 | 0.0217
| 380.5575 | 0.0358 |  | 87.0808 | 0.3884 |  | 226.4214 | 0.2165 |  | 495.1702 | 0.0215
| 388.1687 | 0.0348 |  | 88.8224 | 0.3728 |  | 230.9498 | 0.2079 |  | 505.0736 | 0.0213
| 395.9321 | 0.0338 |  | 90.5989 | 0.3581 |  | 235.5688 | 0.1997 |  | 515.175 | 0.0212
| 403.8507 | 0.0329 |  | 92.4108 | 0.3441 |  | 240.2802 | 0.1919 |  | 525.4785 | 0.021
| 411.9277 | 0.032 |  | 94.259 | 0.3309 |  | 245.0858 | 0.1843 |  | 535.9881 | 0.0209
| 420.1663 | 0.0311 |  | 96.1442 | 0.3182 |  | 249.9875 | 0.177 |  | 546.7079 | 0.0207
| 428.5696 | 0.0303 |  | 98.0671 | 0.3063 |  | 254.9873 | 0.1701 |  | 557.642 | 0.0206
| 437.141 | 0.0295 |  | 100.0285 | 0.2948 |  | 260.087 | 0.1634 |  | 568.7949 | 0.0205
| 445.8838 | 0.0288 |  | 102.029 | 0.284 |  | 265.2887 | 0.1569 |  | 580.1708 | 0.0203
| 454.8015 | 0.028 |  | 104.0696 | 0.2736 |  | 270.5945 | 0.1508 |  | 591.7742 | 0.0202
| 463.8975 | 0.0273 |  | 106.151 | 0.2638 |  | 276.0064 | 0.1448 |  | 603.6097 | 0.0201
| 473.1755 | 0.0267 |  | 108.274 | 0.2544 |  | 281.5265 | 0.1392 |  | 613.254 | 0.016
| 482.639 | 0.026 |  | 110.4395 | 0.2455 |  | 287.1571 | 0.1337 |  | 625.519 | 0.016
| 492.2918 | 0.0254 |  | 112.6483 | 0.2372 |  | 292.9002 | 0.1284 |  | 638.0294 | 0.016
| 502.1376 | 0.0248 |  | 114.9013 | 0.2296 |  | 298.7582 | 0.1234 |  | 650.79 | 0.016
| 512.1803 | 0.0242 |  | 117.1993 | 0.2223 |  | 304.7334 | 0.1186 |  | 663.8058 | 0.016
| 522.4239 | 0.0237 |  | 119.5433 | 0.2153 |  | 310.828 | 0.1139 |  | 677.0819 | 0.016
| 532.8724 | 0.0231 |  | 121.9341 | 0.2086 |  | 317.0446 | 0.1095 |  | 690.6236 | 0.016
| 543.5299 | 0.0226 |  | 124.3728 | 0.2023 |  | 323.3855 | 0.1052 |  | 704.436 | 0.016
| 554.4005 | 0.0221 |  | 126.8603 | 0.1962 |  | 329.8532 | 0.1011 |  | 718.5248 | 0.016
| 565.4885 | 0.0217 |  | 129.3975 | 0.1903 |  | 336.4503 | 0.0971 |  | 732.8953 | 0.016
| 576.7983 | 0.0212 |  | 131.9854 | 0.1847 |  | 343.1793 | 0.0933 |  | 747.5532 | 0.016
| 588.3342 | 0.0208 |  | 134.6251 | 0.1794 |  | 350.0429 | 0.0896 |  | 762.5042 | 0.016
| 600.1009 | 0.0203 |  | 137.3176 | 0.1743 |  | 357.0437 | 0.0861 |  | 777.7543 | 0.016
| 610.3081 | 0.016 |  | 140.064 | 0.1694 |  | 364.1846 | 0.0828 |  | 793.3094 | 0.016
| 622.5143 | 0.016 |  | 142.8653 | 0.1647 |  | 371.4683 | 0.0795 |  | 809.1756 | 0.016
| 634.9646 | 0.016 |  | 145.7226 | 0.1602 |  | 378.8977 | 0.0764 |  | 825.3591 | 0.016
| 647.6639 | 0.016 |  | 148.637 | 0.1559 |  | 386.4756 | 0.0734 |  | 841.8663 | 0.016
| 660.6171 | 0.016 |  | 151.6098 | 0.1518 |  | 394.2051 | 0.0706 |  | 858.7036 | 0.016
| 673.8295 | 0.016 |  | 154.642 | 0.1479 |  | 402.0892 | 0.0678 |  | 875.8777 | 0.016
| 687.3061 | 0.016 |  | 157.7348 | 0.1441 |  | 410.131 | 0.0652 |  | 893.3952 | 0.016
| 701.0522 | 0.016 |  | 160.8895 | 0.1405 |  | 418.3336 | 0.0626 |  | 911.2631 | 0.016
| 715.0732 | 0.016 |  | 164.1073 | 0.137 |  | 426.7003 | 0.0602 |  | 929.4884 | 0.016
| 729.3747 | 0.016 |  | 167.3894 | 0.1336 |  | 435.2343 | 0.0578 |  | 948.0782 | 0.016
| 743.9622 | 0.016 |  | 170.7372 | 0.1305 |  | 443.939 | 0.0556 |  | 967.0397 | 0.016
| 758.8414 | 0.016 |  | 174.152 | 0.1274 |  | 452.8178 | 0.0534 |  | 986.3805 | 0.016
| 774.0183 | 0.016 |  | 177.635 | 0.1245 |  | 461.8741 | 0.0515 |  | 1006.1081 | 0.016
| 789.4986 | 0.016 |  | 181.1877 | 0.1217 |  | 471.1116 | 0.0499 |  | 1026.2303 | 0.016
| 805.2886 | 0.016 |  | 184.8115 | 0.119 |  | 480.5338 | 0.0484 |  | 1046.7549 | 0.016
| 821.3944 | 0.016 |  | 188.5077 | 0.1164 |  | 490.1445 | 0.0469 |  | 1067.69 | 0.016
| 837.8223 | 0.016 |  | 192.2778 | 0.1139 |  | 499.9474 | 0.0454 |  | 1089.0438 | 0.016
| 854.5787 | 0.016 |  | 196.1234 | 0.1115 |  | 509.9464 | 0.0441 |  | 1110.8247 | 0.016
| 871.6703 | 0.016 |  | 200.0459 | 0.1092 |  | 520.1453 | 0.0427 |  | 1133.0412 | 0.016
| 889.1037 | 0.016 |  | 204.0468 | 0.107 |  | 530.5482 | 0.0415 |  | 1155.702 | 0.016
| 906.8858 | 0.016 |  | 208.1277 | 0.1049 |  | 541.1591 | 0.0402 |  | 1178.816 | 0.016
| 925.0235 | 0.016 |  | 212.2903 | 0.1029 |  | 551.9823 | 0.0391 |  | 1202.3923 | 0.016
| 943.5239 | 0.016 |  | 216.5361 | 0.101 |  | 563.022 | 0.0379 |  | 1226.4402 | 0.016
| 962.3944 | 0.016 |  | 220.8668 | 0.0991 |  | 574.2824 | 0.0368 |  | 1226.5079 | 0.014
| 981.6423 | 0.016 |  | 225.2841 | 0.0973 |  | 585.7681 | 0.0358 |  | 1251.0381 | 0.014
| 1001.2752 | 0.016 |  | 229.7898 | 0.0956 |  | 597.4834 | 0.0348 |  | 1276.0588 | 0.014
| 1021.3007 | 0.016 |  | 234.3856 | 0.094 |  | 609.4331 | 0.0338 |  | 1301.58 | 0.014
| 1041.7267 | 0.016 |  | 239.0733 | 0.0924 |  | 621.6218 | 0.0329 |  | 1327.6116 | 0.014
| 1062.5612 | 0.016 |  | 243.8548 | 0.0909 |  | 634.0542 | 0.032 |  | 1354.1638 | 0.014
| 1083.8124 | 0.016 |  | 248.7319 | 0.0894 |  | 646.7353 | 0.0312 |  | 1381.2471 | 0.014
| 1105.4887 | 0.016 |  | 253.7065 | 0.088 |  | 659.67 | 0.0303 |  | 1408.8721 | 0.014
| 1127.5985 | 0.016 |  | 258.7807 | 0.0867 |  | 672.8634 | 0.0295 |  | 1437.0495 | 0.014
| 1150.1504 | 0.016 |  | 263.9563 | 0.0854 |  | 686.3207 | 0.0288 |  | 1465.7905 | 0.014
| 1173.1534 | 0.016 |  | 269.2354 | 0.0842 |  | 700.0471 | 0.028 |  | 1495.1063 | 0.014
| 1196.6165 | 0.016 |  | 274.6201 | 0.083 |  | 714.048 | 0.0273 |  | 1525.0084 | 0.014
| 1220.5488 | 0.016 |  | 280.1125 | 0.0818 |  | 728.329 | 0.0267 |  | 1555.5086 | 0.014
| 1220.6162 | 0.014 |  | 285.7147 | 0.0808 |  | 742.8955 | 0.026 |  | 1586.6188 | 0.014
| 1245.0286 | 0.014 |  | 291.429 | 0.0797 |  | 757.7535 | 0.0254 |  | 1618.3512 | 0.014
| 1269.9291 | 0.014 |  | 297.2576 | 0.0787 |  | 772.9085 | 0.0248 |  | 1650.7182 | 0.014
| 1295.3277 | 0.014 |  | 303.2028 | 0.0777 |  | 788.3667 | 0.0242 |  | 1683.7325 | 0.014
| 1321.2343 | 0.014 |  | 309.2668 | 0.0768 |  | 804.134 | 0.0237 |  | 1717.4072 | 0.014
| 1347.659 | 0.014 |  | 315.4522 | 0.0759 |  | 820.2167 | 0.0231 |  | 1751.7553 | 0.014
| 1374.6121 | 0.014 |  | 321.7612 | 0.075 |  | 836.621 | 0.0226 |  | 1786.7904 | 0.014
| 1402.1044 | 0.014 |  | 328.1964 | 0.0742 |  | 853.3535 | 0.0221 |  | 1822.5262 | 0.014
| 1430.1465 | 0.014 |  | 334.7604 | 0.0734 |  | 870.4205 | 0.0217 |  | 1858.9768 | 0.014
| 1458.7494 | 0.014 |  | 341.4556 | 0.0727 |  | 887.8289 | 0.0212 |  | 1896.1563 | 0.014
| 1487.9244 | 0.014 |  | 348.2847 | 0.0719 |  | 905.5855 | 0.0208 |  | 1934.0794 | 0.014
| 1517.6829 | 0.014 |  | 355.2504 | 0.0712 |  | 923.6972 | 0.0204 |  | 1972.761 | 0.014
| 1548.0365 | 0.014 |  | 362.3554 | 0.0706 |  | 940.1758 | 0.016 |  | 2012.2162 | 0.014
| 1578.9973 | 0.014 |  | 369.6025 | 0.0699 |  | 958.9793 | 0.016 |  | 2052.4606 | 0.014
| 1610.5772 | 0.014 |  | 376.9945 | 0.0693 |  | 978.1589 | 0.016 |  | 2093.5098 | 0.014
| 1642.7887 | 0.014 |  | 384.5344 | 0.0687 |  | 997.7221 | 0.016 |  | 2135.38 | 0.014
| 1675.6445 | 0.014 |  | 392.2251 | 0.0681 |  | 1017.6765 | 0.016 |  | 2178.0876 | 0.014
| 1709.1574 | 0.014 |  | 400.0696 | 0.0676 |  | 1038.03 | 0.016 |  | 2221.6493 | 0.014
| 1743.3406 | 0.014 |  | 408.071 | 0.067 |  | 1058.7906 | 0.016 |  | 2266.0823 | 0.014
| 1778.2074 | 0.014 |  | 416.2324 | 0.0665 |  | 1079.9664 | 0.016 |  | 2311.404 | 0.014
| 1813.7715 | 0.014 |  | 424.5571 | 0.066 |  | 1101.5658 | 0.016 |  | 2357.632 | 0.014
| 1850.0469 | 0.014 |  | 433.0482 | 0.0656 |  | 1123.5971 | 0.016 |  | 2404.7847 | 0.014
| 1887.0479 | 0.014 |  | 441.7092 | 0.0651 |  | 1146.069 | 0.016 |  | 2452.8804 | 0.014
| 1924.7888 | 0.014 |  | 450.5434 | 0.0647 |  | 1168.9904 | 0.016 |  | 2501.938 | 0.014
| 1963.2846 | 0.014 |  | 459.5542 | 0.0643 |  | 1192.3702 | 0.016 |  | 2551.9767 | 0.014
| 2002.5503 | 0.014 |  | 468.7453 | 0.0639 |  | 1216.2176 | 0.016 |  | 2603.0163 | 0.014
| 2042.6013 | 0.014 |  | 478.1202 | 0.0635 |  | 1240.542 | 0.016 |  | 2655.0766 | 0.014
| 2083.4533 | 0.014 |  | 487.6826 | 0.0631 |  | 1265.3528 | 0.016 |  | 2708.1781 | 0.014
| 2125.1224 | 0.014 |  | 497.4363 | 0.0628 |  | 1290.6599 | 0.016 |  | 2762.3417 | 0.014
| 2167.6249 | 0.014 |  | 507.385 | 0.0624 |  | 1316.4731 | 0.016 |  | 2817.5885 | 0.014
| 2210.9774 | 0.014 |  | 517.5327 | 0.0621 |  | 1342.8025 | 0.016 |  | 2873.9403 | 0.014
| 2255.1969 | 0.014 |  | 527.8834 | 0.0618 |  | 1369.6586 | 0.016 |  | 2931.4191 | 0.014
| 2300.3008 | 0.014 |  | 538.441 | 0.0615 |  | 1397.0518 | 0.016 |  | 2990.0475 | 0.014
| 2346.3069 | 0.014 |  | 549.2099 | 0.0612 |  | 1424.9928 | 0.016 |  | 3049.8484 | 0.014
| 2393.233 | 0.014 |  | 560.1941 | 0.0609 |  | 1453.4926 | 0.016 |  | 3110.8454 | 0.014
| 2441.0977 | 0.014 |  | 571.3979 | 0.0606 |  | 1482.5625 | 0.016 |  | 3173.0623 | 0.014
| 2489.9196 | 0.014 |  | 582.8259 | 0.0604 |  | 1512.2138 | 0.016 |  | 3236.5236 | 0.014
| 2539.718 | 0.014 |  | 594.4824 | 0.0601 |  | 1542.458 | 0.016 |  | 3301.254 | 0.014
| 2590.5124 | 0.014 |  | 606.3721 | 0.0599 |  | 1573.3072 | 0.016 |  | 3367.2791 | 0.014
| 2642.3226 | 0.014 |  | 618.4995 | 0.0597 |  | 1604.7733 | 0.016 |  | 3434.6247 | 0.014
| 2695.1691 | 0.014 |  | 630.8695 | 0.0595 |  | 1636.8688 | 0.016 |  | 3503.3172 | 0.014
| 2749.0724 | 0.014 |  | 643.4869 | 0.0594 |  | 1669.6062 | 0.016 |  | 3573.3835 | 0.014
| 2804.0539 | 0.014 |  | 656.3566 | 0.0592 |  | 1702.9983 | 0.016 |  | 3644.8512 | 0.014
| 2860.135 | 0.014 |  | 669.4838 | 0.059 |  | 1737.0583 | 0.016 |  | 3717.7482 | 0.014
| 2917.3377 | 0.014 |  | 682.8734 | 0.0589 |  | 1771.7994 | 0.016 |  | 3792.1032 | 0.014
| 2975.6844 | 0.014 |  | 696.5309 | 0.0587 |  | 1807.2354 | 0.016 |  | 3867.9453 | 0.014
| 3035.1981 | 0.014 |  | 710.4615 | 0.0586 |  | 1843.3801 | 0.016 |  | 3945.3042 | 0.014
| 3095.9021 | 0.014 |  | 724.6708 | 0.0584 |  | 1880.2477 | 0.016 |  | 4024.2102 | 0.014
| 3157.8201 | 0.014 |  | 739.1642 | 0.0583 |  | 1880.3516 | 0.014 |  | 4104.6945 | 0.014
| 3220.9765 | 0.014 |  | 753.9475 | 0.0582 |  | 1917.9586 | 0.014 |  | 4186.7883 | 0.014
| 3285.3961 | 0.014 |  | 769.0264 | 0.058 |  | 1956.3178 | 0.014 |  | 4270.5241 | 0.014
| 3351.104 | 0.014 |  | 784.4069 | 0.0579 |  | 1995.4441 | 0.014 |  | 4355.9346 | 0.014
| 3418.1261 | 0.014 |  | 800.0951 | 0.0578 |  | 2035.353 | 0.014 |  | 4443.0533 | 0.014
| 3486.4886 | 0.014 |  | 816.097 | 0.0577 |  | 2076.0601 | 0.014 |  | 4531.9143 | 0.014
| 3556.2183 | 0.014 |  | 832.4189 | 0.0576 |  | 2117.5813 | 0.014 |  | 4622.5526 | 0.014
| 3627.3427 | 0.014 |  | 849.0673 | 0.0575 |  | 2159.9329 | 0.014 |  | 4715.0037 | 0.014
| 3699.8896 | 0.014 |  | 866.0486 | 0.0574 |  | 2203.1316 | 0.014 |  | 4809.3038 | 0.014
| 3773.8874 | 0.014 |  | 883.3696 | 0.0573 |  | 2247.1942 | 0.014 |  | 4905.4898 | 0.014
| 3849.3651 | 0.014 |  | 901.037 | 0.0572 |  | 2292.1381 | 0.014 |  | 5003.5996 | 0.014
| 3926.3524 | 0.014 |  | 919.0577 | 0.0571 |  | 2337.9808 | 0.014 |  | 5103.6716 | 0.014
| 4004.8795 | 0.014 |  | 937.4389 | 0.0571 |  | 2384.7404 | 0.014 |  | 5205.7451 | 0.014
| 4084.977 | 0.014 |  | 956.1877 | 0.057 |  | 2432.4353 | 0.014 |  | 5309.86 | 0.014
| 4166.6766 | 0.014 |  | 975.3114 | 0.0569 |  | 2481.084 | 0.014 |  | 5416.0572 | 0.014
| 4250.0101 | 0.014 |  | 994.8177 | 0.0568 |  | 2530.7056 | 0.014 |  | 5524.3783 | 0.014
| 4335.0103 | 0.014 |  | 1014.714 | 0.0567 |  | 2581.3198 | 0.014 |  | 5634.8659 | 0.014
| 4421.7105 | 0.014 |  | 1035.0083 | 0.0567 |  | 2632.9461 | 0.014 |  | 5747.5632 | 0.014
| 4510.1447 | 0.014 |  | 1055.7085 | 0.0566 |  | 2685.6051 | 0.014 |  | 5862.5144 | 0.014
| 4600.3476 | 0.014 |  | 1076.8226 | 0.0566 |  | 2739.3172 | 0.014 |  | 5979.7647 | 0.014
| 4692.3546 | 0.014 |  | 1098.3591 | 0.0565 |  | 2794.1035 | 0.014 |  | 6099.36 | 0.014
| 4786.2017 | 0.014 |  | 1120.3263 | 0.0564 |  | 2849.9856 | 0.014 |  | 6221.3472 | 0.014
| 4881.9257 | 0.014 |  | 1142.7328 | 0.0564 |  | 2906.9853 | 0.014 |  | 6345.7742 | 0.014
| 4979.5642 | 0.014 |  | 1165.5874 | 0.0563 |  | 2965.125 | 0.014 |  | 6472.6897 | 0.014
| 5079.1555 | 0.014 |  | 1188.8992 | 0.0563 |  | 3024.4275 | 0.014 |  | 6602.1435 | 0.014
| 5180.7386 | 0.014 |  | 1212.6772 | 0.0562 |  | 3084.9161 | 0.014 |  | 6734.1863 | 0.014
| 5284.3534 | 0.014 |  | 1236.9307 | 0.0562 |  | 3146.6144 | 0.014 |  | 6868.8701 | 0.014
| 5390.0405 | 0.014 |  | 1261.6693 | 0.0561 |  | 3209.5467 | 0.014 |  | 7006.2475 | 0.014
| 5497.8413 | 0.014 |  | 1286.9027 | 0.0561 |  | 3273.7376 | 0.014 |  | 7146.3724 | 0.014
| 5607.7981 | 0.014 |  | 1312.6408 | 0.056 |  | 3339.2123 | 0.014 |  | 7289.2998 | 0.014
| 5719.9541 | 0.014 |  | 1338.8936 | 0.056 |  | 3405.9966 | 0.014 |  | 7435.0858 | 0.014
| 5834.3531 | 0.014 |  | 1365.6715 | 0.056 |  | 3474.1165 | 0.014 |  | 7583.7876 | 0.014
| 5951.0402 | 0.014 |  | 1392.9849 | 0.0559 |  | 3543.5989 | 0.014 |  | 7735.4633 | 0.014
| 6070.061 | 0.014 |  | 1420.8446 | 0.0559 |  | 3614.4708 | 0.014 |  | 7890.1726 | 0.014
| 6191.4622 | 0.014 |  | 1449.2615 | 0.0559 |  | 3686.7603 | 0.014 |  | 8047.976 | 0.014
| 6315.2915 | 0.014 |  | 1478.2467 | 0.0558 |  | 3760.4955 | 0.014 |  | 8208.9356 | 0.014
| 6441.5973 | 0.014 |  | 1507.8116 | 0.0558 |  | 3835.7054 | 0.014 |  | 8373.1143 | 0.014
| 6570.4292 | 0.014 |  | 1537.9679 | 0.0558 |  | 3912.4195 | 0.014 |  | 8540.5765 | 0.014
| 6701.8378 | 0.014 |  | 1568.7272 | 0.0557 |  | 3990.6679 | 0.014 |  | 8711.3881 | 0.014
| 6835.8746 | 0.014 |  | 1600.1018 | 0.0557 |  | 4070.4812 | 0.014 |  | 8885.6158 | 0.014
| 6972.5921 | 0.014 |  | 1632.1038 | 0.0557 |  | 4151.8908 | 0.014 |  | 9063.3282 | 0.014
| 7112.0439 | 0.014 |  | 1664.7459 | 0.0556 |  | 4234.9287 | 0.014 |  | 9244.5947 | 0.014
| 7254.2848 | 0.014 |  | 1698.0408 | 0.0556 |  | 4319.6272 | 0.014 |  | 9429.4866 | 0.014
| 7399.3705 | 0.014 |  | 1732.0016 | 0.0556 |  | 4406.0198 | 0.014 |  | 9618.0763 | 0.014
| 7547.3579 | 0.014 |  | 1766.6416 | 0.0556 |  | 4494.1402 | 0.014 |  | 9810.4379 | 0.014
| 7698.3051 | 0.014 |  | 1801.9745 | 0.0556 |  | 4584.023 | 0.014 |  | 10006.6466 | 0.014
| 7852.2712 | 0.014 |  | 1838.014 | 0.0555 |  | 4675.7034 | 0.014 |  | 10206.7796 | 0.014
| 8009.3166 | 0.014 |  | 1874.7742 | 0.0555 |  | 4769.2175 | 0.014 |  | 10410.9152 | 0.014
| 8169.5029 | 0.014 |  | 1912.2697 | 0.0555 |  | 4864.6019 | 0.014 |  | 10619.1335 | 0.014
| 8332.893 | 0.014 |  | 1950.5151 | 0.0555 |  | 4961.8939 | 0.014 |  | 10831.5161 | 0.014
| 8499.5508 | 0.014 |  | 1989.5254 | 0.0555 |  | 5061.1318 | 0.014 |  | 11048.1465 | 0.014
| 8669.5419 | 0.014 |  | 2029.3159 | 0.0554 |  | 5162.3544 | 0.014 |  | 11269.1094 | 0.014
| 8842.9327 | 0.014 |  | 2069.9023 | 0.0554 |  | 5265.6015 | 0.014 |  | 11494.4916 | 0.014
| 9019.7913 | 0.014 |  | 2111.3003 | 0.0554 |  | 5370.9135 | 0.014 |  | 11724.3814 | 0.014
| 9200.1872 | 0.014 |  | 2153.5263 | 0.0554 |  | 5478.3318 | 0.014 |  | 11958.869 | 0.014
| 9384.1909 | 0.014 |  | 2196.5968 | 0.0554 |  | 5587.8984 | 0.014 | 250Tap | 281.3844 | 80.6087
| 9571.8747 | 0.014 |  | 2240.5288 | 0.0554 |  | 5699.6564 | 0.014 |  | 287.3002 | 30.2473
| 9763.3122 | 0.014 |  | 2285.3393 | 0.0553 |  | 5813.6495 | 0.014 |  | 290.9 | 21.8265
| 9958.5785 | 0.014 |  | 2331.0461 | 0.0553 |  | 5929.9225 | 0.014 |  | 294.5624 | 16.9673
| 10157.75 | 0.014 |  | 2377.6671 | 0.0553 |  | 6048.521 | 0.014 |  | 298.3 | 13.7975
| 10360.905 | 0.014 |  | 2425.2204 | 0.0553 |  | 6169.4914 | 0.014 |  | 302.0083 | 11.6198
| 10568.1231 | 0.014 |  | 2473.7248 | 0.0553 |  | 6292.8812 | 0.014 |  | 306.6 | 9.7008
| 10779.4856 | 0.014 |  | 2523.1993 | 0.0553 |  | 6418.7388 | 0.014 |  | 311.2571 | 8.293
| 10995.0753 | 0.014 |  | 2573.6633 | 0.0553 |  | 6547.1136 | 0.014 |  | 316.9 | 7.0374
| 11214.9768 | 0.014 |  | 2625.1366 | 0.0553 |  | 6678.0559 | 0.014 |  | 322.4617 | 6.1111
| 11439.2764 | 0.014 |  | 2677.6393 | 0.0553 |  | 6811.617 | 0.014 |  | 329.8 | 5.1932
| 11668.0619 | 0.014 |  | 2731.1921 | 0.0552 |  | 6947.8493 | 0.014 |  | 337.2127 | 4.4972
| 11901.4231 | 0.014 |  | 2785.8159 | 0.0552 |  | 7086.8063 | 0.014 |  | 355.2142 | 3.3653
150E | 402.7199 | 1615.3968 |  | 2841.5322 | 0.0552 |  | 7228.5425 | 0.014 |  | 373.0111 | 2.6707
| 405.1432 | 274.4061 |  | 2898.3629 | 0.0552 |  | 7373.1133 | 0.014 |  | 395.3851 | 2.0996
| 409.2154 | 114.0414 |  | 2956.3301 | 0.0552 |  | 7520.5756 | 0.014 |  | 424.3635 | 1.6237
| 410.4 | 97.3796 |  | 3015.4567 | 0.0552 |  | 7670.9871 | 0.014 |  | 449.3489 | 1.3458
| 411.6783 | 84.0833 |  | 3075.7659 | 0.0552 |  | 7824.4068 | 0.014 |  | 483.2883 | 1.08
| 413.1 | 72.9664 |  | 3137.2812 | 0.0552 |  | 7980.895 | 0.014 |  | 524.6791 | 0.8588
| 414.5702 | 64.163 |  | 3200.0268 | 0.0552 |  | 8140.5129 | 0.014 |  | 573.7776 | 0.6808
| 416.2 | 56.5687 |  | 3264.0273 | 0.0552 |  | 8303.3231 | 0.014 |  | 624.8649 | 0.5525
| 417.8999 | 50.3306 |  | 3329.3079 | 0.0552 |  | 8469.3896 | 0.014 |  | 669.2697 | 0.4703
| 420 | 44.2716 |  | 3395.8941 | 0.0552 |  | 8638.7774 | 0.014 |  | 709.4021 | 0.412
| 422.0997 | 39.4943 |  | 3463.8119 | 0.0552 |  | 8811.5529 | 0.014 |  | 771.7732 | 0.342
| 425.5 | 33.5866 |  | 3533.0882 | 0.0551 |  | 8987.784 | 0.014 |  | 837.8711 | 0.2868
| 428.9076 | 29.1776 |  | 3603.7499 | 0.0551 |  | 9167.5397 | 0.014 |  | 913.775 | 0.2394
| 431.7 | 26.3252 |  | 3675.8249 | 0.0551 |  | 9350.8905 | 0.014 |  | 987.863 | 0.2042
| 434.5198 | 23.9459 |  | 3749.3414 | 0.0551 |  | 9537.9083 | 0.014 |  | 1090.524 | 0.1677
| 439.1 | 20.8576 |  | 3824.3283 | 0.0551 |  | 9728.6664 | 0.014 |  | 1177.78 | 0.1444
| 443.7411 | 18.4245 |  | 3900.8148 | 0.0551 |  | 9923.2398 | 0.014 |  | 1281.313 | 0.1229
| 449.4 | 16.1067 |  | 3978.8311 | 0.0551 |  | 10121.7046 | 0.014 |  | 1427.698 | 0.1003
| 454.9743 | 14.3111 |  | 4058.4077 | 0.0551 |  | 10324.1386 | 0.014 |  | 1610.788 | 0.0805
| 459.8 | 13.0382 |  | 4139.5759 | 0.0551 |  | 10530.6214 | 0.014 |  | 1789.222 | 0.0668
| 464.6301 | 11.9621 |  | 4222.3674 | 0.0551 |  | 10741.2338 | 0.014 |  | 2018.674 | 0.0555
| 470.5 | 10.8602 |  | 4306.8148 | 0.0551 |  | 10956.0585 | 0.014 |  | 2232.982 | 0.0487
| 476.3924 | 9.9303 |  | 4392.9511 | 0.0551 |  | 11175.1797 | 0.014 |  | 2477.76 | 0.0429
| 484.4 | 8.8818 |  | 4480.8101 | 0.0551 |  | 11398.6833 | 0.014 |  | 2725 | 0.0386
| 492.3754 | 8.0239 |  | 4570.4263 | 0.0551 |  | 11626.657 | 0.014 |  | 2957.027 | 0.0355
| 516.5853 | 6.1586 |  | 4661.8348 | 0.0551 |  | 11859.1901 | 0.014 |  | 3257.371 | 0.0323
| 549.0782 | 4.6322 |  | 4755.0715 | 0.0551 | 140T | 336.6 | 788.682 |  | 3690.424 | 0.0291
| 593.0276 | 3.4078 |  | 4850.1729 | 0.0551 |  | 343.332 | 255.3629 |  | 4142.09 | 0.0267
| 640.4948 | 2.6047 |  | 4947.1764 | 0.0551 |  | 346.8 | 188.7308 |  | 4615.307 | 0.0249
| 701.514 | 1.959 |  | 5046.1199 | 0.0551 |  | 350.1986 | 150.0244 |  | 5311.115 | 0.023
| 757.6646 | 1.5697 |  | 5147.0423 | 0.0551 |  | 353.7 | 123.6633 |  | 6143.693 | 0.0216
| 818.3098 | 1.2743 |  | 5249.9832 | 0.0551 |  | 357.2026 | 105.0354 |  | 6866.981 | 0.0207
| 889.1278 | 1.0292 |  | 5354.9828 | 0.0551 |  | 360.8 | 90.8533 |  | 8116.2053 | 0.016
| 975.7836 | 0.8188 |  | 5462.0825 | 0.0551 |  | 364.3467 | 80.0956 |  | 10435.1211 | 0.016
| 1066.6106 | 0.6631 |  | 5571.3241 | 0.0551 |  | 368 | 71.3193 | 25Tap | 28.56 | 46.5309
| 1176.428 | 0.5295 |  | 5682.7506 | 0.0551 |  | 371.6336 | 64.2541 |  | 28.8 | 32.4353
| 1326.413 | 0.4051 |  | 5796.4056 | 0.0551 |  | 375.3 | 58.3679 |  | 29.1312 | 22.8071
| 1471.789 | 0.3229 |  | 5912.3337 | 0.0551 |  | 379.0663 | 53.3067 |  | 29.4 | 18.3428
| 1686.212 | 0.2413 |  | 6030.5804 | 0.055 |  | 382.9 | 48.9472 |  | 29.7138 | 14.9035
| 1859.825 | 0.1963 |  | 6151.192 | 0.055 |  | 386.6476 | 45.2938 |  | 30 | 12.7088
| 2047.221 | 0.1606 |  | 6274.2159 | 0.055 |  | 390.5 | 42.0396 |  | 30.3081 | 11.109
| 2262.524 | 0.1305 |  | 6399.7002 | 0.055 |  | 394.3805 | 39.1787 |  | 30.6 | 9.916
| 2545.895 | 0.1024 |  | 6527.6942 | 0.055 |  | 398.3 | 36.638 |  | 30.9143 | 8.8803
| 2905.144 | 0.0782 |  | 6658.2481 | 0.055 |  | 402.2682 | 34.3618 |  | 31.2 | 8.104
| 3217.104 | 0.0635 |  | 6791.413 | 0.055 |  | 410.3135 | 30.4716 |  | 31.5325 | 7.3497
| 3584.009 | 0.0512 |  | 6927.2413 | 0.055 |  | 418.5198 | 27.2664 |  | 31.8 | 6.8338
| 3937.252 | 0.0441 |  | 7065.7861 | 0.055 |  | 426.8902 | 24.5817 |  | 32.1632 | 6.2343
| 4338.301 | 0.038 |  | 7207.1018 | 0.055 |  | 435.428 | 22.3015 |  | 32.5 | 5.7611
| 4684.1 | 0.034 |  | 7351.2439 | 0.055 |  | 444.1366 | 20.3423 |  | 32.8065 | 5.3859
| 5064.08 | 0.0305 |  | 7498.2688 | 0.055 |  | 453.0193 | 18.6418 |  | 33.1 | 5.0673
| 5613.49 | 0.0267 |  | 7648.2341 | 0.055 |  | 462.0797 | 17.1529 |  | 33.4626 | 4.7193
| 6074.94 | 0.0243 |  | 7801.1988 | 0.055 |  | 471.3213 | 15.8394 |  | 34.1318 | 4.1821
| 6574.33 | 0.0222 |  | 7957.2228 | 0.055 |  | 480.7477 | 14.6727 |  | 34.8145 | 3.7401
| 7079.28 | 0.0205 |  | 8116.3672 | 0.055 |  | 490.3626 | 13.6302 |  | 35.5108 | 3.3705
| 7577.42 | 0.016 |  | 8278.6946 | 0.055 |  | 500.1699 | 12.6937 |  | 36.221 | 3.0569
| 7769.24 | 0.016 |  | 8444.2685 | 0.055 |  | 510.1733 | 11.8485 |  | 36.9454 | 2.7877
| 8154.6191 | 0.016 |  | 8613.1539 | 0.055 |  | 520.3768 | 11.0822 |  | 37.6843 | 2.5542
| 9173.9465 | 0.016 |  | 8785.4169 | 0.055 |  | 530.7843 | 10.3849 |  | 38.438 | 2.35
| 10193.2739 | 0.016 |  | 8961.1253 | 0.055 |  | 541.4 | 9.748 |  | 39.2068 | 2.1699
| 11416.4668 | 0.016 |  | 9140.3478 | 0.055 |  | 552.228 | 9.1644 |  | 39.9909 | 2.01
15E | 33.66 | 279.2439 |  | 9323.1547 | 0.055 |  | 563.2725 | 8.628 |  | 40.7907 | 1.8673
| 34.3332 | 90.3242 |  | 9509.6178 | 0.055 |  | 574.538 | 8.1338 |  | 41.6065 | 1.7391
| 34.7 | 65.7258 |  | 9699.8102 | 0.055 |  | 586.0287 | 7.6771 |  | 42.4387 | 1.6234
| 35.0199 | 53.0111 |  | 9893.8064 | 0.055 |  | 597.7493 | 7.2542 |  | 43.2874 | 1.5186
| 35.4 | 43.0212 |  | 10091.6825 | 0.055 |  | 609.7043 | 6.8617 |  | 44.1532 | 1.4233
| 35.7203 | 37.0762 |  | 10293.5162 | 0.055 |  | 621.8984 | 6.4967 |  | 45.0362 | 1.3362
| 36.1 | 31.8123 |  | 10499.3865 | 0.055 |  | 634.3364 | 6.1567 |  | 45.937 | 1.2565
| 36.4347 | 28.2433 |  | 10709.3742 | 0.055 |  | 647.0231 | 5.8394 |  | 46.8557 | 1.1832
| 36.8 | 25.1353 |  | 10923.5617 | 0.055 |  | 659.9636 | 5.5427 |  | 47.7928 | 1.1157
| 37.1634 | 22.6334 |  | 11142.0329 | 0.055 |  | 673.1628 | 5.265 |  | 48.7487 | 1.0533
| 37.5 | 20.7059 |  | 11364.8736 | 0.055 |  | 686.6261 | 5.0046 |  | 49.7237 | 0.9956
| 37.9066 | 18.7572 |  | 11592.1711 | 0.055 |  | 700.3586 | 4.7602 |  | 50.7181 | 0.942
| 38.3 | 17.1767 |  | 11824.0145 | 0.055 |  | 714.3658 | 4.5304 |  | 51.7325 | 0.8922
| 38.6648 | 15.9205 | 350Main | 389.8147 | 419.5977 |  | 728.6531 | 4.3142 |  | 52.7671 | 0.8458
| 39.1 | 14.6304 |  | 392.2666 | 114.681 |  | 743.2262 | 4.1105 |  | 53.8225 | 0.8025
| 39.4381 | 13.756 |  | 398.0493 | 42.004 |  | 758.0907 | 3.9184 |  | 54.8989 | 0.7621
| 39.8 | 12.9218 |  | 403.5 | 26.1702 |  | 773.2525 | 3.737 |  | 55.9969 | 0.7242
| 40.2268 | 12.0514 |  | 409.013 | 18.8821 |  | 788.7175 | 3.5657 |  | 57.1168 | 0.6887
| 41.0314 | 10.6752 |  | 412.2 | 16.2421 |  | 804.4919 | 3.4036 |  | 58.2592 | 0.6553
| 41.852 | 9.5415 |  | 415.4755 | 14.1888 |  | 820.5817 | 3.2502 |  | 59.4244 | 0.624
| 42.689 | 8.5922 |  | 421.2 | 11.6007 |  | 836.9934 | 3.105 |  | 60.6129 | 0.5945
| 43.5428 | 7.7862 |  | 426.9199 | 9.7939 |  | 853.7332 | 2.9672 |  | 61.8251 | 0.5668
| 44.4137 | 7.0939 |  | 431.4 | 8.7188 |  | 870.8079 | 2.8366 |  | 63.0616 | 0.5406
| 45.3019 | 6.4932 |  | 435.9377 | 7.8392 |  | 888.2241 | 2.7126 |  | 64.3228 | 0.5159
| 46.208 | 5.9675 |  | 442.2 | 6.8718 |  | 905.9885 | 2.5948 |  | 65.6093 | 0.4925
| 47.1321 | 5.5039 |  | 448.4139 | 6.1137 |  | 924.1083 | 2.4829 |  | 66.9215 | 0.4704
| 48.0748 | 5.0923 |  | 453.4 | 5.6115 |  | 942.5905 | 2.3764 |  | 68.2599 | 0.4495
| 49.0363 | 4.7247 |  | 458.3645 | 5.1835 |  | 961.4423 | 2.2751 |  | 69.6251 | 0.4297
| 50.017 | 4.3946 |  | 467.4 | 4.5441 |  | 980.6711 | 2.1787 |  | 71.0176 | 0.411
| 51.0173 | 4.0969 |  | 476.4364 | 4.0376 |  | 1000.2845 | 2.0869 |  | 72.438 | 0.3932
| 52.0377 | 3.8271 |  | 492.1246 | 3.3706 |  | 1020.2902 | 1.9994 |  | 73.8867 | 0.3763
| 53.0784 | 3.5817 |  | 504.625 | 2.9699 |  | 1040.696 | 1.916 |  | 75.3645 | 0.3602
| 54.14 | 3.3577 |  | 523.9729 | 2.4979 |  | 1061.51 | 1.8364 |  | 76.8718 | 0.345
| 55.2228 | 3.1526 |  | 537.8428 | 2.2362 |  | 1082.7402 | 1.7605 |  | 78.4092 | 0.3305
| 56.3273 | 2.9642 |  | 556.7166 | 1.9509 |  | 1104.395 | 1.688 |  | 79.9774 | 0.3167
| 57.4538 | 2.7907 |  | 573.848 | 1.7436 |  | 1126.4829 | 1.6189 |  | 81.5769 | 0.3036
| 58.6029 | 2.6305 |  | 597.7202 | 1.513 |  | 1149.0125 | 1.5528 |  | 83.2085 | 0.2911
| 59.7749 | 2.4822 |  | 622.5868 | 1.3246 |  | 1171.9928 | 1.4897 |  | 84.8726 | 0.2791
| 60.9704 | 2.3448 |  | 643.7607 | 1.1942 |  | 1195.4326 | 1.4293 |  | 86.5701 | 0.2678
| 62.1898 | 2.217 |  | 667.744 | 1.0715 |  | 1219.3413 | 1.3716 |  | 88.3015 | 0.257
| 63.4336 | 2.0981 |  | 701.3633 | 0.9329 |  | 1243.7281 | 1.3165 |  | 90.0675 | 0.2466
| 64.7023 | 1.9872 |  | 730.5408 | 0.8359 |  | 1268.6027 | 1.2637 |  | 91.8689 | 0.2368
| 65.9964 | 1.8836 |  | 768.9264 | 0.7324 |  | 1293.9747 | 1.2132 |  | 93.7062 | 0.2273
| 67.3163 | 1.7867 |  | 804.2705 | 0.6553 |  | 1319.8542 | 1.1649 |  | 95.5804 | 0.2183
| 68.6626 | 1.6959 |  | 836.8536 | 0.5959 |  | 1346.2513 | 1.1186 |  | 97.492 | 0.2097
| 70.0359 | 1.6108 |  | 879.9065 | 0.5305 |  | 1373.1763 | 1.0743 |  | 99.4418 | 0.2015
| 71.4366 | 1.5308 |  | 920.162 | 0.4799 |  | 1400.6399 | 1.0318 |  | 101.4306 | 0.1937
| 72.8653 | 1.4556 |  | 978.687 | 0.42 |  | 1428.6526 | 0.9912 |  | 103.4593 | 0.1862
| 74.3226 | 1.3849 |  | 1044.202 | 0.3671 |  | 1457.2257 | 0.9522 |  | 105.5284 | 0.179
| 75.8091 | 1.3182 |  | 1108.297 | 0.3258 |  | 1486.3702 | 0.9149 |  | 107.639 | 0.1721
| 77.3252 | 1.2553 |  | 1181.254 | 0.2881 |  | 1516.0976 | 0.8791 |  | 109.7918 | 0.1655
| 78.8718 | 1.196 |  | 1276.236 | 0.2497 |  | 1546.4196 | 0.8447 |  | 111.9876 | 0.1592
| 80.4492 | 1.1399 |  | 1357.408 | 0.2249 |  | 1577.348 | 0.8118 |  | 114.2274 | 0.1532
| 82.0582 | 1.0869 |  | 1439.222 | 0.2049 |  | 1608.8949 | 0.7803 |  | 116.5119 | 0.1474
| 83.6993 | 1.0368 |  | 1532.361 | 0.1861 |  | 1641.0728 | 0.75 |  | 118.8422 | 0.1419
| 85.3733 | 0.9893 |  | 1645.225 | 0.1678 |  | 1673.8943 | 0.7209 |  | 121.219 | 0.1366
| 87.0808 | 0.9442 |  | 1768.25 | 0.1519 |  | 1707.3722 | 0.6931 |  | 123.6434 | 0.1315
| 88.8224 | 0.9016 |  | 1924.458 | 0.1361 |  | 1741.5196 | 0.6663 |  | 126.1163 | 0.1266
| 90.5989 | 0.8611 |  | 2070.525 | 0.1246 |  | 1776.35 | 0.6407 |  | 128.6386 | 0.122
| 92.4108 | 0.8226 |  | 2237.011 | 0.1142 |  | 1811.877 | 0.616 |  | 131.2114 | 0.1175
| 94.259 | 0.7861 |  | 2437.176 | 0.1045 |  | 1848.1145 | 0.5923 |  | 133.8356 | 0.1132
| 96.1442 | 0.7514 |  | 2646.939 | 0.0967 |  | 1885.0768 | 0.5696 |  | 136.5123 | 0.1091
| 98.0671 | 0.7184 |  | 2889.817 | 0.0897 |  | 1922.7784 | 0.5478 |  | 139.2425 | 0.1051
| 100.0285 | 0.6871 |  | 3122.18 | 0.0845 |  | 1961.2339 | 0.5269 |  | 142.0274 | 0.1013
| 102.029 | 0.6572 |  | 3412.23 | 0.0795 |  | 2000.4586 | 0.5067 |  | 144.8679 | 0.0977
| 104.0696 | 0.6288 |  | 3721.439 | 0.0754 |  | 2040.4678 | 0.4874 |  | 147.7653 | 0.0942
| 106.151 | 0.6017 |  | 4157.41 | 0.0711 |  | 2081.2771 | 0.4688 |  | 150.7206 | 0.0908
| 108.274 | 0.5759 |  | 4515.231 | 0.0685 |  | 2122.9027 | 0.451 |  | 153.735 | 0.0876
| 110.4395 | 0.5513 |  | 4970.928 | 0.066 |  | 2165.3607 | 0.4339 |  | 156.8097 | 0.0845
| 112.6483 | 0.5278 |  | 5501.29 | 0.0638 |  | 2208.6679 | 0.4174 |  | 159.9459 | 0.0815
| 114.9013 | 0.5054 |  | 5925.029 | 0.0624 |  | 2252.8413 | 0.4015 |  | 163.1448 | 0.0787
| 117.1993 | 0.4841 |  | 6570.906 | 0.0608 |  | 2297.8981 | 0.3863 |  | 166.4077 | 0.076
| 119.5433 | 0.4637 |  | 7334.596 | 0.0596 |  | 2343.8561 | 0.3717 |  | 169.7359 | 0.0733
| 121.9341 | 0.4442 |  | 8352.64 | 0.0585 |  | 2390.7332 | 0.3576 |  | 173.1306 | 0.0708
| 124.3728 | 0.4256 |  | 8934.452 | 0.0581 |  | 2438.5479 | 0.3441 |  | 176.5932 | 0.0684
| 126.8603 | 0.4079 |  | 9693.287 | 0.0576 |  | 2487.3188 | 0.3311 |  | 180.1251 | 0.0661
| 129.3975 | 0.3909 |  | 10705.09 | 0.0571 |  | 2537.0652 | 0.3186 |  | 183.7276 | 0.0639
| 131.9854 | 0.3747 |  | 11946.713 | 0.0567 |  | 2587.8065 | 0.3066 |  | 187.4021 | 0.0618
| 134.6251 | 0.3592 | 400Main | 446.7529 | 192.0752 |  | 2639.5627 | 0.2951 |  | 191.1502 | 0.0598
| 137.3176 | 0.3444 |  | 451.132 | 66.0072 |  | 2692.3539 | 0.284 |  | 194.9732 | 0.0582
| 140.064 | 0.3302 |  | 457.3787 | 33.9139 |  | 2746.201 | 0.2733 |  | 198.8726 | 0.0567
| 142.8653 | 0.3166 |  | 457.6693 | 33.1591 |  | 2801.125 | 0.263 |  | 202.8501 | 0.0552
| 145.7226 | 0.3037 |  | 465.1955 | 20.9743 |  | 2857.1475 | 0.2532 |  | 206.9071 | 0.0537
| 148.637 | 0.2913 |  | 473.6704 | 14.7681 |  | 2914.2905 | 0.2436 |  | 211.0452 | 0.0524
| 151.6098 | 0.2794 |  | 475.6389 | 13.8095 |  | 2972.5763 | 0.2345 |  | 215.2661 | 0.051
| 154.642 | 0.268 |  | 484.6633 | 10.6173 |  | 3032.0278 | 0.2257 |  | 219.5715 | 0.0497
| 157.7348 | 0.2571 |  | 487.1209 | 9.9822 |  | 3092.6683 | 0.2173 |  | 223.9629 | 0.0485
| 160.8895 | 0.2467 |  | 495.4092 | 8.2927 |  | 3154.5217 | 0.2091 |  | 228.4421 | 0.0473
| 164.1073 | 0.2367 |  | 505.4819 | 6.8586 |  | 3217.6121 | 0.2013 |  | 233.011 | 0.0462
| 167.3894 | 0.2271 |  | 507.9822 | 6.5733 |  | 3281.9644 | 0.1938 |  | 237.6712 | 0.0451
| 170.7372 | 0.2179 |  | 521.9621 | 5.3186 |  | 3347.6037 | 0.1865 |  | 242.4246 | 0.0441
| 174.152 | 0.2092 |  | 531.9298 | 4.67 |  | 3414.5557 | 0.1795 |  | 247.2731 | 0.043
| 177.635 | 0.2007 |  | 539.1353 | 4.2868 |  | 3482.8469 | 0.1728 |  | 252.2186 | 0.0421
| 181.1877 | 0.1927 |  | 555.7112 | 3.595 |  | 3552.5038 | 0.1664 |  | 257.263 | 0.0411
| 184.8115 | 0.1849 |  | 563.1305 | 3.3486 |  | 3623.5539 | 0.1602 |  | 262.4082 | 0.0402
| 188.5077 | 0.1775 |  | 574.5949 | 3.0237 |  | 3696.025 | 0.1542 |  | 267.6564 | 0.0394
| 192.2778 | 0.1704 |  | 589.7925 | 2.6731 |  | 3769.9455 | 0.1484 |  | 273.0095 | 0.0385
| 196.1234 | 0.1636 |  | 599.1492 | 2.492 |  | 3845.3444 | 0.1429 |  | 278.4697 | 0.0377
| 200.0459 | 0.1571 |  | 614.3071 | 2.2417 |  | 3922.2512 | 0.1376 |  | 284.0391 | 0.037
| 204.0468 | 0.1508 |  | 627.9818 | 2.0521 |  | 4000.6963 | 0.1325 |  | 289.7199 | 0.0362
| 208.1277 | 0.1448 |  | 640.5102 | 1.9022 |  | 4080.7102 | 0.1275 |  | 295.5143 | 0.0355
| 212.2903 | 0.139 |  | 660.2035 | 1.7026 |  | 4162.3244 | 0.1228 |  | 301.4246 | 0.0348
| 216.5361 | 0.1335 |  | 671.4986 | 1.6042 |  | 4245.5709 | 0.1182 |  | 307.4531 | 0.0341
| 220.8668 | 0.1282 |  | 686.9269 | 1.4851 |  | 4330.4823 | 0.1138 |  | 313.6021 | 0.0335
| 225.2841 | 0.1231 |  | 703.8117 | 1.3715 |  | 4417.092 | 0.1096 |  | 319.8742 | 0.0329
| 229.7898 | 0.1182 |  | 735.9396 | 1.1932 |  | 4505.4338 | 0.1055 |  | 326.2716 | 0.0323
| 234.3856 | 0.1135 |  | 742.1203 | 1.1635 |  | 4595.5425 | 0.1016 |  | 332.7971 | 0.0317
| 239.0733 | 0.109 |  | 764.1315 | 1.0675 |  | 4687.4533 | 0.0978 |  | 339.453 | 0.0312
| 243.8548 | 0.1047 |  | 786.4364 | 0.9835 |  | 4781.2024 | 0.0942 |  | 346.2421 | 0.0307
| 248.7319 | 0.1006 |  | 803.4081 | 0.927 |  | 4876.8264 | 0.0907 |  | 353.1669 | 0.0301
| 253.7065 | 0.0966 |  | 834.232 | 0.8376 |  | 4974.363 | 0.0873 |  | 360.2303 | 0.0297
| 258.7807 | 0.0928 |  | 839.4276 | 0.824 |  | 5073.8502 | 0.0841 |  | 367.4349 | 0.0292
| 263.9563 | 0.0891 |  | 872.4958 | 0.7458 |  | 5175.3272 | 0.0809 |  | 374.7836 | 0.0287
| 269.2354 | 0.0856 |  | 883.1642 | 0.7233 |  | 5278.8338 | 0.0779 |  | 382.2792 | 0.0283
| 274.6201 | 0.0822 |  | 920.2204 | 0.6535 |  | 5384.4104 | 0.075 |  | 389.9248 | 0.0279
| 280.1125 | 0.079 |  | 954.8091 | 0.5982 |  | 5492.0987 | 0.0723 |  | 397.7233 | 0.0275
| 285.7147 | 0.0759 |  | 966.5106 | 0.5813 |  | 5601.9406 | 0.0696 |  | 405.6778 | 0.0271
| 291.429 | 0.0729 |  | 1007.7864 | 0.5279 |  | 5713.9794 | 0.067 |  | 413.7913 | 0.0267
| 297.2576 | 0.07 |  | 1011.9538 | 0.523 |  | 5828.259 | 0.0645 |  | 422.0672 | 0.0264
| 303.2028 | 0.0673 |  | 1067.9664 | 0.4639 |  | 5944.8242 | 0.0621 |  | 430.5085 | 0.026
| 309.2668 | 0.0646 |  | 1079.6368 | 0.4531 |  | 6063.7207 | 0.0598 |  | 439.1187 | 0.0257
| 315.4522 | 0.0621 |  | 1131.7383 | 0.4097 |  | 6184.9951 | 0.0576 |  | 447.901 | 0.0253
| 321.7612 | 0.0597 |  | 1132.7635 | 0.4089 |  | 6308.695 | 0.0555 |  | 456.8591 | 0.025
| 328.1964 | 0.0573 |  | 1176.1563 | 0.3782 |  | 6434.8689 | 0.0537 |  | 465.9962 | 0.0247
| 334.7604 | 0.0551 |  | 1191.892 | 0.368 |  | 6563.5663 | 0.0521 |  | 475.3162 | 0.0245
| 341.4556 | 0.0529 |  | 1201.714 | 0.3619 |  | 6694.8376 | 0.0505 |  | 484.8225 | 0.0242
| 348.2847 | 0.0511 |  | 1272.939 | 0.3227 |  | 6828.7344 | 0.049 |  | 494.5189 | 0.0239
| 355.2504 | 0.0495 |  | 1304.4118 | 0.3077 |  | 6965.3091 | 0.0476 |  | 504.4093 | 0.0237
| 362.3554 | 0.048 |  | 1334.183 | 0.2946 |  | 7104.6152 | 0.0462 |  | 514.4975 | 0.0234
| 369.6025 | 0.0465 |  | 1411.577 | 0.2651 |  | 7246.7075 | 0.0448 |  | 524.7875 | 0.0232
| 376.9945 | 0.0451 |  | 1428.6856 | 0.2593 |  | 7391.6417 | 0.0436 |  | 535.2832 | 0.0229
| 384.5344 | 0.0437 |  | 1495.021 | 0.2391 |  | 7539.4745 | 0.0423 |  | 545.9889 | 0.0227
| 392.2251 | 0.0424 |  | 1582.0985 | 0.2179 |  | 7690.264 | 0.0411 |  | 556.9087 | 0.0225
| 400.0696 | 0.0411 |  | 1590.025 | 0.2161 |  | 7844.0693 | 0.04 |  | 568.0468 | 0.0223
| 408.071 | 0.0399 |  | 1682.26 | 0.1978 |  | 8000.9507 | 0.0389 |  | 579.4078 | 0.0221
| 416.2324 | 0.0387 |  | 1724.1777 | 0.1905 |  | 8160.9697 | 0.0378 |  | 590.9959 | 0.0219
| 424.5571 | 0.0376 |  | 1815.511 | 0.1764 |  | 8324.1891 | 0.0368 |  | 602.8158 | 0.0217
| 433.0482 | 0.0365 |  | 1884.6686 | 0.1672 |  | 8490.6729 | 0.0358 |  | 614.8722 | 0.0216
| 441.7092 | 0.0355 |  | 1924.842 | 0.1623 |  | 8660.4863 | 0.0348 |  | 627.1696 | 0.0214
| 450.5434 | 0.0345 |  | 2051.8738 | 0.1488 |  | 8833.6961 | 0.0339 |  | 639.713 | 0.0212
| 459.5542 | 0.0335 |  | 2055.729 | 0.1484 |  | 9010.37 | 0.033 |  | 652.5072 | 0.0211
| 468.7453 | 0.0326 |  | 2186.365 | 0.1371 |  | 9190.5774 | 0.0322 |  | 665.5574 | 0.0209
| 478.1202 | 0.0317 |  | 2279.0329 | 0.1303 |  | 9374.3889 | 0.0313 |  | 678.8685 | 0.0208
| 487.6826 | 0.0309 |  | 2419.427 | 0.1214 |  | 9561.8767 | 0.0306 |  | 692.4459 | 0.0206
| 497.4363 | 0.0301 |  | 2476.2701 | 0.1183 |  | 9753.1142 | 0.0298 |  | 706.2948 | 0.0205
| 507.385 | 0.0293 |  | 2627.479 | 0.1109 |  | 9948.1765 | 0.0291 |  | 720.4207 | 0.0204
| 517.5327 | 0.0285 |  | 2766.9663 | 0.1052 |  | 10147.14 | 0.0284 |  | 734.8291 | 0.0203
| 527.8834 | 0.0278 |  | 2901.497 | 0.1005 |  | 10350.0829 | 0.0277 |  | 749.5257 | 0.0201
| 538.441 | 0.0271 |  | 3024.5213 | 0.0967 |  | 10557.0845 | 0.027 |  | 764.5162 | 0.02
| 549.2099 | 0.0265 |  | 3108.518 | 0.0944 |  | 10768.2262 | 0.0264 |  | 766.5675 | 0.016
| 560.1941 | 0.0258 |  | 3345.9552 | 0.0888 |  | 10983.5907 | 0.0258 |  | 781.8988 | 0.016
| 571.3979 | 0.0252 |  | 3361.756 | 0.0885 |  | 11203.2625 | 0.0252 |  | 797.5368 | 0.016
| 582.8259 | 0.0246 |  | 3595.7486 | 0.0841 |  | 11427.3278 | 0.0246 |  | 813.4875 | 0.016
| 594.4824 | 0.024 |  | 3669.953 | 0.0829 |  | 11655.8744 | 0.0241 |  | 829.7573 | 0.016
| 606.3721 | 0.0235 |  | 3899.1346 | 0.0795 |  | 11888.9918 | 0.0236 |  | 846.3524 | 0.016
| 618.4995 | 0.023 |  | 3956.514 | 0.0788 | 15T | 37.8787 | 670.9521 |  | 863.2795 | 0.016
| 630.8695 | 0.0225 |  | 4177.6702 | 0.0762 |  | 38.6363 | 217.0262 |  | 880.545 | 0.016
| 643.4869 | 0.022 |  | 4305.728 | 0.0749 |  | 39 | 163.2313 |  | 898.1559 | 0.016
| 656.3566 | 0.0215 |  | 4566.5329 | 0.0726 |  | 39.409 | 127.3723 |  | 916.1191 | 0.016
| 669.4838 | 0.0211 |  | 4730.008 | 0.0713 |  | 39.8 | 105.0809 |  | 934.4414 | 0.016
| 682.8734 | 0.0206 |  | 4800.6599 | 0.0708 |  | 40.1972 | 89.0845 |  | 953.1303 | 0.016
| 696.5309 | 0.0202 |  | 5041.7545 | 0.0692 |  | 40.6 | 77.0682 |  | 972.1929 | 0.016
| 704.2017 | 0.016 |  | 5169.038 | 0.0685 |  | 41.0011 | 67.8615 |  | 991.6367 | 0.016
| 718.2857 | 0.016 |  | 5660.627 | 0.066 |  | 41.4 | 60.5936 |  | 1011.4695 | 0.016
| 732.6514 | 0.016 |  | 6109.003 | 0.0643 |  | 41.8212 | 54.3823 |  | 1031.6989 | 0.016
| 747.3045 | 0.016 |  | 6788.506 | 0.0624 |  | 42.2 | 49.751 |  | 1052.3328 | 0.016
| 762.2505 | 0.016 |  | 7543.591 | 0.0608 |  | 42.6576 | 45.0687 |  | 1073.3795 | 0.016
| 777.4956 | 0.016 |  | 8470.656 | 0.0595 |  | 43.1 | 41.2734 |  | 1094.8471 | 0.016
| 793.0455 | 0.016 |  | 9227.931 | 0.0588 |  | 43.5107 | 38.2528 |  | 1116.744 | 0.016
| 808.9064 | 0.016 |  | 9938.094 | 0.0582 |  | 43.9 | 35.7504 |  | 1139.0789 | 0.016
| 825.0845 | 0.016 |  | 10691.74 | 0.0578 |  | 44.381 | 33.0523 |  | 1161.8605 | 0.016
| 841.5862 | 0.016 |  | 11806.774 | 0.0573 |  | 44.8 | 30.9935 |  | 1185.0977 | 0.016
| 858.4179 | 0.016 | 40Main | 44.88 | 101.5883 |  | 45.2686 | 28.9565 |  | 1208.7996 | 0.016
| 875.5863 | 0.016 |  | 45.7776 | 32.8902 |  | 46.1739 | 25.6497 |  | 1232.9756 | 0.016
| 893.098 | 0.016 |  | 46.2 | 24.8711 |  | 47.0974 | 22.9258 |  | 1257.6352 | 0.016
| 910.96 | 0.016 |  | 46.6932 | 19.3218 |  | 48.0394 | 20.6448 |  | 1282.7879 | 0.016
| 929.1792 | 0.016 |  | 47.2 | 15.6891 |  | 49.0002 | 18.7083 |  | 1308.4436 | 0.016
| 947.7627 | 0.016 |  | 47.627 | 13.5272 |  | 49.9802 | 17.0448 |  | 1334.6125 | 0.016
| 966.718 | 0.016 |  | 48.1 | 11.7228 |  | 50.9798 | 15.6015 |  | 1361.3047 | 0.016
| 986.0524 | 0.016 |  | 48.5796 | 10.3153 |  | 51.9994 | 14.3384 |  | 1388.5308 | 0.016
| 1005.7734 | 0.016 |  | 49.1 | 9.1164 |  | 53.0394 | 13.2244 |  | 1416.3014 | 0.016
| 1025.8889 | 0.016 |  | 49.5511 | 8.2753 |  | 54.1001 | 12.2355 |  | 1444.6275 | 0.016
| 1046.4066 | 0.016 |  | 50 | 7.5744 |  | 55.1821 | 11.3522 |  | 1473.52 | 0.016
| 1067.3348 | 0.016 |  | 50.5422 | 6.8658 |  | 56.2858 | 10.5592 |  | 1502.9904 | 0.016
| 1088.6815 | 0.016 |  | 51 | 6.359 |  | 57.4115 | 9.8437 |  | 1533.0502 | 0.016
| 1110.4551 | 0.016 |  | 51.553 | 5.8343 |  | 58.5597 | 9.1955 |  | 1533.1349 | 0.014
| 1132.6642 | 0.016 |  | 52.1 | 5.3902 |  | 59.7309 | 8.6059 |  | 1563.7976 | 0.014
| 1155.3175 | 0.016 |  | 52.5841 | 5.0472 |  | 60.9255 | 8.0677 |  | 1595.0736 | 0.014
| 1178.4238 | 0.016 |  | 53.1 | 4.7242 |  | 62.1441 | 7.5749 |  | 1626.975 | 0.014
| 1201.9923 | 0.016 |  | 53.6358 | 4.4273 |  | 63.3869 | 7.1222 |  | 1659.5145 | 0.014
| 1226.0322 | 0.016 |  | 54.7085 | 3.9269 |  | 64.6547 | 6.7053 |  | 1692.7048 | 0.014
| 1250.5528 | 0.016 |  | 55.8026 | 3.5146 |  | 65.9478 | 6.3204 |  | 1726.5589 | 0.014
| 1275.5639 | 0.016 |  | 56.9187 | 3.1694 |  | 67.2667 | 5.9642 |  | 1761.0901 | 0.014
| 1301.0751 | 0.016 |  | 58.0571 | 2.8763 |  | 68.6121 | 5.6339 |  | 1796.3119 | 0.014
| 1327.0966 | 0.016 |  | 59.2182 | 2.6246 |  | 69.9843 | 5.3269 |  | 1832.2381 | 0.014
| 1353.6386 | 0.016 |  | 60.4026 | 2.4062 |  | 71.384 | 5.0412 |  | 1868.8829 | 0.014
| 1380.7113 | 0.016 |  | 61.6106 | 2.215 |  | 72.8117 | 4.7747 |  | 1906.2605 | 0.014
| 1408.3256 | 0.016 |  | 62.8428 | 2.0464 |  | 74.2679 | 4.5258 |  | 1944.3858 | 0.014
| 1408.4034 | 0.016 |  | 64.0997 | 1.8967 |  | 75.7533 | 4.2929 |  | 1983.2735 | 0.014
| 1436.5714 | 0.014 |  | 65.3817 | 1.7631 |  | 77.2683 | 4.0748 |  | 2022.9389 | 0.014
| 1465.3028 | 0.014 |  | 66.6893 | 1.643 |  | 78.8137 | 3.8703 |  | 2063.3977 | 0.014
| 1494.6089 | 0.014 |  | 68.0231 | 1.5348 |  | 80.39 | 3.6781 |  | 2104.6657 | 0.014
| 1524.5011 | 0.014 |  | 69.3836 | 1.4367 |  | 81.9978 | 3.4975 |  | 2146.759 | 0.014
| 1554.9911 | 0.014 |  | 70.7712 | 1.3474 |  | 83.6377 | 3.3275 |  | 2189.6942 | 0.014
| 1586.0909 | 0.014 |  | 72.1867 | 1.266 |  | 85.3105 | 3.1673 |  | 2233.4881 | 0.014
| 1617.8127 | 0.014 |  | 73.6304 | 1.1914 |  | 87.0167 | 3.0163 |  | 2278.1578 | 0.014
| 1650.169 | 0.014 |  | 75.103 | 1.1229 |  | 88.757 | 2.8737 |  | 2323.721 | 0.014
| 1683.1724 | 0.014 |  | 76.6051 | 1.0598 |  | 90.5322 | 2.739 |  | 2370.1954 | 0.014
| 1716.8358 | 0.014 |  | 78.1372 | 1.0015 |  | 92.3428 | 2.6116 |  | 2417.5993 | 0.014
| 1751.1725 | 0.014 |  | 79.6999 | 0.9476 |  | 94.1897 | 2.4911 |  | 2465.9513 | 0.014
| 1786.196 | 0.014 |  | 81.2939 | 0.8976 |  | 96.0734 | 2.3769 |  | 2515.2703 | 0.014
| 1821.9199 | 0.014 |  | 82.9198 | 0.8512 |  | 97.9949 | 2.2688 |  | 2565.5757 | 0.014
| 1858.3583 | 0.014 |  | 84.5782 | 0.8079 |  | 99.9548 | 2.1662 |  | 2616.8872 | 0.014
| 1895.5255 | 0.014 |  | 86.2697 | 0.7676 |  | 101.9539 | 2.069 |  | 2669.225 | 0.014
| 1933.436 | 0.014 |  | 87.9951 | 0.7299 |  | 103.993 | 1.9766 |  | 2722.6095 | 0.014
| 1972.1047 | 0.014 |  | 89.755 | 0.6947 |  | 106.0728 | 1.8889 |  | 2777.0617 | 0.014
| 2011.5468 | 0.014 |  | 91.5501 | 0.6617 |  | 108.1943 | 1.8055 |  | 2832.6029 | 0.014
| 2051.7777 | 0.014 |  | 93.3811 | 0.6307 |  | 110.3582 | 1.7262 |  | 2889.255 | 0.014
| 2092.8133 | 0.014 |  | 95.2488 | 0.6017 |  | 112.5654 | 1.6508 |  | 2947.0401 | 0.014
| 2134.6696 | 0.014 |  | 97.1537 | 0.5743 |  | 114.8167 | 1.5791 |  | 3005.9809 | 0.014
| 2177.3629 | 0.014 |  | 99.0968 | 0.5486 |  | 117.113 | 1.5107 |  | 3066.1005 | 0.014
| 2220.9102 | 0.014 |  | 101.0788 | 0.5244 |  | 119.4553 | 1.4457 |  | 3127.4225 | 0.014
| 2265.3284 | 0.014 |  | 103.1003 | 0.5015 |  | 121.8444 | 1.3836 |  | 3189.9709 | 0.014
| 2310.635 | 0.014 |  | 105.1623 | 0.4799 |  | 124.2812 | 1.3245 |  | 3253.7703 | 0.014
| 2356.8477 | 0.014 |  | 107.2656 | 0.4595 |  | 126.7669 | 1.2682 |  | 3318.8458 | 0.014
| 2403.9846 | 0.014 |  | 109.4109 | 0.4402 |  | 129.3022 | 1.2144 |  | 3385.2227 | 0.014
| 2452.0643 | 0.014 |  | 111.5991 | 0.422 |  | 131.8883 | 1.1631 |  | 3452.9271 | 0.014
| 2501.1056 | 0.014 |  | 113.8311 | 0.4047 |  | 134.526 | 1.1141 |  | 3521.9857 | 0.014
| 2551.1277 | 0.014 |  | 116.1077 | 0.3884 |  | 137.2165 | 1.0674 |  | 3592.4254 | 0.014
| 2602.1503 | 0.014 |  | 118.4299 | 0.3728 |  | 139.9609 | 1.0227 |  | 3664.2739 | 0.014
| 2654.1933 | 0.014 |  | 120.7985 | 0.3581 |  | 142.7601 | 0.98 |  | 3737.5594 | 0.014
| 2707.2772 | 0.014 |  | 123.2144 | 0.3441 |  | 145.6153 | 0.9393 |  | 3812.3106 | 0.014
| 2761.4227 | 0.014 |  | 125.6787 | 0.3309 |  | 148.5276 | 0.9003 |  | 3888.5568 | 0.014
| 2816.6511 | 0.014 |  | 128.1923 | 0.3182 |  | 151.4981 | 0.8631 |  | 3966.3279 | 0.014
| 2872.9842 | 0.014 |  | 130.7561 | 0.3063 |  | 154.5281 | 0.8275 |  | 4045.6545 | 0.014
| 2930.4439 | 0.014 |  | 133.3713 | 0.2948 |  | 157.6187 | 0.7934 |  | 4126.5675 | 0.014
| 2989.0527 | 0.014 |  | 136.0387 | 0.284 |  | 160.771 | 0.7608 |  | 4209.0989 | 0.014
| 3048.8338 | 0.014 |  | 138.7595 | 0.2736 |  | 163.9865 | 0.7296 |  | 4293.2809 | 0.014
| 3109.8105 | 0.014 |  | 141.5347 | 0.2638 |  | 167.2662 | 0.6998 |  | 4379.1465 | 0.014
| 3172.0067 | 0.014 |  | 144.3654 | 0.2544 |  | 170.6115 | 0.6713 |  | 4466.7294 | 0.014
| 3235.4468 | 0.014 |  | 147.2527 | 0.2455 |  | 174.0237 | 0.6439 |  | 4556.064 | 0.014
| 3300.1557 | 0.014 |  | 150.1977 | 0.2372 |  | 177.5042 | 0.6178 |  | 4647.1853 | 0.014
| 3366.1589 | 0.014 |  | 153.2017 | 0.2296 |  | 181.0543 | 0.5927 |  | 4740.129 | 0.014
| 3433.482 | 0.014 |  | 156.2657 | 0.2223 |  | 184.6754 | 0.5687 |  | 4834.9316 | 0.014
| 3502.1517 | 0.014 |  | 159.391 | 0.2153 |  | 188.3689 | 0.5457 |  | 4931.6302 | 0.014
| 3572.1947 | 0.014 |  | 162.5788 | 0.2086 |  | 192.1363 | 0.5237 |  | 5030.2628 | 0.014
| 3643.6386 | 0.014 |  | 165.8304 | 0.2023 |  | 195.979 | 0.5026 |  | 5130.8681 | 0.014
| 3716.5114 | 0.014 |  | 169.147 | 0.1962 |  | 199.8986 | 0.4823 |  | 5233.4854 | 0.014
| 3790.8416 | 0.014 |  | 172.53 | 0.1903 |  | 203.8966 | 0.4629 |  | 5338.1551 | 0.014
| 3866.6584 | 0.014 |  | 175.9806 | 0.1847 |  | 207.9745 | 0.4444 |  | 5444.9182 | 0.014
| 3943.9916 | 0.014 |  | 179.5002 | 0.1794 |  | 212.134 | 0.4265 |  | 5553.8166 | 0.014
| 4022.8714 | 0.014 |  | 183.0902 | 0.1743 |  | 216.3767 | 0.4095 |  | 5664.8929 | 0.014
| 4103.3289 | 0.014 |  | 186.752 | 0.1694 |  | 220.7042 | 0.3931 |  | 5778.1908 | 0.014
| 4185.3954 | 0.014 |  | 190.487 | 0.1647 |  | 225.1183 | 0.3774 |  | 5893.7546 | 0.014
| 4269.1033 | 0.014 |  | 194.2968 | 0.1602 |  | 229.6206 | 0.3623 |  | 6011.6297 | 0.014
| 4354.4854 | 0.014 |  | 198.1827 | 0.1559 |  | 234.2131 | 0.3479 |  | 6131.8623 | 0.014
| 4441.5751 | 0.014 |  | 202.1463 | 0.1518 |  | 238.8973 | 0.334 |  | 6254.4995 | 0.014
| 4530.4066 | 0.014 |  | 206.1893 | 0.1479 |  | 243.6753 | 0.3208 |  | 6379.5895 | 0.014
| 4621.0148 | 0.014 |  | 210.3131 | 0.1441 |  | 248.5488 | 0.308 |  | 6507.1813 | 0.014
| 4713.4351 | 0.014 |  | 214.5193 | 0.1405 |  | 253.5197 | 0.2958 |  | 6637.3249 | 0.014
| 4807.7038 | 0.014 |  | 218.8097 | 0.137 |  | 258.5901 | 0.2841 |  | 6770.0714 | 0.014
| 4903.8578 | 0.014 |  | 223.1859 | 0.1336 |  | 263.7619 | 0.2728 |  | 6905.4729 | 0.014
| 5001.935 | 0.014 |  | 227.6496 | 0.1305 |  | 269.0372 | 0.262 |  | 7043.5823 | 0.014
| 5101.9737 | 0.014 |  | 232.2026 | 0.1274 |  | 274.4179 | 0.2516 |  | 7184.454 | 0.014
| 5204.0132 | 0.014 |  | 236.8467 | 0.1245 |  | 279.9063 | 0.2417 |  | 7328.1431 | 0.014
| 5308.0934 | 0.014 |  | 241.5836 | 0.1217 |  | 285.5044 | 0.2321 |  | 7474.7059 | 0.014
| 5414.2553 | 0.014 |  | 246.4153 | 0.119 |  | 291.2145 | 0.223 |  | 7624.2 | 0.014
| 5522.5404 | 0.014 |  | 251.3436 | 0.1164 |  | 297.0388 | 0.2142 |  | 7776.684 | 0.014
| 5632.9912 | 0.014 |  | 256.3704 | 0.1139 |  | 302.9796 | 0.2057 |  | 7932.2177 | 0.014
| 5745.651 | 0.014 |  | 261.4979 | 0.1115 |  | 309.0392 | 0.1976 |  | 8090.8621 | 0.014
| 5860.564 | 0.014 |  | 266.7278 | 0.1092 |  | 315.2199 | 0.1898 |  | 8252.6793 | 0.014
| 5977.7753 | 0.014 |  | 272.0624 | 0.107 |  | 321.5243 | 0.1824 |  | 8417.7329 | 0.014
| 6097.3308 | 0.014 |  | 277.5036 | 0.1049 |  | 327.9548 | 0.1752 |  | 8586.0876 | 0.014
| 6219.2775 | 0.014 |  | 283.0537 | 0.1029 |  | 334.5139 | 0.1683 |  | 8757.8093 | 0.014
| 6343.663 | 0.014 |  | 288.7148 | 0.101 |  | 341.2042 | 0.1617 |  | 8932.9655 | 0.014
| 6470.5363 | 0.014 |  | 294.4891 | 0.0991 |  | 348.0283 | 0.1553 |  | 9111.6248 | 0.014
| 6599.947 | 0.014 |  | 300.3788 | 0.0973 |  | 354.9888 | 0.1492 |  | 9293.8573 | 0.014
| 6731.9459 | 0.014 |  | 306.3864 | 0.0956 |  | 362.0886 | 0.1434 |  | 9479.7345 | 0.014
| 6866.5848 | 0.014 |  | 312.5141 | 0.094 |  | 369.3304 | 0.1377 |  | 9669.3291 | 0.014
| 7003.9165 | 0.014 |  | 318.7644 | 0.0924 |  | 376.717 | 0.1323 |  | 9862.7157 | 0.014
| 7143.9949 | 0.014 |  | 325.1397 | 0.0909 |  | 384.2513 | 0.1272 |  | 10059.97 | 0.014
| 7286.8748 | 0.014 |  | 331.6425 | 0.0894 |  | 391.9364 | 0.1222 |  | 10261.1694 | 0.014
| 7432.6123 | 0.014 |  | 338.2754 | 0.088 |  | 399.7751 | 0.1174 |  | 10466.3928 | 0.014
| 7581.2645 | 0.014 |  | 345.0409 | 0.0867 |  | 407.7706 | 0.1128 |  | 10675.7207 | 0.014
| 7732.8898 | 0.014 |  | 351.9417 | 0.0854 |  | 415.926 | 0.1084 |  | 10889.2351 | 0.014
| 7887.5476 | 0.014 |  | 358.9805 | 0.0842 |  | 424.2445 | 0.1041 |  | 11107.0198 | 0.014
| 8045.2986 | 0.014 |  | 366.1601 | 0.083 |  | 432.7294 | 0.1001 |  | 11329.1602 | 0.014
| 8206.2045 | 0.014 |  | 373.4833 | 0.0818 |  | 441.384 | 0.0961 |  | 11555.7434 | 0.014
| 8370.3286 | 0.014 |  | 380.953 | 0.0808 |  | 450.2117 | 0.0924 |  | 11786.8583 | 0.014
| 8537.7352 | 0.014 |  | 388.5721 | 0.0797 |  | 459.2159 | 0.0888 | 300Tap | 338.3842 | 69.0055
| 8708.4899 | 0.014 |  | 396.3435 | 0.0787 |  | 468.4002 | 0.0853 |  | 345.972 | 27.304
| 8882.6597 | 0.014 |  | 404.2704 | 0.0777 |  | 477.7682 | 0.082 |  | 352 | 18.3428
| 9060.3129 | 0.014 |  | 412.3558 | 0.0768 |  | 487.3236 | 0.0788 |  | 357.9917 | 13.7792
| 9241.5191 | 0.014 |  | 420.6029 | 0.0759 |  | 497.0701 | 0.0757 |  | 363.8 | 11.0701
| 9426.3495 | 0.014 |  | 429.015 | 0.075 |  | 507.0115 | 0.0727 |  | 369.5329 | 9.2498
| 9614.8765 | 0.014 |  | 437.5953 | 0.0742 |  | 517.1517 | 0.0699 |  | 375.8 | 7.8232
| 9807.174 | 0.014 |  | 446.3472 | 0.0734 |  | 527.4947 | 0.0672 |  | 381.986 | 6.7763
| 10003.3175 | 0.014 |  | 455.2741 | 0.0727 |  | 538.0446 | 0.0645 |  | 387.2 | 6.0814
| 10203.3839 | 0.014 |  | 464.3796 | 0.0719 |  | 548.8055 | 0.062 |  | 392.4404 | 5.5069
| 10407.4515 | 0.014 |  | 473.6672 | 0.0712 |  | 559.7816 | 0.0596 |  | 401 | 4.7609
| 10615.6006 | 0.014 |  | 483.1405 | 0.0706 |  | 570.9773 | 0.0573 |  | 409.563 | 4.1832
| 10827.9126 | 0.014 |  | 492.8033 | 0.0699 |  | 582.3968 | 0.0551 |  | 425.8672 | 3.381
| 11044.4708 | 0.014 |  | 502.6594 | 0.0693 |  | 594.0448 | 0.0529 |  | 449.911 | 2.6113
| 11265.3603 | 0.014 |  | 512.7126 | 0.0687 |  | 605.9257 | 0.0512 |  | 473.2882 | 2.1199
| 11490.6675 | 0.014 |  | 522.9668 | 0.0681 |  | 618.0442 | 0.0495 |  | 502.2039 | 1.7037
| 11720.4808 | 0.014 |  | 533.4262 | 0.0676 |  | 630.4051 | 0.048 |  | 532.8873 | 1.3973
| 11954.8904 | 0.014 |  | 544.0947 | 0.067 |  | 643.0132 | 0.0465 |  | 571.3576 | 1.1281
175E | 469.4525 | 1662.8744 |  | 554.9766 | 0.0665 |  | 655.8734 | 0.0451 |  | 610.0622 | 0.9359
| 475.9161 | 132.4569 |  | 566.0761 | 0.066 |  | 668.9909 | 0.0437 |  | 664.3923 | 0.7456
| 480.6989 | 78.4178 |  | 577.3976 | 0.0656 |  | 682.3707 | 0.0424 |  | 704.2508 | 0.6435
| 483.1 | 65.004 |  | 588.9456 | 0.0651 |  | 696.0181 | 0.0412 |  | 752.7399 | 0.5474
| 485.5301 | 55.3702 |  | 600.7245 | 0.0647 |  | 709.9385 | 0.04 |  | 812.9814 | 0.4573
| 489 | 45.6508 |  | 612.739 | 0.0643 |  | 724.1372 | 0.0388 |  | 877.1312 | 0.3854
| 492.3754 | 38.9528 |  | 624.9938 | 0.0639 |  | 738.62 | 0.0377 |  | 959.2297 | 0.3171
| 495.6 | 34.1358 |  | 637.4937 | 0.0635 |  | 753.3924 | 0.0366 |  | 1033.8438 | 0.2705
| 498.8181 | 30.3641 |  | 650.2435 | 0.0631 |  | 768.4602 | 0.0356 |  | 1084.965 | 0.2447
| 502.6 | 26.8528 |  | 663.2484 | 0.0628 |  | 783.8294 | 0.0346 |  | 1185.359 | 0.2043
| 506.3564 | 24.0675 |  | 676.5134 | 0.0624 |  | 799.506 | 0.0336 |  | 1270.851 | 0.1777
| 510.7 | 21.4716 |  | 690.0436 | 0.0621 |  | 815.4962 | 0.0327 |  | 1386.912 | 0.1497
| 515.0387 | 19.3672 |  | 703.8445 | 0.0618 |  | 831.8061 | 0.0318 |  | 1535.78 | 0.1231
| 518.9 | 17.802 |  | 717.9214 | 0.0615 |  | 848.4422 | 0.031 |  | 1679.527 | 0.1041
| 522.8223 | 16.4421 |  | 732.2798 | 0.0612 |  | 865.411 | 0.0301 |  | 1831.004 | 0.0888
| 526.8 | 15.2516 |  | 746.9254 | 0.0609 |  | 882.7193 | 0.0294 |  | 1996.143 | 0.076
| 530.7236 | 14.2277 |  | 761.8639 | 0.0606 |  | 900.3736 | 0.0286 |  | 2226.561 | 0.0628
| 534.5 | 13.3584 |  | 777.1012 | 0.0604 |  | 918.3811 | 0.0279 |  | 2475.836 | 0.0539
| 538.2058 | 12.5977 |  | 792.6432 | 0.0601 |  | 936.7487 | 0.0272 |  | 2767.377 | 0.0468
| 543.1 | 11.71 |  | 808.4961 | 0.0599 |  | 955.4837 | 0.0265 |  | 3007.567 | 0.0424
| 547.9815 | 10.9345 |  | 824.666 | 0.0597 |  | 974.5934 | 0.0259 |  | 3295.921 | 0.0383
| 551.8 | 10.3919 |  | 841.1593 | 0.0595 |  | 994.0853 | 0.0253 |  | 3645.902 | 0.0345
| 555.7068 | 9.8864 |  | 857.9825 | 0.0594 |  | 1013.967 | 0.0247 |  | 4020.477 | 0.0315
| 560.8 | 9.2924 |  | 875.1422 | 0.0592 |  | 1034.2463 | 0.0241 |  | 4419.719 | 0.0291
| 565.8004 | 8.7703 |  | 892.645 | 0.059 |  | 1054.9312 | 0.0235 |  | 4894.12 | 0.027
| 574.926 | 7.9455 |  | 910.4979 | 0.0589 |  | 1076.0299 | 0.023 |  | 5363.351 | 0.0254
| 584.199 | 7.2422 |  | 928.7079 | 0.0587 |  | 1097.5505 | 0.0225 |  | 5914.375 | 0.024
| 596.5971 | 6.463 |  | 947.282 | 0.0586 |  | 1119.5015 | 0.022 |  | 6522.01 | 0.0228
| 609.8675 | 5.7826 |  | 966.2277 | 0.0584 |  | 1141.8915 | 0.0216 |  | 7274.854 | 0.0217
| 622.1875 | 5.2578 |  | 985.5522 | 0.0583 |  | 1164.7293 | 0.0211 |  | 7922.73 | 0.021
| 636.6635 | 4.7413 |  | 1005.2633 | 0.0582 |  | 1188.0239 | 0.0207 |  | 8637.286 | 0.0204
| 650.1748 | 4.3349 |  | 1025.3685 | 0.058 |  | 1211.7844 | 0.0203 |  | 10208.5598 | 0.016
| 668.6372 | 3.8704 |  | 1045.8759 | 0.0579 |  | 1227.7273 | 0.02 | 30Tap | 33.66 | 106.9469
| 686.2493 | 3.5026 |  | 1066.7934 | 0.0578 |  | 1252.2819 | 0.016 |  | 34.3332 | 34.6325
| 704.3256 | 3.1838 |  | 1088.1293 | 0.0577 |  | 1277.3275 | 0.016 |  | 34.7 | 25.2165
| 725.7756 | 2.8656 |  | 1109.8919 | 0.0576 |  | 1302.8741 | 0.016 |  | 35.0199 | 20.3493
| 744.8936 | 2.6251 |  | 1132.0897 | 0.0575 |  | 1328.9315 | 0.016 |  | 35.4 | 16.525
| 765.2799 | 2.4041 |  | 1154.7315 | 0.0574 |  | 1355.5102 | 0.016 |  | 35.7203 | 14.2491
| 787.798 | 2.1943 |  | 1177.8261 | 0.0573 |  | 1382.6204 | 0.016 |  | 36.1 | 12.2339
| 814.2288 | 1.9847 |  | 1201.3827 | 0.0572 |  | 1410.2728 | 0.016 |  | 36.4347 | 10.8674
| 838.1868 | 1.8219 |  | 1225.4103 | 0.0571 |  | 1438.4782 | 0.016 |  | 36.8 | 9.6774
| 875.8904 | 1.6068 |  | 1249.9185 | 0.0571 |  | 1467.2478 | 0.016 |  | 37.1634 | 8.7194
| 912.5479 | 1.4349 |  | 1274.9169 | 0.057 |  | 1496.5928 | 0.016 |  | 37.5 | 7.9813
| 950.7399 | 1.2856 |  | 1300.4152 | 0.0569 |  | 1526.5246 | 0.016 |  | 37.9066 | 7.235
| 984.6056 | 1.1732 |  | 1326.4235 | 0.0568 |  | 1557.0551 | 0.016 |  | 38.3 | 6.6297
| 1022.7404 | 1.0645 |  | 1352.952 | 0.0567 |  | 1588.1962 | 0.016 |  | 38.6648 | 6.1485
| 1064.4788 | 0.963 |  | 1380.011 | 0.0567 |  | 1619.9601 | 0.016 |  | 39.1 | 5.6544
| 1106.809 | 0.8749 |  | 1407.6113 | 0.0566 |  | 1652.3593 | 0.016 |  | 39.4381 | 5.3194
| 1162.392 | 0.7774 |  | 1435.7635 | 0.0566 |  | 1685.4065 | 0.016 |  | 39.8 | 4.9997
| 1213.465 | 0.7021 |  | 1464.4788 | 0.0565 |  | 1719.1146 | 0.016 |  | 40.2268 | 4.6662
| 1260.468 | 0.6424 |  | 1493.7683 | 0.0564 |  | 1753.4969 | 0.016 |  | 41.0314 | 4.1387
| 1342.429 | 0.5558 |  | 1523.6437 | 0.0564 |  | 1788.5669 | 0.016 |  | 41.852 | 3.7041
| 1408.44 | 0.4986 |  | 1554.1166 | 0.0563 |  | 1824.3382 | 0.016 |  | 42.689 | 3.3401
| 1486.584 | 0.4419 |  | 1585.1989 | 0.0563 |  | 1860.825 | 0.016 |  | 43.5428 | 3.0309
| 1586.42 | 0.3829 |  | 1616.9029 | 0.0562 |  | 1898.0415 | 0.016 |  | 44.4137 | 2.7653
| 1677.797 | 0.3389 |  | 1649.2409 | 0.0562 |  | 1936.0023 | 0.016 |  | 45.3019 | 2.5347
| 1760.297 | 0.3055 |  | 1682.2258 | 0.0561 |  | 1974.7224 | 0.016 |  | 46.208 | 2.3328
| 1846.856 | 0.2756 |  | 1715.8703 | 0.0561 |  | 2014.2168 | 0.016 |  | 47.1321 | 2.1547
| 1949.321 | 0.2457 |  | 1750.1877 | 0.056 |  | 2054.5011 | 0.016 |  | 48.0748 | 1.9965
| 2065.723 | 0.2173 |  | 1785.1914 | 0.056 |  | 2095.5912 | 0.016 |  | 49.0363 | 1.8552
| 2202.255 | 0.1899 |  | 1820.8953 | 0.056 |  | 2137.503 | 0.016 |  | 50.017 | 1.7282
| 2357.223 | 0.1648 |  | 1857.3132 | 0.0559 |  | 2180.253 | 0.016 |  | 51.0173 | 1.6136
| 2510.497 | 0.1446 |  | 1894.4594 | 0.0559 |  | 2223.8581 | 0.016 |  | 52.0377 | 1.5097
| 2689.841 | 0.1254 |  | 1932.3486 | 0.0559 |  | 2268.3353 | 0.016 |  | 53.0784 | 1.4151
| 2844.776 | 0.1117 |  | 1970.9956 | 0.0558 |  | 2313.702 | 0.016 |  | 54.14 | 1.3288
| 3023.702 | 0.0986 |  | 2010.4155 | 0.0558 |  | 2359.976 | 0.016 |  | 55.2228 | 1.2496
| 3194.664 | 0.0881 |  | 2050.6238 | 0.0558 |  | 2407.1755 | 0.016 |  | 56.3273 | 1.1769
| 3395.612 | 0.0778 |  | 2091.6363 | 0.0557 |  | 2455.319 | 0.016 |  | 57.4538 | 1.1099
| 3591.192 | 0.0694 |  | 2133.469 | 0.0557 |  | 2455.4546 | 0.014 |  | 58.6029 | 1.048
| 3794.241 | 0.062 |  | 2176.1384 | 0.0557 |  | 2504.5637 | 0.014 |  | 59.7749 | 0.9906
| 4012.778 | 0.0554 |  | 2219.6612 | 0.0556 |  | 2554.655 | 0.014 |  | 60.9704 | 0.9374
| 4252.402 | 0.0498 |  | 2264.0544 | 0.0556 |  | 2605.7481 | 0.014 |  | 62.1898 | 0.8879
| 4470.422 | 0.046 |  | 2309.3355 | 0.0556 |  | 2657.8631 | 0.014 |  | 63.4336 | 0.8418
| 4709.034 | 0.0424 |  | 2355.5222 | 0.0556 |  | 2711.0203 | 0.014 |  | 64.7023 | 0.7988
| 4960.384 | 0.0392 |  | 2402.6326 | 0.0556 |  | 2765.2407 | 0.014 |  | 65.9964 | 0.7586
| 5239.22 | 0.0361 |  | 2450.6853 | 0.0555 |  | 2820.5456 | 0.014 |  | 67.3163 | 0.7209
| 5546.53 | 0.0333 |  | 2499.699 | 0.0555 |  | 2876.9565 | 0.014 |  | 68.6626 | 0.6856
| 5830.91 | 0.0311 |  | 2549.693 | 0.0555 |  | 2934.4956 | 0.014 |  | 70.0359 | 0.6524
| 6142.14 | 0.029 |  | 2600.6868 | 0.0555 |  | 2993.1855 | 0.014 |  | 71.4366 | 0.6213
| 6418.43 | 0.0274 |  | 2652.7006 | 0.0555 |  | 3053.0492 | 0.014 |  | 72.8653 | 0.592
| 6788.11 | 0.0255 |  | 2705.7546 | 0.0554 |  | 3114.1102 | 0.014 |  | 74.3226 | 0.5644
| 7058.08 | 0.0244 |  | 2759.8697 | 0.0554 |  | 3176.3924 | 0.014 |  | 75.8091 | 0.5383
| 7397.73 | 0.0231 |  | 2815.0671 | 0.0554 |  | 3239.9203 | 0.014 |  | 77.3252 | 0.5137
| 7691.94 | 0.0221 |  | 2871.3684 | 0.0554 |  | 3304.7187 | 0.014 |  | 78.8718 | 0.4905
| 8005.85 | 0.0211 |  | 2928.7958 | 0.0554 |  | 3370.813 | 0.014 |  | 80.4492 | 0.4685
| 8299.31 | 0.0204 |  | 2987.3717 | 0.0554 |  | 3438.2293 | 0.014 |  | 82.0582 | 0.4477
| 8509.41 | 0.016 |  | 3047.1191 | 0.0553 |  | 3506.9939 | 0.014 |  | 83.6993 | 0.428
| 8724.83 | 0.016 |  | 3108.0615 | 0.0553 |  | 3577.1338 | 0.014 |  | 85.3733 | 0.4093
| 9157.6095 | 0.016 |  | 3170.2227 | 0.0553 |  | 3648.6764 | 0.014 |  | 87.0808 | 0.3916
| 10302.3106 | 0.016 |  | 3233.6272 | 0.0553 |  | 3721.65 | 0.014 |  | 88.8224 | 0.3748
| 11447.0118 | 0.016 |  | 3298.2997 | 0.0553 |  | 3796.083 | 0.014 |  | 90.5989 | 0.3588
200E | 540.9041 | 252.3019 |  | 3364.2657 | 0.0553 |  | 3872.0046 | 0.014 |  | 92.4108 | 0.3437
| 546.887 | 104.0288 |  | 3431.5511 | 0.0553 |  | 3949.4447 | 0.014 |  | 94.259 | 0.3292
| 550.5 | 76.6031 |  | 3500.1821 | 0.0553 |  | 4028.4336 | 0.014 |  | 96.1442 | 0.3155
| 554.0425 | 60.7875 |  | 3570.1857 | 0.0553 |  | 4109.0023 | 0.014 |  | 98.0671 | 0.3024
| 557.9 | 49.5688 |  | 3641.5894 | 0.0552 |  | 4191.1823 | 0.014 |  | 100.0285 | 0.29
| 561.8536 | 41.6376 |  | 3714.4212 | 0.0552 |  | 4275.006 | 0.014 |  | 102.029 | 0.2781
| 567 | 34.4121 |  | 3788.7096 | 0.0552 |  | 4360.5061 | 0.014 |  | 104.0696 | 0.2668
| 572.0583 | 29.3592 |  | 3864.4838 | 0.0552 |  | 4447.7162 | 0.014 |  | 106.151 | 0.256
| 577.8 | 25.1309 |  | 3941.7735 | 0.0552 |  | 4536.6705 | 0.014 |  | 108.274 | 0.2457
| 583.6149 | 21.904 |  | 4020.609 | 0.0552 |  | 4627.4039 | 0.014 |  | 110.4395 | 0.2359
| 589.8 | 19.2479 |  | 4101.0212 | 0.0552 |  | 4719.952 | 0.014 |  | 112.6483 | 0.2265
| 596.0009 | 17.142 |  | 4183.0416 | 0.0552 |  | 4814.3511 | 0.014 |  | 114.9013 | 0.2175
| 603.5 | 15.1185 |  | 4266.7024 | 0.0552 |  | 4910.6381 | 0.014 |  | 117.1993 | 0.209
| 611.0885 | 13.4871 |  | 4352.0365 | 0.0552 |  | 5008.8508 | 0.014 |  | 119.5433 | 0.2008
| 618.2 | 12.2349 |  | 4439.0772 | 0.0552 |  | 5109.0279 | 0.014 |  | 121.9341 | 0.193
| 625.306 | 11.1853 |  | 4527.8587 | 0.0552 |  | 5211.2084 | 0.014 |  | 124.3728 | 0.1855
| 634.2 | 10.0881 |  | 4618.4159 | 0.0552 |  | 5315.4326 | 0.014 |  | 126.8603 | 0.1783
| 643.0622 | 9.1783 |  | 4710.7842 | 0.0551 |  | 5421.7412 | 0.014 |  | 129.3975 | 0.1715
| 664.6376 | 7.4938 |  | 4804.9999 | 0.0551 |  | 5530.1761 | 0.014 |  | 131.9854 | 0.1649
| 681.4621 | 6.5316 |  | 4901.0999 | 0.0551 |  | 5640.7796 | 0.014 |  | 134.6251 | 0.1587
| 695.9249 | 5.8688 |  | 4999.1219 | 0.0551 |  | 5753.5952 | 0.014 |  | 137.3176 | 0.1527
| 715.6853 | 5.1386 |  | 5099.1043 | 0.0551 |  | 5868.6671 | 0.014 |  | 140.064 | 0.1469
| 739.6972 | 4.4456 |  | 5201.0864 | 0.0551 |  | 5986.0404 | 0.014 |  | 142.8653 | 0.1414
| 764.5143 | 3.8859 |  | 5305.1082 | 0.0551 |  | 6105.7612 | 0.014 |  | 145.7226 | 0.1361
| 791.7459 | 3.3999 |  | 5411.2103 | 0.0551 |  | 6227.8765 | 0.014 |  | 148.637 | 0.131
| 818.3098 | 3.0188 |  | 5519.4345 | 0.0551 |  | 6352.434 | 0.014 |  | 151.6098 | 0.1262
| 849.1549 | 2.6603 |  | 5629.8232 | 0.0551 |  | 6479.4827 | 0.014 |  | 154.642 | 0.1215
| 875.0148 | 2.412 |  | 5742.4197 | 0.0551 |  | 6609.0723 | 0.014 |  | 157.7348 | 0.1171
| 906.1833 | 2.1608 |  | 5857.2681 | 0.0551 |  | 6741.2538 | 0.014 |  | 160.8895 | 0.1128
| 942.2226 | 1.9208 |  | 5974.4134 | 0.0551 |  | 6876.0788 | 0.014 |  | 164.1073 | 0.1087
| 981.6565 | 1.7051 |  | 6093.9017 | 0.0551 |  | 7013.6004 | 0.014 |  | 167.3894 | 0.1048
| 1025.8127 | 1.5074 |  | 6215.7797 | 0.0551 |  | 7153.8724 | 0.014 |  | 170.7372 | 0.101
| 1070.8852 | 1.3415 |  | 6340.0953 | 0.0551 |  | 7296.9499 | 0.014 |  | 174.152 | 0.0973
| 1116.819 | 1.201 |  | 6466.8972 | 0.0551 |  | 7442.8889 | 0.014 |  | 177.635 | 0.0939
| 1171.731 | 1.0618 |  | 6596.2352 | 0.0551 |  | 7591.7466 | 0.014 |  | 181.1877 | 0.0905
| 1230.57 | 0.9395 |  | 6728.1599 | 0.0551 |  | 7743.5816 | 0.014 |  | 184.8115 | 0.0873
| 1296.262 | 0.8274 |  | 6862.7231 | 0.0551 |  | 7898.4532 | 0.014 |  | 188.5077 | 0.0842
| 1353.209 | 0.7465 |  | 6999.9776 | 0.0551 |  | 8056.4223 | 0.014 |  | 192.2778 | 0.0813
| 1419.748 | 0.6668 |  | 7139.9771 | 0.0551 |  | 8217.5507 | 0.014 |  | 196.1234 | 0.0784
| 1485.099 | 0.6008 |  | 7282.7766 | 0.0551 |  | 8381.9017 | 0.014 |  | 200.0459 | 0.0757
| 1558.128 | 0.5384 |  | 7428.4322 | 0.0551 |  | 8549.5398 | 0.014 |  | 204.0468 | 0.0731
| 1633.104 | 0.4843 |  | 7577.0008 | 0.0551 |  | 8720.5306 | 0.014 |  | 208.1277 | 0.0706
| 1734.084 | 0.4237 |  | 7728.5408 | 0.0551 |  | 8894.9412 | 0.014 |  | 212.2903 | 0.0682
| 1833.964 | 0.3746 |  | 7883.1117 | 0.0551 |  | 9072.84 | 0.014 |  | 216.5361 | 0.0659
| 2000.669 | 0.3101 |  | 8040.7739 | 0.055 |  | 9254.2968 | 0.014 |  | 220.8668 | 0.0637
| 2195.655 | 0.2542 |  | 8201.5894 | 0.055 |  | 9439.3827 | 0.014 |  | 225.2841 | 0.0616
| 2392.841 | 0.2119 |  | 8365.6212 | 0.055 |  | 9628.1704 | 0.014 |  | 229.7898 | 0.0597
| 2668.413 | 0.1686 |  | 8532.9336 | 0.055 |  | 9820.7338 | 0.014 |  | 234.3856 | 0.0581
| 2910.963 | 0.1407 |  | 8703.5923 | 0.055 |  | 10017.1485 | 0.014 |  | 239.0733 | 0.0565
| 3169.21 | 0.1181 |  | 8877.6641 | 0.055 |  | 10217.4914 | 0.014 |  | 243.8548 | 0.055
| 3440.041 | 0.0998 |  | 9055.2174 | 0.055 |  | 10421.8413 | 0.014 |  | 248.7319 | 0.0536
| 3798.036 | 0.0815 |  | 9236.3217 | 0.055 |  | 10630.2781 | 0.014 |  | 253.7065 | 0.0522
| 4189.086 | 0.0667 |  | 9421.0482 | 0.055 |  | 10842.8837 | 0.014 |  | 258.7807 | 0.0509
| 4737.37 | 0.052 |  | 9609.4691 | 0.055 |  | 11059.7413 | 0.014 |  | 263.9563 | 0.0496
| 5235.604 | 0.0443 |  | 9801.6585 | 0.055 |  | 11280.9362 | 0.014 |  | 269.2354 | 0.0484
| 5825.08 | 0.0377 |  | 9997.6917 | 0.055 |  | 11506.5549 | 0.014 |  | 274.6201 | 0.0472
| 6444.15 | 0.0326 |  | 10197.6455 | 0.055 |  | 11736.686 | 0.014 |  | 280.1125 | 0.0461
| 7086.37 | 0.0287 |  | 10401.5984 | 0.055 |  | 11971.4197 | 0.014 |  | 285.7147 | 0.045
| 7792.59 | 0.0254 |  | 10609.6304 | 0.055 | 200T | 538.56 | 788.682 |  | 291.429 | 0.044
| 8475.44 | 0.023 |  | 10821.823 | 0.055 |  | 549.3312 | 255.3629 |  | 297.2576 | 0.043
| 9135.54 | 0.0212 |  | 11038.2595 | 0.055 |  | 554.8 | 189.4467 |  | 303.2028 | 0.042
| 9527.41 | 0.0203 |  | 11259.0246 | 0.055 |  | 560.3178 | 150.0244 |  | 309.2668 | 0.0411
| 10000 | 0.016 |  | 11484.2051 | 0.055 |  | 565.9 | 123.7413 |  | 315.4522 | 0.0402
| 11250 | 0.016 |  | 11713.8892 | 0.055 |  | 571.5242 | 105.0354 |  | 321.7612 | 0.0393
20E | 44.88 | 279.2439 |  | 11948.167 | 0.055 |  | 577.2 | 91.0249 |  | 328.1964 | 0.0385
| 45.7776 | 90.3242 | 450Main | 502.3722 | 210.321 |  | 582.9547 | 80.0956 |  | 334.7604 | 0.0377
| 46.2 | 68.2719 |  | 507.6885 | 64.581 |  | 588.8 | 71.3193 |  | 341.4556 | 0.0369
| 46.6932 | 53.0111 |  | 519.0449 | 25.8081 |  | 594.6138 | 64.2541 |  | 348.2847 | 0.0361
| 47.2 | 43.0212 |  | 523.7 | 20.6536 |  | 600.6 | 58.2582 |  | 355.2504 | 0.0354
| 47.627 | 37.0761 |  | 528.3861 | 17.1731 |  | 606.506 | 53.3067 |  | 362.3554 | 0.0347
| 48.1 | 32.114 |  | 531.4 | 15.4838 |  | 612.6 | 48.9734 |  | 369.6025 | 0.0341
| 48.5796 | 28.2433 |  | 534.4768 | 14.0642 |  | 618.6362 | 45.2938 |  | 376.9945 | 0.0334
| 49.1 | 24.9464 |  | 539.3 | 12.2866 |  | 624.8 | 42.0396 |  | 384.5344 | 0.0328
| 49.5511 | 22.6334 |  | 544.0446 | 10.9182 |  | 631.0089 | 39.1787 |  | 392.2251 | 0.0322
| 50 | 20.7059 |  | 550.1 | 9.5489 |  | 637.3 | 36.6304 |  | 400.0696 | 0.0317
| 50.5422 | 18.7572 |  | 556.1006 | 8.4841 |  | 643.6291 | 34.3618 |  | 408.071 | 0.0311
| 51 | 17.3635 |  | 562.6 | 7.5617 |  | 656.5016 | 30.4716 |  | 416.2324 | 0.0306
| 51.553 | 15.9205 |  | 569.0168 | 6.8219 |  | 669.6317 | 27.2664 |  | 424.5571 | 0.0301
| 52.1 | 14.6992 |  | 577.5 | 6.0326 |  | 683.0243 | 24.5817 |  | 433.0482 | 0.0296
| 52.5841 | 13.756 |  | 585.8908 | 5.4059 |  | 696.6848 | 22.3015 |  | 441.7092 | 0.0291
| 53.1 | 12.8677 |  | 594.9 | 4.857 |  | 710.6185 | 20.3423 |  | 450.5434 | 0.0287
| 53.6358 | 12.0514 |  | 603.8945 | 4.4046 |  | 724.8309 | 18.6418 |  | 459.5542 | 0.0283
| 54.7085 | 10.6752 |  | 622.4515 | 3.6828 |  | 739.3275 | 17.1529 |  | 468.7453 | 0.0278
| 55.8026 | 9.5415 |  | 637.5743 | 3.2399 |  | 754.114 | 15.8394 |  | 478.1202 | 0.0274
| 56.9187 | 8.5922 |  | 660.605 | 2.7274 |  | 769.1963 | 14.6727 |  | 487.6826 | 0.0271
| 58.0571 | 7.7862 |  | 676.654 | 2.4505 |  | 784.5802 | 13.6302 |  | 497.4363 | 0.0267
| 59.2182 | 7.0939 |  | 709.192 | 2.0216 |  | 800.2718 | 12.6937 |  | 507.385 | 0.0263
| 60.4026 | 6.4932 |  | 727.9393 | 1.8314 |  | 816.2773 | 11.8485 |  | 517.5327 | 0.026
| 61.6106 | 5.9675 |  | 750.3089 | 1.6426 |  | 832.6028 | 11.0822 |  | 527.8834 | 0.0256
| 62.8428 | 5.5039 |  | 786.3878 | 1.4022 |  | 849.2549 | 10.3849 |  | 538.441 | 0.0253
| 64.0997 | 5.0923 |  | 815.6456 | 1.249 |  | 866.24 | 9.748 |  | 549.2099 | 0.025
| 65.3817 | 4.7247 |  | 848.6434 | 1.1084 |  | 883.5648 | 9.1644 |  | 560.1941 | 0.0247
| 66.6893 | 4.3946 |  | 882.0559 | 0.9919 |  | 901.2361 | 8.628 |  | 571.3979 | 0.0244
| 68.0231 | 4.0969 |  | 920.6186 | 0.8818 |  | 919.2608 | 8.1338 |  | 582.8259 | 0.0242
| 69.3836 | 3.8271 |  | 961.8719 | 0.7855 |  | 937.646 | 7.6771 |  | 594.4824 | 0.0239
| 70.7712 | 3.5817 |  | 1008.1236 | 0.6975 |  | 956.3989 | 7.2542 |  | 606.3721 | 0.0236
| 72.1867 | 3.3577 |  | 1054.3973 | 0.6252 |  | 975.5269 | 6.8617 |  | 618.4995 | 0.0234
| 73.6304 | 3.1526 |  | 1123.332 | 0.5391 |  | 995.0374 | 6.4967 |  | 630.8695 | 0.0232
| 75.103 | 2.9642 |  | 1198.424 | 0.4665 |  | 1014.9382 | 6.1567 |  | 643.4869 | 0.0229
| 76.6051 | 2.7907 |  | 1254.741 | 0.4225 |  | 1035.2369 | 5.8394 |  | 656.3566 | 0.0227
| 78.1372 | 2.6305 |  | 1365.427 | 0.3547 |  | 1055.9417 | 5.5427 |  | 669.4838 | 0.0225
| 79.6999 | 2.4822 |  | 1487.429 | 0.2998 |  | 1077.0605 | 5.265 |  | 682.8734 | 0.0223
| 81.2939 | 2.3448 |  | 1576.954 | 0.2685 |  | 1098.6017 | 5.0046 |  | 696.5309 | 0.0221
| 82.9198 | 2.217 |  | 1698.247 | 0.2352 |  | 1120.5738 | 4.7602 |  | 710.4615 | 0.0219
| 84.5782 | 2.0981 |  | 1836.52 | 0.2073 |  | 1142.9852 | 4.5304 |  | 724.6708 | 0.0217
| 86.2697 | 1.9872 |  | 1947.056 | 0.1894 |  | 1165.8449 | 4.3142 |  | 739.1642 | 0.0215
| 87.9951 | 1.8836 |  | 2075.046 | 0.1724 |  | 1189.1618 | 4.1105 |  | 753.9475 | 0.0214
| 89.755 | 1.7867 |  | 2183.925 | 0.1604 |  | 1212.9451 | 3.9184 |  | 769.0264 | 0.0212
| 91.5501 | 1.6959 |  | 2332.348 | 0.1468 |  | 1237.204 | 3.737 |  | 784.4069 | 0.0211
| 93.3811 | 1.6108 |  | 2444.501 | 0.1382 |  | 1261.9481 | 3.5657 |  | 800.0951 | 0.0209
| 95.2488 | 1.5308 |  | 2632.522 | 0.1262 |  | 1287.187 | 3.4036 |  | 816.097 | 0.0208
| 97.1537 | 1.4556 |  | 2808.5 | 0.1172 |  | 1312.9308 | 3.2502 |  | 832.4189 | 0.0206
| 99.0968 | 1.3849 |  | 3055 | 0.1072 |  | 1339.1894 | 3.105 |  | 849.0673 | 0.0205
| 101.0788 | 1.3182 |  | 3300 | 0.0995 |  | 1365.9732 | 2.9672 |  | 866.0486 | 0.0204
| 103.1003 | 1.2553 |  | 3585.407 | 0.0924 |  | 1393.2926 | 2.8366 |  | 883.3696 | 0.0202
| 105.1623 | 1.196 |  | 3849.111 | 0.0873 |  | 1421.1585 | 2.7126 |  | 901.037 | 0.0201
| 107.2656 | 1.1399 |  | 4114.996 | 0.083 |  | 1449.5816 | 2.5948 |  | 919.0577 | 0.02
| 109.4109 | 1.0869 |  | 4459.342 | 0.0787 |  | 1478.5733 | 2.4829 |  | 919.8809 | 0.016
| 111.5991 | 1.0368 |  | 4873.021 | 0.0746 |  | 1508.1447 | 2.3764 |  | 938.2786 | 0.016
| 113.8311 | 0.9893 |  | 5386.563 | 0.0709 |  | 1538.3076 | 2.2751 |  | 957.0441 | 0.016
| 116.1077 | 0.9442 |  | 5898.557 | 0.0681 |  | 1569.0738 | 2.1787 |  | 976.185 | 0.016
| 118.4299 | 0.9016 |  | 6385.485 | 0.066 |  | 1600.4553 | 2.0869 |  | 995.7087 | 0.016
| 120.7985 | 0.8611 |  | 6948.777 | 0.0641 |  | 1632.4644 | 1.9994 |  | 1015.6229 | 0.016
| 123.2144 | 0.8226 |  | 7538.119 | 0.0626 |  | 1665.1137 | 1.916 |  | 1035.9353 | 0.016
| 125.6787 | 0.7861 |  | 8332.521 | 0.061 |  | 1698.4159 | 1.8364 |  | 1056.6541 | 0.016
| 128.1923 | 0.7514 |  | 8954.714 | 0.0601 |  | 1732.3843 | 1.7605 |  | 1077.7871 | 0.016
| 130.7561 | 0.7184 |  | 9734.483 | 0.0593 |  | 1767.0319 | 1.688 |  | 1099.3429 | 0.016
| 133.3713 | 0.6871 |  | 10907.338 | 0.0584 |  | 1802.3726 | 1.6189 |  | 1121.3297 | 0.016
| 136.0387 | 0.6572 |  | 11431.828 | 0.0581 |  | 1838.42 | 1.5528 |  | 1143.7563 | 0.016
| 138.7595 | 0.6288 | 500Main | 556.6814 | 493.0023 |  | 1875.1884 | 1.4897 |  | 1166.6315 | 0.016
| 141.5347 | 0.6017 |  | 564.2857 | 63.1854 |  | 1912.6922 | 1.4293 |  | 1189.9641 | 0.016
| 144.3654 | 0.5759 |  | 571.9934 | 33.3496 |  | 1950.946 | 1.3716 |  | 1213.7634 | 0.016
| 147.2527 | 0.5513 |  | 576.2 | 26.4648 |  | 1989.965 | 1.3165 |  | 1238.0386 | 0.016
| 150.1977 | 0.5278 |  | 580.4128 | 21.9058 |  | 2029.7643 | 1.2637 |  | 1262.7994 | 0.016
| 153.2017 | 0.5054 |  | 587.8 | 16.7886 |  | 2070.3596 | 1.2132 |  | 1288.0554 | 0.016
| 156.2657 | 0.4841 |  | 595.1352 | 13.5986 |  | 2111.7667 | 1.1649 |  | 1313.8165 | 0.016
| 159.391 | 0.4637 |  | 604 | 11.0338 |  | 2154.0021 | 1.1186 |  | 1340.0928 | 0.016
| 162.5788 | 0.4442 |  | 612.7825 | 9.2774 |  | 2197.0821 | 1.0743 |  | 1366.8947 | 0.016
| 165.8304 | 0.4256 |  | 620.9 | 8.0747 |  | 2241.0238 | 1.0318 |  | 1394.2326 | 0.016
| 169.147 | 0.4079 |  | 628.9822 | 7.1421 |  | 2285.8442 | 0.9912 |  | 1422.1172 | 0.016
| 172.53 | 0.3909 |  | 637 | 6.4004 |  | 2331.5611 | 0.9522 |  | 1450.5596 | 0.016
| 175.9806 | 0.3747 |  | 644.9355 | 5.7979 |  | 2378.1923 | 0.9149 |  | 1479.5708 | 0.016
| 179.5002 | 0.3592 |  | 653.8 | 5.2404 |  | 2425.7562 | 0.8791 |  | 1509.1622 | 0.016
| 183.0902 | 0.3444 |  | 662.6763 | 4.7752 |  | 2474.2713 | 0.8447 |  | 1539.3454 | 0.016
| 186.752 | 0.3302 |  | 685.1823 | 3.883 |  | 2523.7567 | 0.8118 |  | 1570.1323 | 0.016
| 190.487 | 0.3166 |  | 709.192 | 3.2218 |  | 2574.2319 | 0.7803 |  | 1601.535 | 0.016
| 194.2968 | 0.3037 |  | 741.7443 | 2.6006 |  | 2625.7165 | 0.75 |  | 1633.5657 | 0.016
| 198.1827 | 0.2913 |  | 773.3649 | 2.1776 |  | 2678.2308 | 0.7209 |  | 1666.237 | 0.016
| 202.1463 | 0.2794 |  | 816.497 | 1.7691 |  | 2731.7955 | 0.6931 |  | 1699.5617 | 0.016
| 206.1893 | 0.268 |  | 865.6395 | 1.4457 |  | 2786.4314 | 0.6663 |  | 1733.553 | 0.016
| 210.3131 | 0.2571 |  | 914.8722 | 1.2133 |  | 2842.16 | 0.6407 |  | 1768.224 | 0.016
| 214.5193 | 0.2467 |  | 958.8645 | 1.0556 |  | 2899.0032 | 0.616 |  | 1803.5885 | 0.016
| 218.8097 | 0.2367 |  | 1010.2301 | 0.9121 |  | 2956.9833 | 0.5923 |  | 1839.6603 | 0.016
| 223.1859 | 0.2271 |  | 1065.46 | 0.7918 |  | 3016.1229 | 0.5696 |  | 1839.7619 | 0.014
| 227.6496 | 0.2179 |  | 1124.882 | 0.6902 |  | 3076.4454 | 0.5478 |  | 1876.5571 | 0.014
| 232.2026 | 0.2092 |  | 1180.2032 | 0.6143 |  | 3137.9743 | 0.5269 |  | 1914.0883 | 0.014
| 236.8467 | 0.2007 |  | 1259.0974 | 0.5285 |  | 3200.7338 | 0.5067 |  | 1952.37 | 0.014
| 241.5836 | 0.1927 |  | 1332.0967 | 0.4661 |  | 3264.7485 | 0.4874 |  | 1991.4174 | 0.014
| 246.4153 | 0.1849 |  | 1365.427 | 0.4418 |  | 3330.0434 | 0.4688 |  | 2031.2458 | 0.014
| 251.3436 | 0.1775 |  | 1467.384 | 0.3796 |  | 3396.6443 | 0.451 |  | 2071.8707 | 0.014
| 256.3704 | 0.1704 |  | 1563.842 | 0.3339 |  | 3464.5772 | 0.4339 |  | 2113.3081 | 0.014
| 261.4979 | 0.1636 |  | 1728.647 | 0.2754 |  | 3533.8687 | 0.4174 |  | 2155.5743 | 0.014
| 266.7278 | 0.1571 |  | 1869.396 | 0.2389 |  | 3604.5461 | 0.4015 |  | 2198.6858 | 0.014
| 272.0624 | 0.1508 |  | 2006.888 | 0.2128 |  | 3676.637 | 0.3863 |  | 2242.6595 | 0.014
| 277.5036 | 0.1448 |  | 2186.205 | 0.1865 |  | 3750.1698 | 0.3717 |  | 2287.5127 | 0.014
| 283.0537 | 0.139 |  | 2369.149 | 0.1659 |  | 3825.1732 | 0.3576 |  | 2333.2629 | 0.014
| 288.7148 | 0.1335 |  | 2540.745 | 0.1507 |  | 3901.6766 | 0.3441 |  | 2379.9282 | 0.014
| 294.4891 | 0.1282 |  | 2716.252 | 0.1382 |  | 3979.7101 | 0.3311 |  | 2427.5267 | 0.014
| 300.3788 | 0.1231 |  | 2906.914 | 0.1272 |  | 4059.3043 | 0.3186 |  | 2476.0773 | 0.014
| 306.3864 | 0.1182 |  | 3146.881 | 0.1162 |  | 4140.4904 | 0.3066 |  | 2525.5988 | 0.014
| 312.5141 | 0.1135 |  | 3445.993 | 0.1056 |  | 4223.3002 | 0.2951 |  | 2576.1108 | 0.014
| 318.7644 | 0.109 |  | 3676.35 | 0.0992 |  | 4307.7662 | 0.284 |  | 2627.633 | 0.014
| 325.1397 | 0.1047 |  | 3988.15 | 0.0923 |  | 4393.9216 | 0.2733 |  | 2680.1857 | 0.014
| 331.6425 | 0.1006 |  | 4349.03 | 0.0861 |  | 4481.8 | 0.263 |  | 2733.7894 | 0.014
| 338.2754 | 0.0966 |  | 4693.327 | 0.0816 |  | 4571.436 | 0.2532 |  | 2788.4652 | 0.014
| 345.0409 | 0.0928 |  | 4970.617 | 0.0785 |  | 4662.8647 | 0.2436 |  | 2844.2345 | 0.014
| 351.9417 | 0.0891 |  | 5448.76 | 0.0744 |  | 4756.122 | 0.2345 |  | 2901.1192 | 0.014
| 358.9805 | 0.0856 |  | 5892.404 | 0.0714 |  | 4851.2445 | 0.2257 |  | 2959.1415 | 0.014
| 366.1601 | 0.0822 |  | 6418.894 | 0.0687 |  | 4948.2693 | 0.2173 |  | 3018.3244 | 0.014
| 373.4833 | 0.079 |  | 7162.309 | 0.0658 |  | 5047.2347 | 0.2091 |  | 3078.6909 | 0.014
| 380.953 | 0.0759 |  | 7721.259 | 0.0641 |  | 5148.1794 | 0.2013 |  | 3140.2647 | 0.014
| 388.5721 | 0.0729 |  | 8437.535 | 0.0625 |  | 5251.143 | 0.1938 |  | 3203.07 | 0.014
| 396.3435 | 0.07 |  | 9326.722 | 0.0609 |  | 5356.1659 | 0.1865 |  | 3267.1314 | 0.014
| 404.2704 | 0.0673 |  | 10086.115 | 0.0599 |  | 5463.2892 | 0.1795 |  | 3332.474 | 0.014
| 412.3558 | 0.0646 |  | 11033.281 | 0.0591 |  | 5572.555 | 0.1728 |  | 3399.1235 | 0.014
| 420.6029 | 0.0621 | 50Main | 56.1 | 101.5883 |  | 5684.0061 | 0.1664 |  | 3467.1059 | 0.014
| 429.015 | 0.0597 |  | 57.222 | 32.8902 |  | 5797.6862 | 0.1602 |  | 3536.4481 | 0.014
| 437.5953 | 0.0573 |  | 57.8 | 24.3074 |  | 5913.6399 | 0.1542 |  | 3607.177 | 0.014
| 446.3472 | 0.0551 |  | 58.3664 | 19.3218 |  | 6031.9127 | 0.1484 |  | 3679.3206 | 0.014
| 455.2741 | 0.0529 |  | 59 | 15.6891 |  | 6152.551 | 0.1429 |  | 3752.907 | 0.014
| 464.3796 | 0.0511 |  | 59.5338 | 13.5272 |  | 6275.602 | 0.1376 |  | 3827.9651 | 0.014
| 473.6672 | 0.0495 |  | 60.1 | 11.7896 |  | 6401.114 | 0.1325 |  | 3904.5244 | 0.014
| 483.1405 | 0.048 |  | 60.7244 | 10.3153 |  | 6529.1363 | 0.1275 |  | 3982.6149 | 0.014
| 492.8033 | 0.0465 |  | 61.3 | 9.2408 |  | 6659.719 | 0.1228 |  | 4062.2672 | 0.014
| 502.6594 | 0.0451 |  | 61.9389 | 8.2753 |  | 6792.9134 | 0.1182 |  | 4143.5125 | 0.014
| 512.7126 | 0.0437 |  | 62.6 | 7.4612 |  | 6928.7717 | 0.1138 |  | 4226.3828 | 0.014
| 522.9668 | 0.0424 |  | 63.1777 | 6.8658 |  | 7067.3471 | 0.1096 |  | 4310.9105 | 0.014
| 533.4262 | 0.0411 |  | 63.8 | 6.3181 |  | 7208.6941 | 0.1055 |  | 4397.1287 | 0.014
| 544.0947 | 0.0399 |  | 64.4413 | 5.8343 |  | 7352.868 | 0.1016 |  | 4485.0712 | 0.014
| 554.9766 | 0.0387 |  | 65.1 | 5.4053 |  | 7499.9253 | 0.0978 |  | 4574.7727 | 0.014
| 566.0761 | 0.0376 |  | 65.7301 | 5.0472 |  | 7649.9238 | 0.0942 |  | 4666.2681 | 0.014
| 577.3976 | 0.0365 |  | 66.4 | 4.7124 |  | 7802.9223 | 0.0907 |  | 4759.5935 | 0.014
| 588.9456 | 0.0355 |  | 67.0447 | 4.4273 |  | 7958.9807 | 0.0873 |  | 4854.7853 | 0.014
| 600.7245 | 0.0345 |  | 68.3856 | 3.9269 |  | 8118.1604 | 0.0841 |  | 4951.8811 | 0.014
| 612.739 | 0.0335 |  | 69.7533 | 3.5146 |  | 8280.5236 | 0.0809 |  | 5050.9187 | 0.014
| 624.9938 | 0.0326 |  | 71.1484 | 3.1694 |  | 8446.134 | 0.0779 |  | 5151.937 | 0.014
| 637.4937 | 0.0317 |  | 72.5713 | 2.8763 |  | 8615.0567 | 0.075 |  | 5254.9758 | 0.014
| 650.2435 | 0.0309 |  | 74.0228 | 2.6246 |  | 8787.3579 | 0.0723 |  | 5360.0753 | 0.014
| 663.2484 | 0.0301 |  | 75.5032 | 2.4062 |  | 8963.105 | 0.0696 |  | 5467.2768 | 0.014
| 676.5134 | 0.0293 |  | 77.0133 | 2.215 |  | 9142.3671 | 0.067 |  | 5576.6223 | 0.014
| 690.0436 | 0.0285 |  | 78.5535 | 2.0464 |  | 9325.2145 | 0.0645 |  | 5688.1548 | 0.014
| 703.8445 | 0.0278 |  | 80.1246 | 1.8967 |  | 9511.7187 | 0.0621 |  | 5801.9179 | 0.014
| 717.9214 | 0.0271 |  | 81.7271 | 1.7631 |  | 9701.9531 | 0.0598 |  | 5917.9562 | 0.014
| 732.2798 | 0.0265 |  | 83.3616 | 1.643 |  | 9895.9922 | 0.0576 |  | 6036.3154 | 0.014
| 746.9254 | 0.0258 |  | 85.0289 | 1.5348 |  | 10093.912 | 0.0555 |  | 6157.0417 | 0.014
| 761.8639 | 0.0252 |  | 86.7295 | 1.4367 |  | 10295.7903 | 0.0537 |  | 6280.1825 | 0.014
| 777.1012 | 0.0246 |  | 88.464 | 1.3474 |  | 10501.7061 | 0.0521 |  | 6405.7862 | 0.014
| 792.6432 | 0.024 |  | 90.2333 | 1.266 |  | 10711.7402 | 0.0505 |  | 6533.9019 | 0.014
| 808.4961 | 0.0235 |  | 92.038 | 1.1914 |  | 10925.975 | 0.049 |  | 6664.5799 | 0.014
| 824.666 | 0.023 |  | 93.8788 | 1.1229 |  | 11144.4945 | 0.0476 |  | 6797.8715 | 0.014
| 841.1593 | 0.0225 |  | 95.7563 | 1.0598 |  | 11367.3844 | 0.0462 |  | 6933.829 | 0.014
| 857.9825 | 0.022 |  | 97.6715 | 1.0015 |  | 11594.7321 | 0.0448 |  | 7072.5055 | 0.014
| 875.1422 | 0.0215 |  | 99.6249 | 0.9476 |  | 11826.6267 | 0.0436 |  | 7213.9556 | 0.014
| 892.645 | 0.0211 |  | 101.6174 | 0.8976 | 20T | 47.685 | 685.224 |  | 7358.2348 | 0.014
| 910.4979 | 0.0206 |  | 103.6497 | 0.8512 |  | 48.6387 | 221.6425 |  | 7505.3994 | 0.014
| 928.7079 | 0.0202 |  | 105.7227 | 0.8079 |  | 49.1 | 166.3925 |  | 7655.5074 | 0.014
| 938.9356 | 0.016 |  | 107.8372 | 0.7676 |  | 49.6115 | 130.0816 |  | 7808.6176 | 0.014
| 957.7143 | 0.016 |  | 109.9939 | 0.7299 |  | 50.1 | 107.4571 |  | 7964.7899 | 0.014
| 976.8686 | 0.016 |  | 112.1938 | 0.6947 |  | 50.6037 | 90.9795 |  | 8124.0857 | 0.014
| 996.4059 | 0.016 |  | 114.4377 | 0.6617 |  | 51.1 | 78.935 |  | 8286.5675 | 0.014
| 1016.3341 | 0.016 |  | 116.7264 | 0.6307 |  | 51.6158 | 69.3049 |  | 8452.2988 | 0.014
| 1036.6607 | 0.016 |  | 119.061 | 0.6017 |  | 52.1 | 62.1206 |  | 8621.3448 | 0.014
| 1057.3939 | 0.016 |  | 121.4422 | 0.5743 |  | 52.6481 | 55.5391 |  | 8793.7717 | 0.014
| 1078.5418 | 0.016 |  | 123.871 | 0.5486 |  | 53.2 | 50.1343 |  | 8969.6471 | 0.014
| 1100.1127 | 0.016 |  | 126.3484 | 0.5244 |  | 53.7011 | 46.0274 |  | 9149.04 | 0.014
| 1122.1149 | 0.016 |  | 128.8754 | 0.5015 |  | 54.2 | 42.526 |  | 9332.0209 | 0.014
| 1144.5572 | 0.016 |  | 131.4529 | 0.4799 |  | 54.7751 | 39.0665 |  | 9518.6613 | 0.014
| 1167.4484 | 0.016 |  | 134.082 | 0.4595 |  | 55.3 | 36.3408 |  | 9709.0345 | 0.014
| 1190.7973 | 0.016 |  | 136.7636 | 0.4402 |  | 55.8706 | 33.7553 |  | 9903.2152 | 0.014
| 1214.6133 | 0.016 |  | 139.4989 | 0.422 |  | 56.4 | 31.6456 |  | 10101.2795 | 0.014
| 1238.9055 | 0.016 |  | 142.2889 | 0.4047 |  | 56.988 | 29.5725 |  | 10303.3051 | 0.014
| 1263.6837 | 0.016 |  | 145.1346 | 0.3884 |  | 58.1277 | 26.1953 |  | 10509.3712 | 0.014
| 1288.9573 | 0.016 |  | 148.0373 | 0.3728 |  | 59.2903 | 23.4135 |  | 10719.5586 | 0.014
| 1314.7365 | 0.016 |  | 150.9981 | 0.3581 |  | 60.4761 | 21.084 |  | 10933.9498 | 0.014
| 1341.0312 | 0.016 |  | 154.018 | 0.3441 |  | 61.6856 | 19.1062 |  | 11152.6288 | 0.014
| 1367.8518 | 0.016 |  | 157.0984 | 0.3309 |  | 62.9193 | 17.4074 |  | 11375.6813 | 0.014
| 1395.2089 | 0.016 |  | 160.2404 | 0.3182 |  | 64.1777 | 15.9334 |  | 11603.195 | 0.014
| 1423.113 | 0.016 |  | 163.4452 | 0.3063 |  | 65.4613 | 14.6434 |  | 11835.2589 | 0.014
| 1451.5753 | 0.016 |  | 166.7141 | 0.2948 |  | 66.7705 | 13.5057 | 350Tap | 393.2984 | 92.3708
| 1480.6068 | 0.016 |  | 170.0484 | 0.284 |  | 68.1059 | 12.4957 |  | 401.6122 | 31.7144
| 1510.2189 | 0.016 |  | 173.4493 | 0.2736 |  | 69.468 | 11.5937 |  | 406.3 | 23.0546
| 1540.4233 | 0.016 |  | 176.9183 | 0.2638 |  | 70.8574 | 10.7838 |  | 410.927 | 18.1209
| 1571.2318 | 0.016 |  | 180.4567 | 0.2544 |  | 72.2746 | 10.0531 |  | 418.8 | 13.236
| 1602.6564 | 0.016 |  | 184.0658 | 0.2455 |  | 73.72 | 9.3911 |  | 426.591 | 10.4121
| 1634.7096 | 0.016 |  | 187.7471 | 0.2372 |  | 75.1944 | 8.7889 |  | 431.4 | 9.1865
| 1667.4037 | 0.016 |  | 191.5021 | 0.2296 |  | 76.6983 | 8.2393 |  | 436.1764 | 8.2163
| 1700.7518 | 0.016 |  | 195.3321 | 0.2223 |  | 78.2323 | 7.736 |  | 443.3 | 7.0867
| 1734.7669 | 0.016 |  | 199.2388 | 0.2153 |  | 79.7969 | 7.2737 |  | 450.4863 | 6.2126
| 1769.4622 | 0.016 |  | 203.2235 | 0.2086 |  | 81.3929 | 6.8479 |  | 458.4 | 5.46
| 1804.8514 | 0.016 |  | 207.288 | 0.2023 |  | 83.0207 | 6.4548 |  | 466.2273 | 4.8678
| 1840.9485 | 0.016 |  | 211.4338 | 0.1962 |  | 84.6812 | 6.0911 |  | 488.0634 | 3.7128
| 1877.7674 | 0.016 |  | 215.6625 | 0.1903 |  | 86.3748 | 5.7537 |  | 510.9225 | 2.9499
| 1877.8711 | 0.016 |  | 219.9757 | 0.1847 |  | 88.1023 | 5.4402 |  | 537.0827 | 2.369
| 1915.4286 | 0.014 |  | 224.3752 | 0.1794 |  | 89.8643 | 5.1484 |  | 562.2375 | 1.9783
| 1953.7371 | 0.014 |  | 228.8627 | 0.1743 |  | 91.6616 | 4.8762 |  | 601.8782 | 1.5538
| 1992.8119 | 0.014 |  | 233.44 | 0.1694 |  | 93.4948 | 4.622 |  | 642.9841 | 1.2573
| 2032.6681 | 0.014 |  | 238.1088 | 0.1647 |  | 95.3647 | 4.3843 |  | 682.264 | 1.0543
| 2073.3215 | 0.014 |  | 242.8709 | 0.1602 |  | 97.272 | 4.1615 |  | 719.4385 | 0.9086
| 2114.7879 | 0.014 |  | 247.7284 | 0.1559 |  | 99.2175 | 3.9526 |  | 759.4279 | 0.7862
| 2157.0837 | 0.014 |  | 252.6829 | 0.1518 |  | 101.2018 | 3.7564 |  | 818.4935 | 0.6497
| 2200.2253 | 0.014 |  | 257.7366 | 0.1479 |  | 103.2259 | 3.5719 |  | 866.69 | 0.565
| 2244.2298 | 0.014 |  | 262.8913 | 0.1441 |  | 105.2904 | 3.3983 |  | 934.098 | 0.4737
| 2289.1144 | 0.014 |  | 268.1492 | 0.1405 |  | 107.3962 | 3.2347 |  | 997.3678 | 0.4081
| 2334.8967 | 0.014 |  | 273.5121 | 0.137 |  | 109.5441 | 3.0804 |  | 1051.7111 | 0.3628
| 2381.5947 | 0.014 |  | 278.9824 | 0.1336 |  | 111.735 | 2.9348 |  | 1133 | 0.3088
| 2429.2266 | 0.014 |  | 284.562 | 0.1305 |  | 113.9697 | 2.7972 |  | 1205 | 0.271
| 2477.8111 | 0.014 |  | 290.2533 | 0.1274 |  | 116.2491 | 2.6671 |  | 1298.164 | 0.2323
| 2527.3673 | 0.014 |  | 296.0583 | 0.1245 |  | 118.5741 | 2.544 |  | 1404.965 | 0.1979
| 2577.9147 | 0.014 |  | 301.9795 | 0.1217 |  | 120.9455 | 2.4275 |  | 1525.306 | 0.168
| 2629.4729 | 0.014 |  | 308.0191 | 0.119 |  | 123.3645 | 2.317 |  | 1681.997 | 0.1389
| 2682.0624 | 0.014 |  | 314.1795 | 0.1164 |  | 125.8317 | 2.2123 |  | 1839.412 | 0.1172
| 2735.7036 | 0.014 |  | 320.4631 | 0.1139 |  | 128.3484 | 2.113 |  | 1993 | 0.1009
| 2790.4177 | 0.014 |  | 326.8723 | 0.1115 |  | 130.9153 | 2.0186 |  | 2177.052 | 0.0858
| 2846.2261 | 0.014 |  | 333.4098 | 0.1092 |  | 133.5336 | 1.9291 |  | 2395.705 | 0.0723
| 2903.1506 | 0.014 |  | 340.078 | 0.107 |  | 136.2043 | 1.8439 |  | 2639.063 | 0.0612
| 2961.2136 | 0.014 |  | 346.8795 | 0.1049 |  | 138.9284 | 1.763 |  | 2874.064 | 0.0543
| 3020.4379 | 0.014 |  | 353.8171 | 0.1029 |  | 141.707 | 1.6859 |  | 3123.486 | 0.0488
| 3080.8466 | 0.014 |  | 360.8935 | 0.101 |  | 144.5411 | 1.6127 |  | 3391.024 | 0.0441
| 3142.4636 | 0.014 |  | 368.1113 | 0.0991 |  | 147.4319 | 1.5429 |  | 3628.249 | 0.0408
| 3205.3128 | 0.014 |  | 375.4736 | 0.0973 |  | 150.3806 | 1.4764 |  | 3947.226 | 0.0372
| 3269.4191 | 0.014 |  | 382.983 | 0.0956 |  | 153.3882 | 1.4131 |  | 4240.972 | 0.0346
| 3334.8075 | 0.014 |  | 390.6427 | 0.094 |  | 156.456 | 1.3527 |  | 4618.619 | 0.032
| 3401.5036 | 0.014 |  | 398.4555 | 0.0924 |  | 159.5851 | 1.2951 |  | 4967.494 | 0.03
| 3469.5337 | 0.014 |  | 406.4246 | 0.0909 |  | 162.7768 | 1.2402 |  | 5494.913 | 0.0277
| 3538.9244 | 0.014 |  | 414.5531 | 0.0894 |  | 166.0323 | 1.1878 |  | 5950 | 0.0262
| 3609.7029 | 0.014 |  | 422.8442 | 0.088 |  | 169.353 | 1.1378 |  | 6564.728 | 0.0247
| 3681.8969 | 0.014 |  | 431.3011 | 0.0867 |  | 172.74 | 1.0901 |  | 7112.209 | 0.0236
| 3755.5349 | 0.014 |  | 439.9271 | 0.0854 |  | 176.1948 | 1.0445 |  | 7818.389 | 0.0225
| 3830.6456 | 0.014 |  | 448.7257 | 0.0842 |  | 179.7187 | 1.0009 |  | 8590 | 0.0216
| 3907.2585 | 0.014 |  | 457.7002 | 0.083 |  | 183.3131 | 0.9593 |  | 9275 | 0.021
| 3985.4036 | 0.014 |  | 466.8542 | 0.0818 |  | 186.9793 | 0.9195 |  | 10236.008 | 0.0203
| 4065.1117 | 0.014 |  | 476.1913 | 0.0808 |  | 190.7189 | 0.8814 | 400Tap | 448.7835 | 107.3554
| 4146.4139 | 0.014 |  | 485.7151 | 0.0797 |  | 194.5333 | 0.8451 |  | 459.4898 | 30.636
| 4229.3422 | 0.014 |  | 495.4294 | 0.0787 |  | 198.424 | 0.8103 |  | 464.3 | 23.1053
| 4313.9291 | 0.014 |  | 505.338 | 0.0777 |  | 202.3925 | 0.777 |  | 469.0378 | 18.5685
| 4400.2077 | 0.014 |  | 515.4447 | 0.0768 |  | 206.4403 | 0.7452 |  | 479.2 | 13.0113
| 4488.2118 | 0.014 |  | 525.7536 | 0.0759 |  | 210.5691 | 0.7147 |  | 489.4285 | 9.9554
| 4577.976 | 0.014 |  | 536.2687 | 0.075 |  | 214.7805 | 0.6855 |  | 498 | 8.2949
| 4669.5356 | 0.014 |  | 546.9941 | 0.0742 |  | 219.0761 | 0.6576 |  | 506.5434 | 7.0969
| 4762.9263 | 0.014 |  | 557.9339 | 0.0734 |  | 223.4576 | 0.6309 |  | 516.4 | 6.0694
| 4858.1848 | 0.014 |  | 569.0926 | 0.0727 |  | 227.9268 | 0.6053 |  | 526.2675 | 5.2896
| 4955.3485 | 0.014 |  | 580.4745 | 0.0719 |  | 232.4853 | 0.5808 |  | 533 | 4.8578
| 5054.4555 | 0.014 |  | 592.084 | 0.0712 |  | 237.135 | 0.5573 |  | 539.7579 | 4.4861
| 5155.5446 | 0.014 |  | 603.9256 | 0.0706 |  | 241.8777 | 0.5348 |  | 564.6333 | 3.4804
| 5258.6555 | 0.014 |  | 616.0042 | 0.0699 |  | 246.7153 | 0.5132 |  | 598.0601 | 2.6463
| 5363.8286 | 0.014 |  | 628.3242 | 0.0693 |  | 251.6496 | 0.4926 |  | 629.1428 | 2.1451
| 5471.1051 | 0.014 |  | 640.8907 | 0.0687 |  | 256.6826 | 0.4728 |  | 666.0412 | 1.736
| 5580.5273 | 0.014 |  | 653.7085 | 0.0681 |  | 261.8162 | 0.4538 |  | 704.9735 | 1.433
| 5692.1378 | 0.014 |  | 666.7827 | 0.0676 |  | 267.0526 | 0.4356 |  | 750.6477 | 1.1787
| 5805.9806 | 0.014 |  | 680.1184 | 0.067 |  | 272.3936 | 0.4182 |  | 796.2438 | 0.9933
| 5922.1002 | 0.014 |  | 693.7207 | 0.0665 |  | 277.8415 | 0.4015 |  | 844.0234 | 0.8465
| 6040.5422 | 0.014 |  | 707.5951 | 0.066 |  | 283.3983 | 0.3854 |  | 907.7981 | 0.7004
| 6161.353 | 0.014 |  | 721.7471 | 0.0656 |  | 289.0663 | 0.37 |  | 984.555 | 0.5732
| 6284.5801 | 0.014 |  | 736.182 | 0.0651 |  | 294.8476 | 0.3553 |  | 1057.848 | 0.4838
| 6410.2717 | 0.014 |  | 750.9056 | 0.0647 |  | 300.7445 | 0.3412 |  | 1142.526 | 0.406
| 6538.4771 | 0.014 |  | 765.9237 | 0.0643 |  | 306.7594 | 0.3276 |  | 1228.8573 | 0.3457
| 6669.2466 | 0.014 |  | 781.2422 | 0.0639 |  | 312.8946 | 0.3146 |  | 1320.3366 | 0.2962
| 6802.6316 | 0.014 |  | 796.8671 | 0.0635 |  | 319.1525 | 0.3021 |  | 1446.9543 | 0.2446
| 6938.6842 | 0.014 |  | 812.8044 | 0.0631 |  | 325.5356 | 0.2901 |  | 1583.091 | 0.2036
| 7077.4579 | 0.014 |  | 829.0605 | 0.0628 |  | 332.0463 | 0.2786 |  | 1742.142 | 0.1682
| 7219.0071 | 0.014 |  | 845.6417 | 0.0624 |  | 338.6872 | 0.2676 |  | 1917.172 | 0.1397
| 7363.3872 | 0.014 |  | 862.5545 | 0.0621 |  | 345.461 | 0.257 |  | 2077.112 | 0.1199
| 7510.6549 | 0.014 |  | 879.8056 | 0.0618 |  | 352.3702 | 0.2468 |  | 2275.558 | 0.1011
| 7660.868 | 0.014 |  | 897.4017 | 0.0615 |  | 359.4176 | 0.2371 |  | 2520.837 | 0.0838
| 7814.0854 | 0.014 |  | 915.3498 | 0.0612 |  | 366.6059 | 0.2277 |  | 2800.039 | 0.0695
| 7970.3671 | 0.014 |  | 933.6568 | 0.0609 |  | 373.938 | 0.2187 |  | 3090.99 | 0.059
| 8129.7744 | 0.014 |  | 952.3299 | 0.0606 |  | 381.4168 | 0.2101 |  | 3447.866 | 0.051
| 8292.3699 | 0.014 |  | 971.3765 | 0.0604 |  | 389.0451 | 0.2018 |  | 3790.322 | 0.0453
| 8458.2173 | 0.014 |  | 990.804 | 0.0601 |  | 396.826 | 0.1939 |  | 4227.941 | 0.0399
| 8627.3817 | 0.014 |  | 1010.6201 | 0.0599 |  | 404.7626 | 0.1862 |  | 4730.832 | 0.0355
| 8799.9293 | 0.014 |  | 1030.8325 | 0.0597 |  | 412.8578 | 0.1789 |  | 5348.911 | 0.0316
| 8975.9279 | 0.014 |  | 1051.4492 | 0.0595 |  | 421.115 | 0.1719 |  | 6066.652 | 0.0285
| 9155.4465 | 0.014 |  | 1072.4782 | 0.0594 |  | 429.5373 | 0.1651 |  | 7010.799 | 0.0257
| 9338.5554 | 0.014 |  | 1093.9277 | 0.0592 |  | 438.128 | 0.1586 |  | 7731.238 | 0.0242
| 9525.3265 | 0.014 |  | 1115.8063 | 0.059 |  | 446.8906 | 0.1524 |  | 8614.893 | 0.0229
| 9715.833 | 0.014 |  | 1138.1224 | 0.0589 |  | 455.8284 | 0.1464 |  | 9649.624 | 0.0217
| 9910.1497 | 0.014 |  | 1160.8848 | 0.0587 |  | 464.945 | 0.1407 |  | 10707.881 | 0.0209
| 10108.3527 | 0.014 |  | 1184.1025 | 0.0586 |  | 474.2439 | 0.1352 |  | 11845.158 | 0.0202
| 10310.5197 | 0.014 |  | 1207.7846 | 0.0584 |  | 483.7287 | 0.1299 | 40Tap | 44.88 | 106.9469
| 10516.7301 | 0.014 |  | 1231.9403 | 0.0583 |  | 493.4033 | 0.1248 |  | 45.7776 | 34.6325
| 10727.0647 | 0.014 |  | 1256.5791 | 0.0582 |  | 503.2714 | 0.1199 |  | 46.2 | 26.1911
| 10941.606 | 0.014 |  | 1281.7107 | 0.058 |  | 513.3368 | 0.1152 |  | 46.6932 | 20.3493
| 11160.4381 | 0.014 |  | 1307.3449 | 0.0579 |  | 523.6035 | 0.1107 |  | 47.2 | 16.525
| 11383.6469 | 0.014 |  | 1333.4918 | 0.0578 |  | 534.0756 | 0.1063 |  | 47.627 | 14.2491
| 11611.3198 | 0.014 |  | 1360.1616 | 0.0577 |  | 544.7571 | 0.1022 |  | 48.1 | 12.3494
| 11843.5462 | 0.014 |  | 1387.3648 | 0.0576 |  | 555.6523 | 0.0982 |  | 48.5796 | 10.8674
250E | 650.8249 | 424.1758 |  | 1415.1121 | 0.0575 |  | 566.7653 | 0.0943 |  | 49.1 | 9.6051
| 667.3007 | 65.3756 |  | 1443.4144 | 0.0574 |  | 578.1006 | 0.0907 |  | 49.5511 | 8.7194
| 676.4 | 44.2856 |  | 1472.2827 | 0.0573 |  | 589.6626 | 0.0871 |  | 50 | 7.9813
| 685.564 | 33.3148 |  | 1501.7283 | 0.0572 |  | 601.4559 | 0.0837 |  | 50.5422 | 7.235
| 696 | 25.9022 |  | 1531.7629 | 0.0571 |  | 613.485 | 0.0804 |  | 51 | 6.7013
| 706.442 | 21.1276 |  | 1562.3982 | 0.0571 |  | 625.7547 | 0.0773 |  | 51.553 | 6.1485
| 720.5 | 16.8683 |  | 1593.6461 | 0.057 |  | 638.2698 | 0.0743 |  | 52.1 | 5.6807
| 734.5371 | 13.9955 |  | 1625.519 | 0.0569 |  | 651.0352 | 0.0714 |  | 52.5841 | 5.3194
| 749.1 | 11.859 |  | 1658.0294 | 0.0568 |  | 664.0559 | 0.0686 |  | 53.1 | 4.979
| 763.7509 | 10.2533 |  | 1691.19 | 0.0567 |  | 677.337 | 0.0659 |  | 53.6358 | 4.6662
| 777 | 9.1165 |  | 1725.0138 | 0.0567 |  | 690.8837 | 0.0633 |  | 54.7085 | 4.1387
| 790.1641 | 8.1979 |  | 1759.5141 | 0.0566 |  | 704.7014 | 0.0609 |  | 55.8026 | 3.7041
| 815.859 | 6.8228 |  | 1794.7044 | 0.0566 |  | 718.7954 | 0.0585 |  | 56.9187 | 3.3401
| 843.2314 | 5.7595 |  | 1830.5985 | 0.0565 |  | 733.1714 | 0.0562 |  | 58.0571 | 3.0309
| 869.781 | 4.982 |  | 1867.2104 | 0.0564 |  | 747.8348 | 0.054 |  | 59.2182 | 2.7653
| 893.585 | 4.4301 |  | 1904.5546 | 0.0564 |  | 762.7915 | 0.052 |  | 60.4026 | 2.5347
| 920.7979 | 3.9193 |  | 1942.6457 | 0.0563 |  | 778.0473 | 0.0504 |  | 61.6106 | 2.3328
| 946.9449 | 3.5181 |  | 1981.4986 | 0.0563 |  | 793.6083 | 0.0488 |  | 62.8428 | 2.1547
| 988.5513 | 3.0101 |  | 2021.1286 | 0.0562 |  | 809.4804 | 0.0473 |  | 64.0997 | 1.9965
| 1026.8401 | 2.6441 |  | 2061.5512 | 0.0562 |  | 825.67 | 0.0459 |  | 65.3817 | 1.8552
| 1094.7057 | 2.1553 |  | 2102.7822 | 0.0561 |  | 842.1834 | 0.0445 |  | 66.6893 | 1.7282
| 1170.554 | 1.7657 |  | 2144.8379 | 0.0561 |  | 859.0271 | 0.0431 |  | 68.0231 | 1.6136
| 1274.405 | 1.3935 |  | 2187.7346 | 0.056 |  | 876.2076 | 0.0418 |  | 69.3836 | 1.5097
| 1365.452 | 1.1617 |  | 2231.4893 | 0.056 |  | 893.7318 | 0.0406 |  | 70.7712 | 1.4151
| 1500.026 | 0.917 |  | 2276.1191 | 0.056 |  | 911.6064 | 0.0394 |  | 72.1867 | 1.3288
| 1652.816 | 0.7259 |  | 2321.6415 | 0.0559 |  | 929.8386 | 0.0383 |  | 73.6304 | 1.2496
| 1837.638 | 0.5676 |  | 2368.0743 | 0.0559 |  | 948.4353 | 0.0372 |  | 75.103 | 1.1769
| 2080.243 | 0.4295 |  | 2415.4358 | 0.0559 |  | 967.404 | 0.0361 |  | 76.6051 | 1.1099
| 2331.428 | 0.3346 |  | 2463.7445 | 0.0558 |  | 986.7521 | 0.0351 |  | 78.1372 | 1.048
| 2633.95 | 0.2575 |  | 2513.0194 | 0.0558 |  | 1006.4872 | 0.0341 |  | 79.6999 | 0.9906
| 3057.153 | 0.188 |  | 2563.2798 | 0.0558 |  | 1026.6169 | 0.0332 |  | 81.2939 | 0.9374
| 3474.614 | 0.144 |  | 2614.5454 | 0.0557 |  | 1047.1492 | 0.0323 |  | 82.9198 | 0.8879
| 4045.008 | 0.1053 |  | 2666.8363 | 0.0557 |  | 1068.0922 | 0.0314 |  | 84.5782 | 0.8418
| 4723.18 | 0.0767 |  | 2720.173 | 0.0557 |  | 1089.4541 | 0.0306 |  | 86.2697 | 0.7988
| 5570.488 | 0.0548 |  | 2774.5765 | 0.0556 |  | 1111.2432 | 0.0298 |  | 87.9951 | 0.7586
| 6343.832 | 0.0441 |  | 2830.068 | 0.0556 |  | 1133.468 | 0.029 |  | 89.755 | 0.7209
| 7564.623 | 0.0339 |  | 2886.6694 | 0.0556 |  | 1156.1374 | 0.0283 |  | 91.5501 | 0.6856
| 8649.344 | 0.0283 |  | 2944.4027 | 0.0556 |  | 1179.2601 | 0.0276 |  | 93.3811 | 0.6524
| 10129.812 | 0.0233 |  | 3003.2908 | 0.0556 |  | 1202.8453 | 0.0269 |  | 95.2488 | 0.6213
| 11409.86 | 0.0205 |  | 3063.3566 | 0.0555 |  | 1226.9022 | 0.0262 |  | 97.1537 | 0.592
25E | 55 | 26.9855 |  | 3124.6237 | 0.0555 |  | 1251.4403 | 0.0256 |  | 99.0968 | 0.5644
| 55.659 | 24.0848 |  | 3187.1162 | 0.0555 |  | 1276.4691 | 0.025 |  | 101.0788 | 0.5383
| 56.5567 | 20.9766 |  | 3250.8585 | 0.0555 |  | 1301.9985 | 0.0244 |  | 103.1003 | 0.5137
| 57.1 | 19.4416 |  | 3315.8757 | 0.0555 |  | 1328.0384 | 0.0238 |  | 105.1623 | 0.4905
| 57.584 | 18.2432 |  | 3382.1932 | 0.0554 |  | 1354.5992 | 0.0233 |  | 107.2656 | 0.4685
| 58.1 | 17.1104 |  | 3449.8371 | 0.0554 |  | 1381.6912 | 0.0228 |  | 109.4109 | 0.4477
| 58.6885 | 15.9702 |  | 3518.8338 | 0.0554 |  | 1409.325 | 0.0223 |  | 111.5991 | 0.428
| 59.1 | 15.2543 |  | 3589.2105 | 0.0554 |  | 1437.5115 | 0.0218 |  | 113.8311 | 0.4093
| 59.5754 | 14.4986 |  | 3660.9947 | 0.0554 |  | 1466.2617 | 0.0213 |  | 116.1077 | 0.3916
| 60.3 | 13.4726 |  | 3734.2146 | 0.0554 |  | 1495.587 | 0.0209 |  | 118.4299 | 0.3748
| 60.9616 | 12.6475 |  | 3808.8989 | 0.0553 |  | 1525.4987 | 0.0205 |  | 120.7985 | 0.3588
| 61.9 | 11.6261 |  | 3885.0769 | 0.0553 |  | 1556.0087 | 0.0201 |  | 123.2144 | 0.3437
| 62.8811 | 10.7098 |  | 3962.7784 | 0.0553 |  | 1561.9082 | 0.016 |  | 125.6787 | 0.3292
| 63.7 | 10.0412 |  | 4042.034 | 0.0553 |  | 1593.1464 | 0.016 |  | 128.1923 | 0.3155
| 64.5373 | 9.4324 |  | 4122.8747 | 0.0553 |  | 1625.0093 | 0.016 |  | 130.7561 | 0.3024
| 65.5 | 8.8109 |  | 4205.3322 | 0.0553 |  | 1657.5095 | 0.016 |  | 133.3713 | 0.29
| 66.3699 | 8.3102 |  | 4289.4388 | 0.0553 |  | 1690.6597 | 0.016 |  | 136.0387 | 0.2781
| 68.5281 | 7.2659 |  | 4375.2276 | 0.0553 |  | 1724.4729 | 0.016 |  | 138.7595 | 0.2668
| 71.0401 | 6.315 |  | 4462.7321 | 0.0553 |  | 1758.9624 | 0.016 |  | 141.5347 | 0.256
| 73.6441 | 5.5401 |  | 4551.9868 | 0.0552 |  | 1794.1416 | 0.016 |  | 144.3654 | 0.2457
| 76.3436 | 4.8977 |  | 4643.0265 | 0.0552 |  | 1830.0245 | 0.016 |  | 147.2527 | 0.2359
| 80.7408 | 4.0936 |  | 4735.887 | 0.0552 |  | 1866.6249 | 0.016 |  | 150.1977 | 0.2265
| 85.1355 | 3.4932 |  | 4830.6048 | 0.0552 |  | 1903.9574 | 0.016 |  | 153.2017 | 0.2175
| 89.8592 | 2.9985 |  | 4927.2169 | 0.0552 |  | 1942.0366 | 0.016 |  | 156.2657 | 0.209
| 93.3395 | 2.7051 |  | 5025.7612 | 0.0552 |  | 1980.8773 | 0.016 |  | 159.391 | 0.2008
| 99.0123 | 2.3194 |  | 5126.2764 | 0.0552 |  | 2020.4949 | 0.016 |  | 162.5788 | 0.193
| 104.7152 | 2.016 |  | 5228.802 | 0.0552 |  | 2060.9048 | 0.016 |  | 165.8304 | 0.1855
| 109.9739 | 1.7903 |  | 5333.378 | 0.0552 |  | 2102.1229 | 0.016 |  | 169.147 | 0.1783
| 116.8904 | 1.5509 |  | 5440.0456 | 0.0552 |  | 2144.1653 | 0.016 |  | 172.53 | 0.1715
| 123.1296 | 1.3766 |  | 5548.8465 | 0.0552 |  | 2187.0486 | 0.016 |  | 175.9806 | 0.1649
| 131.3994 | 1.1903 |  | 5659.8234 | 0.0552 |  | 2230.7896 | 0.016 |  | 179.5002 | 0.1587
| 140.9265 | 1.0216 |  | 5773.0199 | 0.0552 |  | 2275.4054 | 0.016 |  | 183.0902 | 0.1527
| 150.843 | 0.8835 |  | 5888.4803 | 0.0551 |  | 2320.9135 | 0.016 |  | 186.752 | 0.1469
| 161.6186 | 0.7644 |  | 6006.2499 | 0.0551 |  | 2367.3318 | 0.016 |  | 190.487 | 0.1414
| 175.6051 | 0.6441 |  | 6126.3749 | 0.0551 |  | 2414.6784 | 0.016 |  | 194.2968 | 0.1361
| 192.335 | 0.5356 |  | 6248.9024 | 0.0551 |  | 2462.972 | 0.016 |  | 198.1827 | 0.131
| 212.564 | 0.4387 |  | 6373.8804 | 0.0551 |  | 2512.2314 | 0.016 |  | 202.1463 | 0.1262
| 241.5897 | 0.341 |  | 6501.358 | 0.0551 |  | 2562.476 | 0.016 |  | 206.1893 | 0.1215
| 261.9727 | 0.2913 |  | 6631.3852 | 0.0551 |  | 2613.7256 | 0.016 |  | 210.3131 | 0.1171
| 286.3575 | 0.2453 |  | 6764.0129 | 0.0551 |  | 2666.0001 | 0.016 |  | 214.5193 | 0.1128
| 310.8281 | 0.2096 |  | 6899.2932 | 0.0551 |  | 2719.3201 | 0.016 |  | 218.8097 | 0.1087
| 333.6993 | 0.183 |  | 7037.279 | 0.0551 |  | 2773.7065 | 0.016 |  | 223.1859 | 0.1048
| 354.6895 | 0.163 |  | 7178.0246 | 0.0551 |  | 2829.1806 | 0.016 |  | 227.6496 | 0.101
| 390.8179 | 0.1356 |  | 7321.5851 | 0.0551 |  | 2885.7642 | 0.016 |  | 232.2026 | 0.0973
| 421.256 | 0.1177 |  | 7468.0168 | 0.0551 |  | 2943.4795 | 0.016 |  | 236.8467 | 0.0939
| 454.0657 | 0.1022 |  | 7617.3771 | 0.0551 |  | 3002.3491 | 0.016 |  | 241.5836 | 0.0905
| 494.3488 | 0.0871 |  | 7769.7247 | 0.0551 |  | 3062.3961 | 0.016 |  | 246.4153 | 0.0873
| 540.9041 | 0.0736 |  | 7925.1192 | 0.0551 |  | 3123.644 | 0.016 |  | 251.3436 | 0.0842
| 606.2188 | 0.0595 |  | 8083.6216 | 0.0551 |  | 3123.8165 | 0.014 |  | 256.3704 | 0.0813
| 656.0532 | 0.0522 |  | 8245.294 | 0.0551 |  | 3186.2928 | 0.014 |  | 261.4979 | 0.0784
| 708.565 | 0.0465 |  | 8410.1999 | 0.0551 |  | 3250.0187 | 0.014 |  | 266.7278 | 0.0757
| 715 | 0.0459 |  | 8578.4039 | 0.0551 |  | 3315.0191 | 0.014 |  | 272.0624 | 0.0731
| 775 | 0.0409 |  | 8749.9719 | 0.0551 |  | 3381.3194 | 0.014 |  | 277.5036 | 0.0706
| 829.589 | 0.0372 |  | 8924.9714 | 0.0551 |  | 3448.9458 | 0.014 |  | 283.0537 | 0.0682
| 897.785 | 0.0335 |  | 9103.4708 | 0.0551 |  | 3517.9247 | 0.014 |  | 288.7148 | 0.0659
| 980.371 | 0.03 |  | 9285.5402 | 0.0551 |  | 3588.2832 | 0.014 |  | 294.4891 | 0.0637
| 1053.56 | 0.0275 |  | 9471.251 | 0.0551 |  | 3660.0489 | 0.014 |  | 300.3788 | 0.0616
| 1151.62 | 0.0248 |  | 9660.6761 | 0.0551 |  | 3733.2499 | 0.014 |  | 306.3864 | 0.0597
| 1222.83 | 0.0233 |  | 9853.8896 | 0.0551 |  | 3807.9149 | 0.014 |  | 312.5141 | 0.0581
| 1295.86 | 0.0219 |  | 10050.9674 | 0.055 |  | 3884.0732 | 0.014 |  | 318.7644 | 0.0565
| 1326.01 | 0.0214 |  | 10251.9867 | 0.055 |  | 3961.7546 | 0.014 |  | 325.1397 | 0.055
| 1391.7843 | 0.0204 |  | 10457.0264 | 0.055 |  | 4040.9897 | 0.014 |  | 331.6425 | 0.0536
| 1565.7574 | 0.016 |  | 10666.167 | 0.055 |  | 4121.8095 | 0.014 |  | 338.2754 | 0.0522
| 1739.7304 | 0.016 |  | 10879.4903 | 0.055 |  | 4204.2457 | 0.014 |  | 345.0409 | 0.0509
| 1948.4981 | 0.016 |  | 11097.0801 | 0.055 |  | 4288.3306 | 0.014 |  | 351.9417 | 0.0496
| 2652.0451 | 0.016 |  | 11319.0217 | 0.055 |  | 4374.0972 | 0.014 |  | 358.9805 | 0.0484
300E | 772.1978 | 229.5154 |  | 11545.4022 | 0.055 |  | 4461.5792 | 0.014 |  | 366.1601 | 0.0472
| 783.8688 | 82.6186 |  | 11776.3102 | 0.055 |  | 4550.8108 | 0.014 |  | 373.4833 | 0.0461
| 789.8 | 62.1687 | 600Main | 674.8401 | 81.1131 |  | 4641.827 | 0.014 |  | 380.953 | 0.045
| 795.7147 | 49.787 |  | 694.8634 | 23.1988 |  | 4734.6635 | 0.014 |  | 388.5721 | 0.044
| 800.1 | 43.345 |  | 704.1 | 17.3681 |  | 4829.3568 | 0.014 |  | 396.3435 | 0.043
| 804.5158 | 38.3241 |  | 713.2422 | 13.8755 |  | 4925.9439 | 0.014 |  | 404.2704 | 0.042
| 810.6 | 33.0197 |  | 723.8 | 11.2342 |  | 5024.4628 | 0.014 |  | 412.3558 | 0.0411
| 816.6752 | 28.9838 |  | 734.404 | 9.4111 |  | 5124.9521 | 0.014 |  | 420.6029 | 0.0402
| 823.7 | 25.3695 |  | 746.1 | 7.9659 |  | 5227.4511 | 0.014 |  | 429.015 | 0.0393
| 830.6771 | 22.5524 |  | 757.7746 | 6.8943 |  | 5332.0001 | 0.014 |  | 437.5953 | 0.0385
| 837.4 | 20.3563 |  | 773.1 | 5.8457 |  | 5438.6401 | 0.014 |  | 446.3472 | 0.0377
| 844.0751 | 18.5485 |  | 788.4481 | 5.0611 |  | 5547.4129 | 0.014 |  | 455.2741 | 0.0369
| 852.2 | 16.7248 |  | 804.8 | 4.4182 |  | 5658.3612 | 0.014 |  | 464.3796 | 0.0361
| 860.266 | 15.2245 |  | 821.2204 | 3.9104 |  | 5771.5284 | 0.014 |  | 473.6672 | 0.0354
| 867.6 | 14.0668 |  | 848.2397 | 3.2765 |  | 5886.959 | 0.014 |  | 483.1405 | 0.0347
| 875.0148 | 13.0547 |  | 877.9793 | 2.7683 |  | 6004.6982 | 0.014 |  | 492.8033 | 0.0341
| 883 | 12.1081 |  | 908.7617 | 2.3756 |  | 6124.7921 | 0.014 |  | 502.6594 | 0.0334
| 890.9076 | 11.2902 |  | 941.6055 | 2.0553 |  | 6247.288 | 0.014 |  | 512.7126 | 0.0328
| 899.5 | 10.5114 |  | 987.9386 | 1.7172 |  | 6372.2337 | 0.014 |  | 522.9668 | 0.0322
| 907.9972 | 9.8342 |  | 1043.0673 | 1.4262 |  | 6499.6784 | 0.014 |  | 533.4262 | 0.0317
| 921.8 | 8.8921 |  | 1111.6699 | 1.1682 |  | 6629.672 | 0.014 |  | 544.0947 | 0.0311
| 935.6501 | 8.1015 |  | 1176.1563 | 0.9917 |  | 6762.2654 | 0.014 |  | 554.9766 | 0.0306
| 961.2559 | 6.9371 |  | 1262.7098 | 0.818 |  | 6897.5107 | 0.014 |  | 566.0761 | 0.0301
| 999.4864 | 5.6777 |  | 1355.6312 | 0.683 |  | 7035.4609 | 0.014 |  | 577.3976 | 0.0296
| 1035.0868 | 4.8303 |  | 1444.7928 | 0.586 |  | 7176.1702 | 0.014 |  | 588.9456 | 0.0291
| 1073.0291 | 4.1469 |  | 1515.8858 | 0.5246 |  | 7319.6936 | 0.014 |  | 600.7245 | 0.0287
| 1119.052 | 3.5189 |  | 1575.152 | 0.4814 |  | 7466.0874 | 0.014 |  | 612.739 | 0.0283
| 1170.554 | 2.9897 |  | 1698.145 | 0.4094 |  | 7615.4092 | 0.014 |  | 624.9938 | 0.0278
| 1214.686 | 2.6359 |  | 1825.015 | 0.353 |  | 7767.7174 | 0.014 |  | 637.4937 | 0.0274
| 1285.933 | 2.196 |  | 1940.989 | 0.3125 |  | 7923.0717 | 0.014 |  | 650.2435 | 0.0271
| 1373.669 | 1.8021 |  | 2105.7 | 0.2678 |  | 8081.5331 | 0.014 |  | 663.2484 | 0.0267
| 1482.129 | 1.4555 |  | 2303.551 | 0.2287 |  | 8243.1638 | 0.014 |  | 676.5134 | 0.0263
| 1580.095 | 1.227 |  | 2491.211 | 0.2018 |  | 8408.0271 | 0.014 |  | 690.0436 | 0.026
| 1676.125 | 1.0544 |  | 2719.599 | 0.1768 |  | 8576.1876 | 0.014 |  | 703.8445 | 0.0256
| 1763.817 | 0.9284 |  | 2959.639 | 0.1569 |  | 8747.7114 | 0.014 |  | 717.9214 | 0.0253
| 1910.722 | 0.7649 |  | 3200.748 | 0.1414 |  | 8922.6656 | 0.014 |  | 732.2798 | 0.025
| 2061.598 | 0.6398 |  | 3501.489 | 0.1266 |  | 9101.1189 | 0.014 |  | 746.9254 | 0.0247
| 2255.748 | 0.5207 |  | 3755 | 0.1169 |  | 9283.1413 | 0.014 |  | 761.8639 | 0.0244
| 2561.218 | 0.3924 |  | 4050 | 0.1079 |  | 9468.8041 | 0.014 |  | 777.1012 | 0.0242
| 2963.829 | 0.286 |  | 4500 | 0.0974 |  | 9658.1802 | 0.014 |  | 792.6432 | 0.0239
| 3355.11 | 0.2197 |  | 4993.949 | 0.0892 |  | 9851.3438 | 0.014 |  | 808.4961 | 0.0236
| 3809.443 | 0.1683 |  | 5450 | 0.0834 |  | 10048.3707 | 0.014 |  | 824.666 | 0.0234
| 4342.646 | 0.1283 |  | 5951.586 | 0.0786 |  | 10249.3381 | 0.014 |  | 841.1593 | 0.0232
| 5178.338 | 0.0894 |  | 6620.49 | 0.0739 |  | 10454.3249 | 0.014 |  | 857.9825 | 0.0229
| 5838.558 | 0.07 |  | 7356.886 | 0.0701 |  | 10663.4114 | 0.014 |  | 875.1422 | 0.0227
| 6715.94 | 0.0527 |  | 8149.621 | 0.0671 |  | 10876.6796 | 0.014 |  | 892.645 | 0.0225
| 7504.354 | 0.044 |  | 9295.631 | 0.064 |  | 11094.2132 | 0.014 |  | 910.4979 | 0.0223
| 8503.539 | 0.0364 |  | 10094.985 | 0.0625 |  | 11316.0974 | 0.014 |  | 928.7079 | 0.0221
| 9674.401 | 0.0304 |  | 11300.147 | 0.0608 |  | 11542.4194 | 0.014 |  | 947.282 | 0.0219
| 10940.622 | 0.0259 | 65Main | 72.93 | 101.5883 |  | 11773.2678 | 0.014 |  | 966.2277 | 0.0217
30E | 66.903 | 696.7135 |  | 74.3886 | 32.8902 | 25T | 60.4982 | 709.4827 |  | 985.5522 | 0.0215
| 67.373 | 232.3625 |  | 75.1 | 24.6513 |  | 61.7082 | 229.4892 |  | 1005.2633 | 0.0214
| 67.9141 | 131.097 |  | 75.8764 | 19.3218 |  | 62.3 | 171.8022 |  | 1025.3685 | 0.0212
| 68.2 | 106.4506 |  | 76.6 | 16.0572 |  | 62.9424 | 134.6868 |  | 1045.8759 | 0.0211
| 68.5281 | 87.4945 |  | 77.3939 | 13.5272 |  | 63.6 | 110.0865 |  | 1066.7934 | 0.0209
| 68.9 | 72.7459 |  | 78.2 | 11.6467 |  | 64.2012 | 94.2004 |  | 1088.1293 | 0.0208
| 69.2168 | 63.5741 |  | 78.9418 | 10.3153 |  | 64.8 | 82.266 |  | 1109.8919 | 0.0206
| 69.5 | 57.1136 |  | 79.7 | 9.2279 |  | 65.4852 | 71.7585 |  | 1132.0897 | 0.0205
| 69.8426 | 50.837 |  | 80.5206 | 8.2753 |  | 66.1 | 64.3152 |  | 1154.7315 | 0.0204
| 70.2 | 45.5879 |  | 81.3 | 7.5305 |  | 66.7949 | 57.5053 |  | 1177.8261 | 0.0202
| 70.474 | 42.2308 |  | 82.131 | 6.8658 |  | 67.5 | 51.874 |  | 1201.3827 | 0.0201
| 70.9 | 37.8756 |  | 83 | 6.2807 |  | 68.1308 | 47.6569 |  | 1225.4103 | 0.02
| 71.3962 | 33.7926 |  | 83.7736 | 5.8343 |  | 68.8 | 43.8401 |  | 1226.5079 | 0.016
| 71.7 | 31.69 |  | 84.6 | 5.4193 |  | 69.4935 | 40.4496 |  | 1251.0381 | 0.016
| 72.0416 | 29.61 |  | 85.4491 | 5.0472 |  | 70.2 | 37.4673 |  | 1276.0588 | 0.016
| 72.5 | 27.2026 |  | 86.3 | 4.7196 |  | 70.8833 | 34.9504 |  | 1301.58 | 0.016
| 72.9842 | 25.0393 |  | 87.1581 | 4.4273 |  | 71.6 | 32.6287 |  | 1327.6116 | 0.016
| 73.8 | 22.06 |  | 88.9013 | 3.9269 |  | 72.301 | 30.6194 |  | 1354.1638 | 0.016
| 74.6824 | 19.5214 |  | 90.6793 | 3.5146 |  | 73.747 | 27.1227 |  | 1381.2471 | 0.016
| 75.6 | 17.4147 |  | 92.4929 | 3.1694 |  | 75.222 | 24.2423 |  | 1408.8721 | 0.016
| 76.573 | 15.6085 |  | 94.3427 | 2.8763 |  | 76.7264 | 21.8304 |  | 1437.0495 | 0.016
| 77.6 | 14.0518 |  | 96.2296 | 2.6246 |  | 78.2609 | 19.7826 |  | 1465.7905 | 0.016
| 78.6686 | 12.7162 |  | 98.1542 | 2.4062 |  | 79.8261 | 18.0236 |  | 1495.1063 | 0.016
| 79.7 | 11.6358 |  | 100.1173 | 2.215 |  | 81.4227 | 16.4975 |  | 1525.0084 | 0.016
| 80.8216 | 10.6406 |  | 102.1196 | 2.0464 |  | 83.0511 | 15.1618 |  | 1555.5086 | 0.016
| 83.3662 | 8.8819 |  | 104.162 | 1.8967 |  | 84.7121 | 13.9839 |  | 1586.6188 | 0.016
| 85.4767 | 7.7872 |  | 106.2452 | 1.7631 |  | 86.4064 | 12.9381 |  | 1618.3512 | 0.016
| 88.168 | 6.7062 |  | 108.3701 | 1.643 |  | 88.1345 | 12.0041 |  | 1650.7182 | 0.016
| 90.5809 | 5.9466 |  | 110.5375 | 1.5348 |  | 89.8972 | 11.1655 |  | 1683.7325 | 0.016
| 93.2462 | 5.2703 |  | 112.7483 | 1.4367 |  | 91.6951 | 10.409 |  | 1717.4072 | 0.016
| 96.1821 | 4.6694 |  | 115.0033 | 1.3474 |  | 93.529 | 9.7236 |  | 1751.7553 | 0.016
| 99.8075 | 4.0774 |  | 117.3033 | 1.266 |  | 95.3996 | 9.1001 |  | 1786.7904 | 0.016
| 103.6732 | 3.5772 |  | 119.6494 | 1.1914 |  | 97.3076 | 8.531 |  | 1822.5262 | 0.016
| 108.1202 | 3.1207 |  | 122.0424 | 1.1229 |  | 99.2538 | 8.0099 |  | 1858.9768 | 0.016
| 113.0965 | 2.7171 |  | 124.4832 | 1.0598 |  | 101.2389 | 7.5312 |  | 1896.1563 | 0.016
| 118.7758 | 2.3546 |  | 126.9729 | 1.0015 |  | 103.2636 | 7.0904 |  | 1934.0794 | 0.016
| 124.4914 | 2.0651 |  | 129.5124 | 0.9476 |  | 105.3289 | 6.6834 |  | 1972.761 | 0.016
| 130.7438 | 1.8107 |  | 132.1026 | 0.8976 |  | 107.4355 | 6.3067 |  | 2012.2162 | 0.016
| 137.0358 | 1.6033 |  | 134.7447 | 0.8512 |  | 109.5842 | 5.9574 |  | 2052.4606 | 0.016
| 145.3639 | 1.3832 |  | 137.4395 | 0.8079 |  | 111.7759 | 5.6328 |  | 2093.5098 | 0.016
| 153.89 | 1.2049 |  | 140.1883 | 0.7676 |  | 114.0114 | 5.3307 |  | 2135.38 | 0.016
| 163.8978 | 1.0389 |  | 142.9921 | 0.7299 |  | 116.2916 | 5.0489 |  | 2178.0876 | 0.016
| 173.5107 | 0.9116 |  | 145.8519 | 0.6947 |  | 118.6174 | 4.7857 |  | 2221.6493 | 0.016
| 188.716 | 0.7555 |  | 148.769 | 0.6617 |  | 120.9898 | 4.5395 |  | 2266.0823 | 0.016
| 211.5036 | 0.5899 |  | 151.7444 | 0.6307 |  | 123.4096 | 4.3088 |  | 2311.404 | 0.016
| 231.1903 | 0.4886 |  | 154.7793 | 0.6017 |  | 125.8778 | 4.0925 |  | 2357.632 | 0.016
| 253.7227 | 0.4027 |  | 157.8748 | 0.5743 |  | 128.3953 | 3.8894 |  | 2404.7847 | 0.016
| 274.3048 | 0.3432 |  | 161.0323 | 0.5486 |  | 130.9632 | 3.6984 |  | 2452.8804 | 0.016
| 303.1545 | 0.2802 |  | 164.253 | 0.5244 |  | 133.5825 | 3.5186 |  | 2453.0158 | 0.014
| 323.8378 | 0.2455 |  | 167.538 | 0.5015 |  | 136.2542 | 3.3492 |  | 2502.0762 | 0.014
| 351.1596 | 0.2089 |  | 170.8888 | 0.4799 |  | 138.9792 | 3.1895 |  | 2552.1177 | 0.014
| 374.7436 | 0.1837 |  | 174.3066 | 0.4595 |  | 141.7588 | 3.0387 |  | 2603.16 | 0.014
| 404.7384 | 0.1578 |  | 177.7927 | 0.4402 |  | 144.594 | 2.8962 |  | 2655.2232 | 0.014
| 437.1345 | 0.1357 |  | 181.3486 | 0.422 |  | 147.4859 | 2.7616 |  | 2708.3277 | 0.014
| 473.5423 | 0.1161 |  | 184.9755 | 0.4047 |  | 150.4356 | 2.6341 |  | 2762.4943 | 0.014
| 512.9828 | 0.0994 |  | 188.675 | 0.3884 |  | 153.4443 | 2.5134 |  | 2817.7441 | 0.014
| 547.9815 | 0.0875 |  | 192.4485 | 0.3728 |  | 156.5132 | 2.3991 |  | 2874.099 | 0.014
| 600.1875 | 0.0734 |  | 196.2975 | 0.3581 |  | 159.6435 | 2.2906 |  | 2931.581 | 0.014
| 641.7774 | 0.0645 |  | 200.2235 | 0.3441 |  | 162.8363 | 2.1878 |  | 2990.2126 | 0.014
| 686.9357 | 0.0566 |  | 204.2279 | 0.3309 |  | 166.0931 | 2.0901 |  | 3050.0169 | 0.014
| 753.8861 | 0.0487 |  | 208.3125 | 0.3182 |  | 169.4149 | 1.9973 |  | 3111.0172 | 0.014
| 830.6771 | 0.0421 |  | 212.4787 | 0.3063 |  | 172.8032 | 1.9092 |  | 3173.2376 | 0.014
| 898.683 | 0.0376 |  | 216.7283 | 0.2948 |  | 176.2593 | 1.8254 |  | 3236.7023 | 0.014
| 962.882 | 0.0342 |  | 221.0629 | 0.284 |  | 179.7845 | 1.7456 |  | 3301.4364 | 0.014
| 1042.03 | 0.0308 |  | 225.4841 | 0.2736 |  | 183.3802 | 1.6697 |  | 3367.4651 | 0.014
| 1120.94 | 0.0281 |  | 229.9938 | 0.2638 |  | 187.0478 | 1.5975 |  | 3434.8144 | 0.014
| 1197.42 | 0.026 |  | 234.5937 | 0.2544 |  | 190.7887 | 1.5287 |  | 3503.5107 | 0.014
| 1277.84 | 0.0241 |  | 239.2856 | 0.2455 |  | 194.6045 | 1.4631 |  | 3573.5809 | 0.014
| 1343.36 | 0.0228 |  | 244.0713 | 0.2372 |  | 198.4966 | 1.4006 |  | 3645.0525 | 0.014
| 1396.78 | 0.0219 |  | 248.9527 | 0.2296 |  | 202.4665 | 1.341 |  | 3717.9535 | 0.014
| 1436.45 | 0.0213 |  | 253.9318 | 0.2223 |  | 206.5159 | 1.2841 |  | 3792.3126 | 0.014
| 1462.54 | 0.0209 |  | 259.0104 | 0.2153 |  | 210.6462 | 1.2299 |  | 3868.1589 | 0.014
| 1535.0867 | 0.016 |  | 264.1906 | 0.2086 |  | 214.8591 | 1.1781 |  | 3945.5221 | 0.014
| 1726.9725 | 0.016 |  | 269.4744 | 0.2023 |  | 219.1563 | 1.1287 |  | 4024.4325 | 0.014
| 1918.8583 | 0.016 |  | 274.8639 | 0.1962 |  | 223.5394 | 1.0814 |  | 4104.9211 | 0.014
| 2149.1213 | 0.016 |  | 280.3612 | 0.1903 |  | 228.0102 | 1.0363 |  | 4187.0196 | 0.014
| 2925.1076 | 0.016 |  | 285.9684 | 0.1847 |  | 232.5704 | 0.9932 |  | 4270.76 | 0.014
400E | 1010.5414 | 211.3229 |  | 291.6878 | 0.1794 |  | 237.2218 | 0.952 |  | 4356.1752 | 0.014
| 1033.0188 | 61.7661 |  | 297.5215 | 0.1743 |  | 241.9662 | 0.9126 |  | 4443.2987 | 0.014
| 1045 | 44.6417 |  | 303.472 | 0.1694 |  | 246.8056 | 0.875 |  | 4532.1646 | 0.014
| 1057.0538 | 34.8178 |  | 309.5414 | 0.1647 |  | 251.7417 | 0.839 |  | 4622.8079 | 0.014
| 1068.3 | 28.8324 |  | 315.7322 | 0.1602 |  | 256.7765 | 0.8045 |  | 4715.2641 | 0.014
| 1079.4872 | 24.584 |  | 322.0469 | 0.1559 |  | 261.912 | 0.7716 |  | 4809.5694 | 0.014
| 1092 | 21.0728 |  | 328.4878 | 0.1518 |  | 267.1503 | 0.74 |  | 4905.7608 | 0.014
| 1104.598 | 18.3967 |  | 335.0576 | 0.1479 |  | 272.4933 | 0.7098 |  | 5003.876 | 0.014
| 1117.4 | 16.2725 |  | 341.7587 | 0.1441 |  | 277.9431 | 0.6809 |  | 5103.9535 | 0.014
| 1130.294 | 14.5597 |  | 348.5939 | 0.1405 |  | 283.502 | 0.6532 |  | 5206.0326 | 0.014
| 1145.8 | 12.9055 |  | 355.5658 | 0.137 |  | 289.172 | 0.6267 |  | 5310.1532 | 0.014
| 1161.237 | 11.5781 |  | 362.6771 | 0.1336 |  | 294.9555 | 0.6013 |  | 5416.3563 | 0.014
| 1174.2 | 10.6472 |  | 369.9306 | 0.1305 |  | 300.8546 | 0.577 |  | 5524.6834 | 0.014
| 1187.065 | 9.8523 |  | 377.3292 | 0.1274 |  | 306.8717 | 0.5537 |  | 5635.1771 | 0.014
| 1202.7 | 9.0237 |  | 384.8758 | 0.1245 |  | 313.0091 | 0.5314 |  | 5747.8806 | 0.014
| 1218.327 | 8.3155 |  | 392.5733 | 0.1217 |  | 319.2693 | 0.51 |  | 5862.8382 | 0.014
| 1247.928 | 7.2219 |  | 400.4248 | 0.119 |  | 325.6547 | 0.4895 |  | 5980.095 | 0.014
| 1276.957 | 6.3796 |  | 408.4333 | 0.1164 |  | 332.1678 | 0.4699 |  | 6099.6969 | 0.014
| 1313.224 | 5.5499 |  | 416.602 | 0.1139 |  | 338.8111 | 0.451 |  | 6221.6908 | 0.014
| 1341.087 | 5.0345 |  | 424.934 | 0.1115 |  | 345.5874 | 0.433 |  | 6346.1246 | 0.014
| 1373.669 | 4.5311 |  | 433.4327 | 0.1092 |  | 352.4991 | 0.4157 |  | 6473.0471 | 0.014
| 1400.014 | 4.1855 |  | 442.1014 | 0.107 |  | 359.5491 | 0.3991 |  | 6602.5081 | 0.014
| 1436.886 | 3.7734 |  | 450.9434 | 0.1049 |  | 366.7401 | 0.3831 |  | 6734.5582 | 0.014
| 1465.915 | 3.4961 |  | 459.9622 | 0.1029 |  | 374.0749 | 0.3679 |  | 6869.2494 | 0.014
| 1501.522 | 3.2011 |  | 469.1615 | 0.101 |  | 381.5564 | 0.3532 |  | 7006.6344 | 0.014
| 1534.929 | 2.9613 |  | 478.5447 | 0.0991 |  | 389.1875 | 0.3392 |  | 7146.7671 | 0.014
| 1565.938 | 2.7649 |  | 488.1156 | 0.0973 |  | 396.9713 | 0.3257 |  | 7289.7024 | 0.014
| 1608.794 | 2.5277 |  | 497.8779 | 0.0956 |  | 404.9107 | 0.3128 |  | 7435.4965 | 0.014
| 1639.649 | 2.3774 |  | 507.8355 | 0.094 |  | 413.0089 | 0.3004 |  | 7584.2064 | 0.014
| 1677.797 | 2.2115 |  | 517.9922 | 0.0924 |  | 421.2691 | 0.2885 |  | 7735.8905 | 0.014
| 1721.995 | 2.0422 |  | 528.352 | 0.0909 |  | 429.6945 | 0.277 |  | 7890.6083 | 0.014
| 1777.985 | 1.8568 |  | 538.9191 | 0.0894 |  | 438.2883 | 0.2661 |  | 8048.4205 | 0.014
| 1845.008 | 1.6691 |  | 549.6975 | 0.088 |  | 447.0541 | 0.2556 |  | 8209.3889 | 0.014
| 1912.636 | 1.5094 |  | 560.6914 | 0.0867 |  | 455.9952 | 0.2455 |  | 8373.5767 | 0.014
| 2008.688 | 1.3219 |  | 571.9052 | 0.0854 |  | 465.1151 | 0.2358 |  | 8541.0482 | 0.014
| 2139.313 | 1.1215 |  | 583.3433 | 0.0842 |  | 474.4174 | 0.2265 |  | 8711.8692 | 0.014
| 2258.003 | 0.9786 |  | 595.0102 | 0.083 |  | 483.9057 | 0.2175 |  | 8886.1066 | 0.014
| 2402.433 | 0.8405 |  | 606.9104 | 0.0818 |  | 493.5839 | 0.209 |  | 9063.8287 | 0.014
| 2528.141 | 0.7439 |  | 619.0486 | 0.0808 |  | 503.4555 | 0.2007 |  | 9245.1053 | 0.014
| 2644.499 | 0.6691 |  | 631.4296 | 0.0797 |  | 513.5246 | 0.1928 |  | 9430.0074 | 0.014
| 2805.22 | 0.5838 |  | 644.0582 | 0.0787 |  | 523.7951 | 0.1852 |  | 9618.6075 | 0.014
| 2972.739 | 0.5117 |  | 656.9394 | 0.0777 |  | 534.271 | 0.178 |  | 9810.9797 | 0.014
| 3204.267 | 0.4327 |  | 670.0781 | 0.0768 |  | 544.9565 | 0.171 |  | 10007.1993 | 0.014
| 3562.57 | 0.3429 |  | 683.4797 | 0.0759 |  | 555.8556 | 0.1642 |  | 10207.3432 | 0.014
| 3847.734 | 0.2904 |  | 697.1493 | 0.075 |  | 566.9727 | 0.1578 |  | 10411.4901 | 0.014
| 4189.086 | 0.2423 |  | 711.0923 | 0.0742 |  | 578.3122 | 0.1516 |  | 10619.7199 | 0.014
| 4569.862 | 0.2016 |  | 725.3141 | 0.0734 |  | 589.8784 | 0.1457 |  | 10832.1143 | 0.014
| 4965.345 | 0.1695 |  | 739.8204 | 0.0727 |  | 601.676 | 0.1399 |  | 11048.7566 | 0.014
| 5246.087 | 0.1512 |  | 754.6168 | 0.0719 |  | 613.7095 | 0.1345 |  | 11269.7317 | 0.014
| 5576.065 | 0.1332 |  | 769.7092 | 0.0712 |  | 625.9837 | 0.1292 |  | 11495.1264 | 0.014
| 6022.379 | 0.1137 |  | 785.1033 | 0.0706 |  | 638.5033 | 0.1241 |  | 11725.0289 | 0.014
| 6362.895 | 0.1015 |  | 800.8054 | 0.0699 |  | 651.2734 | 0.1193 |  | 11959.5295 | 0.014
| 6844.761 | 0.0874 |  | 816.8215 | 0.0693 |  | 664.2989 | 0.1146 | 50Tap | 55.6303 | 781.9267
| 7297.147 | 0.0767 |  | 833.1579 | 0.0687 |  | 677.5849 | 0.1101 |  | 56.2815 | 80.0928
| 7904.897 | 0.0652 |  | 849.8211 | 0.0681 |  | 691.1366 | 0.1058 |  | 57.1021 | 37.3526
| 8452.675 | 0.0569 |  | 866.8175 | 0.0676 |  | 704.9593 | 0.1017 |  | 57.7 | 26.8122
| 9111.003 | 0.0495 |  | 884.1539 | 0.067 |  | 719.0585 | 0.0977 |  | 58.2714 | 21.077
| 9840.27 | 0.0438 |  | 901.837 | 0.0665 |  | 733.4396 | 0.0939 |  | 58.9 | 17.0323
| 10564.323 | 0.0393 |  | 919.8737 | 0.066 |  | 748.1084 | 0.0902 |  | 59.4495 | 14.5669
| 11273.79 | 0.0357 |  | 938.2712 | 0.0656 |  | 763.0706 | 0.0867 |  | 60 | 12.7088
40E | 89.7531 | 281.4942 |  | 957.0366 | 0.0651 |  | 778.332 | 0.0833 |  | 60.511 | 11.3539
| 90.7399 | 130.7006 |  | 976.1773 | 0.0647 |  | 793.8987 | 0.08 |  | 61.3 | 9.736
| 91.4 | 95.9893 |  | 995.7009 | 0.0643 |  | 809.7766 | 0.0769 |  | 62.0411 | 8.5755
| 92.0419 | 76.175 |  | 1015.6149 | 0.0639 |  | 825.9722 | 0.0739 |  | 62.7 | 7.7463
| 92.6 | 64.5214 |  | 1035.9272 | 0.0635 |  | 842.4916 | 0.071 |  | 63.3468 | 7.0691
| 93.06 | 57.2607 |  | 1056.6457 | 0.0631 |  | 859.3414 | 0.0683 |  | 64.3 | 6.2543
| 93.5 | 51.6718 |  | 1077.7786 | 0.0628 |  | 876.5283 | 0.0656 |  | 65.3466 | 5.5432
| 93.9013 | 47.4307 |  | 1099.3342 | 0.0624 |  | 894.0588 | 0.063 |  | 66.4 | 4.9666
| 94.5 | 42.2314 |  | 1121.3209 | 0.0621 |  | 911.94 | 0.0606 |  | 67.3585 | 4.532
| 95.0348 | 38.4443 |  | 1143.7473 | 0.0618 |  | 930.1788 | 0.0582 |  | 69.7114 | 3.7162
| 95.4 | 36.2162 |  | 1166.6223 | 0.0615 |  | 948.7824 | 0.0559 |  | 72.6 | 3.0252
| 95.7982 | 34.0553 |  | 1189.9547 | 0.0612 |  | 967.758 | 0.0538 |  | 72.9025 | 2.9664
| 96.4 | 31.2251 |  | 1213.7538 | 0.0609 |  | 987.1132 | 0.0518 |  | 76.7173 | 2.3701
| 97.0517 | 28.6315 |  | 1238.0289 | 0.0606 |  | 1006.8555 | 0.0502 |  | 81.1525 | 1.9038
| 97.6 | 26.7505 |  | 1262.7895 | 0.0604 |  | 1026.9926 | 0.0486 |  | 85.844 | 1.5623
| 98.1252 | 25.1586 |  | 1288.0452 | 0.0601 |  | 1047.5324 | 0.0471 |  | 90.8072 | 1.3027
| 98.8 | 23.3613 |  | 1313.8062 | 0.0599 |  | 1068.4831 | 0.0457 |  | 95.7583 | 1.1098
| 99.5085 | 21.7207 |  | 1340.0823 | 0.0597 |  | 1089.8527 | 0.0443 |  | 101.5047 | 0.9403
| 100.8 | 19.2337 |  | 1366.8839 | 0.0595 |  | 1111.6498 | 0.043 |  | 107.822 | 0.7991
| 102.0276 | 17.3245 |  | 1394.2216 | 0.0594 |  | 1133.8828 | 0.0417 |  | 115.3691 | 0.6718
| 103 | 16.0489 |  | 1422.106 | 0.0592 |  | 1156.5604 | 0.0404 |  | 123.8303 | 0.5648
| 103.9848 | 14.9254 |  | 1450.5482 | 0.059 |  | 1179.6916 | 0.0393 |  | 129.074 | 0.5119
| 104.9 | 14.0058 |  | 1479.5591 | 0.0589 |  | 1203.2855 | 0.0381 |  | 137.4131 | 0.4429
| 105.8734 | 13.1371 |  | 1509.1503 | 0.0587 |  | 1227.3512 | 0.037 |  | 148.7244 | 0.371
| 108.0122 | 11.5411 |  | 1539.3333 | 0.0586 |  | 1251.8982 | 0.036 |  | 158.1437 | 0.3246
| 110.0836 | 10.3047 |  | 1570.12 | 0.0584 |  | 1276.9362 | 0.035 |  | 171.3393 | 0.2737
| 112.6444 | 9.0771 |  | 1601.5224 | 0.0583 |  | 1302.4749 | 0.034 |  | 182.8057 | 0.2392
| 114.3472 | 8.399 |  | 1633.5528 | 0.0582 |  | 1328.5244 | 0.0331 |  | 192.81 | 0.2146
| 117.2424 | 7.4354 |  | 1666.2239 | 0.058 |  | 1355.0949 | 0.0322 |  | 209.116 | 0.1823
| 119.7306 | 6.7541 |  | 1699.5483 | 0.0579 |  | 1382.1968 | 0.0313 |  | 222.437 | 0.1614
| 122.3937 | 6.1388 |  | 1733.5393 | 0.0578 |  | 1409.8407 | 0.0305 |  | 239.415 | 0.1399
| 125.2405 | 5.5829 |  | 1768.2101 | 0.0577 |  | 1438.0375 | 0.0297 |  | 256.173 | 0.123
| 128.7968 | 5.0023 |  | 1803.5743 | 0.0576 |  | 1466.7983 | 0.0289 |  | 275.675 | 0.1071
| 134.3221 | 4.2852 |  | 1839.6458 | 0.0575 |  | 1496.1343 | 0.0282 |  | 297.285 | 0.0932
| 139.6637 | 3.7448 |  | 1876.4387 | 0.0574 |  | 1526.0569 | 0.0275 |  | 325.14 | 0.0792
| 144.7831 | 3.3272 |  | 1913.9675 | 0.0573 |  | 1556.5781 | 0.0268 |  | 356.679 | 0.0672
| 150.3909 | 2.953 |  | 1952.2468 | 0.0572 |  | 1587.7096 | 0.0261 |  | 380.059 | 0.0604
| 155.2815 | 2.6807 |  | 1991.2918 | 0.0571 |  | 1619.4638 | 0.0255 |  | 400.362 | 0.0562
| 160.4911 | 2.4337 |  | 2031.1176 | 0.0571 |  | 1651.8531 | 0.0249 |  | 440.136 | 0.0496
| 165.2134 | 2.2407 |  | 2071.74 | 0.057 |  | 1684.8902 | 0.0243 |  | 468.499 | 0.0459
| 170.9279 | 2.0388 |  | 2113.1748 | 0.0569 |  | 1718.588 | 0.0238 |  | 504.432 | 0.0421
| 176.3091 | 1.8745 |  | 2155.4382 | 0.0568 |  | 1752.9597 | 0.0232 |  | 566 | 0.0371
| 183.1379 | 1.695 |  | 2198.547 | 0.0567 |  | 1788.0189 | 0.0227 |  | 609.637 | 0.0344
| 190.4221 | 1.5324 |  | 2242.518 | 0.0567 |  | 1823.7793 | 0.0222 |  | 648.923 | 0.0325
| 198.5896 | 1.378 |  | 2287.3683 | 0.0566 |  | 1860.2549 | 0.0218 |  | 714.877 | 0.0298
| 208.3543 | 1.2238 |  | 2333.1157 | 0.0566 |  | 1897.46 | 0.0213 |  | 767.307 | 0.0282
| 221.4597 | 1.0562 |  | 2379.778 | 0.0565 |  | 1935.4092 | 0.0209 |  | 833.065 | 0.0266
| 234.6839 | 0.9212 |  | 2427.3736 | 0.0564 |  | 1974.1174 | 0.0204 |  | 882 | 0.0256
| 246.9632 | 0.8186 |  | 2475.921 | 0.0564 |  | 2013.5997 | 0.02 |  | 932 | 0.0247
| 257.8147 | 0.742 |  | 2525.4394 | 0.0563 |  | 2016.3485 | 0.02 |  | 980 | 0.024
| 267.2648 | 0.684 |  | 2575.9482 | 0.0563 |  | 2056.6754 | 0.016 |  | 1030 | 0.0234
| 278.1724 | 0.6255 |  | 2627.4672 | 0.0562 |  | 2097.809 | 0.016 |  | 1100 | 0.0226
| 294.195 | 0.5525 |  | 2680.0165 | 0.0562 |  | 2139.7651 | 0.016 |  | 1175 | 0.022
| 305.5888 | 0.5084 |  | 2733.6169 | 0.0561 |  | 2182.5604 | 0.016 |  | 1260 | 0.0214
| 320.6148 | 0.458 |  | 2788.2892 | 0.0561 |  | 2226.2116 | 0.016 |  | 1340 | 0.0209
| 337.3909 | 0.4102 |  | 2844.055 | 0.056 |  | 2270.7359 | 0.016 |  | 1422.396 | 0.0205
| 362.9417 | 0.351 |  | 2900.9361 | 0.056 |  | 2316.1506 | 0.016 |  | 1681.1548 | 0.016
| 390.0369 | 0.3013 |  | 2958.9548 | 0.056 |  | 2362.4736 | 0.016 |  | 2161.4847 | 0.016
| 442.4123 | 0.2314 |  | 3018.1339 | 0.0559 |  | 2409.7231 | 0.016 |  | 3122.1446 | 0.014
| 485.5301 | 0.1907 |  | 3078.4966 | 0.0559 |  | 2457.9175 | 0.016 | 65Tap | 72.6011 | 200.1886
| 533.918 | 0.1568 |  | 3140.0665 | 0.0559 |  | 2507.0759 | 0.016 |  | 73.7627 | 48.8887
| 583.6149 | 0.1306 |  | 3202.8679 | 0.0558 |  | 2557.2174 | 0.016 |  | 74.1 | 40.025
| 642.4198 | 0.1074 |  | 3266.9252 | 0.0558 |  | 2608.3618 | 0.016 |  | 74.5338 | 32.4286
| 712.8286 | 0.0869 |  | 3332.2637 | 0.0558 |  | 2660.529 | 0.016 |  | 75.4 | 23.4666
| 779.1795 | 0.0725 |  | 3398.909 | 0.0557 |  | 2713.7396 | 0.016 |  | 76.1816 | 18.7464
| 856.8318 | 0.0598 |  | 3466.8872 | 0.0557 |  | 2768.0144 | 0.016 |  | 76.9 | 15.7997
| 932.8473 | 0.0507 |  | 3536.2249 | 0.0557 |  | 2823.3747 | 0.016 |  | 77.6226 | 13.6272
| 1019.6769 | 0.0441 |  | 3606.9494 | 0.0556 |  | 2879.8421 | 0.016 |  | 78.4 | 11.858
| 1100 | 0.0392 |  | 3679.0884 | 0.0556 |  | 2937.439 | 0.016 |  | 79.255 | 10.3644
| 1185.51 | 0.0352 |  | 3752.6702 | 0.0556 |  | 2996.1878 | 0.016 |  | 80.3 | 8.969
| 1298.45 | 0.031 |  | 3827.7236 | 0.0556 |  | 3056.1115 | 0.016 |  | 81.2603 | 7.9717
| 1453.79 | 0.0267 |  | 3904.278 | 0.0556 |  | 3117.2338 | 0.016 |  | 83 | 6.6188
| 1559.2 | 0.0245 |  | 3982.3636 | 0.0555 |  | 3179.5784 | 0.016 |  | 84.7154 | 5.655
| 1649.01 | 0.023 |  | 4062.0109 | 0.0555 |  | 3243.17 | 0.016 |  | 86.7 | 4.8261
| 1724.91 | 0.0219 |  | 4143.2511 | 0.0555 |  | 3308.0334 | 0.016 |  | 88.6853 | 4.198
| 1798.89 | 0.0209 |  | 4226.1161 | 0.0555 |  | 3374.1941 | 0.016 |  | 93.3262 | 3.194
| 1849.98 | 0.0203 |  | 4310.6384 | 0.0555 |  | 3441.6779 | 0.016 |  | 100.1715 | 2.3277
| 1877.93 | 0.016 |  | 4396.8512 | 0.0554 |  | 3510.5115 | 0.016 |  | 106.9607 | 1.8106
| 1971.0813 | 0.016 |  | 4484.7882 | 0.0554 |  | 3580.7217 | 0.016 |  | 113.4991 | 1.477
| 2217.4665 | 0.016 |  | 4574.484 | 0.0554 |  | 3652.3362 | 0.016 |  | 120.5556 | 1.2212
| 2463.8517 | 0.016 |  | 4665.9737 | 0.0554 |  | 3725.3829 | 0.016 |  | 130.1003 | 0.9781
| 2759.5139 | 0.016 |  | 4759.2931 | 0.0554 |  | 3799.8905 | 0.016 |  | 141.0838 | 0.7855
| 3755.8955 | 0.014 |  | 4854.479 | 0.0554 |  | 3875.8884 | 0.016 |  | 152.5392 | 0.644
50E | 111.3013 | 1605.2161 |  | 4951.5686 | 0.0553 |  | 3953.4061 | 0.016 |  | 164.582 | 0.5358
| 111.6357 | 581.0949 |  | 5050.6 | 0.0553 |  | 4032.4743 | 0.016 |  | 176.6545 | 0.4543
| 112.5322 | 213.6488 |  | 5151.612 | 0.0553 |  | 4032.697 | 0.014 |  | 191.5958 | 0.3785
| 113.0965 | 152.5393 |  | 5254.6442 | 0.0553 |  | 4113.3509 | 0.014 |  | 203.3086 | 0.3325
| 113.6 | 121.4081 |  | 5359.7371 | 0.0553 |  | 4195.6179 | 0.014 |  | 218.4479 | 0.2852
| 114.0051 | 104.2255 |  | 5466.9318 | 0.0553 |  | 4279.5303 | 0.014 |  | 238.021 | 0.2385
| 114.5 | 88.8096 |  | 5576.2705 | 0.0553 |  | 4365.1209 | 0.014 |  | 263.036 | 0.1947
| 114.9203 | 78.8636 |  | 5687.7959 | 0.0553 |  | 4452.4233 | 0.014 |  | 287.474 | 0.1633
| 115.6 | 66.7215 |  | 5801.5518 | 0.0553 |  | 4541.4718 | 0.014 |  | 318.896 | 0.1335
| 116.1919 | 58.7951 |  | 5917.5828 | 0.0552 |  | 4632.3012 | 0.014 |  | 351.311 | 0.1112
| 116.7 | 53.3307 |  | 6035.9345 | 0.0552 |  | 4724.9472 | 0.014 |  | 400.963 | 0.0871
| 117.2424 | 48.4974 |  | 6156.6532 | 0.0552 |  | 4819.4462 | 0.014 |  | 446.343 | 0.0719
| 117.8 | 44.3462 |  | 6279.7862 | 0.0552 |  | 4915.8351 | 0.014 |  | 497.375 | 0.0598
| 118.4205 | 40.4719 |  | 6405.382 | 0.0552 |  | 5014.1518 | 0.014 |  | 557.135 | 0.0513
| 119.2 | 36.448 |  | 6533.4896 | 0.0552 |  | 5114.4348 | 0.014 |  | 626.026 | 0.0444
| 119.9693 | 33.1718 |  | 6664.1594 | 0.0552 |  | 5216.7235 | 0.014 |  | 715.25 | 0.0382
| 120.7 | 30.5475 |  | 6797.4426 | 0.0552 |  | 5321.058 | 0.014 |  | 788.774 | 0.0346
| 121.418 | 28.3317 |  | 6933.3914 | 0.0552 |  | 5427.4791 | 0.014 |  | 899.32 | 0.0307
| 122.3 | 25.9998 |  | 7072.0593 | 0.0552 |  | 5536.0287 | 0.014 |  | 1007.372 | 0.028
| 123.2528 | 23.8621 |  | 7213.5004 | 0.0552 |  | 5646.7493 | 0.014 |  | 1125.886 | 0.0259
| 124.1 | 22.2253 |  | 7357.7704 | 0.0552 |  | 5759.6843 | 0.014 |  | 1215.634 | 0.0247
| 124.9908 | 20.7204 |  | 7504.9259 | 0.0552 |  | 5874.878 | 0.014 |  | 1421.761 | 0.0227
| 125.8 | 19.5121 |  | 7655.0244 | 0.0551 |  | 5992.3755 | 0.014 |  | 1791.377 | 0.0207
| 126.6265 | 18.4084 |  | 7808.1249 | 0.0551 |  | 6112.223 | 0.014 |  | 2117.2599 | 0.016
| 127.6 | 17.251 |  | 7964.2874 | 0.0551 |  | 6234.4675 | 0.014 |  | 2722.1913 | 0.016
| 128.5405 | 16.2561 |  | 8123.5731 | 0.0551 |  | 6359.1569 | 0.014 |  | 3932.0541 | 0.016
| 129.6 | 15.2571 |  | 8286.0446 | 0.0551 |  | 6486.34 | 0.014 | 80Tap | 89.4531 | 165.3721
| 130.6129 | 14.404 |  | 8451.7655 | 0.0551 |  | 6616.0668 | 0.014 |  | 90.6719 | 52.015
| 131.6 | 13.6543 |  | 8620.8008 | 0.0551 |  | 6748.3881 | 0.014 |  | 91.2 | 40.025
| 132.5874 | 12.9738 |  | 8793.2168 | 0.0551 |  | 6883.3559 | 0.014 |  | 91.8115 | 31.5557
| 135.1306 | 11.4803 |  | 8969.0811 | 0.0551 |  | 7021.023 | 0.014 |  | 92.7 | 24.0941
| 137.5847 | 10.3133 |  | 9148.4627 | 0.0551 |  | 7161.4435 | 0.014 |  | 93.6463 | 19.2129
| 139.9442 | 9.3803 |  | 9331.432 | 0.0551 |  | 7304.6723 | 0.014 |  | 95 | 14.8595
| 142.3433 | 8.5778 |  | 9518.0606 | 0.0551 |  | 7450.7658 | 0.014 |  | 96.4161 | 11.9825
| 144.7831 | 7.8804 |  | 9708.4218 | 0.0551 |  | 7599.7811 | 0.014 |  | 98.2 | 9.6051
| 147.5606 | 7.2017 |  | 9902.5903 | 0.0551 |  | 7751.7767 | 0.014 |  | 99.9933 | 7.9864
| 150.5416 | 6.5814 |  | 10100.6421 | 0.0551 |  | 7906.8123 | 0.014 |  | 102.4 | 6.4909
| 154.8162 | 5.8423 |  | 10302.6549 | 0.0551 |  | 8064.9485 | 0.014 |  | 104.7893 | 5.4555
| 160.171 | 5.1019 |  | 10508.708 | 0.0551 |  | 8226.2475 | 0.014 |  | 107.1 | 4.7138
| 166.2078 | 4.444 |  | 10718.8822 | 0.0551 |  | 8390.7724 | 0.014 |  | 109.3587 | 4.1516
| 173.5107 | 3.8232 |  | 10933.2598 | 0.0551 |  | 8558.5879 | 0.014 |  | 113.5354 | 3.3855
| 181.6793 | 3.2863 |  | 11151.925 | 0.0551 |  | 8729.7596 | 0.014 |  | 117.5262 | 2.8642
| 189.8512 | 2.8653 |  | 11374.9635 | 0.0551 |  | 8904.3548 | 0.014 |  | 124.7136 | 2.222
| 196.8109 | 2.5731 |  | 11602.4628 | 0.0551 |  | 9082.4419 | 0.014 |  | 133.4575 | 1.7246
| 204.6374 | 2.2993 |  | 11834.512 | 0.0551 |  | 9264.0908 | 0.014 |  | 144.5092 | 1.3248
| 212.7763 | 2.0621 | 700Main | 778.6295 | 912.7277 |  | 9449.3726 | 0.014 |  | 155.1902 | 1.0692
| 223.685 | 1.8016 |  | 789.2698 | 67.2285 |  | 9638.36 | 0.014 |  | 165.3278 | 0.8954
| 232.8139 | 1.6222 |  | 801.7273 | 32.0283 |  | 9831.1272 | 0.014 |  | 178.9403 | 0.7268
| 244.7511 | 1.4278 |  | 810.6 | 23.252 |  | 10027.7498 | 0.014 |  | 195.0894 | 0.5862
| 256.7851 | 1.267 |  | 819.4989 | 18.2004 |  | 10228.3048 | 0.014 |  | 215.3701 | 0.4643
| 268.873 | 1.1327 |  | 832.5 | 13.7752 |  | 10432.8708 | 0.014 |  | 237.7595 | 0.3717
| 284.0761 | 0.9934 |  | 845.5711 | 11.0387 |  | 10641.5283 | 0.014 |  | 256.2659 | 0.3158
| 298.0439 | 0.8878 |  | 860.8 | 8.9386 |  | 10854.3588 | 0.014 |  | 279.103 | 0.2636
| 314.2667 | 0.7857 |  | 876.1258 | 7.4832 |  | 11071.446 | 0.014 |  | 304.751 | 0.22
| 330.3795 | 0.7014 |  | 891.5 | 6.4183 |  | 11292.8749 | 0.014 |  | 333.947 | 0.183
| 343.8622 | 0.6412 |  | 906.8356 | 5.6099 |  | 11518.7324 | 0.014 |  | 368.27 | 0.151
| 361.493 | 0.5738 |  | 925.7 | 4.8464 |  | 11749.1071 | 0.014 |  | 405.768 | 0.1253
| 381.931 | 0.5085 |  | 944.5205 | 4.2579 |  | 11984.0892 | 0.014 |  | 449.82 | 0.1033
| 409.6246 | 0.4368 |  | 988.9209 | 3.2884 | 30T | 78.9888 | 668.6928 |  | 493.489 | 0.0871
| 457.2546 | 0.3451 |  | 1035.408 | 2.635 |  | 80.5686 | 216.2953 |  | 552.788 | 0.0711
| 504.3357 | 0.2806 |  | 1084.0808 | 2.1665 |  | 81.4 | 158.8726 |  | 610.253 | 0.06
| 577.808 | 0.2112 |  | 1151.7528 | 1.7217 |  | 82.1799 | 126.9433 |  | 681.451 | 0.0517
| 667.3007 | 0.1568 |  | 1217.2776 | 1.4248 |  | 83 | 104.6201 |  | 771.325 | 0.0444
| 725.7756 | 0.132 |  | 1298.8734 | 1.163 |  | 83.8235 | 88.7846 |  | 849.737 | 0.0397
| 788.5856 | 0.1114 |  | 1385.5193 | 0.9653 |  | 84.7 | 76.3589 |  | 941.006 | 0.0357
| 840.7047 | 0.0978 |  | 1476.6257 | 0.8129 |  | 85.5 | 67.633 |  | 1037.748 | 0.0325
| 902.5654 | 0.0846 |  | 1560.6338 | 0.7059 |  | 86.4 | 59.8607 |  | 1123.189 | 0.0303
| 991.5224 | 0.0699 |  | 1668.4723 | 0.6003 |  | 87.21 | 54.1992 |  | 1249.02 | 0.0279
| 1049.6805 | 0.0623 |  | 1778.1852 | 0.5182 |  | 88.1 | 49.052 |  | 1364.582 | 0.0262
| 1117.93 | 0.0549 |  | 1847.653 | 0.4757 |  | 88.9542 | 44.917 |  | 1492.389 | 0.0247
| 1181.147 | 0.0497 |  | 2004.409 | 0.3995 |  | 89.8 | 41.4261 |  | 1715.799 | 0.0229
| 1240.459 | 0.046 |  | 2142.913 | 0.3484 |  | 90.7333 | 38.124 |  | 1974.707 | 0.0215
| 1335 | 0.041 |  | 2271.932 | 0.3105 |  | 91.6 | 35.4721 |  | 2253.835 | 0.0205
| 1393.99 | 0.0385 |  | 2459.543 | 0.2672 |  | 92.548 | 32.941 |  | 2663.8471 | 0.016
| 1496.56 | 0.0347 |  | 2626.752 | 0.2375 |  | 93.5 | 30.717 |  | 3424.9463 | 0.016
| 1576.44 | 0.0322 |  | 2837.731 | 0.2095 |  | 94.3989 | 28.859 |  | 4947.1446 | 0.014
| 1685.69 | 0.0294 |  | 3020 | 0.1903 |  | 96.2869 | 25.5633 | Total Result |  | 781.9267
| 1781 | 0.0274 |  | 3290 | 0.1678 |  | 98.2126 | 22.8486
| 1893.02 | 0.0254 |  | 3514.957 | 0.1531 |  | 100.1769 | 20.5753
| 1984.11 | 0.024 |  | 3800 | 0.1383 |  | 102.1804 | 18.6453
| 2060.96 | 0.023 |  | 4055 | 0.1277 |  | 104.224 | 16.9874
| 2138.65 | 0.0221 |  | 4350 | 0.1178 |  | 106.3085 | 15.549
| 2208.19 | 0.0213 |  | 4772.749 | 0.1068 |  | 108.4347 | 14.2901
| 2261.83 | 0.0208 |  | 5150.713 | 0.0992 |  | 110.6034 | 13.1799
| 2289.13 | 0.0205 |  | 5658.145 | 0.0913 |  | 112.8155 | 12.1943
| 2402.6782 | 0.016 |  | 6241.579 | 0.0846 |  | 115.0718 | 11.314
| 2703.0129 | 0.016 |  | 6778.19 | 0.0799 |  | 117.3732 | 10.5236
| 3003.3477 | 0.016 |  | 7461.519 | 0.0753 |  | 119.7207 | 9.8106
| 3363.7494 | 0.016 |  | 8162.447 | 0.0718 |  | 122.1151 | 9.1645
| 4578.3032 | 0.016 |  | 8892.008 | 0.069 |  | 124.5574 | 8.5769
65E | 144.9283 | 819.5794 |  | 9707.025 | 0.0665 |  | 127.0485 | 8.0405
| 146.2384 | 220.056 |  | 10519.58 | 0.0647 |  | 129.5895 | 7.5493
| 147.4132 | 132.4399 |  | 11898.73 | 0.0623 |  | 132.1813 | 7.0982
| 148 | 110.3605 | 800Main | 889.5018 | 1449.8189 |  | 134.8249 | 6.6827
| 148.5968 | 94.3064 |  | 900.7163 | 74.7033 |  | 137.5214 | 6.2991
| 149.6 | 75.6965 |  | 912.0738 | 37.8905 |  | 140.2718 | 5.9441
| 150.5416 | 63.8022 |  | 922.2 | 26.2387 |  | 143.0773 | 5.6149
| 151.5 | 54.957 |  | 932.2929 | 20.0363 |  | 145.9388 | 5.309
| 152.3588 | 48.8518 |  | 944.1 | 15.6599 |  | 148.8576 | 5.0242
| 153.3 | 43.5216 |  | 955.9506 | 12.818 |  | 151.8348 | 4.7586
| 154.198 | 39.3958 |  | 968.6 | 10.7178 |  | 154.8714 | 4.5105
| 155.1 | 35.9523 |  | 981.2319 | 9.1956 |  | 157.9689 | 4.2785
| 155.9041 | 33.3401 |  | 999 | 7.6468 |  | 161.1283 | 4.0611
| 156.8 | 30.8307 |  | 1016.6915 | 6.5337 |  | 164.3508 | 3.8572
| 157.6289 | 28.8131 |  | 1035.1 | 5.6625 |  | 167.6378 | 3.6658
| 158.6 | 26.7505 |  | 1053.4326 | 4.9895 |  | 170.9906 | 3.4857
| 159.5308 | 25.0231 |  | 1073.6 | 4.4044 |  | 174.4104 | 3.3163
| 160.5 | 23.4379 |  | 1093.7828 | 3.935 |  | 177.8986 | 3.1567
| 161.4569 | 22.0504 |  | 1139.2414 | 3.1573 |  | 181.4566 | 3.0061
| 162.5 | 20.7059 |  | 1181.6442 | 2.652 |  | 185.0857 | 2.864
| 163.57 | 19.4796 |  | 1229.4711 | 2.2353 |  | 188.7874 | 2.7297
| 164.7 | 18.3256 |  | 1287.2717 | 1.8678 |  | 192.5632 | 2.6028
| 165.8756 | 17.2548 |  | 1333.7907 | 1.643 |  | 196.4144 | 2.4827
| 167 | 16.3354 |  | 1395.0387 | 1.412 |  | 200.3427 | 2.3689
| 168.047 | 15.5585 |  | 1466.7367 | 1.2059 |  | 204.3496 | 2.2611
| 169.4 | 14.6515 |  | 1540.5104 | 1.0432 |  | 208.4366 | 2.1589
| 170.7563 | 13.8365 |  | 1617.9944 | 0.9096 |  | 212.6053 | 2.062
| 172.4 | 12.9554 |  | 1706.4883 | 0.7897 |  | 216.8574 | 1.9699
| 174.0321 | 12.178 |  | 1794.1935 | 0.6956 |  | 221.1946 | 1.8825
| 176.4862 | 11.1593 |  | 1890.3489 | 0.6128 |  | 225.6185 | 1.7994
| 180.0513 | 9.9317 |  | 1999.9936 | 0.5373 |  | 230.1308 | 1.7204
| 183.5053 | 8.9581 |  | 2131.5206 | 0.466 |  | 234.7334 | 1.6453
| 187.3993 | 8.0504 |  | 2278.151 | 0.4042 |  | 239.4281 | 1.5737
| 191.1844 | 7.315 |  | 2505.226 | 0.333 |  | 244.2167 | 1.5057
| 195.6328 | 6.592 |  | 2706.467 | 0.2868 |  | 249.101 | 1.4408
| 199.9844 | 5.9987 |  | 2973.129 | 0.2413 |  | 254.083 | 1.379
| 205.0477 | 5.4179 |  | 3148.863 | 0.2196 |  | 259.1647 | 1.3201
| 209.6083 | 4.9738 |  | 3433.924 | 0.1917 |  | 264.348 | 1.2639
| 216.4239 | 4.4178 |  | 3748.702 | 0.1685 |  | 269.6349 | 1.2103
| 224.5815 | 3.8804 |  | 4079.537 | 0.15 |  | 275.0276 | 1.1592
| 231.6534 | 3.4987 |  | 4448.85 | 0.1342 |  | 280.5282 | 1.1104
| 239.9045 | 3.1276 |  | 4940.639 | 0.1186 |  | 286.1388 | 1.0638
| 246.9632 | 2.8598 |  | 5482.725 | 0.1062 |  | 291.8615 | 1.0193
| 254.7391 | 2.6064 |  | 6170.942 | 0.095 |  | 297.6988 | 0.9767
| 263.2861 | 2.3682 |  | 6962.742 | 0.0861 |  | 303.6527 | 0.9361
| 270.7628 | 2.1879 |  | 7892.145 | 0.0789 |  | 309.7258 | 0.8973
| 282.3766 | 1.9492 |  | 8936.271 | 0.0734 |  | 315.9203 | 0.8602
| 296.5578 | 1.7106 |  | 9961.293 | 0.0696 |  | 322.2387 | 0.8247
| 310.2077 | 1.5226 |  | 11338.204 | 0.066 |  | 328.6835 | 0.7907
| 327.4194 | 1.3291 | 80Main | 89.76 | 101.5883 |  | 335.2572 | 0.7583
| 347.666 | 1.1474 |  | 91.5552 | 32.8902 |  | 341.9623 | 0.7272
| 367.6904 | 1.0037 |  | 92.5 | 24.1703 |  | 348.8015 | 0.6975
| 389.6475 | 0.8762 |  | 93.3863 | 19.3218 |  | 355.7776 | 0.669
| 417.8999 | 0.7462 |  | 94.3 | 15.9869 |  | 362.8931 | 0.6418
| 440.6457 | 0.6621 |  | 95.254 | 13.5272 |  | 370.151 | 0.6157
| 470.7098 | 0.5718 |  | 96.2 | 11.7228 |  | 377.554 | 0.5907
| 489.9191 | 0.5236 |  | 97.1591 | 10.3153 |  | 385.1051 | 0.5668
| 509.4045 | 0.4809 |  | 98.1 | 9.2198 |  | 392.8072 | 0.5439
| 531.2549 | 0.439 |  | 99.1023 | 8.2753 |  | 400.6633 | 0.5219
| 561.8536 | 0.3892 |  | 100.1 | 7.5033 |  | 408.6766 | 0.5009
| 597.1933 | 0.3418 |  | 101.0843 | 6.8658 |  | 416.8501 | 0.4807
| 641.7774 | 0.2935 |  | 102.1 | 6.3079 |  | 425.1871 | 0.4614
| 680.7812 | 0.2593 |  | 103.106 | 5.8343 |  | 433.6909 | 0.4429
| 729.4133 | 0.2245 |  | 104.1 | 5.4281 |  | 442.3647 | 0.4251
| 791.7459 | 0.1894 |  | 105.1681 | 5.0472 |  | 451.212 | 0.4081
| 868.043 | 0.1566 |  | 106.2 | 4.7242 |  | 460.2362 | 0.3918
| 952.644 | 0.1294 |  | 107.2715 | 4.4273 |  | 469.441 | 0.3761
| 1093.6112 | 0.0977 |  | 109.4169 | 3.9269 |  | 478.8298 | 0.3611
| 1196.602 | 0.0813 |  | 111.6053 | 3.5146 |  | 488.4064 | 0.3467
| 1309.286 | 0.0678 |  | 113.8374 | 3.1694 |  | 498.1745 | 0.3329
| 1428.295 | 0.0568 |  | 116.1141 | 2.8763 |  | 508.138 | 0.3197
| 1559.679 | 0.0485 |  | 118.4364 | 2.6246 |  | 518.3007 | 0.307
| 1750 | 0.0405 |  | 120.8051 | 2.4062 |  | 528.6668 | 0.2948
| 1935 | 0.0349 |  | 123.2212 | 2.215 |  | 539.2401 | 0.2831
| 2125.85 | 0.0306 |  | 125.6857 | 2.0464 |  | 550.0249 | 0.2719
| 2296.01 | 0.0277 |  | 128.1994 | 1.8967 |  | 561.0254 | 0.2611
| 2464.95 | 0.0253 |  | 130.7634 | 1.7631 |  | 572.2459 | 0.2508
| 2659.59 | 0.0232 |  | 133.3786 | 1.643 |  | 583.6908 | 0.2409
| 2762.6 | 0.0222 |  | 136.0462 | 1.5348 |  | 595.3646 | 0.2313
| 2875.35 | 0.0213 |  | 138.7671 | 1.4367 |  | 607.2719 | 0.2222
| 2980.74 | 0.0205 |  | 141.5425 | 1.3474 |  | 619.4174 | 0.2134
| 3090.01 | 0.016 |  | 144.3733 | 1.266 |  | 631.8057 | 0.205
| 3133.57 | 0.016 |  | 147.2608 | 1.1914 |  | 644.4418 | 0.1969
| 3289.0051 | 0.016 |  | 150.206 | 1.1229 |  | 657.3307 | 0.1892
| 3700.1307 | 0.016 |  | 153.2101 | 1.0598 |  | 670.4773 | 0.1817
| 4111.2564 | 0.016 |  | 156.2743 | 1.0015 |  | 683.8868 | 0.1746
| 4604.6071 | 0.016 |  | 159.3998 | 0.9476 |  | 697.5646 | 0.1677
| 6267.1992 | 0.014 |  | 162.5878 | 0.8976 |  | 711.5159 | 0.1611
7E | 17.34 | 111.8768 |  | 165.8396 | 0.8512 |  | 725.7462 | 0.1548
| 17.5 | 75.6491 |  | 169.1564 | 0.8079 |  | 740.2611 | 0.1487
| 17.6868 | 54.715 |  | 172.5395 | 0.7676 |  | 755.0663 | 0.1429
| 17.9 | 41.4456 |  | 175.9903 | 0.7299 |  | 770.1676 | 0.1373
| 18.0405 | 35.6744 |  | 179.5101 | 0.6947 |  | 785.571 | 0.1319
| 18.2 | 30.7648 |  | 183.1003 | 0.6617 |  | 801.2824 | 0.1267
| 18.4013 | 26.1641 |  | 186.7623 | 0.6307 |  | 817.3081 | 0.1218
| 18.6 | 22.7618 |  | 190.4975 | 0.6017 |  | 833.6542 | 0.117
| 18.7694 | 20.4658 |  | 194.3075 | 0.5743 |  | 850.3273 | 0.1124
| 19.1448 | 16.6735 |  | 198.1936 | 0.5486 |  | 867.3339 | 0.108
| 19.5277 | 13.9704 |  | 202.1575 | 0.5244 |  | 884.6805 | 0.1038
| 19.9182 | 11.9478 |  | 206.2007 | 0.5015 |  | 902.3741 | 0.0997
| 20.3166 | 10.379 |  | 210.3247 | 0.4799 |  | 920.4216 | 0.0958
| 20.7229 | 9.1278 |  | 214.5312 | 0.4595 |  | 938.8301 | 0.0921
| 21.1374 | 8.1075 |  | 218.8218 | 0.4402 |  | 957.6067 | 0.0885
| 21.5601 | 7.2603 |  | 223.1982 | 0.422 |  | 976.7588 | 0.085
| 21.9913 | 6.5464 |  | 227.6622 | 0.4047 |  | 996.294 | 0.0817
| 22.4311 | 5.9371 |  | 232.2154 | 0.3884 |  | 1016.2198 | 0.0785
| 22.8798 | 5.4115 |  | 236.8597 | 0.3728 |  | 1036.5442 | 0.0754
| 23.3374 | 4.9539 |  | 241.5969 | 0.3581 |  | 1057.2751 | 0.0725
| 23.8041 | 4.5522 |  | 246.4289 | 0.3441 |  | 1078.4206 | 0.0697
| 24.2802 | 4.1971 |  | 251.3575 | 0.3309 |  | 1099.989 | 0.0669
| 24.7658 | 3.8812 |  | 256.3846 | 0.3182 |  | 1121.9888 | 0.0643
| 25.2611 | 3.5986 |  | 261.5123 | 0.3063 |  | 1144.4286 | 0.0618
| 25.7663 | 3.3447 |  | 266.7425 | 0.2948 |  | 1167.3172 | 0.0594
| 26.2817 | 3.1153 |  | 272.0774 | 0.284 |  | 1190.6635 | 0.0571
| 26.8073 | 2.9073 |  | 277.5189 | 0.2736 |  | 1214.4768 | 0.0549
| 27.3434 | 2.7181 |  | 283.0693 | 0.2638 |  | 1238.7663 | 0.0527
| 27.8903 | 2.5453 |  | 288.7307 | 0.2544 |  | 1263.5417 | 0.051
| 28.4481 | 2.387 |  | 294.5053 | 0.2455 |  | 1288.8125 | 0.0494
| 29.0171 | 2.2417 |  | 300.3954 | 0.2372 |  | 1314.5887 | 0.0479
| 29.5974 | 2.1078 |  | 306.4033 | 0.2296 |  | 1340.8805 | 0.0464
| 30.1894 | 1.9881 |  | 312.5314 | 0.2223 |  | 1367.6981 | 0.045
| 30.7931 | 1.8844 |  | 318.782 | 0.2153 |  | 1395.0521 | 0.0436
| 31.409 | 1.7875 |  | 325.1577 | 0.2086 |  | 1422.9531 | 0.0423
| 32.0372 | 1.6967 |  | 331.6608 | 0.2023 |  | 1451.4122 | 0.0411
| 32.6779 | 1.6115 |  | 338.294 | 0.1962 |  | 1480.4404 | 0.0399
| 33.3315 | 1.5315 |  | 345.0599 | 0.1903 |  | 1510.0492 | 0.0387
| 33.9981 | 1.4563 |  | 351.9611 | 0.1847 |  | 1540.2502 | 0.0376
| 34.6781 | 1.3855 |  | 359.0003 | 0.1794 |  | 1571.0552 | 0.0365
| 35.3716 | 1.3188 |  | 366.1804 | 0.1743 |  | 1602.4763 | 0.0355
| 36.0791 | 1.2559 |  | 373.504 | 0.1694 |  | 1634.5259 | 0.0345
| 36.8007 | 1.1965 |  | 380.974 | 0.1647 |  | 1667.2164 | 0.0335
| 37.5367 | 1.1404 |  | 388.5935 | 0.1602 |  | 1700.5607 | 0.0326
| 38.2874 | 1.0874 |  | 396.3654 | 0.1559 |  | 1734.5719 | 0.0317
| 39.0532 | 1.0372 |  | 404.2927 | 0.1518 |  | 1769.2634 | 0.0309
| 39.8342 | 0.9896 |  | 412.3786 | 0.1479 |  | 1804.6486 | 0.0301
| 40.6309 | 0.9446 |  | 420.6261 | 0.1441 |  | 1840.7416 | 0.0293
| 41.4435 | 0.9019 |  | 429.0386 | 0.1405 |  | 1877.5564 | 0.0285
| 42.2724 | 0.8614 |  | 437.6194 | 0.137 |  | 1915.1076 | 0.0278
| 43.1178 | 0.823 |  | 446.3718 | 0.1336 |  | 1953.4097 | 0.0271
| 43.9802 | 0.7864 |  | 455.2992 | 0.1305 |  | 1992.4779 | 0.0265
| 44.8598 | 0.7517 |  | 464.4052 | 0.1274 |  | 2032.3275 | 0.0258
| 45.757 | 0.7187 |  | 473.6933 | 0.1245 |  | 2072.974 | 0.0252
| 46.6721 | 0.6873 |  | 483.1672 | 0.1217 |  | 2114.4335 | 0.0246
| 47.6056 | 0.6574 |  | 492.8305 | 0.119 |  | 2156.7222 | 0.024
| 48.5577 | 0.629 |  | 502.6872 | 0.1164 |  | 2199.8566 | 0.0235
| 49.5288 | 0.6019 |  | 512.7409 | 0.1139 |  | 2243.8537 | 0.023
| 50.5194 | 0.5761 |  | 522.9957 | 0.1115 |  | 2288.7308 | 0.0225
| 51.5298 | 0.5515 |  | 533.4556 | 0.1092 |  | 2334.5054 | 0.022
| 52.5604 | 0.528 |  | 544.1247 | 0.107 |  | 2381.1955 | 0.0215
| 53.6116 | 0.5056 |  | 555.0072 | 0.1049 |  | 2428.8194 | 0.0211
| 54.6838 | 0.4842 |  | 566.1074 | 0.1029 |  | 2477.3958 | 0.0206
| 55.7775 | 0.4639 |  | 577.4295 | 0.101 |  | 2526.9437 | 0.0202
| 56.8931 | 0.4444 |  | 588.9781 | 0.0991 |  | 2555.8788 | 0.016
| 58.0309 | 0.4258 |  | 600.7577 | 0.0973 |  | 2606.9963 | 0.016
| 59.1916 | 0.408 |  | 612.7728 | 0.0956 |  | 2659.1363 | 0.016
| 60.3754 | 0.3911 |  | 625.0283 | 0.094 |  | 2712.319 | 0.016
| 61.5829 | 0.3748 |  | 637.5289 | 0.0924 |  | 2766.5654 | 0.016
| 62.8146 | 0.3593 |  | 650.2794 | 0.0909 |  | 2821.8967 | 0.016
| 64.0708 | 0.3445 |  | 663.285 | 0.0894 |  | 2878.3346 | 0.016
| 65.3523 | 0.3303 |  | 676.5507 | 0.088 |  | 2935.9013 | 0.016
| 66.6593 | 0.3168 |  | 690.0817 | 0.0867 |  | 2994.6193 | 0.016
| 67.9925 | 0.3038 |  | 703.8834 | 0.0854 |  | 3054.5117 | 0.016
| 69.3523 | 0.2914 |  | 717.961 | 0.0842 |  | 3115.602 | 0.016
| 70.7394 | 0.2795 |  | 732.3203 | 0.083 |  | 3177.914 | 0.016
| 72.1542 | 0.2681 |  | 746.9667 | 0.0818 |  | 3241.4723 | 0.016
| 73.5973 | 0.2572 |  | 761.906 | 0.0808 |  | 3306.3017 | 0.016
| 75.0692 | 0.2468 |  | 777.1441 | 0.0797 |  | 3372.4277 | 0.016
| 76.5706 | 0.2368 |  | 792.687 | 0.0787 |  | 3439.8763 | 0.016
| 78.102 | 0.2272 |  | 808.5407 | 0.0777 |  | 3508.6738 | 0.016
| 79.664 | 0.218 |  | 824.7116 | 0.0768 |  | 3578.8473 | 0.016
| 81.2573 | 0.2092 |  | 841.2058 | 0.0759 |  | 3650.4243 | 0.016
| 82.8825 | 0.2008 |  | 858.0299 | 0.075 |  | 3723.4327 | 0.016
| 84.5401 | 0.1927 |  | 875.1905 | 0.0742 |  | 3797.9014 | 0.016
| 86.2309 | 0.185 |  | 892.6943 | 0.0734 |  | 3873.8594 | 0.016
| 87.9555 | 0.1776 |  | 910.5482 | 0.0727 |  | 3951.3366 | 0.016
| 89.7146 | 0.1705 |  | 928.7592 | 0.0719 |  | 4030.3633 | 0.016
| 91.5089 | 0.1637 |  | 947.3343 | 0.0712 |  | 4110.9706 | 0.016
| 93.3391 | 0.1571 |  | 966.281 | 0.0706 |  | 4193.19 | 0.016
| 95.2059 | 0.1509 |  | 985.6067 | 0.0699 |  | 4277.0538 | 0.016
| 97.11 | 0.1448 |  | 1005.3188 | 0.0693 |  | 4362.5949 | 0.016
| 99.0522 | 0.1391 |  | 1025.4252 | 0.0687 |  | 4449.8468 | 0.016
| 101.0333 | 0.1335 |  | 1045.9337 | 0.0681 |  | 4538.8437 | 0.016
| 103.0539 | 0.1282 |  | 1066.8523 | 0.0676 |  | 4629.6206 | 0.016
| 105.115 | 0.1231 |  | 1088.1894 | 0.067 |  | 4722.213 | 0.016
| 107.2173 | 0.1183 |  | 1109.9532 | 0.0665 |  | 4816.6573 | 0.016
| 109.3617 | 0.1136 |  | 1132.1522 | 0.066 |  | 4912.9904 | 0.016
| 111.5489 | 0.1091 |  | 1154.7953 | 0.0656 |  | 5011.2502 | 0.016
| 113.7799 | 0.1048 |  | 1177.8912 | 0.0651 |  | 5111.4752 | 0.016
| 116.0555 | 0.1006 |  | 1201.449 | 0.0647 |  | 5111.7575 | 0.016
| 118.3766 | 0.0966 |  | 1225.478 | 0.0643 |  | 5213.9927 | 0.014
| 120.7441 | 0.0928 |  | 1249.9876 | 0.0639 |  | 5318.2725 | 0.014
| 123.159 | 0.0892 |  | 1274.9873 | 0.0635 |  | 5424.638 | 0.014
| 125.6222 | 0.0856 |  | 1300.487 | 0.0631 |  | 5533.1307 | 0.014
| 128.1346 | 0.0823 |  | 1326.4968 | 0.0628 |  | 5643.7934 | 0.014
| 130.6973 | 0.079 |  | 1353.0267 | 0.0624 |  | 5756.6692 | 0.014
| 133.3112 | 0.0759 |  | 1380.0873 | 0.0621 |  | 5871.8026 | 0.014
| 135.9775 | 0.0729 |  | 1407.689 | 0.0618 |  | 5989.2387 | 0.014
| 138.697 | 0.0701 |  | 1435.8428 | 0.0615 |  | 6109.0234 | 0.014
| 141.471 | 0.0673 |  | 1464.5596 | 0.0612 |  | 6231.2039 | 0.014
| 144.3004 | 0.0647 |  | 1493.8508 | 0.0609 |  | 6355.828 | 0.014
| 147.1864 | 0.0621 |  | 1523.7279 | 0.0606 |  | 6482.9445 | 0.014
| 150.1301 | 0.0597 |  | 1554.2024 | 0.0604 |  | 6612.6034 | 0.014
| 153.1327 | 0.0573 |  | 1585.2865 | 0.0601 |  | 6744.8555 | 0.014
| 156.1954 | 0.0551 |  | 1616.9922 | 0.0599 |  | 6879.7526 | 0.014
| 159.3193 | 0.0529 |  | 1649.332 | 0.0597 |  | 7017.3477 | 0.014
| 162.5057 | 0.0511 |  | 1682.3187 | 0.0595 |  | 7157.6946 | 0.014
| 165.7558 | 0.0495 |  | 1715.965 | 0.0594 |  | 7300.8485 | 0.014
| 169.0709 | 0.048 |  | 1750.2843 | 0.0592 |  | 7446.8655 | 0.014
| 172.4523 | 0.0465 |  | 1785.29 | 0.059 |  | 7595.8028 | 0.014
| 175.9014 | 0.0451 |  | 1820.9958 | 0.0589 |  | 7747.7188 | 0.014
| 179.4194 | 0.0437 |  | 1857.4157 | 0.0587 |  | 7902.6732 | 0.014
| 183.0078 | 0.0424 |  | 1894.5641 | 0.0586 |  | 8060.7267 | 0.014
| 186.6679 | 0.0411 |  | 1932.4553 | 0.0584 |  | 8221.9412 | 0.014
| 190.4013 | 0.0399 |  | 1971.1045 | 0.0583 |  | 8386.38 | 0.014
| 194.2093 | 0.0387 |  | 2010.5265 | 0.0582 |  | 8554.1076 | 0.014
| 198.0935 | 0.0376 |  | 2050.7371 | 0.058 |  | 8725.1898 | 0.014
| 202.0554 | 0.0365 |  | 2091.7518 | 0.0579 |  | 8899.6936 | 0.014
| 206.0965 | 0.0355 |  | 2133.5868 | 0.0578 |  | 9077.6875 | 0.014
| 210.2184 | 0.0345 |  | 2176.2586 | 0.0577 |  | 9259.2412 | 0.014
| 214.4228 | 0.0335 |  | 2219.7838 | 0.0576 |  | 9444.426 | 0.014
| 218.7112 | 0.0326 |  | 2264.1794 | 0.0575 |  | 9633.3146 | 0.014
| 223.0855 | 0.0317 |  | 2309.463 | 0.0574 |  | 9825.9808 | 0.014
| 227.5472 | 0.0309 |  | 2355.6523 | 0.0573 |  | 10022.5005 | 0.014
| 232.0981 | 0.0301 |  | 2402.7653 | 0.0572 |  | 10222.9505 | 0.014
| 236.7401 | 0.0293 |  | 2450.8206 | 0.0571 |  | 10427.4095 | 0.014
| 241.4749 | 0.0285 |  | 2499.837 | 0.0571 |  | 10635.9577 | 0.014
| 246.3044 | 0.0278 |  | 2549.8338 | 0.057 |  | 10848.6768 | 0.014
| 251.2305 | 0.0271 |  | 2600.8305 | 0.0569 |  | 11065.6504 | 0.014
| 256.2551 | 0.0265 |  | 2652.8471 | 0.0568 |  | 11286.9634 | 0.014
| 261.3802 | 0.0258 |  | 2705.904 | 0.0567 |  | 11512.7026 | 0.014
| 266.6078 | 0.0252 |  | 2760.0221 | 0.0567 |  | 11742.9567 | 0.014
| 271.9399 | 0.0246 |  | 2815.2225 | 0.0566 |  | 11977.8158 | 0.014
| 277.3787 | 0.024 |  | 2871.527 | 0.0566 | 40T | 100.0824 | 685.6911
| 282.9263 | 0.0235 |  | 2928.9575 | 0.0565 |  | 102.084 | 221.7936
| 288.5848 | 0.023 |  | 2987.5367 | 0.0564 |  | 103.1 | 164.4732
| 294.3565 | 0.0225 |  | 3047.2874 | 0.0564 |  | 104.1257 | 130.1703
| 300.2436 | 0.022 |  | 3108.2332 | 0.0563 |  | 105.2 | 106.6405
| 306.2485 | 0.0215 |  | 3170.3978 | 0.0563 |  | 106.2082 | 91.0415
| 312.3735 | 0.0211 |  | 3233.8058 | 0.0562 |  | 107.3 | 78.4863
| 318.621 | 0.0206 |  | 3298.4819 | 0.0562 |  | 108.3324 | 69.3522
| 324.9934 | 0.0202 |  | 3364.4515 | 0.0561 |  | 109.4 | 61.8379
| 328.6274 | 0.016 |  | 3431.7406 | 0.0561 |  | 110.4991 | 55.5769
| 335.2 | 0.016 |  | 3500.3754 | 0.056 |  | 111.6 | 50.4128
| 341.904 | 0.016 |  | 3570.3829 | 0.056 |  | 112.709 | 46.0588
| 348.7421 | 0.016 |  | 3641.7905 | 0.056 |  | 113.8 | 42.4194
| 355.7169 | 0.016 |  | 3714.6264 | 0.0559 |  | 114.9632 | 39.0931
| 362.8313 | 0.016 |  | 3788.9189 | 0.0559 |  | 116.1 | 36.2846
| 370.0879 | 0.016 |  | 3864.6973 | 0.0559 |  | 117.2625 | 33.7783
| 377.4896 | 0.016 |  | 3941.9912 | 0.0558 |  | 118.4 | 31.6201
| 385.0394 | 0.016 |  | 4020.831 | 0.0558 |  | 119.6077 | 29.5926
| 392.7402 | 0.016 |  | 4101.2476 | 0.0558 |  | 121.9999 | 26.2132
| 400.595 | 0.016 |  | 4183.2726 | 0.0557 |  | 124.4399 | 23.4294
| 408.6069 | 0.016 |  | 4266.938 | 0.0557 |  | 126.9287 | 21.0983
| 416.7791 | 0.016 |  | 4352.2768 | 0.0557 |  | 129.4673 | 19.1192
| 425.1146 | 0.016 |  | 4439.3223 | 0.0556 |  | 132.0566 | 17.4192
| 433.6169 | 0.016 |  | 4528.1088 | 0.0556 |  | 134.6977 | 15.9443
| 442.2893 | 0.016 |  | 4618.671 | 0.0556 |  | 137.3917 | 14.6534
| 451.1351 | 0.016 |  | 4711.0444 | 0.0556 |  | 140.1395 | 13.5149
| 460.1578 | 0.016 |  | 4805.2653 | 0.0556 |  | 142.9423 | 12.5042
| 469.3609 | 0.016 |  | 4901.3706 | 0.0555 |  | 145.8012 | 11.6016
| 478.7481 | 0.016 |  | 4999.398 | 0.0555 |  | 148.7172 | 10.7911
| 488.3231 | 0.016 |  | 5099.386 | 0.0555 |  | 151.6915 | 10.06
| 498.0896 | 0.016 |  | 5201.3737 | 0.0555 |  | 154.7254 | 9.3975
| 508.0514 | 0.016 |  | 5305.4011 | 0.0555 |  | 157.8199 | 8.7949
| 518.2124 | 0.016 |  | 5411.5092 | 0.0554 |  | 160.9763 | 8.2449
| 528.5766 | 0.016 |  | 5519.7394 | 0.0554 |  | 164.1958 | 7.7413
| 539.1482 | 0.016 |  | 5630.1341 | 0.0554 |  | 167.4797 | 7.2786
| 549.9311 | 0.016 |  | 5742.7368 | 0.0554 |  | 170.8293 | 6.8526
| 560.9297 | 0.016 |  | 5857.5916 | 0.0554 |  | 174.2459 | 6.4592
| 572.1483 | 0.016 |  | 5974.7434 | 0.0554 |  | 177.7308 | 6.0952
| 583.5913 | 0.016 |  | 6094.2383 | 0.0553 |  | 181.2854 | 5.7576
| 595.2631 | 0.016 |  | 6216.123 | 0.0553 |  | 184.9111 | 5.4439
| 607.1684 | 0.016 |  | 6340.4455 | 0.0553 |  | 188.6093 | 5.1519
| 619.3118 | 0.016 |  | 6467.2544 | 0.0553 |  | 192.3815 | 4.8796
| 631.698 | 0.016 |  | 6596.5995 | 0.0553 |  | 196.2292 | 4.6252
| 644.332 | 0.016 |  | 6728.5315 | 0.0553 |  | 200.1537 | 4.3872
| 657.2186 | 0.016 |  | 6863.1021 | 0.0553 |  | 204.1568 | 4.1644
| 657.2549 | 0.016 |  | 7000.3641 | 0.0553 |  | 208.24 | 3.9553
| 670.4 | 0.014 |  | 7140.3714 | 0.0553 |  | 212.4048 | 3.7589
| 683.808 | 0.014 |  | 7283.1789 | 0.0552 |  | 216.6529 | 3.5744
| 697.4842 | 0.014 |  | 7428.8424 | 0.0552 |  | 220.9859 | 3.4006
| 711.4338 | 0.014 |  | 7577.4193 | 0.0552 |  | 225.4056 | 3.2369
| 725.6625 | 0.014 |  | 7728.9677 | 0.0552 |  | 229.9137 | 3.0825
| 740.1758 | 0.014 |  | 7883.547 | 0.0552 |  | 234.512 | 2.9368
| 754.9793 | 0.014 |  | 8041.218 | 0.0552 |  | 239.2023 | 2.7991
| 770.0789 | 0.014 |  | 8202.0423 | 0.0552 |  | 243.9863 | 2.669
| 785.4804 | 0.014 |  | 8366.0832 | 0.0552 |  | 248.866 | 2.5458
| 801.1901 | 0.014 |  | 8533.4048 | 0.0552 |  | 253.8433 | 2.4291
| 817.2139 | 0.014 |  | 8704.0729 | 0.0552 |  | 258.9202 | 2.3186
| 833.5581 | 0.014 |  | 8878.1544 | 0.0552 |  | 264.0986 | 2.2138
| 850.2293 | 0.014 |  | 9055.7175 | 0.0552 |  | 269.3806 | 2.1144
| 867.2339 | 0.014 |  | 9236.8318 | 0.0552 |  | 274.7682 | 2.02
| 884.5786 | 0.014 |  | 9421.5685 | 0.0551 |  | 280.2636 | 1.9304
| 902.2701 | 0.014 |  | 9609.9998 | 0.0551 |  | 285.8688 | 1.8452
| 920.3155 | 0.014 |  | 9802.1998 | 0.0551 |  | 291.5862 | 1.7642
| 938.7218 | 0.014 |  | 9998.2438 | 0.0551 |  | 297.4179 | 1.6871
| 957.4963 | 0.014 |  | 10198.2087 | 0.0551 |  | 303.3663 | 1.6138
| 976.6462 | 0.014 |  | 10402.1729 | 0.0551 |  | 309.4336 | 1.5439
| 996.1791 | 0.014 |  | 10610.2163 | 0.0551 |  | 315.6223 | 1.4774
| 1016.1027 | 0.014 |  | 10822.4207 | 0.0551 |  | 321.9347 | 1.414
| 1036.4248 | 0.014 |  | 11038.8691 | 0.0551 |  | 328.3734 | 1.3536
| 1057.1533 | 0.014 |  | 11259.6465 | 0.0551 |  | 334.9409 | 1.296
| 1078.2963 | 0.014 |  | 11484.8394 | 0.0551 |  | 341.6397 | 1.2411
| 1099.8623 | 0.014 |  | 11714.5362 | 0.0551 |  | 348.4725 | 1.1886
| 1121.8595 | 0.014 |  | 11948.8269 | 0.0551 |  | 355.442 | 1.1386
| 1144.2967 | 0.014 | Total Result |  | 1449.8189 |  | 362.5508 | 1.0908
| 1167.1826 | 0.014 |  |  |  |  | 369.8018 | 1.0452
| 1190.5263 | 0.014 |  |  |  |  | 377.1979 | 1.0016
| 1214.3368 | 0.014 |  |  |  |  | 384.7418 | 0.9599
| 1238.6235 | 0.014 |  |  |  |  | 392.4367 | 0.9201
| 1263.396 | 0.014 |  |  |  |  | 400.2854 | 0.882
| 1288.6639 | 0.014 |  |  |  |  | 408.2911 | 0.8456
| 1314.4372 | 0.014 |  |  |  |  | 416.4569 | 0.8108
| 1340.7259 | 0.014 |  |  |  |  | 424.7861 | 0.7775
| 1367.5405 | 0.014 |  |  |  |  | 433.2818 | 0.7457
| 1394.8913 | 0.014 |  |  |  |  | 441.9474 | 0.7152
| 1422.7891 | 0.014 |  |  |  |  | 450.7864 | 0.686
| 1451.2449 | 0.014 |  |  |  |  | 459.8021 | 0.6581
| 1480.2698 | 0.014 |  |  |  |  | 468.9981 | 0.6313
| 1509.8752 | 0.014 |  |  |  |  | 478.3781 | 0.6057
| 1540.0727 | 0.014 |  |  |  |  | 487.9457 | 0.5812
| 1570.8741 | 0.014 |  |  |  |  | 497.7046 | 0.5577
| 1602.2916 | 0.014 |  |  |  |  | 507.6587 | 0.5352
| 1634.3374 | 0.014 |  |  |  |  | 517.8118 | 0.5136
| 1667.0242 | 0.014 |  |  |  |  | 528.1681 | 0.4929
| 1700.3647 | 0.014 |  |  |  |  | 538.7314 | 0.4731
| 1734.372 | 0.014 |  |  |  |  | 549.5061 | 0.4541
| 1769.0594 | 0.014 |  |  |  |  | 560.4962 | 0.4359
| 1804.4406 | 0.014 |  |  |  |  | 571.7061 | 0.4185
| 1840.5294 | 0.014 |  |  |  |  | 583.1402 | 0.4017
| 1877.34 | 0.014 |  |  |  |  | 594.803 | 0.3857
| 1914.8868 | 0.014 |  |  |  |  | 606.6991 | 0.3703
| 1953.1845 | 0.014 |  |  |  |  | 618.8331 | 0.3555
| 1992.2482 | 0.014 |  |  |  |  | 631.2097 | 0.3414
| 2032.0932 | 0.014 |  |  |  |  | 643.8339 | 0.3278
| 2072.7351 | 0.014 |  |  |  |  | 656.7106 | 0.3148
| 2114.1898 | 0.014 |  |  |  |  | 669.8448 | 0.3023
| 2156.4736 | 0.014 |  |  |  |  | 683.2417 | 0.2903
| 2199.603 | 0.014 |  |  |  |  | 696.9065 | 0.2788
| 2243.5951 | 0.014 |  |  |  |  | 710.8447 | 0.2677
| 2288.467 | 0.014 |  |  |  |  | 725.0616 | 0.2572
| 2334.2363 | 0.014 |  |  |  |  | 739.5628 | 0.247
| 2380.9211 | 0.014 |  |  |  |  | 754.3541 | 0.2372
| 2428.5395 | 0.014 |  |  |  |  | 769.4411 | 0.2279
| 2477.1103 | 0.014 |  |  |  |  | 784.83 | 0.2189
| 2526.6525 | 0.014 |  |  |  |  | 800.5266 | 0.2102
| 2577.1855 | 0.014 |  |  |  |  | 816.5371 | 0.202
| 2628.7292 | 0.014 |  |  |  |  | 832.8678 | 0.194
| 2681.3038 | 0.014 |  |  |  |  | 849.5252 | 0.1864
| 2734.9299 | 0.014 |  |  |  |  | 866.5157 | 0.179
| 2789.6285 | 0.014 |  |  |  |  | 883.846 | 0.172
| 2845.4211 | 0.014 |  |  |  |  | 901.5229 | 0.1652
| 2902.3295 | 0.014 |  |  |  |  | 919.5534 | 0.1587
| 2960.3761 | 0.014 |  |  |  |  | 937.9445 | 0.1525
| 3019.5836 | 0.014 |  |  |  |  | 956.7033 | 0.1465
| 3079.9753 | 0.014 |  |  |  |  | 975.8374 | 0.1408
| 3141.5748 | 0.014 |  |  |  |  | 995.3542 | 0.1352
| 3204.4063 | 0.014 |  |  |  |  | 1015.2612 | 0.1299
| 3268.4944 | 0.014 |  |  |  |  | 1035.5665 | 0.1249
| 3333.8643 | 0.014 |  |  |  |  | 1056.2778 | 0.12
| 3400.5416 | 0.014 |  |  |  |  | 1077.4034 | 0.1153
| 3468.5524 | 0.014 |  |  |  |  | 1098.9514 | 0.1107
| 3537.9234 | 0.014 |  |  |  |  | 1120.9304 | 0.1064
| 3608.6819 | 0.014 |  |  |  |  | 1143.3491 | 0.1023
| 3680.8555 | 0.014 |  |  |  |  | 1166.216 | 0.0983
| 3754.4727 | 0.014 |  |  |  |  | 1189.5404 | 0.0944
| 3829.5621 | 0.014 |  |  |  |  | 1213.3312 | 0.0907
| 3906.1534 | 0.014 |  |  |  |  | 1237.5978 | 0.0872
| 3984.2764 | 0.014 |  |  |  |  | 1262.3497 | 0.0838
| 4063.9619 | 0.014 |  |  |  |  | 1287.5967 | 0.0805
| 4145.2412 | 0.014 |  |  |  |  | 1313.3487 | 0.0774
| 4228.146 | 0.014 |  |  |  |  | 1339.6156 | 0.0743
| 4312.7089 | 0.014 |  |  |  |  | 1366.408 | 0.0714
| 4398.9631 | 0.014 |  |  |  |  | 1393.7361 | 0.0686
| 4486.9424 | 0.014 |  |  |  |  | 1421.6108 | 0.066
| 4576.6812 | 0.014 |  |  |  |  | 1450.0431 | 0.0634
| 4668.2148 | 0.014 |  |  |  |  | 1479.0439 | 0.0609
| 4761.5791 | 0.014 |  |  |  |  | 1508.6248 | 0.0585
| 4856.8107 | 0.014 |  |  |  |  | 1538.7973 | 0.0563
| 4953.9469 | 0.014 |  |  |  |  | 1569.5732 | 0.0541
| 5053.0259 | 0.014 |  |  |  |  | 1600.9647 | 0.0521
| 5154.0864 | 0.014 |  |  |  |  | 1632.984 | 0.0504
| 5257.1681 | 0.014 |  |  |  |  | 1665.6437 | 0.0488
| 5362.3115 | 0.014 |  |  |  |  | 1698.9566 | 0.0473
| 5469.5577 | 0.014 |  |  |  |  | 1732.9357 | 0.0459
| 5578.9489 | 0.014 |  |  |  |  | 1767.5944 | 0.0445
| 5690.5278 | 0.014 |  |  |  |  | 1802.9463 | 0.0431
| 5804.3384 | 0.014 |  |  |  |  | 1839.0052 | 0.0418
| 5920.4252 | 0.014 |  |  |  |  | 1875.7853 | 0.0406
| 6038.8337 | 0.014 |  |  |  |  | 1913.301 | 0.0394
| 6159.6103 | 0.014 |  |  |  |  | 1951.567 | 0.0383
| 6282.8026 | 0.014 |  |  |  |  | 1990.5984 | 0.0372
| 6408.4586 | 0.014 |  |  |  |  | 2030.4104 | 0.0361
| 6536.6278 | 0.014 |  |  |  |  | 2071.0186 | 0.0351
| 6667.3603 | 0.014 |  |  |  |  | 2112.4389 | 0.0341
| 6800.7075 | 0.014 |  |  |  |  | 2154.6877 | 0.0332
| 6936.7217 | 0.014 |  |  |  |  | 2197.7815 | 0.0323
| 7075.4561 | 0.014 |  |  |  |  | 2241.7371 | 0.0314
| 7216.9652 | 0.014 |  |  |  |  | 2286.5718 | 0.0306
| 7361.3046 | 0.014 |  |  |  |  | 2332.3033 | 0.0298
| 7508.5306 | 0.014 |  |  |  |  | 2378.9493 | 0.029
| 7658.7013 | 0.014 |  |  |  |  | 2426.5283 | 0.0283
| 7811.8753 | 0.014 |  |  |  |  | 2475.0589 | 0.0276
| 7968.1128 | 0.014 |  |  |  |  | 2524.5601 | 0.0269
| 8127.475 | 0.014 |  |  |  |  | 2575.0513 | 0.0262
| 8290.0245 | 0.014 |  |  |  |  | 2626.5523 | 0.0256
| 8455.825 | 0.014 |  |  |  |  | 2679.0833 | 0.025
| 8624.9415 | 0.014 |  |  |  |  | 2732.665 | 0.0244
| 8797.4404 | 0.014 |  |  |  |  | 2787.3183 | 0.0238
| 8973.3892 | 0.014 |  |  |  |  | 2843.0647 | 0.0233
| 9152.857 | 0.014 |  |  |  |  | 2899.926 | 0.0228
| 9335.9141 | 0.014 |  |  |  |  | 2957.9245 | 0.0223
| 9522.6324 | 0.014 |  |  |  |  | 3017.083 | 0.0218
| 9713.085 | 0.014 |  |  |  |  | 3077.4246 | 0.0214
| 9907.3467 | 0.014 |  |  |  |  | 3138.9731 | 0.0209
| 10105.4937 | 0.014 |  |  |  |  | 3201.7526 | 0.0205
| 10307.6035 | 0.014 |  |  |  |  | 3265.7876 | 0.0201
| 10513.7556 | 0.014 |  |  |  |  | 3279.2861 | 0.016
| 10724.0307 | 0.014 |  |  |  |  | 3344.8718 | 0.016
| 10938.5113 | 0.014 |  |  |  |  | 3411.7692 | 0.016
| 11157.2816 | 0.014 |  |  |  |  | 3480.0046 | 0.016
| 11380.4272 | 0.014 |  |  |  |  | 3549.6047 | 0.016
| 11608.0357 | 0.014 |  |  |  |  | 3620.5968 | 0.016
| 11840.1964 | 0.014 |  |  |  |  | 3693.0088 | 0.016
80E | 178.7951 | 479.1934 |  |  |  |  | 3766.8689 | 0.016
| 180.0513 | 213.6696 |  |  |  |  | 3842.2063 | 0.016
| 181.3163 | 136.8004 |  |  |  |  | 3919.0504 | 0.016
| 182 | 114.4306 |  |  |  |  | 3997.4314 | 0.016
| 182.7727 | 96.5212 |  |  |  |  | 4077.3801 | 0.016
| 183.8 | 79.8287 |  |  |  |  | 4158.9277 | 0.016
| 184.7934 | 68.3374 |  |  |  |  | 4242.1062 | 0.016
| 186.1 | 57.4014 |  |  |  |  | 4326.9483 | 0.016
| 187.3993 | 49.4732 |  |  |  |  | 4413.4873 | 0.016
| 188.6 | 43.8402 |  |  |  |  | 4501.7571 | 0.016
| 189.8512 | 39.1631 |  |  |  |  | 4591.7922 | 0.016
| 191.3 | 34.8299 |  |  |  |  | 4683.628 | 0.016
| 192.72 | 31.3991 |  |  |  |  | 4777.3006 | 0.016
| 194.3 | 28.2758 |  |  |  |  | 4872.8466 | 0.016
| 195.8286 | 25.7755 |  |  |  |  | 4970.3036 | 0.016
| 197.5 | 23.486 |  |  |  |  | 5069.7096 | 0.016
| 199.1869 | 21.5386 |  |  |  |  | 5171.1038 | 0.016
| 201 | 19.7619 |  |  |  |  | 5274.5259 | 0.016
| 202.8037 | 18.2507 |  |  |  |  | 5380.0164 | 0.016
| 204.6 | 16.9485 |  |  |  |  | 5487.6167 | 0.016
| 206.4876 | 15.7564 |  |  |  |  | 5597.3691 | 0.016
| 208.7 | 14.5453 |  |  |  |  | 5709.3165 | 0.016
| 210.87 | 13.5156 |  |  |  |  | 5823.5028 | 0.016
| 213.2 | 12.5513 |  |  |  |  | 5939.9728 | 0.016
| 215.5604 | 11.6966 |  |  |  |  | 6058.7723 | 0.016
| 219.9153 | 10.3729 |  |  |  |  | 6179.9477 | 0.016
| 224.1338 | 9.33 |  |  |  |  | 6303.5467 | 0.016
| 228.4326 | 8.4478 |  |  |  |  | 6429.6176 | 0.016
| 232.8139 | 7.6924 |  |  |  |  | 6558.21 | 0.016
| 237.2799 | 7.0384 |  |  |  |  | 6558.5722 | 0.016
| 243.287 | 6.3018 |  |  |  |  | 6689.7436 | 0.014
| 248.4504 | 5.7706 |  |  |  |  | 6823.5385 | 0.014
| 252.9626 | 5.3675 |  |  |  |  | 6960.0093 | 0.014
| 257.8147 | 4.9859 |  |  |  |  | 7099.2094 | 0.014
| 264.077 | 4.5586 |  |  |  |  | 7241.1936 | 0.014
| 268.6046 | 4.2874 |  |  |  |  | 7386.0175 | 0.014
| 277.6169 | 3.8232 |  |  |  |  | 7533.7379 | 0.014
| 284.3599 | 3.5291 |  |  |  |  | 7684.4126 | 0.014
| 295.9649 | 3.1046 |  |  |  |  | 7838.1009 | 0.014
| 304.9783 | 2.8307 |  |  |  |  | 7994.8629 | 0.014
| 318.3785 | 2.4918 |  |  |  |  | 8154.7601 | 0.014
| 330.7095 | 2.2353 |  |  |  |  | 8317.8553 | 0.014
| 342.1473 | 2.034 |  |  |  |  | 8484.2124 | 0.014
| 354.6895 | 1.8453 |  |  |  |  | 8653.8967 | 0.014
| 367.323 | 1.6824 |  |  |  |  | 8826.9746 | 0.014
| 382.3138 | 1.5174 |  |  |  |  | 9003.5141 | 0.014
| 395.1409 | 1.3959 |  |  |  |  | 9183.5844 | 0.014
| 407.99 | 1.289 |  |  |  |  | 9367.2561 | 0.014
| 424.215 | 1.1717 |  |  |  |  | 9554.6012 | 0.014
| 439.3257 | 1.077 |  |  |  |  | 9745.6932 | 0.014
| 461.3884 | 0.9589 |  |  |  |  | 9940.6071 | 0.014
| 490.4097 | 0.8321 |  |  |  |  | 10139.4192 | 0.014
| 521.2559 | 0.724 |  |  |  |  | 10342.2076 | 0.014
| 551.8304 | 0.6369 |  |  |  |  | 10549.0518 | 0.014
| 587.7146 | 0.5539 |  |  |  |  | 10760.0328 | 0.014
| 616.6127 | 0.4986 |  |  |  |  | 10975.2335 | 0.014
| 650.1748 | 0.4444 |  |  |  |  | 11194.7381 | 0.014
| 686.2493 | 0.3957 |  |  |  |  | 11418.6329 | 0.014
| 727.9569 | 0.3488 |  |  |  |  | 11647.0056 | 0.014
| 795.7147 | 0.289 |  |  |  |  | 11879.9457 | 0.014
| 886.4647 | 0.2305 |  |  |  | 50T | 127.1226 | 675.7704
| 977.7372 | 0.1881 |  |  |  |  | 129.6651 | 218.5846
| 1097.9947 | 0.1481 |  |  |  |  | 131 | 160.6542
| 1212.255 | 0.1209 |  |  |  |  | 132.2584 | 128.2869
| 1315.853 | 0.1023 |  |  |  |  | 133.6 | 105.4186
| 1425.446 | 0.0869 |  |  |  |  | 134.9035 | 89.7243
| 1565.938 | 0.0718 |  |  |  |  | 136.3 | 77.2754
| 1671.098 | 0.063 |  |  |  |  | 137.6016 | 68.3488
| 1795.86 | 0.0544 |  |  |  |  | 139 | 60.7365
| 1964.985 | 0.0467 |  |  |  |  | 140.3536 | 54.7728
| 2137.168 | 0.041 |  |  |  |  | 141.8 | 49.5247
| 2385 | 0.0349 |  |  |  |  | 143.1607 | 45.3924
| 2542.56 | 0.0319 |  |  |  |  | 144.6 | 41.6777
| 2787.58 | 0.0282 |  |  |  |  | 146.0239 | 38.5275
| 3025.79 | 0.0254 |  |  |  |  | 147.5 | 35.7022
| 3258.19 | 0.0233 |  |  |  |  | 148.9444 | 33.2896
| 3543.71 | 0.0212 |  |  |  |  | 150.4 | 31.1477
| 3800.65 | 0.016 |  |  |  |  | 151.9233 | 29.1645
| 3916.4 | 0.016 |  |  |  |  | 154.9617 | 25.8339
| 3967.65 | 0.016 |  |  |  |  | 158.061 | 23.0904
| 4164.4581 | 0.016 |  |  |  |  | 161.2222 | 20.7931
| 4685.0154 | 0.016 |  |  |  |  | 164.4466 | 18.8426
| 5205.5727 | 0.016 |  |  |  |  | 167.7356 | 17.1672
| 5830.2414 | 0.016 |  |  |  |  | 171.0903 | 15.7136
| 7935.375 | 0.014 |  |  |  |  | 174.5121 | 14.4414
Total Result |  | 1662.8744 |  |  |  |  | 178.0023 | 13.3194
[7 empty] | 181.5624 | 12.3233
[7 empty] | 185.1936 | 11.4337
[7 empty] | 188.8975 | 10.635
[7 empty] | 192.6754 | 9.9144
[7 empty] | 196.529 | 9.2615
[7 empty] | 200.4595 | 8.6677
[7 empty] | 204.4687 | 8.1256
[7 empty] | 208.5581 | 7.6292
[7 empty] | 212.7293 | 7.1733
[7 empty] | 216.9838 | 6.7534
[7 empty] | 221.3235 | 6.3658
[7 empty] | 225.75 | 6.007
[7 empty] | 230.265 | 5.6743
[7 empty] | 234.8703 | 5.3652
[7 empty] | 239.5677 | 5.0774
[7 empty] | 244.3591 | 4.809
[7 empty] | 249.2462 | 4.5583
[7 empty] | 254.2312 | 4.3238
[7 empty] | 259.3158 | 4.1041
[7 empty] | 264.5021 | 3.8981
[7 empty] | 269.7921 | 3.7046
[7 empty] | 275.188 | 3.5226
[7 empty] | 280.6917 | 3.3514
[7 empty] | 286.3056 | 3.1901
[7 empty] | 292.0317 | 3.0379
[7 empty] | 297.8723 | 2.8943
[7 empty] | 303.8298 | 2.7586
[7 empty] | 309.9064 | 2.6303
[7 empty] | 316.1045 | 2.5089
[7 empty] | 322.4266 | 2.394
[7 empty] | 328.8751 | 2.2851
[7 empty] | 335.4526 | 2.1818
[7 empty] | 342.1617 | 2.0838
[7 empty] | 349.0049 | 1.9908
[7 empty] | 355.985 | 1.9024
[7 empty] | 363.1047 | 1.8185
[7 empty] | 370.3668 | 1.7386
[7 empty] | 377.7741 | 1.6627
[7 empty] | 385.3296 | 1.5904
[7 empty] | 393.0362 | 1.5216
[7 empty] | 400.8969 | 1.456
[7 empty] | 408.9149 | 1.3936
[7 empty] | 417.0932 | 1.334
[7 empty] | 425.435 | 1.2773
[7 empty] | 433.9437 | 1.2231
[7 empty] | 442.6226 | 1.1714
[7 empty] | 451.4751 | 1.1221
[7 empty] | 460.5046 | 1.075
[7 empty] | 469.7146 | 1.03
[7 empty] | 479.1089 | 0.9871
[7 empty] | 488.6911 | 0.946
[7 empty] | 498.4649 | 0.9068
[7 empty] | 508.4342 | 0.8693
[7 empty] | 518.6029 | 0.8334
[7 empty] | 528.975 | 0.7991
[7 empty] | 539.5545 | 0.7663
[7 empty] | 550.3456 | 0.7349
[7 empty] | 561.3525 | 0.7048
[7 empty] | 572.5795 | 0.6761
[7 empty] | 584.0311 | 0.6485
[7 empty] | 595.7117 | 0.6222
[7 empty] | 607.626 | 0.5969
[7 empty] | 619.7785 | 0.5728
[7 empty] | 632.1741 | 0.5496
[7 empty] | 644.8176 | 0.5274
[7 empty] | 657.7139 | 0.5062
[7 empty] | 670.8682 | 0.4858
[7 empty] | 684.2855 | 0.4663
[7 empty] | 697.9713 | 0.4475
[7 empty] | 711.9307 | 0.4296
[7 empty] | 726.1693 | 0.4124
[7 empty] | 740.6927 | 0.3959
[7 empty] | 755.5065 | 0.3801
[7 empty] | 770.6167 | 0.3649
[7 empty] | 786.029 | 0.3504
[7 empty] | 801.7496 | 0.3364
[7 empty] | 817.7846 | 0.3231
[7 empty] | 834.1403 | 0.3102
[7 empty] | 850.8231 | 0.2979
[7 empty] | 867.8395 | 0.2861
[7 empty] | 885.1963 | 0.2748
[7 empty] | 902.9002 | 0.2639
[7 empty] | 920.9583 | 0.2534
[7 empty] | 939.3774 | 0.2434
[7 empty] | 958.165 | 0.2338
[7 empty] | 977.3283 | 0.2246
[7 empty] | 996.8748 | 0.2157
[7 empty] | 1016.8123 | 0.2072
[7 empty] | 1037.1486 | 0.199
[7 empty] | 1057.8915 | 0.1912
[7 empty] | 1079.0494 | 0.1837
[7 empty] | 1100.6304 | 0.1764
[7 empty] | 1122.643 | 0.1695
[7 empty] | 1145.0958 | 0.1628
[7 empty] | 1167.9977 | 0.1564
[7 empty] | 1191.3577 | 0.1503
[7 empty] | 1215.1849 | 0.1444
[7 empty] | 1239.4886 | 0.1387
[7 empty] | 1264.2783 | 0.1333
[7 empty] | 1289.5639 | 0.1281
[7 empty] | 1315.3552 | 0.123
[7 empty] | 1341.6623 | 0.1182
[7 empty] | 1368.4955 | 0.1136
[7 empty] | 1395.8654 | 0.1091
[7 empty] | 1423.7827 | 0.1049
[7 empty] | 1452.2584 | 0.1008
[7 empty] | 1481.3036 | 0.0968
[7 empty] | 1510.9296 | 0.093
[7 empty] | 1541.1482 | 0.0894
[7 empty] | 1571.9712 | 0.0859
[7 empty] | 1603.4106 | 0.0826
[7 empty] | 1635.4788 | 0.0793
[7 empty] | 1668.1884 | 0.0762
[7 empty] | 1701.5522 | 0.0733
[7 empty] | 1735.5832 | 0.0704
[7 empty] | 1770.2949 | 0.0676
[7 empty] | 1805.7008 | 0.065
[7 empty] | 1841.8148 | 0.0625
[7 empty] | 1878.6511 | 0.06
[7 empty] | 1916.2241 | 0.0577
[7 empty] | 1954.5486 | 0.0554
[7 empty] | 1993.6396 | 0.0533
[7 empty] | 2033.5123 | 0.0514
[7 empty] | 2074.1826 | 0.0498
[7 empty] | 2115.6662 | 0.0483
[7 empty] | 2157.9796 | 0.0468
[7 empty] | 2201.1392 | 0.0454
[7 empty] | 2245.1619 | 0.044
[7 empty] | 2290.0652 | 0.0427
[7 empty] | 2335.8665 | 0.0414
[7 empty] | 2382.5838 | 0.0402
[7 empty] | 2430.2355 | 0.039
[7 empty] | 2478.8402 | 0.0379
[7 empty] | 2528.417 | 0.0368
[7 empty] | 2578.9853 | 0.0357
[7 empty] | 2630.5651 | 0.0347
[7 empty] | 2683.1764 | 0.0338
[7 empty] | 2736.8399 | 0.0328
[7 empty] | 2791.5767 | 0.032
[7 empty] | 2847.4082 | 0.0311
[7 empty] | 2904.3564 | 0.0303
[7 empty] | 2962.4435 | 0.0295
[7 empty] | 3021.6924 | 0.0287
[7 empty] | 3082.1262 | 0.028
[7 empty] | 3143.7687 | 0.0273
[7 empty] | 3206.6441 | 0.0266
[7 empty] | 3270.777 | 0.026
[7 empty] | 3336.1925 | 0.0254
[7 empty] | 3402.9164 | 0.0248
[7 empty] | 3470.9747 | 0.0242
[7 empty] | 3540.3942 | 0.0236
[7 empty] | 3611.2021 | 0.0231
[7 empty] | 3683.4261 | 0.0226
[7 empty] | 3757.0947 | 0.0221
[7 empty] | 3832.2366 | 0.0216
[7 empty] | 3908.8813 | 0.0212
[7 empty] | 3987.0589 | 0.0208
[7 empty] | 4066.8001 | 0.0203
[7 empty] | 4135.062 | 0.02
[7 empty] | 4217.7632 | 0.016
[7 empty] | 4302.1185 | 0.016
[7 empty] | 4388.1608 | 0.016
[7 empty] | 4475.9241 | 0.016
[7 empty] | 4565.4425 | 0.016
[7 empty] | 4656.7514 | 0.016
[7 empty] | 4749.8864 | 0.016
[7 empty] | 4844.8841 | 0.016
[7 empty] | 4941.7818 | 0.016
[7 empty] | 5040.6175 | 0.016
[7 empty] | 5141.4298 | 0.016
[7 empty] | 5244.2584 | 0.016
[7 empty] | 5349.1436 | 0.016
[7 empty] | 5456.1265 | 0.016
[7 empty] | 5565.249 | 0.016
[7 empty] | 5676.554 | 0.016
[7 empty] | 5790.085 | 0.016
[7 empty] | 5905.8867 | 0.016
[7 empty] | 6024.0045 | 0.016
[7 empty] | 6144.4846 | 0.016
[7 empty] | 6267.3743 | 0.016
[7 empty] | 6392.7217 | 0.016
[7 empty] | 6520.5762 | 0.016
[7 empty] | 6650.9877 | 0.016
[7 empty] | 6784.0075 | 0.016
[7 empty] | 6919.6876 | 0.016
[7 empty] | 7058.0814 | 0.016
[7 empty] | 7199.243 | 0.016
[7 empty] | 7343.2278 | 0.016
[7 empty] | 7490.0924 | 0.016
[7 empty] | 7639.8942 | 0.016
[7 empty] | 7792.6921 | 0.016
[7 empty] | 7948.546 | 0.016
[7 empty] | 8107.5169 | 0.016
[7 empty] | 8269.6672 | 0.016
[7 empty] | 8270.1239 | 0.016
[7 empty] | 8435.5264 | 0.014
[7 empty] | 8604.2369 | 0.014
[7 empty] | 8776.3217 | 0.014
[7 empty] | 8951.8481 | 0.014
[7 empty] | 9130.8851 | 0.014
[7 empty] | 9313.5028 | 0.014
[7 empty] | 9499.7728 | 0.014
[7 empty] | 9689.7683 | 0.014
[7 empty] | 9883.5637 | 0.014
[7 empty] | 10081.2349 | 0.014
[7 empty] | 10282.8596 | 0.014
[7 empty] | 10488.5168 | 0.014
[7 empty] | 10698.2872 | 0.014
[7 empty] | 10912.2529 | 0.014
[7 empty] | 11130.498 | 0.014
[7 empty] | 11353.1079 | 0.014
[7 empty] | 11580.1701 | 0.014
[7 empty] | 11811.7735 | 0.014
[6 empty] | 65T | 160.1094 | 676.2171
[7 empty] | 163.3116 | 218.7291
[7 empty] | 164.9 | 163.1623
[7 empty] | 166.5778 | 128.3718
[7 empty] | 168.2 | 106.2497
[7 empty] | 169.9094 | 89.7836
[7 empty] | 171.6 | 77.747
[7 empty] | 173.3076 | 68.394
[7 empty] | 175 | 61.0437
[7 empty] | 176.7737 | 54.809
[7 empty] | 178.5 | 49.8086
[7 empty] | 180.3092 | 45.4224
[7 empty] | 182.1 | 41.7469
[7 empty] | 183.9154 | 38.553
[7 empty] | 185.8 | 35.6897
[7 empty] | 187.5937 | 33.3116
[7 empty] | 189.5 | 31.0883
[7 empty] | 191.3456 | 29.1838
[7 empty] | 195.1725 | 25.851
[7 empty] | 199.0759 | 23.1057
[7 empty] | 203.0574 | 20.8068
[7 empty] | 207.1186 | 18.8551
[7 empty] | 211.261 | 17.1786
[7 empty] | 215.4862 | 15.724
[7 empty] | 219.7959 | 14.4509
[7 empty] | 224.1918 | 13.3282
[7 empty] | 228.6756 | 12.3315
[7 empty] | 233.2492 | 11.4413
[7 empty] | 237.9141 | 10.642
[7 empty] | 242.6724 | 9.921
[7 empty] | 247.5259 | 9.2677
[7 empty] | 252.4764 | 8.6734
[7 empty] | 257.5259 | 8.131
[7 empty] | 262.6764 | 7.6343
[7 empty] | 267.93 | 7.1781
[7 empty] | 273.2886 | 6.7579
[7 empty] | 278.7543 | 6.37
[7 empty] | 284.3294 | 6.011
[7 empty] | 290.016 | 5.6781
[7 empty] | 295.8163 | 5.3687
[7 empty] | 301.7327 | 5.0807
[7 empty] | 307.7673 | 4.8121
[7 empty] | 313.9227 | 4.5613
[7 empty] | 320.2011 | 4.3266
[7 empty] | 326.6051 | 4.1068
[7 empty] | 333.1372 | 3.9006
[7 empty] | 339.8 | 3.707
[7 empty] | 346.596 | 3.525
[7 empty] | 353.5279 | 3.3536
[7 empty] | 360.5985 | 3.1922
[7 empty] | 367.8104 | 3.0399
[7 empty] | 375.1666 | 2.8962
[7 empty] | 382.67 | 2.7605
[7 empty] | 390.3234 | 2.6321
[7 empty] | 398.1298 | 2.5106
[7 empty] | 406.0924 | 2.3956
[7 empty] | 414.2143 | 2.2866
[7 empty] | 422.4986 | 2.1832
[7 empty] | 430.9485 | 2.0852
[7 empty] | 439.5675 | 1.9921
[7 empty] | 448.3589 | 1.9037
[7 empty] | 457.326 | 1.8197
[7 empty] | 466.4726 | 1.7398
[7 empty] | 475.802 | 1.6638
[7 empty] | 485.3181 | 1.5915
[7 empty] | 495.0244 | 1.5226
[7 empty] | 504.9249 | 1.457
[7 empty] | 515.0234 | 1.3945
[7 empty] | 525.3239 | 1.3349
[7 empty] | 535.8303 | 1.2781
[7 empty] | 546.547 | 1.2239
[7 empty] | 557.4779 | 1.1722
[7 empty] | 568.6275 | 1.1229
[7 empty] | 580 | 1.0757
[7 empty] | 591.6 | 1.0307
[7 empty] | 603.432 | 0.9877
[7 empty] | 615.5006 | 0.9467
[7 empty] | 627.8107 | 0.9074
[7 empty] | 640.3669 | 0.8699
[7 empty] | 653.1742 | 0.834
[7 empty] | 666.2377 | 0.7996
[7 empty] | 679.5624 | 0.7668
[7 empty] | 693.1537 | 0.7354
[7 empty] | 707.0168 | 0.7053
[7 empty] | 721.1571 | 0.6765
[7 empty] | 735.5802 | 0.649
[7 empty] | 750.2918 | 0.6226
[7 empty] | 765.2977 | 0.5973
[7 empty] | 780.6036 | 0.5731
[7 empty] | 796.2157 | 0.55
[7 empty] | 812.14 | 0.5278
[7 empty] | 828.3828 | 0.5065
[7 empty] | 844.9505 | 0.4861
[7 empty] | 861.8495 | 0.4666
[7 empty] | 879.0865 | 0.4478
[7 empty] | 896.6682 | 0.4299
[7 empty] | 914.6016 | 0.4127
[7 empty] | 932.8936 | 0.3962
[7 empty] | 951.5515 | 0.3804
[7 empty] | 970.5825 | 0.3652
[7 empty] | 989.9942 | 0.3506
[7 empty] | 1009.794 | 0.3367
[7 empty] | 1029.9899 | 0.3233
[7 empty] | 1050.5897 | 0.3104
[7 empty] | 1071.6015 | 0.2981
[7 empty] | 1093.0335 | 0.2863
[7 empty] | 1114.8942 | 0.2749
[7 empty] | 1137.1921 | 0.264
[7 empty] | 1159.9359 | 0.2536
[7 empty] | 1183.1347 | 0.2436
[7 empty] | 1206.7974 | 0.2339
[7 empty] | 1230.9333 | 0.2247
[7 empty] | 1255.552 | 0.2158
[7 empty] | 1280.663 | 0.2073
[7 empty] | 1306.2763 | 0.1992
[7 empty] | 1332.4018 | 0.1913
[7 empty] | 1359.0498 | 0.1838
[7 empty] | 1386.2308 | 0.1766
[7 empty] | 1413.9554 | 0.1696
[7 empty] | 1442.2346 | 0.1629
[7 empty] | 1471.0792 | 0.1565
[7 empty] | 1500.5008 | 0.1504
[7 empty] | 1530.5108 | 0.1445
[7 empty] | 1561.1211 | 0.1388
[7 empty] | 1592.3435 | 0.1334
[7 empty] | 1624.1904 | 0.1281
[7 empty] | 1656.6742 | 0.1231
[7 empty] | 1689.8076 | 0.1183
[7 empty] | 1723.6038 | 0.1137
[7 empty] | 1758.0759 | 0.1092
[7 empty] | 1793.2374 | 0.1049
[7 empty] | 1829.1021 | 0.1008
[7 empty] | 1865.6842 | 0.0969
[7 empty] | 1902.9979 | 0.0931
[7 empty] | 1941.0578 | 0.0895
[7 empty] | 1979.879 | 0.086
[7 empty] | 2019.4766 | 0.0826
[7 empty] | 2059.8661 | 0.0794
[7 empty] | 2101.0634 | 0.0763
[7 empty] | 2143.0847 | 0.0733
[7 empty] | 2185.9464 | 0.0704
[7 empty] | 2229.6653 | 0.0677
[7 empty] | 2274.2586 | 0.0651
[7 empty] | 2319.7438 | 0.0625
[7 empty] | 2366.1386 | 0.0601
[7 empty] | 2413.4614 | 0.0577
[7 empty] | 2461.7307 | 0.0555
[7 empty] | 2510.9653 | 0.0533
[7 empty] | 2561.1846 | 0.0515
[7 empty] | 2612.4083 | 0.0499
[7 empty] | 2664.6564 | 0.0483
[7 empty] | 2717.9496 | 0.0468
[7 empty] | 2772.3085 | 0.0454
[7 empty] | 2827.7547 | 0.044
[7 empty] | 2884.3098 | 0.0427
[7 empty] | 2941.996 | 0.0414
[7 empty] | 3000.8359 | 0.0402
[7 empty] | 3060.8526 | 0.039
[7 empty] | 3122.0697 | 0.0379
[7 empty] | 3184.5111 | 0.0368
[7 empty] | 3248.2013 | 0.0358
[7 empty] | 3313.1653 | 0.0348
[7 empty] | 3379.4286 | 0.0338
[7 empty] | 3447.0172 | 0.0329
[7 empty] | 3515.9576 | 0.032
[7 empty] | 3586.2767 | 0.0311
[7 empty] | 3658.0023 | 0.0303
[7 empty] | 3731.1623 | 0.0295
[7 empty] | 3805.7855 | 0.0288
[7 empty] | 3881.9013 | 0.028
[7 empty] | 3959.5393 | 0.0273
[7 empty] | 4038.7301 | 0.0266
[7 empty] | 4119.5047 | 0.026
[7 empty] | 4201.8948 | 0.0254
[7 empty] | 4285.9327 | 0.0248
[7 empty] | 4371.6513 | 0.0242
[7 empty] | 4459.0843 | 0.0237
[7 empty] | 4548.266 | 0.0231
[7 empty] | 4639.2313 | 0.0226
[7 empty] | 4732.016 | 0.0221
[7 empty] | 4826.6563 | 0.0217
[7 empty] | 4923.1894 | 0.0212
[7 empty] | 5021.6532 | 0.0208
[7 empty] | 5122.0863 | 0.0203
[7 empty] | 5209.7814 | 0.016
[7 empty] | 5313.977 | 0.016
[7 empty] | 5420.2565 | 0.016
[7 empty] | 5528.6617 | 0.016
[7 empty] | 5639.2349 | 0.016
[7 empty] | 5752.0196 | 0.016
[7 empty] | 5867.06 | 0.016
[7 empty] | 5984.4012 | 0.016
[7 empty] | 6104.0892 | 0.016
[7 empty] | 6226.171 | 0.016
[7 empty] | 6350.6944 | 0.016
[7 empty] | 6477.7083 | 0.016
[7 empty] | 6607.2625 | 0.016
[7 empty] | 6739.4077 | 0.016
[7 empty] | 6874.1959 | 0.016
[7 empty] | 7011.6798 | 0.016
[7 empty] | 7151.9134 | 0.016
[7 empty] | 7294.9517 | 0.016
[7 empty] | 7440.8507 | 0.016
[7 empty] | 7589.6677 | 0.016
[7 empty] | 7741.4611 | 0.016
[7 empty] | 7896.2903 | 0.016
[7 empty] | 8054.2161 | 0.016
[7 empty] | 8215.3004 | 0.016
[7 empty] | 8379.6064 | 0.016
[7 empty] | 8547.1986 | 0.016
[7 empty] | 8718.1425 | 0.016
[7 empty] | 8892.5054 | 0.016
[7 empty] | 9070.3555 | 0.016
[7 empty] | 9251.7626 | 0.016
[7 empty] | 9436.7978 | 0.016
[7 empty] | 9625.5338 | 0.016
[7 empty] | 9818.0445 | 0.016
[7 empty] | 10014.4054 | 0.016
[7 empty] | 10214.6935 | 0.016
[7 empty] | 10418.9873 | 0.016
[7 empty] | 10419.5627 | 0.014
[7 empty] | 10627.954 | 0.014
[7 empty] | 10840.5131 | 0.014
[7 empty] | 11057.3234 | 0.014
[7 empty] | 11278.4698 | 0.014
[7 empty] | 11504.0392 | 0.014
[7 empty] | 11734.12 | 0.014
[7 empty] | 11968.8024 | 0.014
[6 empty] | 80T | 197.9208 | 695.8708
[7 empty] | 201.8792 | 225.0863
[7 empty] | 203.9 | 166.6638
[7 empty] | 205.9168 | 132.1028
[7 empty] | 208 | 108.6068
[7 empty] | 210.0351 | 92.3931
[7 empty] | 212.1 | 80.1359
[7 empty] | 214.2358 | 70.3818
[7 empty] | 216.4 | 62.5851
[7 empty] | 218.5206 | 56.402
[7 empty] | 220.7 | 51.1563
[7 empty] | 222.891 | 46.7425
[7 empty] | 225.1 | 42.9676
[7 empty] | 227.3488 | 39.6735
[7 empty] | 229.6 | 36.8196
[7 empty] | 231.8958 | 34.2798
[7 empty] | 234.2 | 32.0395
[7 empty] | 236.5337 | 30.032
[7 empty] | 241.2644 | 26.6023
[7 empty] | 246.0896 | 23.7772
[7 empty] | 251.0114 | 21.4116
[7 empty] | 256.0317 | 19.4031
[7 empty] | 261.1523 | 17.6778
[7 empty] | 266.3753 | 16.181
[7 empty] | 271.7028 | 14.8709
[7 empty] | 277.1369 | 13.7156
[7 empty] | 282.6796 | 12.6899
[7 empty] | 288.3332 | 11.7738
[7 empty] | 294.0999 | 10.9513
[7 empty] | 299.9819 | 10.2093
[7 empty] | 305.9815 | 9.537
[7 empty] | 312.1012 | 8.9255
[7 empty] | 318.3432 | 8.3673
[7 empty] | 324.7101 | 7.8562
[7 empty] | 331.2043 | 7.3867
[7 empty] | 337.8283 | 6.9543
[7 empty] | 344.5849 | 6.5551
[7 empty] | 351.4766 | 6.1857
[7 empty] | 358.5061 | 5.8431
[7 empty] | 365.6763 | 5.5247
[7 empty] | 372.9898 | 5.2284
[7 empty] | 380.4496 | 4.952
[7 empty] | 388.0586 | 4.6939
[7 empty] | 395.8197 | 4.4524
[7 empty] | 403.7361 | 4.2262
[7 empty] | 411.8109 | 4.014
[7 empty] | 420.0471 | 3.8148
[7 empty] | 428.448 | 3.6274
[7 empty] | 437.017 | 3.4511
[7 empty] | 445.7573 | 3.285
[7 empty] | 454.6725 | 3.1283
[7 empty] | 463.7659 | 2.9804
[7 empty] | 473.0412 | 2.8407
[7 empty] | 482.5021 | 2.7086
[7 empty] | 492.1521 | 2.5836
[7 empty] | 501.9951 | 2.4652
[7 empty] | 512.035 | 2.353
[7 empty] | 522.2757 | 2.2467
[7 empty] | 532.7213 | 2.1458
[7 empty] | 543.3757 | 2.05
[7 empty] | 554.2432 | 1.959
[7 empty] | 565.3281 | 1.8726
[7 empty] | 576.6346 | 1.7903
[7 empty] | 588.1673 | 1.7121
[7 empty] | 599.9307 | 1.6377
[7 empty] | 611.9293 | 1.5668
[7 empty] | 624.1679 | 1.4993
[7 empty] | 636.6512 | 1.435
[7 empty] | 649.3842 | 1.3737
[7 empty] | 662.3719 | 1.3153
[7 empty] | 675.6194 | 1.2595
[7 empty] | 689.1317 | 1.2063
[7 empty] | 702.9144 | 1.1555
[7 empty] | 716.9727 | 1.107
[7 empty] | 731.3121 | 1.0607
[7 empty] | 745.9384 | 1.0164
[7 empty] | 760.8571 | 0.9742
[7 empty] | 776.0743 | 0.9338
[7 empty] | 791.5958 | 0.8951
[7 empty] | 807.4277 | 0.8582
[7 empty] | 823.5762 | 0.8229
[7 empty] | 840.0478 | 0.7891
[7 empty] | 856.8487 | 0.7567
[7 empty] | 873.9857 | 0.7258
[7 empty] | 891.4654 | 0.6962
[7 empty] | 909.2947 | 0.6678
[7 empty] | 927.4806 | 0.6407
[7 empty] | 946.0302 | 0.6147
[7 empty] | 964.9508 | 0.5898
[7 empty] | 984.2498 | 0.566
[7 empty] | 1003.9348 | 0.5431
[7 empty] | 1024.0135 | 0.5212
[7 empty] | 1044.4938 | 0.5002
[7 empty] | 1065.3837 | 0.4801
[7 empty] | 1086.6913 | 0.4609
[7 empty] | 1108.4252 | 0.4424
[7 empty] | 1130.5937 | 0.4247
[7 empty] | 1153.2056 | 0.4077
[7 empty] | 1176.2697 | 0.3914
[7 empty] | 1199.7951 | 0.3758
[7 empty] | 1223.791 | 0.3608
[7 empty] | 1248.2668 | 0.3465
[7 empty] | 1273.2321 | 0.3327
[7 empty] | 1298.6968 | 0.3195
[7 empty] | 1324.6707 | 0.3068
[7 empty] | 1351.1641 | 0.2946
[7 empty] | 1378.1874 | 0.2829
[7 empty] | 1405.7511 | 0.2717
[7 empty] | 1433.8662 | 0.261
[7 empty] | 1462.5435 | 0.2507
[7 empty] | 1491.7943 | 0.2407
[7 empty] | 1521.6302 | 0.2312
[7 empty] | 1552.0628 | 0.2221
[7 empty] | 1583.1041 | 0.2134
[7 empty] | 1614.7662 | 0.2049
[7 empty] | 1647.0615 | 0.1969
[7 empty] | 1680.0027 | 0.1891
[7 empty] | 1713.6028 | 0.1817
[7 empty] | 1747.8748 | 0.1745
[7 empty] | 1782.8323 | 0.1677
[7 empty] | 1818.489 | 0.1611
[7 empty] | 1854.8588 | 0.1548
[7 empty] | 1891.9559 | 0.1487
[7 empty] | 1929.7951 | 0.1429
[7 empty] | 1968.391 | 0.1373
[7 empty] | 2007.7588 | 0.1319
[7 empty] | 2047.914 | 0.1267
[7 empty] | 2088.8722 | 0.1217
[7 empty] | 2130.6497 | 0.117
[7 empty] | 2173.2627 | 0.1124
[7 empty] | 2216.7279 | 0.108
[7 empty] | 2261.0625 | 0.1038
[7 empty] | 2306.2837 | 0.0997
[7 empty] | 2352.4094 | 0.0958
[7 empty] | 2399.4576 | 0.0921
[7 empty] | 2447.4468 | 0.0885
[7 empty] | 2496.3957 | 0.085
[7 empty] | 2546.3236 | 0.0817
[7 empty] | 2597.2501 | 0.0785
[7 empty] | 2649.1951 | 0.0754
[7 empty] | 2702.179 | 0.0725
[7 empty] | 2756.2226 | 0.0697
[7 empty] | 2811.347 | 0.0669
[7 empty] | 2867.5739 | 0.0643
[7 empty] | 2924.9254 | 0.0618
[7 empty] | 2983.4239 | 0.0594
[7 empty] | 3043.0924 | 0.0571
[7 empty] | 3103.9543 | 0.0549
[7 empty] | 3166.0333 | 0.0527
[7 empty] | 3229.354 | 0.051
[7 empty] | 3293.9411 | 0.0494
[7 empty] | 3359.8199 | 0.0479
[7 empty] | 3427.0163 | 0.0464
[7 empty] | 3495.5566 | 0.045
[7 empty] | 3565.4678 | 0.0436
[7 empty] | 3636.7771 | 0.0423
[7 empty] | 3709.5127 | 0.0411
[7 empty] | 3783.7029 | 0.0399
[7 empty] | 3859.377 | 0.0387
[7 empty] | 3936.5645 | 0.0376
[7 empty] | 4015.2958 | 0.0365
[7 empty] | 4095.6017 | 0.0355
[7 empty] | 4177.5138 | 0.0345
[7 empty] | 4261.064 | 0.0335
[7 empty] | 4346.2853 | 0.0326
[7 empty] | 4433.211 | 0.0317
[7 empty] | 4521.8752 | 0.0309
[7 empty] | 4612.3127 | 0.0301
[7 empty] | 4704.559 | 0.0293
[7 empty] | 4798.6502 | 0.0285
[7 empty] | 4894.6232 | 0.0278
[7 empty] | 4992.5157 | 0.0271
[7 empty] | 5092.366 | 0.0265
[7 empty] | 5194.2133 | 0.0258
[7 empty] | 5298.0975 | 0.0252
[7 empty] | 5404.0595 | 0.0246
[7 empty] | 5512.1407 | 0.0241
[7 empty] | 5622.3835 | 0.0235
[7 empty] | 5734.8312 | 0.023
[7 empty] | 5849.5278 | 0.0225
[7 empty] | 5966.5184 | 0.022
[7 empty] | 6085.8487 | 0.0215
[7 empty] | 6207.5657 | 0.0211
[7 empty] | 6331.717 | 0.0206
[7 empty] | 6458.3513 | 0.0202
[7 empty] | 6532.9711 | 0.016
[7 empty] | 6663.6305 | 0.016
[7 empty] | 6796.9031 | 0.016
[7 empty] | 6932.8412 | 0.016
[7 empty] | 7071.498 | 0.016
[7 empty] | 7212.928 | 0.016
[7 empty] | 7357.1865 | 0.016
[7 empty] | 7504.3302 | 0.016
[7 empty] | 7654.4169 | 0.016
[7 empty] | 7807.5052 | 0.016
[7 empty] | 7963.6553 | 0.016
[7 empty] | 8122.9284 | 0.016
[7 empty] | 8285.387 | 0.016
[7 empty] | 8451.0947 | 0.016
[7 empty] | 8620.1166 | 0.016
[7 empty] | 8792.5189 | 0.016
[7 empty] | 8968.3693 | 0.016
[7 empty] | 9147.7367 | 0.016
[7 empty] | 9330.6914 | 0.016
[7 empty] | 9517.3053 | 0.016
[7 empty] | 9707.6514 | 0.016
[7 empty] | 9901.8044 | 0.016
[7 empty] | 10099.8405 | 0.016
[7 empty] | 10301.8373 | 0.016
[7 empty] | 10507.874 | 0.016
[7 empty] | 10718.0315 | 0.016
[7 empty] | 10932.3921 | 0.016
[7 empty] | 11151.04 | 0.016
[7 empty] | 11374.0608 | 0.016
[7 empty] | 11601.542 | 0.016
[7 empty] | 11833.5729 | 0.016
[6 empty] | 8T | 19.0842 | 232.6691
[7 empty] | 19.3 | 146.5726
[7 empty] | 19.4659 | 113.8164
[7 empty] | 19.7 | 86.2732
[7 empty] | 19.8552 | 74.2257
[7 empty] | 20.1 | 60.6973
[7 empty] | 20.2523 | 54.4505
[7 empty] | 20.5 | 46.5659
[7 empty] | 20.6574 | 42.6014
[7 empty] | 20.9 | 37.6078
[7 empty] | 21.0705 | 34.7153
[7 empty] | 21.4919 | 29.0936
[7 empty] | 21.9217 | 24.8871
[7 empty] | 22.3602 | 21.6241
[7 empty] | 22.8074 | 19.0214
[7 empty] | 23.2635 | 16.8989
[7 empty] | 23.7288 | 15.1365
[7 empty] | 24.2034 | 13.6511
[7 empty] | 24.6874 | 12.3832
[7 empty] | 25.1812 | 11.2893
[7 empty] | 25.6848 | 10.3368
[7 empty] | 26.1985 | 9.5006
[7 empty] | 26.7225 | 8.7613
[7 empty] | 27.2569 | 8.1036
[7 empty] | 27.8021 | 7.5152
[7 empty] | 28.3581 | 6.9862
[7 empty] | 28.9253 | 6.5085
[7 empty] | 29.5038 | 6.0752
[7 empty] | 30.0939 | 5.6868
[7 empty] | 30.6957 | 5.3605
[7 empty] | 31.3097 | 5.0584
[7 empty] | 31.9358 | 4.7783
[7 empty] | 32.5746 | 4.518
[7 empty] | 33.2261 | 4.2757
[7 empty] | 33.8906 | 4.0497
[7 empty] | 34.5684 | 3.8387
[7 empty] | 35.2598 | 3.6412
[7 empty] | 35.965 | 3.4562
[7 empty] | 36.6842 | 3.2828
[7 empty] | 37.4179 | 3.1198
[7 empty] | 38.1663 | 2.9666
[7 empty] | 38.9296 | 2.8224
[7 empty] | 39.7082 | 2.6866
[7 empty] | 40.5024 | 2.5585
[7 empty] | 41.3124 | 2.4375
[7 empty] | 42.1387 | 2.3233
[7 empty] | 42.9814 | 2.2152
[7 empty] | 43.8411 | 2.113
[7 empty] | 44.7179 | 2.0162
[7 empty] | 45.6123 | 1.9245
[7 empty] | 46.5245 | 1.8375
[7 empty] | 47.455 | 1.755
[7 empty] | 48.4041 | 1.6767
[7 empty] | 49.3722 | 1.6023
[7 empty] | 50.3596 | 1.5315
[7 empty] | 51.3668 | 1.4643
[7 empty] | 52.3941 | 1.4003
[7 empty] | 53.442 | 1.3395
[7 empty] | 54.5109 | 1.2815
[7 empty] | 55.6011 | 1.2263
[7 empty] | 56.7131 | 1.1737
[7 empty] | 57.8474 | 1.1236
[7 empty] | 59.0043 | 1.0758
[7 empty] | 60.1844 | 1.0301
[7 empty] | 61.3881 | 0.9866
[7 empty] | 62.6158 | 0.9451
[7 empty] | 63.8682 | 0.9054
[7 empty] | 65.1455 | 0.8675
[7 empty] | 66.4484 | 0.8314
[7 empty] | 67.7774 | 0.7968
[7 empty] | 69.133 | 0.7637
[7 empty] | 70.5156 | 0.7321
[7 empty] | 71.9259 | 0.7019
[7 empty] | 73.3644 | 0.673
[7 empty] | 74.8317 | 0.6454
[7 empty] | 76.3284 | 0.619
[7 empty] | 77.8549 | 0.5937
[7 empty] | 79.412 | 0.5694
[7 empty] | 81.0003 | 0.5462
[7 empty] | 82.6203 | 0.524
[7 empty] | 84.2727 | 0.5028
[7 empty] | 85.9581 | 0.4824
[7 empty] | 87.6773 | 0.4629
[7 empty] | 89.4309 | 0.4442
[7 empty] | 91.2195 | 0.4263
[7 empty] | 93.0439 | 0.4092
[7 empty] | 94.9047 | 0.3927
[7 empty] | 96.8028 | 0.377
[7 empty] | 98.7389 | 0.3618
[7 empty] | 100.7137 | 0.3474
[7 empty] | 102.7279 | 0.3335
[7 empty] | 104.7825 | 0.3201
[7 empty] | 106.8781 | 0.3074
[7 empty] | 109.0157 | 0.2951
[7 empty] | 111.196 | 0.2834
[7 empty] | 113.4199 | 0.2721
[7 empty] | 115.6883 | 0.2613
[7 empty] | 118.0021 | 0.2509
[7 empty] | 120.3621 | 0.241
[7 empty] | 122.7694 | 0.2314
[7 empty] | 125.2248 | 0.2223
[7 empty] | 127.7293 | 0.2135
[7 empty] | 130.2839 | 0.205
[7 empty] | 132.8895 | 0.1969
[7 empty] | 135.5473 | 0.1891
[7 empty] | 138.2583 | 0.1817
[7 empty] | 141.0234 | 0.1745
[7 empty] | 143.8439 | 0.1676
[7 empty] | 146.7208 | 0.161
[7 empty] | 149.6552 | 0.1547
[7 empty] | 152.6483 | 0.1486
[7 empty] | 155.7013 | 0.1428
[7 empty] | 158.8153 | 0.1372
[7 empty] | 161.9916 | 0.1318
[7 empty] | 165.2314 | 0.1266
[7 empty] | 168.5361 | 0.1216
[7 empty] | 171.9068 | 0.1168
[7 empty] | 175.3449 | 0.1123
[7 empty] | 178.8518 | 0.1079
[7 empty] | 182.4289 | 0.1036
[7 empty] | 186.0774 | 0.0996
[7 empty] | 189.799 | 0.0957
[7 empty] | 193.595 | 0.0919
[7 empty] | 197.4669 | 0.0883
[7 empty] | 201.4162 | 0.0849
[7 empty] | 205.4445 | 0.0816
[7 empty] | 209.5534 | 0.0784
[7 empty] | 213.7445 | 0.0753
[7 empty] | 218.0194 | 0.0724
[7 empty] | 222.3798 | 0.0695
[7 empty] | 226.8274 | 0.0668
[7 empty] | 231.3639 | 0.0642
[7 empty] | 235.9912 | 0.0617
[7 empty] | 240.711 | 0.0593
[7 empty] | 245.5252 | 0.057
[7 empty] | 250.4357 | 0.0548
[7 empty] | 255.4444 | 0.0526
[7 empty] | 260.5533 | 0.0509
[7 empty] | 265.7644 | 0.0493
[7 empty] | 271.0797 | 0.0478
[7 empty] | 276.5013 | 0.0463
[7 empty] | 282.0313 | 0.0449
[7 empty] | 287.6719 | 0.0436
[7 empty] | 293.4254 | 0.0422
[7 empty] | 299.2939 | 0.041
[7 empty] | 305.2798 | 0.0398
[7 empty] | 311.3854 | 0.0386
[7 empty] | 317.6131 | 0.0375
[7 empty] | 323.9653 | 0.0364
[7 empty] | 330.4446 | 0.0354
[7 empty] | 337.0535 | 0.0344
[7 empty] | 343.7946 | 0.0335
[7 empty] | 350.6705 | 0.0326
[7 empty] | 357.6839 | 0.0317
[7 empty] | 364.8376 | 0.0308
[7 empty] | 372.1343 | 0.03
[7 empty] | 379.577 | 0.0292
[7 empty] | 387.1685 | 0.0285
[7 empty] | 394.9119 | 0.0278
[7 empty] | 402.8102 | 0.0271
[7 empty] | 410.8664 | 0.0264
[7 empty] | 419.0837 | 0.0258
[7 empty] | 427.4654 | 0.0252
[7 empty] | 436.0147 | 0.0246
[7 empty] | 444.735 | 0.024
[7 empty] | 453.6297 | 0.0235
[7 empty] | 462.7023 | 0.0229
[7 empty] | 471.9563 | 0.0224
[7 empty] | 481.3954 | 0.022
[7 empty] | 491.0233 | 0.0215
[7 empty] | 500.8438 | 0.021
[7 empty] | 510.8607 | 0.0206
[7 empty] | 521.0779 | 0.0202
[7 empty] | 526.3671 | 0.016
[7 empty] | 536.8944 | 0.016
[7 empty] | 547.6323 | 0.016
[7 empty] | 558.5849 | 0.016
[7 empty] | 569.7566 | 0.016
[7 empty] | 581.1518 | 0.016
[7 empty] | 592.7748 | 0.016
[7 empty] | 604.6303 | 0.016
[7 empty] | 616.7229 | 0.016
[7 empty] | 629.0574 | 0.016
[7 empty] | 641.6385 | 0.016
[7 empty] | 654.4713 | 0.016
[7 empty] | 667.5607 | 0.016
[7 empty] | 680.9119 | 0.016
[7 empty] | 694.5302 | 0.016
[7 empty] | 708.4208 | 0.016
[7 empty] | 722.5892 | 0.016
[7 empty] | 737.041 | 0.016
[7 empty] | 751.7818 | 0.016
[7 empty] | 766.8174 | 0.016
[7 empty] | 782.1538 | 0.016
[7 empty] | 797.7968 | 0.016
[7 empty] | 813.7528 | 0.016
[7 empty] | 830.0278 | 0.016
[7 empty] | 846.6284 | 0.016
[7 empty] | 863.561 | 0.016
[7 empty] | 880.8322 | 0.016
[7 empty] | 898.4488 | 0.016
[7 empty] | 916.4178 | 0.016
[7 empty] | 934.7461 | 0.016
[7 empty] | 953.4411 | 0.016
[7 empty] | 972.5099 | 0.016
[7 empty] | 991.9601 | 0.016
[7 empty] | 1011.7993 | 0.016
[7 empty] | 1032.0353 | 0.016
[7 empty] | 1052.676 | 0.016
[7 empty] | 1052.7341 | 0.014
[7 empty] | 1073.7888 | 0.014
[7 empty] | 1095.2646 | 0.014
[7 empty] | 1117.1699 | 0.014
[7 empty] | 1139.5133 | 0.014
[7 empty] | 1162.3035 | 0.014
[7 empty] | 1185.5496 | 0.014
[7 empty] | 1209.2606 | 0.014
[7 empty] | 1233.4458 | 0.014
[7 empty] | 1258.1147 | 0.014
[7 empty] | 1283.277 | 0.014
[7 empty] | 1308.9426 | 0.014
[7 empty] | 1335.1214 | 0.014
[7 empty] | 1361.8238 | 0.014
[7 empty] | 1389.0603 | 0.014
[7 empty] | 1416.8415 | 0.014
[7 empty] | 1445.1784 | 0.014
[7 empty] | 1474.0819 | 0.014
[7 empty] | 1503.5636 | 0.014
[7 empty] | 1533.6348 | 0.014
[7 empty] | 1564.3075 | 0.014
[7 empty] | 1595.5937 | 0.014
[7 empty] | 1627.5056 | 0.014
[7 empty] | 1660.0557 | 0.014
[7 empty] | 1693.2568 | 0.014
[7 empty] | 1727.1219 | 0.014
[7 empty] | 1761.6643 | 0.014
[7 empty] | 1796.8976 | 0.014
[7 empty] | 1832.8356 | 0.014
[7 empty] | 1869.4923 | 0.014
[7 empty] | 1906.8821 | 0.014
[7 empty] | 1945.0198 | 0.014
[7 empty] | 1983.9202 | 0.014
[7 empty] | 2023.5986 | 0.014
[7 empty] | 2064.0706 | 0.014
[7 empty] | 2105.352 | 0.014
[7 empty] | 2147.459 | 0.014
[7 empty] | 2190.4082 | 0.014
[7 empty] | 2234.2164 | 0.014
[7 empty] | 2278.9007 | 0.014
[7 empty] | 2324.4787 | 0.014
[7 empty] | 2370.9683 | 0.014
[7 empty] | 2418.3876 | 0.014
[7 empty] | 2466.7554 | 0.014
[7 empty] | 2516.0905 | 0.014
[7 empty] | 2566.4123 | 0.014
[7 empty] | 2617.7406 | 0.014
[7 empty] | 2670.0954 | 0.014
[7 empty] | 2723.4973 | 0.014
[7 empty] | 2777.9672 | 0.014
[7 empty] | 2833.5266 | 0.014
[7 empty] | 2890.1971 | 0.014
[7 empty] | 2948.001 | 0.014
[7 empty] | 3006.9611 | 0.014
[7 empty] | 3067.1003 | 0.014
[7 empty] | 3128.4423 | 0.014
[7 empty] | 3191.0111 | 0.014
[7 empty] | 3254.8313 | 0.014
[7 empty] | 3319.928 | 0.014
[7 empty] | 3386.3265 | 0.014
[7 empty] | 3454.0531 | 0.014
[7 empty] | 3523.1341 | 0.014
[7 empty] | 3593.5968 | 0.014
[7 empty] | 3665.4687 | 0.014
[7 empty] | 3738.7781 | 0.014
[7 empty] | 3813.5537 | 0.014
[7 empty] | 3889.8248 | 0.014
[7 empty] | 3967.6213 | 0.014
[7 empty] | 4046.9737 | 0.014
[7 empty] | 4127.9131 | 0.014
[7 empty] | 4210.4714 | 0.014
[7 empty] | 4294.6808 | 0.014
[7 empty] | 4380.5745 | 0.014
[7 empty] | 4468.1859 | 0.014
[7 empty] | 4557.5497 | 0.014
[7 empty] | 4648.7007 | 0.014
[7 empty] | 4741.6747 | 0.014
[7 empty] | 4836.5082 | 0.014
[7 empty] | 4933.2383 | 0.014
[7 empty] | 5031.9031 | 0.014
[7 empty] | 5132.5412 | 0.014
[7 empty] | 5235.192 | 0.014
[7 empty] | 5339.8958 | 0.014
[7 empty] | 5446.6937 | 0.014
[7 empty] | 5555.6276 | 0.014
[7 empty] | 5666.7402 | 0.014
[7 empty] | 5780.075 | 0.014
[7 empty] | 5895.6765 | 0.014
[7 empty] | 6013.59 | 0.014
[7 empty] | 6133.8618 | 0.014
[7 empty] | 6256.539 | 0.014
[7 empty] | 6381.6698 | 0.014
[7 empty] | 6509.3032 | 0.014
[7 empty] | 6639.4893 | 0.014
[7 empty] | 6772.2791 | 0.014
[7 empty] | 6907.7246 | 0.014
[7 empty] | 7045.8791 | 0.014
[7 empty] | 7186.7967 | 0.014
[7 empty] | 7330.5326 | 0.014
[7 empty] | 7477.1433 | 0.014
[7 empty] | 7626.6862 | 0.014
[7 empty] | 7779.2199 | 0.014
[7 empty] | 7934.8043 | 0.014
[7 empty] | 8093.5004 | 0.014
[7 empty] | 8255.3704 | 0.014
[7 empty] | 8420.4778 | 0.014
[7 empty] | 8588.8873 | 0.014
[7 empty] | 8760.6651 | 0.014
[7 empty] | 8935.8784 | 0.014
[7 empty] | 9114.596 | 0.014
[7 empty] | 9296.8879 | 0.014
[7 empty] | 9482.8256 | 0.014
[7 empty] | 9672.4822 | 0.014
[7 empty] | 9865.9318 | 0.014
[7 empty] | 10063.2504 | 0.014
[7 empty] | 10264.5154 | 0.014
[7 empty] | 10469.8057 | 0.014
[7 empty] | 10679.2019 | 0.014
[7 empty] | 10892.7859 | 0.014
[7 empty] | 11110.6416 | 0.014
[7 empty] | 11332.8545 | 0.014
[7 empty] | 11559.5115 | 0.014
[7 empty] | 11790.7018 | 0.014
[6 empty] | Total Result |  | 788.682

## E_Charac-20210310 220638-Compil (hidden)
Index | Time Interval | Timestamp | Curve Family | Type | Amp Type | Test Type | Trip Type | Interrupter# | Start Type | PE | DT1 | DT2 | OCC Freq | Source Freq | Current | Phase A:B:C | X/R:Angle | Expected Time | P_Select | Max Delta | Min Time | Max Time | Average | Std Dev | Variance | Count | Min T Spec | Max T Spec | Ave T Result | T Result | Indiv T | TC Result | Indiv TC
1 | 124.414 | 44265.9227 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 17 | 0:240:120 | 0:00 | 11.5914 | 7 | 51.3675 | 71.7176 | 123.0851 | 91.8549 | 23.0108 | 529.4975 | 3 | 11.5914 | Inf | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4 | 426.709 | 44265.9262 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 17.34 | 0:240:120 | 0:00 | 10.2985 | 7 | 28.9751 | 25.6525 | 54.6276 | 35.5696 | 13.9301 | 194.0483 | 3 | 10.2985 | 111.8768 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7 | 561.668 | 44265.9278 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 17.6868 | 0:240:120 | 0:00 | 9.2276 | 7 | 2.5705 | 22.3305 | 24.901 | 23.3028 | 1.1824 | 1.3981 | 3 | 9.2276 | 54.715 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10 | 635.003 | 44265.9286 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 18.0405 | 0:240:120 | 0:00 | 8.3268 | 7 | 2.2619 | 19.0468 | 21.3087 | 19.8577 | 1.0272 | 1.0551 | 3 | 8.3268 | 35.6744 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
13 | 697.823 | 44265.9294 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 18.4013 | 0:240:120 | 0:00 | 7.5591 | 7 | 2.475 | 15.5798 | 18.0548 | 16.5515 | 1.1304 | 1.2777 | 3 | 7.5591 | 26.1641 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
16 | 750.748 | 44265.93 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 18.7694 | 0:240:120 | 0:00 | 6.8975 | 7 | 1.9547 | 12.4456 | 14.4003 | 13.1286 | 0.9398 | 0.8833 | 3 | 6.8975 | 20.4658 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
19 | 793.771 | 44265.9305 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.1448 | 0:240:120 | 0:00 | 6.3218 | 7 | 0.8186 | 11.2204 | 12.039 | 11.531 | 0.3799 | 0.1443 | 3 | 6.3218 | 16.6735 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
22 | 831.25 | 44265.9309 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.5277 | 0:240:120 | 0:00 | 5.8167 | 7 | 0.7449 | 10.0589 | 10.8038 | 10.3217 | 0.3543 | 0.1255 | 3 | 5.8167 | 13.9704 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
25 | 865.008 | 44265.9313 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.9182 | 0:240:120 | 0:00 | 5.3703 | 7 | 0.895 | 8.7444 | 9.6394 | 9.0789 | 0.4106 | 0.1686 | 3 | 5.3703 | 11.9478 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
28 | 895.201 | 44265.9316 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 20.3166 | 0:240:120 | 0:00 | 4.9732 | 7 | 0.701 | 7.7352 | 8.4362 | 7.9923 | 0.3182 | 0.1013 | 3 | 4.9732 | 10.379 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
31 | 922.613 | 44265.932 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 20.7229 | 0:240:120 | 0:00 | 4.6179 | 7 | 0.4809 | 7.0496 | 7.5305 | 7.2354 | 0.2175 | 0.0473 | 3 | 4.6179 | 9.1278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
34 | 947.404 | 44265.9322 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 21.1374 | 0:240:120 | 0:00 | 4.2984 | 7 | 0.4779 | 6.4258 | 6.9037 | 6.6161 | 0.2158 | 0.0466 | 3 | 4.2984 | 8.1075 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
37 | 970.485 | 44265.9325 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 21.5601 | 0:240:120 | 0:00 | 4.0098 | 7 | 0.4625 | 5.7809 | 6.2434 | 5.9654 | 0.2111 | 0.0446 | 3 | 4.0098 | 7.2603 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
40 | 991.691 | 44265.9328 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 21.9913 | 0:240:120 | 0:00 | 3.748 | 7 | 0.3025 | 5.3262 | 5.6287 | 5.4489 | 0.1334 | 0.0178 | 3 | 3.748 | 6.5464 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
43 | 1011.077 | 44265.933 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 22.4311 | 0:240:120 | 0:00 | 3.5096 | 7 | 0.3375 | 4.9033 | 5.2408 | 5.0563 | 0.1429 | 0.0204 | 3 | 3.5096 | 5.9371 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
46 | 1029.282 | 44265.9332 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 22.8798 | 0:240:120 | 0:00 | 3.2918 | 7 | 0.3063 | 4.5208 | 4.8271 | 4.6422 | 0.1381 | 0.0191 | 3 | 3.2918 | 5.4115 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
49 | 1046.254 | 44265.9334 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.3374 | 0:240:120 | 0:00 | 3.0921 | 7 | 0.2204 | 4.1873 | 4.4077 | 4.2779 | 0.0958 | 0.0092 | 3 | 3.0921 | 4.9539 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
52 | 1062.188 | 44265.9336 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.8041 | 0:240:120 | 0:00 | 2.9085 | 7 | 0.239 | 3.8947 | 4.1337 | 3.9998 | 0.1039 | 0.0108 | 3 | 2.9085 | 4.5522 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
55 | 1077.282 | 44265.9337 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.2802 | 0:240:120 | 0:00 | 2.7393 | 7 | 0.2435 | 3.6076 | 3.8511 | 3.7157 | 0.1016 | 0.0103 | 3 | 2.7393 | 4.1971 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
58 | 1091.427 | 44265.9339 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.7658 | 0:240:120 | 0:00 | 2.583 | 7 | 0.1585 | 3.381 | 3.5395 | 3.445 | 0.0706 | 0.005 | 3 | 2.583 | 3.8812 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
61 | 1104.814 | 44265.9341 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.2611 | 0:240:120 | 0:00 | 2.4382 | 7 | 0.1709 | 3.1696 | 3.3405 | 3.2412 | 0.0745 | 0.0055 | 3 | 2.4382 | 3.5986 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
64 | 1117.658 | 44265.9342 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.7663 | 0:240:120 | 0:00 | 2.3039 | 7 | 0.1786 | 2.9403 | 3.1189 | 3.0198 | 0.0774 | 0.006 | 3 | 2.3039 | 3.3447 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
67 | 1129.761 | 44265.9344 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.2817 | 0:240:120 | 0:00 | 2.179 | 7 | 0.1421 | 2.7606 | 2.9027 | 2.8303 | 0.0576 | 0.0033 | 3 | 2.179 | 3.1153 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
70 | 1141.183 | 44265.9345 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.8073 | 0:240:120 | 0:00 | 2.0626 | 7 | 0.1342 | 2.5987 | 2.7329 | 2.6602 | 0.0559 | 0.0031 | 3 | 2.0626 | 2.9073 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
73 | 1152.18 | 44265.9346 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 27.3434 | 0:240:120 | 0:00 | 1.9541 | 7 | 0.133 | 2.4344 | 2.5674 | 2.492 | 0.0575 | 0.0033 | 3 | 1.9541 | 2.7181 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
76 | 1162.662 | 44265.9347 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 27.8903 | 0:240:120 | 0:00 | 1.8527 | 7 | 0.1197 | 2.2958 | 2.4155 | 2.351 | 0.0491 | 0.0024 | 3 | 1.8527 | 2.5453 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
79 | 1172.728 | 44265.9349 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.4481 | 0:240:120 | 0:00 | 1.7577 | 7 | 0.1188 | 2.1628 | 2.2816 | 2.2187 | 0.0495 | 0.0024 | 3 | 1.7577 | 2.387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
82 | 1182.342 | 44265.935 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.0171 | 0:240:120 | 0:00 | 1.6688 | 7 | 0.1055 | 2.0404 | 2.1459 | 2.0902 | 0.0438 | 0.0019 | 3 | 1.6688 | 2.2417 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
85 | 1191.683 | 44265.9351 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.5974 | 0:240:120 | 0:00 | 1.5853 | 7 | 0.0916 | 1.9354 | 2.027 | 1.9771 | 0.0389 | 0.0015 | 3 | 1.5853 | 2.1078 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
88 | 1200.697 | 44265.9352 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.1894 | 0:240:120 | 0:00 | 1.5069 | 7 | 0.0886 | 1.8257 | 1.9143 | 1.8633 | 0.039 | 0.0015 | 3 | 1.5069 | 1.9881 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
91 | 1209.152 | 44265.9353 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.7931 | 0:240:120 | 0:00 | 1.4331 | 7 | 0.0706 | 1.7382 | 1.8088 | 1.7689 | 0.0287 | 0.0008 | 3 | 1.4331 | 1.8844 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
94 | 1217.352 | 44265.9354 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.409 | 0:240:120 | 0:00 | 1.3636 | 7 | 0.0752 | 1.6454 | 1.7206 | 1.6797 | 0.0321 | 0.001 | 3 | 1.3636 | 1.7875 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
97 | 1225.435 | 44265.9355 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.0372 | 0:240:120 | 0:00 | 1.2982 | 7 | 0.0625 | 1.5679 | 1.6304 | 1.5944 | 0.0272 | 0.0007 | 3 | 1.2982 | 1.6967 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
100 | 1233.186 | 44265.9356 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.6779 | 0:240:120 | 0:00 | 1.2365 | 7 | 0.0611 | 1.4918 | 1.5529 | 1.5182 | 0.0266 | 0.0007 | 3 | 1.2365 | 1.6115 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
103 | 1240.747 | 44265.9356 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.3315 | 0:240:120 | 0:00 | 1.1782 | 7 | 0.0588 | 1.4163 | 1.4751 | 1.4409 | 0.0257 | 0.0007 | 3 | 1.1782 | 1.5315 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
106 | 1247.954 | 44265.9357 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.9981 | 0:240:120 | 0:00 | 1.1231 | 7 | 0.0535 | 1.3506 | 1.4041 | 1.3736 | 0.0233 | 0.0005 | 3 | 1.1231 | 1.4563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
109 | 1255.018 | 44265.9358 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.6781 | 0:240:120 | 0:00 | 1.071 | 7 | 0.0565 | 1.2824 | 1.3389 | 1.3055 | 0.0247 | 0.0006 | 3 | 1.071 | 1.3855 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
112 | 1262.039 | 44265.9359 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.3716 | 0:240:120 | 0:00 | 1.0217 | 7 | 0.0475 | 1.2249 | 1.2724 | 1.2441 | 0.0213 | 0.0005 | 3 | 1.0217 | 1.3188 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
115 | 1268.716 | 44265.936 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.0791 | 0:240:120 | 0:00 | 0.9749 | 7 | 0.0502 | 1.1636 | 1.2138 | 1.1853 | 0.021 | 0.0004 | 3 | 0.9749 | 1.2559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
118 | 1275.145 | 44265.936 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.8007 | 0:240:120 | 0:00 | 0.9307 | 7 | 0.0391 | 1.1144 | 1.1535 | 1.1302 | 0.0175 | 0.0003 | 3 | 0.9307 | 1.1965 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
121 | 1281.533 | 44265.9361 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.5367 | 0:240:120 | 0:00 | 0.8887 | 7 | 0.0415 | 1.0618 | 1.1033 | 1.0793 | 0.0181 | 0.0003 | 3 | 0.8887 | 1.1404 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
124 | 1287.825 | 44265.9362 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.2874 | 0:240:120 | 0:00 | 0.8489 | 7 | 0.0368 | 1.0139 | 1.0507 | 1.0295 | 0.016 | 0.0003 | 3 | 0.8489 | 1.0874 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
127 | 1294.013 | 44265.9363 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.0532 | 0:240:120 | 0:00 | 0.811 | 7 | 0.0389 | 0.9663 | 1.0052 | 0.9825 | 0.0171 | 0.0003 | 3 | 0.811 | 1.0372 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
130 | 1299.896 | 44265.9363 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.8342 | 0:240:120 | 0:00 | 0.7751 | 7 | 0.034 | 0.9232 | 0.9572 | 0.9376 | 0.0148 | 0.0002 | 3 | 0.7751 | 0.9896 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
133 | 1305.746 | 44265.9364 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.6309 | 0:240:120 | 0:00 | 0.741 | 7 | 0.0334 | 0.8827 | 0.9161 | 0.8958 | 0.0151 | 0.0002 | 3 | 0.741 | 0.9446 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
136 | 1311.235 | 44265.9365 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.4435 | 0:240:120 | 0:00 | 0.7085 | 7 | 0.0299 | 0.8423 | 0.8722 | 0.8543 | 0.0131 | 0.0002 | 3 | 0.7085 | 0.9019 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
139 | 1316.85 | 44265.9365 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.2724 | 0:240:120 | 0:00 | 0.6776 | 7 | 0.029 | 0.8053 | 0.8343 | 0.8165 | 0.0132 | 0.0002 | 3 | 0.6776 | 0.8614 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
142 | 1322.331 | 44265.9366 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.1178 | 0:240:120 | 0:00 | 0.6482 | 7 | 0.0282 | 0.7707 | 0.7989 | 0.7812 | 0.0129 | 0.0002 | 3 | 0.6482 | 0.823 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
145 | 1327.565 | 44265.9366 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.9802 | 0:240:120 | 0:00 | 0.6202 | 7 | 0.0272 | 0.7361 | 0.7633 | 0.7469 | 0.0122 | 0.0001 | 3 | 0.6202 | 0.7864 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
148 | 1332.889 | 44265.9367 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.8598 | 0:240:120 | 0:00 | 0.5935 | 7 | 0.025 | 0.7054 | 0.7304 | 0.715 | 0.0109 | 0.0001 | 3 | 0.5935 | 0.7517 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
151 | 1337.99 | 44265.9368 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.757 | 0:240:120 | 0:00 | 0.5681 | 7 | 0.0249 | 0.6747 | 0.6996 | 0.6848 | 0.0108 | 0.0001 | 3 | 0.5681 | 0.7187 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
154 | 1343.041 | 44265.9368 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.6721 | 0:240:120 | 0:00 | 0.5438 | 7 | 0.0253 | 0.6443 | 0.6696 | 0.6539 | 0.0114 | 0.0001 | 3 | 0.5438 | 0.6873 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
157 | 1347.992 | 44265.9369 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.6056 | 0:240:120 | 0:00 | 0.5207 | 7 | 0.0218 | 0.6169 | 0.6387 | 0.6257 | 0.0095 | 0.0001 | 3 | 0.5207 | 0.6574 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
160 | 1352.803 | 44265.9369 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.5577 | 0:240:120 | 0:00 | 0.4986 | 7 | 0.0216 | 0.5907 | 0.6123 | 0.5991 | 0.0095 | 0.0001 | 3 | 0.4986 | 0.629 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
163 | 1357.559 | 44265.937 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.5288 | 0:240:120 | 0:00 | 0.4776 | 7 | 0.0201 | 0.5659 | 0.586 | 0.5735 | 0.0089 | 0.0001 | 3 | 0.4776 | 0.6019 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
166 | 1362.32 | 44265.937 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.5194 | 0:240:120 | 0:00 | 0.4575 | 7 | 0.0183 | 0.542 | 0.5603 | 0.5492 | 0.0082 | 0.0001 | 3 | 0.4575 | 0.5761 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
169 | 1366.955 | 44265.9371 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.5298 | 0:240:120 | 0:00 | 0.4383 | 7 | 0.0167 | 0.5199 | 0.5366 | 0.526 | 0.0077 | 0.0001 | 3 | 0.4383 | 0.5515 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
172 | 1371.658 | 44265.9372 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.5604 | 0:240:120 | 0:00 | 0.42 | 7 | 0.0174 | 0.4972 | 0.5146 | 0.5044 | 0.0076 | 0.0001 | 3 | 0.42 | 0.528 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
175 | 1376.335 | 44265.9372 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.6116 | 0:240:120 | 0:00 | 0.4025 | 7 | 0.0153 | 0.4766 | 0.4919 | 0.4827 | 0.0068 | 0 | 3 | 0.4025 | 0.5056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
178 | 1380.865 | 44265.9373 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.6838 | 0:240:120 | 0:00 | 0.3858 | 7 | 0.0157 | 0.4566 | 0.4723 | 0.463 | 0.0067 | 0 | 3 | 0.3858 | 0.4842 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
181 | 1385.527 | 44265.9373 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.7775 | 0:240:120 | 0:00 | 0.3698 | 7 | 0.014 | 0.4377 | 0.4517 | 0.4433 | 0.0063 | 0 | 3 | 0.3698 | 0.4639 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
184 | 1389.972 | 44265.9374 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.8931 | 0:240:120 | 0:00 | 0.3545 | 7 | 0.013 | 0.4191 | 0.4321 | 0.4243 | 0.0058 | 0 | 3 | 0.3545 | 0.4444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
187 | 1394.323 | 44265.9374 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.0309 | 0:240:120 | 0:00 | 0.3399 | 7 | 0.013 | 0.4014 | 0.4144 | 0.4067 | 0.0057 | 0 | 3 | 0.3399 | 0.4258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
190 | 1398.606 | 44265.9375 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.1916 | 0:240:120 | 0:00 | 0.3259 | 7 | 0.0114 | 0.3854 | 0.3968 | 0.3898 | 0.0052 | 0 | 3 | 0.3259 | 0.408 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
193 | 1402.839 | 44265.9375 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.3754 | 0:240:120 | 0:00 | 0.3125 | 7 | 0.0115 | 0.3691 | 0.3806 | 0.3737 | 0.0052 | 0 | 3 | 0.3125 | 0.3911 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
196 | 1407.192 | 44265.9376 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.5829 | 0:240:120 | 0:00 | 0.2997 | 7 | 0.011 | 0.3543 | 0.3653 | 0.3587 | 0.0049 | 0 | 3 | 0.2997 | 0.3748 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
199 | 1411.517 | 44265.9376 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.8146 | 0:240:120 | 0:00 | 0.2875 | 7 | 0.0091 | 0.3409 | 0.35 | 0.3441 | 0.0043 | 0 | 3 | 0.2875 | 0.3593 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
202 | 1415.592 | 44265.9377 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.0708 | 0:240:120 | 0:00 | 0.2758 | 7 | 0.0117 | 0.325 | 0.3367 | 0.3299 | 0.0052 | 0 | 3 | 0.2758 | 0.3445 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
205 | 1419.522 | 44265.9377 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.3523 | 0:240:120 | 0:00 | 0.2645 | 7 | 0.0095 | 0.3124 | 0.3219 | 0.3159 | 0.0042 | 0 | 3 | 0.2645 | 0.3303 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
208 | 1423.409 | 44265.9378 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.6593 | 0:240:120 | 0:00 | 0.2538 | 7 | 0.0104 | 0.299 | 0.3094 | 0.3039 | 0.004 | 0 | 3 | 0.2538 | 0.3168 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
211 | 1427.313 | 44265.9378 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.9925 | 0:240:120 | 0:00 | 0.2435 | 7 | 0.0093 | 0.2875 | 0.2968 | 0.2913 | 0.004 | 0 | 3 | 0.2435 | 0.3038 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
214 | 1431.221 | 44265.9378 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.3523 | 0:240:120 | 0:00 | 0.2336 | 7 | 0.0099 | 0.2753 | 0.2852 | 0.2794 | 0.0041 | 0 | 3 | 0.2336 | 0.2914 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
217 | 1435.028 | 44265.9379 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.7394 | 0:240:120 | 0:00 | 0.2242 | 7 | 0.0092 | 0.2639 | 0.2731 | 0.2679 | 0.0035 | 0 | 3 | 0.2242 | 0.2795 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
220 | 1438.716 | 44265.9379 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.1542 | 0:240:120 | 0:00 | 0.2152 | 7 | 0.0074 | 0.2545 | 0.2619 | 0.2574 | 0.003 | 0 | 3 | 0.2152 | 0.2681 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
223 | 1442.589 | 44265.938 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.5973 | 0:240:120 | 0:00 | 0.2065 | 7 | 0.0073 | 0.2445 | 0.2518 | 0.2472 | 0.0031 | 0 | 3 | 0.2065 | 0.2572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
226 | 1446.108 | 44265.938 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.0692 | 0:240:120 | 0:00 | 0.1982 | 7 | 0.0084 | 0.2324 | 0.2408 | 0.2359 | 0.0032 | 0 | 3 | 0.1982 | 0.2468 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
229 | 1449.896 | 44265.9381 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.5706 | 0:240:120 | 0:00 | 0.1902 | 7 | 0.0075 | 0.2237 | 0.2312 | 0.2272 | 0.003 | 0 | 3 | 0.1902 | 0.2368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
232 | 1453.838 | 44265.9381 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.102 | 0:240:120 | 0:00 | 0.1826 | 7 | 0.0072 | 0.2147 | 0.2219 | 0.2179 | 0.0028 | 0 | 3 | 0.1826 | 0.2272 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
235 | 1457.458 | 44265.9381 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.664 | 0:240:120 | 0:00 | 0.1753 | 7 | 0.0066 | 0.2064 | 0.213 | 0.2093 | 0.0026 | 0 | 3 | 0.1753 | 0.218 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
238 | 1461.324 | 44265.9382 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.2573 | 0:240:120 | 0:00 | 0.1683 | 7 | 0.0067 | 0.198 | 0.2047 | 0.2007 | 0.0026 | 0 | 3 | 0.1683 | 0.2092 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
241 | 1464.98 | 44265.9382 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.8825 | 0:240:120 | 0:00 | 0.1615 | 7 | 0.0058 | 0.19 | 0.1958 | 0.1928 | 0.0023 | 0 | 3 | 0.1615 | 0.2008 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
244 | 1468.704 | 44265.9383 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.5401 | 0:240:120 | 0:00 | 0.1551 | 7 | 0.0066 | 0.1823 | 0.1889 | 0.1853 | 0.0028 | 0 | 3 | 0.1551 | 0.1927 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
247 | 1472.447 | 44265.9383 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.2309 | 0:240:120 | 0:00 | 0.1489 | 7 | 0.0068 | 0.1746 | 0.1814 | 0.1778 | 0.0027 | 0 | 3 | 0.1489 | 0.185 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
250 | 1476.194 | 44265.9384 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.9555 | 0:240:120 | 0:00 | 0.143 | 7 | 0.0065 | 0.1678 | 0.1743 | 0.171 | 0.0026 | 0 | 3 | 0.143 | 0.1776 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
253 | 1479.875 | 44265.9384 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.7146 | 0:240:120 | 0:00 | 0.1373 | 7 | 0.0062 | 0.1611 | 0.1673 | 0.1641 | 0.0024 | 0 | 3 | 0.1373 | 0.1705 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
256 | 1483.497 | 44265.9384 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.5089 | 0:240:120 | 0:00 | 0.1318 | 7 | 0.0062 | 0.1545 | 0.1607 | 0.1574 | 0.0024 | 0 | 3 | 0.1318 | 0.1637 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
259 | 1487.038 | 44265.9385 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.3391 | 0:240:120 | 0:00 | 0.1266 | 7 | 0.0063 | 0.1482 | 0.1545 | 0.151 | 0.0024 | 0 | 3 | 0.1266 | 0.1571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
262 | 1490.552 | 44265.9385 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.2059 | 0:240:120 | 0:00 | 0.1216 | 7 | 0.0047 | 0.1428 | 0.1475 | 0.145 | 0.0018 | 0 | 3 | 0.1216 | 0.1509 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
265 | 1493.994 | 44265.9386 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.11 | 0:240:120 | 0:00 | 0.1167 | 7 | 0.0055 | 0.1368 | 0.1423 | 0.1397 | 0.002 | 0 | 3 | 0.1167 | 0.1448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
268 | 1497.583 | 44265.9386 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.0522 | 0:240:120 | 0:00 | 0.1121 | 7 | 0.0051 | 0.1313 | 0.1364 | 0.1337 | 0.002 | 0 | 3 | 0.1121 | 0.1391 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
271 | 1500.923 | 44265.9387 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.0333 | 0:240:120 | 0:00 | 0.1077 | 7 | 0.0048 | 0.1265 | 0.1313 | 0.1288 | 0.002 | 0 | 3 | 0.1077 | 0.1335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
274 | 1504.436 | 44265.9387 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.0539 | 0:240:120 | 0:00 | 0.1034 | 7 | 0.0043 | 0.1218 | 0.1261 | 0.1237 | 0.0017 | 0 | 3 | 0.1034 | 0.1282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
277 | 1508.026 | 44265.9387 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.115 | 0:240:120 | 0:00 | 0.0993 | 7 | 0.0053 | 0.1167 | 0.122 | 0.1189 | 0.002 | 0 | 3 | 0.0993 | 0.1231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
280 | 1511.37 | 44265.9388 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.2173 | 0:240:120 | 0:00 | 0.0954 | 7 | 0.0053 | 0.1121 | 0.1174 | 0.1146 | 0.002 | 0 | 3 | 0.0954 | 0.1183 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
283 | 1514.735 | 44265.9388 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.3617 | 0:240:120 | 0:00 | 0.0916 | 7 | 0.0038 | 0.1075 | 0.1113 | 0.1094 | 0.0016 | 0 | 3 | 0.0916 | 0.1136 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
286 | 1518.145 | 44265.9389 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.5489 | 0:240:120 | 0:00 | 0.088 | 7 | 0.0048 | 0.1028 | 0.1076 | 0.1054 | 0.0018 | 0 | 3 | 0.088 | 0.1091 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
289 | 1521.531 | 44265.9389 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.7799 | 0:240:120 | 0:00 | 0.0845 | 7 | 0.0038 | 0.1 | 0.1038 | 0.1017 | 0.0014 | 0 | 3 | 0.0845 | 0.1048 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
292 | 1524.969 | 44265.9389 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.0555 | 0:240:120 | 0:00 | 0.0812 | 7 | 0.0027 | 0.0959 | 0.0986 | 0.0972 | 0.0011 | 0 | 3 | 0.0812 | 0.1006 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
295 | 1528.351 | 44265.939 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.3766 | 0:240:120 | 0:00 | 0.078 | 7 | 0.0037 | 0.0911 | 0.0948 | 0.0934 | 0.0014 | 0 | 3 | 0.078 | 0.0966 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
298 | 1531.686 | 44265.939 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.7441 | 0:240:120 | 0:00 | 0.0749 | 7 | 0.0042 | 0.0882 | 0.0924 | 0.0903 | 0.0016 | 0 | 3 | 0.0749 | 0.0928 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
301 | 1535.104 | 44265.939 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.159 | 0:240:120 | 0:00 | 0.072 | 7 | 0.0042 | 0.0842 | 0.0884 | 0.0865 | 0.0017 | 0 | 3 | 0.072 | 0.0892 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
304 | 1538.782 | 44265.9391 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.6222 | 0:240:120 | 0:00 | 0.0692 | 7 | 0.0028 | 0.0812 | 0.084 | 0.083 | 0.0012 | 0 | 3 | 0.0692 | 0.0856 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
307 | 1542.183 | 44265.9391 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.1346 | 0:240:120 | 0:00 | 0.0665 | 7 | 0.0034 | 0.0782 | 0.0816 | 0.0797 | 0.0013 | 0 | 3 | 0.0665 | 0.0823 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
310 | 1545.552 | 44265.9392 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.6973 | 0:240:120 | 0:00 | 0.0638 | 7 | 0.0037 | 0.0746 | 0.0783 | 0.0765 | 0.0014 | 0 | 3 | 0.0638 | 0.079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
313 | 1549.106 | 44265.9392 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.3112 | 0:240:120 | 0:00 | 0.0613 | 7 | 0.0039 | 0.0715 | 0.0754 | 0.0742 | 0.0016 | 0 | 3 | 0.0613 | 0.0759 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
316 | 1552.62 | 44265.9392 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 135.9775 | 0:240:120 | 0:00 | 0.0589 | 7 | 0.0034 | 0.069 | 0.0724 | 0.0709 | 0.0011 | 0 | 3 | 0.0589 | 0.0729 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
319 | 1556.126 | 44265.9393 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.697 | 0:240:120 | 0:00 | 0.0566 | 7 | 0.0034 | 0.0659 | 0.0693 | 0.0679 | 0.0014 | 0 | 3 | 0.0566 | 0.0701 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
322 | 1559.682 | 44265.9393 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.471 | 0:240:120 | 0:00 | 0.0544 | 7 | 0.0035 | 0.0636 | 0.0671 | 0.0654 | 0.0013 | 0 | 3 | 0.0544 | 0.0673 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
325 | 1562.941 | 44265.9394 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.3004 | 0:240:120 | 0:00 | 0.0523 | 7 | 0.003 | 0.0614 | 0.0644 | 0.0633 | 0.0011 | 0 | 3 | 0.0523 | 0.0647 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
328 | 1566.495 | 44265.9394 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.1864 | 0:240:120 | 0:00 | 0.0502 | 7 | 0.0021 | 0.0597 | 0.0618 | 0.0607 | 0.0007 | 0 | 3 | 0.0502 | 0.0621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
331 | 1570.023 | 44265.9395 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.1301 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0046 | 0.0572 | 0.0618 | 0.0594 | 0.0014 | 0 | 3 | 0.0482 | 0.0597 | P | NP | 0-1-0-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
334 | 1573.449 | 44265.9395 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.1327 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0039 | 0.0543 | 0.0582 | 0.0563 | 0.0014 | 0 | 3 | 0.0464 | 0.0573 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
337 | 1577.019 | 44265.9395 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.1954 | 0:240:120 | 0:00 | 0.0445 | 7 | 0.0041 | 0.0517 | 0.0558 | 0.054 | 0.0016 | 0 | 3 | 0.0445 | 0.0551 | P | NP | 1-1-1-1-1-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
340 | 1580.4 | 44265.9396 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 159.3193 | 0:240:120 | 0:00 | 0.0428 | 7 | 0.0027 | 0.0498 | 0.0525 | 0.0517 | 0.0011 | 0 | 3 | 0.0428 | 0.0529 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
343 | 1583.917 | 44265.9396 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 162.5057 | 0:240:120 | 0:00 | 0.0411 | 7 | 0.0026 | 0.0482 | 0.0508 | 0.0498 | 0.001 | 0 | 3 | 0.0411 | 0.0511 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
346 | 1587.254 | 44265.9397 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.7558 | 0:240:120 | 0:00 | 0.0395 | 7 | 0.0035 | 0.0466 | 0.0501 | 0.0486 | 0.0012 | 0 | 3 | 0.0395 | 0.0495 | P | NP | 0-1-1-0-1-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
349 | 1590.74 | 44265.9397 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.0709 | 0:240:120 | 0:00 | 0.038 | 7 | 0.0041 | 0.044 | 0.0481 | 0.0466 | 0.0017 | 0 | 3 | 0.038 | 0.048 | P | NP | 0-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
352 | 1594.294 | 44265.9397 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 172.4523 | 0:240:120 | 0:00 | 0.0365 | 7 | 0.003 | 0.0426 | 0.0456 | 0.0444 | 0.0012 | 0 | 3 | 0.0365 | 0.0465 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
355 | 1597.543 | 44265.9398 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175.9014 | 0:240:120 | 0:00 | 0.0351 | 7 | 0.0028 | 0.0415 | 0.0443 | 0.0434 | 0.0012 | 0 | 3 | 0.0351 | 0.0451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
358 | 1600.997 | 44265.9398 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 179.4194 | 0:240:120 | 0:00 | 0.0337 | 7 | 0.0038 | 0.0392 | 0.043 | 0.0412 | 0.0013 | 0 | 3 | 0.0337 | 0.0437 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
361 | 1604.345 | 44265.9398 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.0078 | 0:240:120 | 0:00 | 0.0324 | 7 | 0.003 | 0.0379 | 0.0409 | 0.0397 | 0.0011 | 0 | 3 | 0.0324 | 0.0424 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
364 | 1607.785 | 44265.9399 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 186.6679 | 0:240:120 | 0:00 | 0.0311 | 7 | 0.0029 | 0.0365 | 0.0394 | 0.0384 | 0.0012 | 0 | 3 | 0.0311 | 0.0411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
367 | 1610.886 | 44265.9399 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 190.4013 | 0:240:120 | 0:00 | 0.0299 | 7 | 0.0038 | 0.0346 | 0.0384 | 0.0369 | 0.0014 | 0 | 3 | 0.0299 | 0.0399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
370 | 1614.333 | 44265.94 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.2093 | 0:240:120 | 0:00 | 0.0287 | 7 | 0.003 | 0.0339 | 0.0369 | 0.0359 | 0.0012 | 0 | 3 | 0.0287 | 0.0387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
373 | 1617.47 | 44265.94 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 198.0935 | 0:240:120 | 0:00 | 0.0276 | 7 | 0.0032 | 0.033 | 0.0362 | 0.0346 | 0.001 | 0 | 3 | 0.0276 | 0.0376 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
376 | 1620.807 | 44265.94 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 202.0554 | 0:240:120 | 0:00 | 0.0265 | 7 | 0.0016 | 0.0325 | 0.0341 | 0.0334 | 0.0006 | 0 | 3 | 0.0265 | 0.0365 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
379 | 1624.156 | 44265.9401 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 206.0965 | 0:240:120 | 0:00 | 0.0255 | 7 | 0.0021 | 0.0309 | 0.033 | 0.0323 | 0.0007 | 0 | 3 | 0.0255 | 0.0355 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
382 | 1627.602 | 44265.9401 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 210.2184 | 0:240:120 | 0:00 | 0.0245 | 7 | 0.0037 | 0.029 | 0.0327 | 0.0311 | 0.0013 | 0 | 3 | 0.0245 | 0.0345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
385 | 1631.018 | 44265.9402 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 214.4228 | 0:240:120 | 0:00 | 0.0235 | 7 | 0.0041 | 0.0277 | 0.0318 | 0.0298 | 0.0013 | 0 | 3 | 0.0235 | 0.0335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
388 | 1634.516 | 44265.9402 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 218.7112 | 0:240:120 | 0:00 | 0.0226 | 7 | 0.0027 | 0.0274 | 0.0301 | 0.0291 | 0.0011 | 0 | 3 | 0.0226 | 0.0326 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
391 | 1637.762 | 44265.9402 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.0855 | 0:240:120 | 0:00 | 0.0217 | 7 | 0.0031 | 0.0264 | 0.0295 | 0.0281 | 0.0012 | 0 | 3 | 0.0217 | 0.0317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
394 | 1641.181 | 44265.9403 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 227.5472 | 0:240:120 | 0:00 | 0.0209 | 7 | 0.0031 | 0.0258 | 0.0289 | 0.0273 | 0.0011 | 0 | 3 | 0.0209 | 0.0309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
397 | 1644.67 | 44265.9403 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 232.0981 | 0:240:120 | 0:00 | 0.0201 | 7 | 0.0028 | 0.0249 | 0.0277 | 0.0263 | 0.001 | 0 | 3 | 0.0201 | 0.0301 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
400 | 1647.976 | 44265.9404 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 236.7401 | 0:240:120 | 0:00 | 0.0193 | 7 | 0.003 | 0.0231 | 0.0261 | 0.0251 | 0.0012 | 0 | 3 | 0.0193 | 0.0293 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
403 | 1651.232 | 44265.9404 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 241.4749 | 0:240:120 | 0:00 | 0.0185 | 7 | 0.0034 | 0.0226 | 0.026 | 0.0247 | 0.0013 | 0 | 3 | 0.0185 | 0.0285 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
406 | 1654.623 | 44265.9404 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.3044 | 0:240:120 | 0:00 | 0.0178 | 7 | 0.0024 | 0.0227 | 0.0251 | 0.024 | 0.0011 | 0 | 3 | 0.0178 | 0.0278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
409 | 1658.018 | 44265.9405 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 251.2305 | 0:240:120 | 0:00 | 0.0171 | 7 | 0.0029 | 0.0222 | 0.0251 | 0.0235 | 0.0009 | 0 | 3 | 0.0171 | 0.0271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
412 | 1661.454 | 44265.9405 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.2551 | 0:240:120 | 0:00 | 0.0165 | 7 | 0.0048 | 0.0201 | 0.0249 | 0.0226 | 0.0016 | 0 | 3 | 0.0165 | 0.0265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
415 | 1664.904 | 44265.9405 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 261.3802 | 0:240:120 | 0:00 | 0.0158 | 7 | 0.0042 | 0.0202 | 0.0244 | 0.0224 | 0.0015 | 0 | 3 | 0.0158 | 0.0258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
418 | 1668.294 | 44265.9406 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 266.6078 | 0:240:120 | 0:00 | 0.0152 | 7 | 0.0046 | 0.0187 | 0.0233 | 0.0215 | 0.0017 | 0 | 3 | 0.0152 | 0.0252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
421 | 1672.188 | 44265.9406 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 271.9399 | 0:240:120 | 0:00 | 0.0146 | 7 | 0.0032 | 0.0194 | 0.0226 | 0.0213 | 0.0012 | 0 | 3 | 0.0146 | 0.0246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
424 | 1675.557 | 44265.9407 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 277.3787 | 0:240:120 | 0:00 | 0.014 | 7 | 0.0041 | 0.0183 | 0.0224 | 0.0207 | 0.0017 | 0 | 3 | 0.014 | 0.024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
427 | 1678.912 | 44265.9407 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 282.9263 | 0:240:120 | 0:00 | 0.0135 | 7 | 0.0038 | 0.0182 | 0.022 | 0.0202 | 0.0015 | 0 | 3 | 0.0135 | 0.0235 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
430 | 1682.084 | 44265.9407 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 288.5848 | 0:240:120 | 0:00 | 0.013 | 7 | 0.0035 | 0.0182 | 0.0217 | 0.0197 | 0.0012 | 0 | 3 | 0.013 | 0.023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
433 | 1685.341 | 44265.9408 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.3565 | 0:240:120 | 0:00 | 0.0125 | 7 | 0.0036 | 0.0175 | 0.0211 | 0.0195 | 0.0014 | 0 | 3 | 0.0125 | 0.0225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
436 | 1688.719 | 44265.9408 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 300.2436 | 0:240:120 | 0:00 | 0.012 | 7 | 0.0029 | 0.0181 | 0.021 | 0.0192 | 0.0012 | 0 | 3 | 0.012 | 0.022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
439 | 1691.96 | 44265.9409 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 306.2485 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0021 | 0.0177 | 0.0198 | 0.0187 | 0.0007 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
442 | 1695.276 | 44265.9409 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 312.3735 | 0:240:120 | 0:00 | 0.0111 | 7 | 0.0012 | 0.0181 | 0.0193 | 0.0186 | 0.0004 | 0 | 3 | 0.0111 | 0.0211 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
445 | 1698.543 | 44265.9409 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 318.621 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0012 | 0.0174 | 0.0186 | 0.0177 | 0.0005 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
448 | 1701.733 | 44265.941 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 324.9934 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.0018 | 0.0159 | 0.0177 | 0.0171 | 0.0006 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
451 | 1705.072 | 44265.941 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 328.6274 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0014 | 0.0164 | 0.0178 | 0.0171 | 0.0006 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
454 | 1708.295 | 44265.9411 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 335.2 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0016 | 0.0156 | 0.0172 | 0.0167 | 0.0005 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-1-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
457 | 1711.651 | 44265.9411 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 341.904 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0031 | 0.0148 | 0.0179 | 0.0162 | 0.0014 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 1-1-0-1-0-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
460 | 1715.061 | 44265.9411 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 348.7421 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0025 | 0.015 | 0.0175 | 0.0161 | 0.0008 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 1-0-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
463 | 1718.401 | 44265.9412 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 355.7169 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0041 | 0.0137 | 0.0178 | 0.0155 | 0.0014 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
466 | 1721.714 | 44265.9412 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 362.8313 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0035 | 0.0136 | 0.0171 | 0.0152 | 0.0013 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
469 | 1725.129 | 44265.9412 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 370.0879 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0038 | 0.0132 | 0.017 | 0.015 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
472 | 1728.345 | 44265.9413 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 377.4896 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0041 | 0.0133 | 0.0174 | 0.0149 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
475 | 1731.621 | 44265.9413 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 385.0394 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0041 | 0.0126 | 0.0167 | 0.0149 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
478 | 1735.233 | 44265.9414 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 392.7402 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0041 | 0.012 | 0.0161 | 0.0141 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
481 | 1738.655 | 44265.9414 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 400.595 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0057 | 0.0116 | 0.0173 | 0.0142 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
484 | 1741.979 | 44265.9414 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 408.6069 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0051 | 0.0121 | 0.0172 | 0.0142 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
487 | 1745.44 | 44265.9415 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 416.7791 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0038 | 0.0123 | 0.0161 | 0.0141 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
490 | 1748.872 | 44265.9415 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 425.1146 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0057 | 0.0113 | 0.017 | 0.0137 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
493 | 1752.198 | 44265.9416 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 433.6169 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0054 | 0.0117 | 0.0171 | 0.0138 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
496 | 1755.674 | 44265.9416 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 442.2893 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0046 | 0.0114 | 0.016 | 0.0139 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
499 | 1759.071 | 44265.9416 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 451.1351 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0036 | 0.0119 | 0.0155 | 0.0136 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
502 | 1762.459 | 44265.9417 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 460.1578 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0046 | 0.0109 | 0.0155 | 0.0133 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
505 | 1765.912 | 44265.9417 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 469.3609 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0046 | 0.0106 | 0.0152 | 0.0132 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
508 | 1769.426 | 44265.9418 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 478.7481 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0052 | 0.0108 | 0.016 | 0.0133 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
511 | 1772.887 | 44265.9418 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 488.3231 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0043 | 0.0108 | 0.0151 | 0.0131 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
514 | 1776.189 | 44265.9418 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 498.0896 | 0:240:120 | 0:00 | 0.0043 | 7 | 0.0051 | 0.0103 | 0.0154 | 0.0132 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
517 | 1779.457 | 44265.9419 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 508.0514 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.004 | 0.0108 | 0.0148 | 0.0128 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
520 | 1782.833 | 44265.9419 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 518.2124 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0052 | 0.0105 | 0.0157 | 0.0132 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
523 | 1786.282 | 44265.942 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 528.5766 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0046 | 0.0106 | 0.0152 | 0.0127 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
526 | 1789.785 | 44265.942 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 539.1482 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0049 | 0.0101 | 0.015 | 0.0126 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
529 | 1793.14 | 44265.942 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 549.9311 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0049 | 0.0102 | 0.0151 | 0.0125 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
532 | 1796.449 | 44265.9421 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 560.9297 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0035 | 0.0109 | 0.0144 | 0.0123 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
535 | 1799.844 | 44265.9421 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 572.1483 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0052 | 0.0099 | 0.0151 | 0.0119 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
538 | 1803.315 | 44265.9422 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 583.5913 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0028 | 0.0104 | 0.0132 | 0.0115 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
541 | 1806.78 | 44265.9422 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 595.2631 | 0:240:120 | 0:00 | 0.003 | 7 | 0.003 | 0.0102 | 0.0132 | 0.0115 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
544 | 1810.228 | 44265.9422 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 607.1684 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0052 | 0.0099 | 0.0151 | 0.0118 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
547 | 1813.67 | 44265.9423 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 619.3118 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0042 | 0.0094 | 0.0136 | 0.011 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
550 | 1817.061 | 44265.9423 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 631.698 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0053 | 0.0099 | 0.0152 | 0.0121 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
553 | 1820.529 | 44265.9424 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 644.332 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0017 | 0.0104 | 0.0121 | 0.0111 | 0.0006 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
556 | 1823.976 | 44265.9424 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 657.2186 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0056 | 0.0095 | 0.0151 | 0.0112 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
559 | 1827.245 | 44265.9424 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 657.2549 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.003 | 0.0091 | 0.0121 | 0.0105 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
562 | 1830.696 | 44265.9425 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 670.4 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0047 | 0.0097 | 0.0144 | 0.0112 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
565 | 1834.179 | 44265.9425 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 683.808 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0042 | 0.009 | 0.0132 | 0.0109 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
568 | 1837.639 | 44265.9425 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 697.4842 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0029 | 0.0093 | 0.0122 | 0.0106 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
571 | 1841.05 | 44265.9426 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 711.4338 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0032 | 0.0094 | 0.0126 | 0.0104 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
574 | 1844.499 | 44265.9426 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 725.6625 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0032 | 0.0095 | 0.0127 | 0.0106 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
577 | 1847.91 | 44265.9427 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 740.1758 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0028 | 0.0094 | 0.0122 | 0.0108 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
580 | 1851.294 | 44265.9427 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 754.9793 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0047 | 0.0095 | 0.0142 | 0.011 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
583 | 1854.724 | 44265.9427 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 770.0789 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0029 | 0.0094 | 0.0123 | 0.0104 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
586 | 1858.178 | 44265.9428 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 785.4804 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0021 | 0.0098 | 0.0119 | 0.0105 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
589 | 1861.665 | 44265.9428 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 801.1901 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0013 | 0.0102 | 0.0115 | 0.0107 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
592 | 1865.125 | 44265.9429 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 817.2139 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0023 | 0.0094 | 0.0117 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
595 | 1868.509 | 44265.9429 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 833.5581 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
598 | 1871.73 | 44265.9429 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 850.2293 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0016 | 0.0099 | 0.0115 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
601 | 1875.174 | 44265.943 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 867.2339 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0026 | 0.0089 | 0.0115 | 0.0101 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
604 | 1878.571 | 44265.943 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 884.5786 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0005 | 0.0098 | 0.0103 | 0.01 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
607 | 1881.95 | 44265.9431 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 902.2701 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0024 | 0.0092 | 0.0116 | 0.0105 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
610 | 1885.078 | 44265.9431 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 920.3155 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0026 | 0.0091 | 0.0117 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
613 | 1888.536 | 44265.9431 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 938.7218 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0018 | 0.0099 | 0.0117 | 0.0107 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
616 | 1891.873 | 44265.9432 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 957.4963 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0019 | 0.0095 | 0.0114 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
619 | 1895.262 | 44265.9432 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 976.6462 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
622 | 1898.713 | 44265.9433 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 996.1791 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.001 | 0.0096 | 0.0106 | 0.0101 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
625 | 1902.039 | 44265.9433 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1016.1027 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0017 | 0.0099 | 0.0116 | 0.0105 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
628 | 1905.461 | 44265.9433 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1036.4248 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
631 | 1908.925 | 44265.9434 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1057.1533 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
634 | 1912.305 | 44265.9434 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1078.2963 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0015 | 0.0098 | 0.0113 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
637 | 1915.798 | 44265.9435 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1099.8623 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0021 | 0.0094 | 0.0115 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
640 | 1919.26 | 44265.9435 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1121.8595 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0012 | 0.0096 | 0.0108 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
643 | 1922.588 | 44265.9435 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1144.2967 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0012 | 0.0101 | 0.0113 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
646 | 1926.114 | 44265.9436 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1167.1826 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0018 | 0.0097 | 0.0115 | 0.0105 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
649 | 1929.701 | 44265.9436 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1190.5263 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0018 | 0.0097 | 0.0115 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
652 | 1933.299 | 44265.9437 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1214.3368 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
655 | 1936.878 | 44265.9437 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1238.6235 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0025 | 0.0089 | 0.0114 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
658 | 1940.402 | 44265.9437 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1263.396 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.001 | 0.0096 | 0.0106 | 0.0101 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
661 | 1943.85 | 44265.9438 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1288.6639 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
664 | 1947.307 | 44265.9438 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1314.4372 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0015 | 0.0097 | 0.0112 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
667 | 1950.772 | 44265.9439 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1340.7259 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0012 | 0.0102 | 0.0114 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
670 | 1954.096 | 44265.9439 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1367.5405 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0007 | 0.0099 | 0.0106 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
673 | 1957.615 | 44265.9439 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1394.8913 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0012 | 0.0097 | 0.0109 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
676 | 1960.958 | 44265.944 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1422.7891 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0015 | 0.0093 | 0.0108 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
679 | 1964.266 | 44265.944 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1451.2449 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0022 | 0.009 | 0.0112 | 0.0097 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
682 | 1967.666 | 44265.9441 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1480.2698 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
685 | 1971.105 | 44265.9441 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1509.8752 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0012 | 0.0093 | 0.0105 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
688 | 1974.545 | 44265.9441 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1540.0727 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0097 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
691 | 1977.886 | 44265.9442 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1570.8741 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0011 | 0.01 | 0.0111 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
694 | 1981.45 | 44265.9442 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1602.2916 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.002 | 0.009 | 0.011 | 0.0097 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
697 | 1984.887 | 44265.9443 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1634.3374 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0008 | 0.01 | 0.0108 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
700 | 1988.004 | 44265.9443 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1667.0242 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0009 | 0.0097 | 0.0106 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
703 | 1991.493 | 44265.9443 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1700.3647 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0009 | 0.0096 | 0.0105 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
706 | 1994.933 | 44265.9444 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1734.372 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0016 | 0.009 | 0.0106 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
709 | 1998.441 | 44265.9444 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1769.0594 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0013 | 0.0096 | 0.0109 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
712 | 2001.793 | 44265.9444 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1804.4406 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
715 | 2005.237 | 44265.9445 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1840.5294 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0018 | 0.0088 | 0.0106 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
718 | 2008.629 | 44265.9445 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1877.34 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
721 | 2012.111 | 44265.9446 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1914.8868 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.0096 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
724 | 2015.35 | 44265.9446 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1953.1845 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
727 | 2018.872 | 44265.9446 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1992.2482 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0011 | 0.0089 | 0.01 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
730 | 2022.178 | 44265.9447 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2032.0932 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
733 | 2025.773 | 44265.9447 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2072.7351 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0021 | 0.009 | 0.0111 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
736 | 2029.321 | 44265.9448 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2114.1898 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0023 | 0.009 | 0.0113 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
739 | 2032.879 | 44265.9448 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2156.4736 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.0093 | 0.011 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
742 | 2036.187 | 44265.9448 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2199.603 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.001 | 0.0097 | 0.0107 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
745 | 2039.695 | 44265.9449 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2243.5951 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
748 | 2043.189 | 44265.9449 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2288.467 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0018 | 0.0093 | 0.0111 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
751 | 2046.667 | 44265.945 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2334.2363 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0018 | 0.0095 | 0.0113 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
754 | 2050.099 | 44265.945 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2380.9211 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
757 | 2053.386 | 44265.945 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2428.5395 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
760 | 2056.806 | 44265.9451 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2477.1103 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
763 | 2060.236 | 44265.9451 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2526.6525 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.001 | 0.0096 | 0.0106 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
766 | 2063.731 | 44265.9452 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2577.1855 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
769 | 2067.215 | 44265.9452 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2628.7292 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
772 | 2070.615 | 44265.9452 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2681.3038 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0005 | 0.0103 | 0.0108 | 0.0105 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
775 | 2074.095 | 44265.9453 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2734.9299 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0096 | 0.0108 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
778 | 2077.59 | 44265.9453 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2789.6285 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
781 | 2081.028 | 44265.9454 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2845.4211 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0009 | 0.0098 | 0.0107 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
784 | 2084.434 | 44265.9454 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2902.3295 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0007 | 0.0093 | 0.01 | 0.0097 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
787 | 2087.852 | 44265.9454 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2960.3761 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0088 | 0.0099 | 0.0094 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
790 | 2091.355 | 44265.9455 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3019.5836 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0009 | 0.0094 | 0.0103 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
793 | 2094.804 | 44265.9455 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3079.9753 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.002 | 0.0092 | 0.0112 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
796 | 2098.379 | 44265.9456 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3141.5748 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0094 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
799 | 2101.898 | 44265.9456 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3204.4063 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0094 | 0.011 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
802 | 2105.429 | 44265.9456 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3268.4944 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
805 | 2109.022 | 44265.9457 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3333.8643 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0021 | 0.0091 | 0.0112 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
808 | 2112.513 | 44265.9457 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3400.5416 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0088 | 0.0104 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
811 | 2116.159 | 44265.9458 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3468.5524 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0089 | 0.0101 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
814 | 2119.828 | 44265.9458 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3537.9234 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
817 | 2123.212 | 44265.9459 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3608.6819 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
820 | 2126.584 | 44265.9459 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3680.8555 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
823 | 2129.853 | 44265.9459 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3754.4727 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
826 | 2133.493 | 44265.946 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3829.5621 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
829 | 2136.973 | 44265.946 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3906.1534 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.001 | 0.0093 | 0.0103 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
832 | 2140.466 | 44265.9461 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3984.2764 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
835 | 2143.928 | 44265.9461 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4063.9619 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
838 | 2147.419 | 44265.9461 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4145.2412 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
841 | 2150.889 | 44265.9462 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4228.146 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
844 | 2154.243 | 44265.9462 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4312.7089 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
847 | 2157.508 | 44265.9463 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4398.9631 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0018 | 0.0089 | 0.0107 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
850 | 2161.057 | 44265.9463 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4486.9424 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.001 | 0.0099 | 0.0109 | 0.0103 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
853 | 2164.405 | 44265.9463 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4576.6812 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0009 | 0.0099 | 0.0108 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
856 | 2167.882 | 44265.9464 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4668.2148 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0088 | 0.0099 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
859 | 2171.456 | 44265.9464 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4761.5791 | 0:240:120 | 0:00 | 0 | 7 | 0.001 | 0.0098 | 0.0108 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
862 | 2174.953 | 44265.9465 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4856.8107 | 0:240:120 | 0:00 | 0 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
865 | 2178.546 | 44265.9465 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4953.9469 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
868 | 2181.857 | 44265.9465 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5053.0259 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
871 | 2185.537 | 44265.9466 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5154.0864 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.01 | 0.0112 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
874 | 2189.118 | 44265.9466 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5257.1681 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0096 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
877 | 2192.605 | 44265.9467 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5362.3115 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0101 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
880 | 2196.112 | 44265.9467 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5469.5577 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
883 | 2199.497 | 44265.9467 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5578.9489 | 0:240:120 | 0:00 | 0 | 7 | 0.001 | 0.01 | 0.011 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
886 | 2202.975 | 44265.9468 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5690.5278 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
889 | 2206.431 | 44265.9468 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5804.3384 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0088 | 0.0099 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
892 | 2209.698 | 44265.9469 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5920.4252 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
895 | 2213.175 | 44265.9469 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6038.8337 | 0:240:120 | 0:00 | 0 | 7 | 0.0009 | 0.0097 | 0.0106 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
898 | 2216.556 | 44265.9469 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6159.6103 | 0:240:120 | 0:00 | 0 | 7 | 0.0005 | 0.0092 | 0.0097 | 0.0095 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
901 | 2219.912 | 44265.947 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6282.8026 | 0:240:120 | 0:00 | 0 | 7 | 0.0021 | 0.0089 | 0.011 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
904 | 2223.613 | 44265.947 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6408.4586 | 0:240:120 | 0:00 | 0 | 7 | 0.0014 | 0.0091 | 0.0105 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
907 | 2227.091 | 44265.9471 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6536.6278 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
910 | 2230.679 | 44265.9471 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6667.3603 | 0:240:120 | 0:00 | 0 | 7 | 0.0015 | 0.0097 | 0.0112 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
913 | 2234.239 | 44265.9471 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6800.7075 | 0:240:120 | 0:00 | 0 | 7 | 0.0008 | 0.0094 | 0.0102 | 0.0098 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
916 | 2237.756 | 44265.9472 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6936.7217 | 0:240:120 | 0:00 | 0 | 7 | 0.002 | 0.0091 | 0.0111 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
919 | 2241.15 | 44265.9472 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7075.4561 | 0:240:120 | 0:00 | 0 | 7 | 0.002 | 0.0091 | 0.0111 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
922 | 2244.623 | 44265.9473 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7216.9652 | 0:240:120 | 0:00 | 0 | 7 | 0.0003 | 0.0093 | 0.0096 | 0.0095 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
925 | 2248.107 | 44265.9473 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7361.3046 | 0:240:120 | 0:00 | 0 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
928 | 2251.693 | 44265.9473 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7508.5306 | 0:240:120 | 0:00 | 0 | 7 | 0.002 | 0.009 | 0.011 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
931 | 2255.117 | 44265.9474 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7658.7013 | 0:240:120 | 0:00 | 0 | 7 | 0.0016 | 0.0094 | 0.011 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
934 | 2258.591 | 44265.9474 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7811.8753 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.0089 | 0.0101 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
937 | 2262.094 | 44265.9475 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7968.1128 | 0:240:120 | 0:00 | 0 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
940 | 2265.634 | 44265.9475 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8127.475 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
943 | 2269.212 | 44265.9475 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8290.0245 | 0:240:120 | 0:00 | 0 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
946 | 2272.779 | 44265.9476 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8455.825 | 0:240:120 | 0:00 | 0 | 7 | 0.001 | 0.0091 | 0.0101 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
949 | 2276.062 | 44265.9476 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8624.9415 | 0:240:120 | 0:00 | 0 | 7 | 0.0015 | 0.0089 | 0.0104 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
952 | 2279.813 | 44265.9477 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8797.4404 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
955 | 2283.105 | 44265.9477 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8973.3892 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
958 | 2286.432 | 44265.9477 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9152.857 | 0:240:120 | 0:00 | 0 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
961 | 2289.938 | 44265.9478 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9335.9141 | 0:240:120 | 0:00 | 0 | 7 | 0.001 | 0.0091 | 0.0101 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
964 | 2293.474 | 44265.9478 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9522.6324 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.0089 | 0.0101 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
967 | 2296.752 | 44265.9479 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9713.085 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.0089 | 0.0101 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
970 | 2300.2 | 44265.9479 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9907.3467 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
973 | 2303.589 | 44265.9479 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10105.4937 | 0:240:120 | 0:00 | 0 | 7 | 0.0001 | 0.0104 | 0.0105 | 0.0105 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
976 | 2307.063 | 44265.948 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10307.6035 | 0:240:120 | 0:00 | 0 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
979 | 2310.375 | 44265.948 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10513.7556 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
982 | 2313.939 | 44265.9481 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10724.0307 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
985 | 2317.247 | 44265.9481 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10938.5113 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.0093 | 0.0105 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
988 | 2320.834 | 44265.9481 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11157.2816 | 0:240:120 | 0:00 | 0 | 7 | 0.0008 | 0.0092 | 0.01 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
991 | 2324.274 | 44265.9482 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11380.4272 | 0:240:120 | 0:00 | 0 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
994 | 2327.867 | 44265.9482 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11608.0357 | 0:240:120 | 0:00 | 0 | 7 | 0.0006 | 0.01 | 0.0106 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
997 | 2331.292 | 44265.9483 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11840.1964 | 0:240:120 | 0:00 | 0 | 7 | 0.0005 | 0.0101 | 0.0106 | 0.0103 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1000 | 2360.941 | 44265.9486 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 17.5 | 0:240:120 | 0:00 | 9.7778 | 7 | 2.9886 | 23.6939 | 26.6825 | 24.7243 | 1.3185 | 1.7385 | 3 | 9.7778 | 75.6491 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1003 | 2439.707 | 44265.9495 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 17.9 | 0:240:120 | 0:00 | 8.6649 | 7 | 2.3063 | 20.0423 | 22.3486 | 20.9422 | 1.0523 | 1.1074 | 3 | 8.6649 | 41.4456 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1006 | 2507.352 | 44265.9503 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 18.2 | 0:240:120 | 0:00 | 7.971 | 7 | 2.2162 | 17.4261 | 19.6423 | 18.2208 | 1.0453 | 1.0927 | 3 | 7.971 | 30.7648 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1009 | 2565.816 | 44265.951 | Vista Speed | E | 7E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 18.6 | 0:240:120 | 0:00 | 7.1886 | 7 | 2.6187 | 13.2857 | 15.9044 | 14.3236 | 1.1856 | 1.4056 | 3 | 7.1886 | 22.7618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1012 | 2798.608 | 44265.9537 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23 | 0:240:120 | 0:00 | 17.0543 | 7 | 47.733 | 149.8322 | 197.5652 | 168.4914 | 21.7871 | 474.6793 | 3 | 17.0543 | Inf | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1015 | 3333.72 | 44265.9599 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.46 | 0:240:120 | 0:00 | 14.6304 | 7 | 41.9286 | 95.0214 | 136.95 | 111.6562 | 18.9132 | 357.7086 | 3 | 14.6304 | 118.2059 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1018 | 3691.656 | 44265.964 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.9292 | 0:240:120 | 0:00 | 12.7457 | 7 | 44.6917 | 37.4164 | 82.1081 | 56.7794 | 19.2348 | 369.9789 | 3 | 12.7457 | 57.8469 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1021 | 3885.626 | 44265.9663 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.4078 | 0:240:120 | 0:00 | 11.2394 | 7 | 3.2809 | 23.5932 | 26.8741 | 24.9519 | 1.363 | 1.8577 | 3 | 11.2394 | 37.7402 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1024 | 3965.446 | 44265.9672 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.8959 | 0:240:120 | 0:00 | 10.0087 | 7 | 2.6101 | 20.4763 | 23.0864 | 21.5375 | 1.1692 | 1.3669 | 3 | 10.0087 | 27.6966 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1027 | 4034.212 | 44265.968 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.3939 | 0:240:120 | 0:00 | 8.9852 | 7 | 2.434 | 17.0998 | 19.5338 | 18.1146 | 1.0681 | 1.1408 | 3 | 8.9852 | 21.6781 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1030 | 4093.019 | 44265.9687 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.9017 | 0:240:120 | 0:00 | 8.1211 | 7 | 2.9212 | 13.5818 | 16.503 | 14.7806 | 1.3007 | 1.6918 | 3 | 8.1211 | 17.6722 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1033 | 4142.177 | 44265.9692 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.4198 | 0:240:120 | 0:00 | 7.3824 | 7 | 1.2334 | 11.6199 | 12.8533 | 12.1934 | 0.5025 | 0.2525 | 3 | 7.3824 | 14.8162 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1036 | 4182.94 | 44265.9697 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.9482 | 0:240:120 | 0:00 | 6.7443 | 7 | 0.9848 | 10.5458 | 11.5306 | 10.9675 | 0.43 | 0.1849 | 3 | 6.7443 | 12.679 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1039 | 4219.526 | 44265.9701 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 27.4871 | 0:240:120 | 0:00 | 6.1877 | 7 | 0.9739 | 9.291 | 10.2649 | 9.7466 | 0.407 | 0.1657 | 3 | 6.1877 | 11.021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1042 | 4252.42 | 44265.9705 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.0369 | 0:240:120 | 0:00 | 5.6985 | 7 | 1.0227 | 8.0781 | 9.1008 | 8.5242 | 0.4235 | 0.1794 | 3 | 5.6985 | 9.6983 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1045 | 4281.692 | 44265.9708 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.5976 | 0:240:120 | 0:00 | 5.2654 | 7 | 0.5201 | 7.4397 | 7.9598 | 7.6547 | 0.231 | 0.0533 | 3 | 5.2654 | 8.6194 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1048 | 4308.156 | 44265.9711 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.1696 | 0:240:120 | 0:00 | 4.8795 | 7 | 0.5239 | 6.7885 | 7.3124 | 7.0345 | 0.2221 | 0.0493 | 3 | 4.8795 | 7.7235 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1051 | 4332.815 | 44265.9714 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.753 | 0:240:120 | 0:00 | 4.5339 | 7 | 0.5316 | 6.156 | 6.6876 | 6.4032 | 0.223 | 0.0497 | 3 | 4.5339 | 6.9682 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1054 | 4355.408 | 44265.9717 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.348 | 0:240:120 | 0:00 | 4.2226 | 7 | 0.4327 | 5.6004 | 6.0331 | 5.7877 | 0.188 | 0.0354 | 3 | 4.2226 | 6.3582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1057 | 4376.338 | 44265.9719 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.955 | 0:240:120 | 0:00 | 3.9412 | 7 | 0.2513 | 5.2684 | 5.5197 | 5.3765 | 0.109 | 0.0119 | 3 | 3.9412 | 5.8487 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1060 | 4396.016 | 44265.9722 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.5741 | 0:240:120 | 0:00 | 3.6856 | 7 | 0.3196 | 4.8632 | 5.1828 | 4.9992 | 0.1372 | 0.0188 | 3 | 3.6856 | 5.3987 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1063 | 4414.654 | 44265.9724 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.2056 | 0:240:120 | 0:00 | 3.4526 | 7 | 0.3266 | 4.4668 | 4.7934 | 4.6036 | 0.1437 | 0.0206 | 3 | 3.4526 | 4.9985 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1066 | 4432.058 | 44265.9726 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.8497 | 0:240:120 | 0:00 | 3.2396 | 7 | 0.2137 | 4.187 | 4.4007 | 4.2763 | 0.0929 | 0.0086 | 3 | 3.2396 | 4.6407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1069 | 4448.155 | 44265.9728 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.5067 | 0:240:120 | 0:00 | 3.0442 | 7 | 0.2081 | 3.9306 | 4.1387 | 4.0131 | 0.0941 | 0.0089 | 3 | 3.0442 | 4.3189 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1072 | 4463.527 | 44265.9729 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.1768 | 0:240:120 | 0:00 | 2.8644 | 7 | 0.2189 | 3.652 | 3.8709 | 3.7458 | 0.0955 | 0.0091 | 3 | 2.8644 | 4.0284 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1075 | 4478.149 | 44265.9731 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.8603 | 0:240:120 | 0:00 | 2.6986 | 7 | 0.1844 | 3.4198 | 3.6042 | 3.4983 | 0.0813 | 0.0066 | 3 | 2.6986 | 3.7649 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1078 | 4492.082 | 44265.9733 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.5575 | 0:240:120 | 0:00 | 2.5453 | 7 | 0.1626 | 3.2213 | 3.3839 | 3.2868 | 0.0735 | 0.0054 | 3 | 2.5453 | 3.525 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1081 | 4505.327 | 44265.9734 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.2687 | 0:240:120 | 0:00 | 2.4033 | 7 | 0.1537 | 3.0239 | 3.1776 | 3.084 | 0.0693 | 0.0048 | 3 | 2.4033 | 3.3058 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1084 | 4518.264 | 44265.9736 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.9941 | 0:240:120 | 0:00 | 2.2714 | 7 | 0.1357 | 2.841 | 2.9767 | 2.8966 | 0.0601 | 0.0036 | 3 | 2.2714 | 3.105 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1087 | 4530.38 | 44265.9737 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.7339 | 0:240:120 | 0:00 | 2.1488 | 7 | 0.1292 | 2.6863 | 2.8155 | 2.7407 | 0.0575 | 0.0033 | 3 | 2.1488 | 2.9204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1090 | 4541.835 | 44265.9738 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.4886 | 0:240:120 | 0:00 | 2.0344 | 7 | 0.1164 | 2.5317 | 2.6481 | 2.5766 | 0.0529 | 0.0028 | 3 | 2.0344 | 2.7503 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1093 | 4552.857 | 44265.974 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.2584 | 0:240:120 | 0:00 | 1.9278 | 7 | 0.102 | 2.3931 | 2.4951 | 2.43 | 0.0483 | 0.0023 | 3 | 1.9278 | 2.5931 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1096 | 4563.61 | 44265.9741 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.0436 | 0:240:120 | 0:00 | 1.828 | 7 | 0.0951 | 2.2611 | 2.3562 | 2.3007 | 0.042 | 0.0018 | 3 | 1.828 | 2.4476 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1099 | 4573.637 | 44265.9742 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.8444 | 0:240:120 | 0:00 | 1.7347 | 7 | 0.0928 | 2.1377 | 2.2305 | 2.1719 | 0.0429 | 0.0018 | 3 | 1.7347 | 2.3126 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1102 | 4583.608 | 44265.9743 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.6613 | 0:240:120 | 0:00 | 1.6471 | 7 | 0.0796 | 2.0267 | 2.1063 | 2.0579 | 0.0364 | 0.0013 | 3 | 1.6471 | 2.1871 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1105 | 4593.041 | 44265.9744 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.4945 | 0:240:120 | 0:00 | 1.565 | 7 | 0.0813 | 1.9203 | 2.0016 | 1.9511 | 0.0377 | 0.0014 | 3 | 1.565 | 2.0702 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1108 | 4602.478 | 44265.9745 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.3444 | 0:240:120 | 0:00 | 1.4878 | 7 | 0.0766 | 1.8177 | 1.8943 | 1.8464 | 0.0353 | 0.0012 | 3 | 1.4878 | 1.9612 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1111 | 4611.742 | 44265.9747 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.2113 | 0:240:120 | 0:00 | 1.4151 | 7 | 0.0645 | 1.7305 | 1.795 | 1.7552 | 0.0293 | 0.0009 | 3 | 1.4151 | 1.8593 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1114 | 4620.653 | 44265.9748 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.0955 | 0:240:120 | 0:00 | 1.3467 | 7 | 0.0693 | 1.637 | 1.7063 | 1.6658 | 0.0305 | 0.0009 | 3 | 1.3467 | 1.7639 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1117 | 4628.851 | 44265.9749 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.9975 | 0:240:120 | 0:00 | 1.2822 | 7 | 0.0553 | 1.5608 | 1.6161 | 1.581 | 0.0262 | 0.0007 | 3 | 1.2822 | 1.6746 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1120 | 4636.863 | 44265.9749 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.9174 | 0:240:120 | 0:00 | 1.2214 | 7 | 0.0591 | 1.4843 | 1.5434 | 1.5068 | 0.0266 | 0.0007 | 3 | 1.2214 | 1.5907 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1123 | 4644.749 | 44265.975 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.8558 | 0:240:120 | 0:00 | 1.1639 | 7 | 0.0593 | 1.4085 | 1.4678 | 1.4311 | 0.0271 | 0.0007 | 3 | 1.1639 | 1.512 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1126 | 4652.382 | 44265.9751 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.8129 | 0:240:120 | 0:00 | 1.1096 | 7 | 0.0467 | 1.3441 | 1.3908 | 1.3622 | 0.0214 | 0.0005 | 3 | 1.1096 | 1.4379 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1129 | 4659.852 | 44265.9752 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.7891 | 0:240:120 | 0:00 | 1.0582 | 7 | 0.05 | 1.2776 | 1.3276 | 1.2969 | 0.0228 | 0.0005 | 3 | 1.0582 | 1.3682 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1132 | 4666.97 | 44265.9753 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.7849 | 0:240:120 | 0:00 | 1.0096 | 7 | 0.0375 | 1.2235 | 1.261 | 1.2364 | 0.0177 | 0.0003 | 3 | 1.0096 | 1.3025 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1135 | 4674.001 | 44265.9754 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.8006 | 0:240:120 | 0:00 | 0.9635 | 7 | 0.0414 | 1.1634 | 1.2048 | 1.1785 | 0.0192 | 0.0004 | 3 | 0.9635 | 1.2405 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1138 | 4680.855 | 44265.9755 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.8366 | 0:240:120 | 0:00 | 0.9198 | 7 | 0.0364 | 1.1098 | 1.1462 | 1.1238 | 0.0168 | 0.0003 | 3 | 0.9198 | 1.182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1141 | 4687.504 | 44265.9755 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.8934 | 0:240:120 | 0:00 | 0.8784 | 7 | 0.0378 | 1.0563 | 1.0941 | 1.0715 | 0.0166 | 0.0003 | 3 | 0.8784 | 1.1267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1144 | 4694.092 | 44265.9756 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.9712 | 0:240:120 | 0:00 | 0.8391 | 7 | 0.0324 | 1.0104 | 1.0428 | 1.0224 | 0.0144 | 0.0002 | 3 | 0.8391 | 1.0744 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1147 | 4700.581 | 44265.9757 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.0706 | 0:240:120 | 0:00 | 0.8018 | 7 | 0.0313 | 0.9641 | 0.9954 | 0.9758 | 0.0144 | 0.0002 | 3 | 0.8018 | 1.0249 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1150 | 4707.121 | 44265.9758 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.1921 | 0:240:120 | 0:00 | 0.7663 | 7 | 0.0289 | 0.9205 | 0.9494 | 0.9316 | 0.0131 | 0.0002 | 3 | 0.7663 | 0.978 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1153 | 4713.375 | 44265.9758 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.3359 | 0:240:120 | 0:00 | 0.7326 | 7 | 0.0306 | 0.8777 | 0.9083 | 0.8886 | 0.0144 | 0.0002 | 3 | 0.7326 | 0.9336 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1156 | 4719.336 | 44265.9759 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.5026 | 0:240:120 | 0:00 | 0.7005 | 7 | 0.0261 | 0.8405 | 0.8666 | 0.8492 | 0.0123 | 0.0002 | 3 | 0.7005 | 0.8915 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1159 | 4725.432 | 44265.976 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.6927 | 0:240:120 | 0:00 | 0.67 | 7 | 0.025 | 0.8021 | 0.8271 | 0.8109 | 0.0118 | 0.0001 | 3 | 0.67 | 0.8515 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1162 | 4731.326 | 44265.976 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.9065 | 0:240:120 | 0:00 | 0.6409 | 7 | 0.025 | 0.7666 | 0.7916 | 0.7759 | 0.011 | 0.0001 | 3 | 0.6409 | 0.8135 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1165 | 4736.919 | 44265.9761 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.1447 | 0:240:120 | 0:00 | 0.6133 | 7 | 0.0223 | 0.7341 | 0.7564 | 0.7421 | 0.0105 | 0.0001 | 3 | 0.6133 | 0.7775 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1168 | 4742.541 | 44265.9762 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.4075 | 0:240:120 | 0:00 | 0.5869 | 7 | 0.0223 | 0.7019 | 0.7242 | 0.7104 | 0.0096 | 0.0001 | 3 | 0.5869 | 0.7432 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1171 | 4747.766 | 44265.9762 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.6957 | 0:240:120 | 0:00 | 0.5618 | 7 | 0.019 | 0.6708 | 0.6898 | 0.6781 | 0.0087 | 0.0001 | 3 | 0.5618 | 0.7106 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1174 | 4753.108 | 44265.9763 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.0096 | 0:240:120 | 0:00 | 0.5379 | 7 | 0.02 | 0.6419 | 0.6619 | 0.649 | 0.0094 | 0.0001 | 3 | 0.5379 | 0.6796 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1177 | 4758.309 | 44265.9764 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.3498 | 0:240:120 | 0:00 | 0.515 | 7 | 0.0188 | 0.6143 | 0.6331 | 0.6209 | 0.0087 | 0.0001 | 3 | 0.515 | 0.6501 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1180 | 4763.26 | 44265.9764 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.7168 | 0:240:120 | 0:00 | 0.4932 | 7 | 0.0175 | 0.5877 | 0.6052 | 0.5941 | 0.008 | 0.0001 | 3 | 0.4932 | 0.622 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1183 | 4768.552 | 44265.9765 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.1111 | 0:240:120 | 0:00 | 0.4724 | 7 | 0.0175 | 0.5624 | 0.5799 | 0.5688 | 0.008 | 0.0001 | 3 | 0.4724 | 0.5952 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1186 | 4773.536 | 44265.9765 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.5334 | 0:240:120 | 0:00 | 0.4526 | 7 | 0.016 | 0.5387 | 0.5547 | 0.5447 | 0.0074 | 0.0001 | 3 | 0.4526 | 0.5697 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1189 | 4778.524 | 44265.9766 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.984 | 0:240:120 | 0:00 | 0.4336 | 7 | 0.0153 | 0.5155 | 0.5308 | 0.5216 | 0.0068 | 0 | 3 | 0.4336 | 0.5454 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1192 | 4783.14 | 44265.9766 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.4637 | 0:240:120 | 0:00 | 0.4155 | 7 | 0.0144 | 0.4943 | 0.5087 | 0.4997 | 0.0066 | 0 | 3 | 0.4155 | 0.5222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1195 | 4787.907 | 44265.9767 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.973 | 0:240:120 | 0:00 | 0.3982 | 7 | 0.0141 | 0.4735 | 0.4876 | 0.4791 | 0.0061 | 0 | 3 | 0.3982 | 0.5001 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1198 | 4792.615 | 44265.9767 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.5124 | 0:240:120 | 0:00 | 0.3817 | 7 | 0.0149 | 0.4523 | 0.4672 | 0.4581 | 0.0063 | 0 | 3 | 0.3817 | 0.479 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1201 | 4797.357 | 44265.9768 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.0827 | 0:240:120 | 0:00 | 0.3659 | 7 | 0.0142 | 0.4327 | 0.4469 | 0.4385 | 0.0062 | 0 | 3 | 0.3659 | 0.4588 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1204 | 4802.193 | 44265.9769 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.6843 | 0:240:120 | 0:00 | 0.3507 | 7 | 0.0117 | 0.4163 | 0.428 | 0.4205 | 0.0054 | 0 | 3 | 0.3507 | 0.4396 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1207 | 4806.677 | 44265.9769 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.318 | 0:240:120 | 0:00 | 0.3363 | 7 | 0.0114 | 0.3988 | 0.4102 | 0.403 | 0.005 | 0 | 3 | 0.3363 | 0.4212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1210 | 4811.36 | 44265.977 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.9844 | 0:240:120 | 0:00 | 0.3225 | 7 | 0.0113 | 0.3825 | 0.3938 | 0.3864 | 0.005 | 0 | 3 | 0.3225 | 0.4037 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1213 | 4815.954 | 44265.977 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.6841 | 0:240:120 | 0:00 | 0.3092 | 7 | 0.0109 | 0.366 | 0.3769 | 0.3702 | 0.0048 | 0 | 3 | 0.3092 | 0.3869 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1216 | 4820.336 | 44265.9771 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.4178 | 0:240:120 | 0:00 | 0.2966 | 7 | 0.0116 | 0.3508 | 0.3624 | 0.3554 | 0.0052 | 0 | 3 | 0.2966 | 0.3708 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1219 | 4824.809 | 44265.9771 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.1861 | 0:240:120 | 0:00 | 0.2845 | 7 | 0.0093 | 0.3372 | 0.3465 | 0.3408 | 0.0043 | 0 | 3 | 0.2845 | 0.3555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1222 | 4829.322 | 44265.9772 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.9898 | 0:240:120 | 0:00 | 0.2729 | 7 | 0.0093 | 0.3232 | 0.3325 | 0.3265 | 0.0041 | 0 | 3 | 0.2729 | 0.3409 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1225 | 4833.736 | 44265.9772 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.8296 | 0:240:120 | 0:00 | 0.2618 | 7 | 0.0088 | 0.3098 | 0.3186 | 0.3131 | 0.004 | 0 | 3 | 0.2618 | 0.3268 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1228 | 4838.059 | 44265.9773 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.7062 | 0:240:120 | 0:00 | 0.2512 | 7 | 0.0092 | 0.2979 | 0.3071 | 0.3013 | 0.0038 | 0 | 3 | 0.2512 | 0.3134 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1231 | 4842.433 | 44265.9773 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.6204 | 0:240:120 | 0:00 | 0.241 | 7 | 0.0086 | 0.2848 | 0.2934 | 0.2882 | 0.0037 | 0 | 3 | 0.241 | 0.3006 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1234 | 4847.205 | 44265.9774 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.5728 | 0:240:120 | 0:00 | 0.2312 | 7 | 0.0079 | 0.2739 | 0.2818 | 0.2769 | 0.0034 | 0 | 3 | 0.2312 | 0.2883 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1237 | 4851.419 | 44265.9774 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.5642 | 0:240:120 | 0:00 | 0.2219 | 7 | 0.0079 | 0.2631 | 0.271 | 0.2662 | 0.0031 | 0 | 3 | 0.2219 | 0.2765 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1240 | 4855.826 | 44265.9775 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.5955 | 0:240:120 | 0:00 | 0.2129 | 7 | 0.0076 | 0.2521 | 0.2597 | 0.2553 | 0.003 | 0 | 3 | 0.2129 | 0.2653 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1243 | 4859.783 | 44265.9775 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.6674 | 0:240:120 | 0:00 | 0.2044 | 7 | 0.0074 | 0.2419 | 0.2493 | 0.2448 | 0.0029 | 0 | 3 | 0.2044 | 0.2545 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1246 | 4863.715 | 44265.9776 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.7808 | 0:240:120 | 0:00 | 0.1961 | 7 | 0.0063 | 0.2315 | 0.2378 | 0.234 | 0.0026 | 0 | 3 | 0.1961 | 0.2442 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1249 | 4867.689 | 44265.9776 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.9364 | 0:240:120 | 0:00 | 0.1883 | 7 | 0.007 | 0.2218 | 0.2288 | 0.225 | 0.0028 | 0 | 3 | 0.1883 | 0.2343 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1252 | 4871.663 | 44265.9777 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.1351 | 0:240:120 | 0:00 | 0.1807 | 7 | 0.0064 | 0.2135 | 0.2199 | 0.2162 | 0.0027 | 0 | 3 | 0.1807 | 0.2248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1255 | 4875.975 | 44265.9777 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.3778 | 0:240:120 | 0:00 | 0.1735 | 7 | 0.0062 | 0.2048 | 0.211 | 0.2074 | 0.0024 | 0 | 3 | 0.1735 | 0.2158 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1258 | 4879.751 | 44265.9778 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.6654 | 0:240:120 | 0:00 | 0.1665 | 7 | 0.0072 | 0.1956 | 0.2028 | 0.1988 | 0.0026 | 0 | 3 | 0.1665 | 0.2071 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1261 | 4883.748 | 44265.9778 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.9987 | 0:240:120 | 0:00 | 0.1599 | 7 | 0.0055 | 0.1884 | 0.1939 | 0.1907 | 0.0023 | 0 | 3 | 0.1599 | 0.1987 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1264 | 4887.578 | 44265.9778 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.3786 | 0:240:120 | 0:00 | 0.1535 | 7 | 0.0053 | 0.1813 | 0.1866 | 0.1836 | 0.0023 | 0 | 3 | 0.1535 | 0.1907 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1267 | 4891.612 | 44265.9779 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.8062 | 0:240:120 | 0:00 | 0.1474 | 7 | 0.0052 | 0.1742 | 0.1794 | 0.1764 | 0.0021 | 0 | 3 | 0.1474 | 0.1831 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1270 | 4895.363 | 44265.9779 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.2823 | 0:240:120 | 0:00 | 0.1415 | 7 | 0.0063 | 0.1669 | 0.1732 | 0.1699 | 0.0023 | 0 | 3 | 0.1415 | 0.1758 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1273 | 4899.309 | 44265.978 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.808 | 0:240:120 | 0:00 | 0.1359 | 7 | 0.0065 | 0.1601 | 0.1666 | 0.1629 | 0.0026 | 0 | 3 | 0.1359 | 0.1687 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1276 | 4903.053 | 44265.978 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131.3841 | 0:240:120 | 0:00 | 0.1305 | 7 | 0.0043 | 0.1539 | 0.1582 | 0.1559 | 0.0017 | 0 | 3 | 0.1305 | 0.162 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1279 | 4906.842 | 44265.9781 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.0118 | 0:240:120 | 0:00 | 0.1253 | 7 | 0.0047 | 0.1476 | 0.1523 | 0.1498 | 0.0019 | 0 | 3 | 0.1253 | 0.1555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1282 | 4910.762 | 44265.9781 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.6921 | 0:240:120 | 0:00 | 0.1203 | 7 | 0.0052 | 0.1415 | 0.1467 | 0.1439 | 0.0019 | 0 | 3 | 0.1203 | 0.1493 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1285 | 4914.918 | 44265.9782 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 139.4259 | 0:240:120 | 0:00 | 0.1155 | 7 | 0.0055 | 0.1359 | 0.1414 | 0.1384 | 0.0023 | 0 | 3 | 0.1155 | 0.1434 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1288 | 4918.712 | 44265.9782 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.2144 | 0:240:120 | 0:00 | 0.111 | 7 | 0.0041 | 0.1301 | 0.1342 | 0.1325 | 0.0015 | 0 | 3 | 0.111 | 0.1377 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1291 | 4922.55 | 44265.9783 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 145.0587 | 0:240:120 | 0:00 | 0.1066 | 7 | 0.0044 | 0.1255 | 0.1299 | 0.1273 | 0.0016 | 0 | 3 | 0.1066 | 0.1322 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1294 | 4926.766 | 44265.9783 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.9599 | 0:240:120 | 0:00 | 0.1024 | 7 | 0.0035 | 0.1216 | 0.1251 | 0.1231 | 0.0014 | 0 | 3 | 0.1024 | 0.1269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1297 | 4930.455 | 44265.9783 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.9191 | 0:240:120 | 0:00 | 0.0983 | 7 | 0.0042 | 0.1157 | 0.1199 | 0.118 | 0.0016 | 0 | 3 | 0.0983 | 0.1219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1300 | 4934.544 | 44265.9784 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.9375 | 0:240:120 | 0:00 | 0.0944 | 7 | 0.0052 | 0.1107 | 0.1159 | 0.1132 | 0.0019 | 0 | 3 | 0.0944 | 0.1171 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1303 | 4938.547 | 44265.9784 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 157.0162 | 0:240:120 | 0:00 | 0.0907 | 7 | 0.0041 | 0.1065 | 0.1106 | 0.1085 | 0.0016 | 0 | 3 | 0.0907 | 0.1124 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1306 | 4942.357 | 44265.9785 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.1565 | 0:240:120 | 0:00 | 0.0871 | 7 | 0.005 | 0.1016 | 0.1066 | 0.1043 | 0.0018 | 0 | 3 | 0.0871 | 0.108 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1309 | 4946.128 | 44265.9785 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 163.3597 | 0:240:120 | 0:00 | 0.0837 | 7 | 0.0036 | 0.0989 | 0.1025 | 0.1007 | 0.0014 | 0 | 3 | 0.0837 | 0.1037 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1312 | 4949.773 | 44265.9786 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.6269 | 0:240:120 | 0:00 | 0.0804 | 7 | 0.0043 | 0.0944 | 0.0987 | 0.0967 | 0.0015 | 0 | 3 | 0.0804 | 0.0996 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1315 | 4953.494 | 44265.9786 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.9594 | 0:240:120 | 0:00 | 0.0772 | 7 | 0.0033 | 0.0913 | 0.0946 | 0.0931 | 0.0013 | 0 | 3 | 0.0772 | 0.0957 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1318 | 4957.188 | 44265.9787 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 173.3586 | 0:240:120 | 0:00 | 0.0742 | 7 | 0.0036 | 0.0873 | 0.0909 | 0.0892 | 0.0015 | 0 | 3 | 0.0742 | 0.0919 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1321 | 4961.128 | 44265.9787 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176.8258 | 0:240:120 | 0:00 | 0.0713 | 7 | 0.0026 | 0.0841 | 0.0867 | 0.0856 | 0.0009 | 0 | 3 | 0.0713 | 0.0883 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1324 | 4964.712 | 44265.9787 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 180.3623 | 0:240:120 | 0:00 | 0.0685 | 7 | 0.0041 | 0.0804 | 0.0845 | 0.0824 | 0.0018 | 0 | 3 | 0.0685 | 0.0848 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1327 | 4968.373 | 44265.9788 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.9695 | 0:240:120 | 0:00 | 0.0658 | 7 | 0.0041 | 0.0764 | 0.0805 | 0.0791 | 0.0016 | 0 | 3 | 0.0658 | 0.0814 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1330 | 4971.951 | 44265.9788 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 187.6489 | 0:240:120 | 0:00 | 0.0632 | 7 | 0.0027 | 0.0745 | 0.0772 | 0.0762 | 0.001 | 0 | 3 | 0.0632 | 0.0782 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1333 | 4975.772 | 44265.9789 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 191.4019 | 0:240:120 | 0:00 | 0.0607 | 7 | 0.0034 | 0.0714 | 0.0748 | 0.0733 | 0.0014 | 0 | 3 | 0.0607 | 0.0752 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1336 | 4979.414 | 44265.9789 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 195.2299 | 0:240:120 | 0:00 | 0.0583 | 7 | 0.0028 | 0.069 | 0.0718 | 0.0705 | 0.0011 | 0 | 3 | 0.0583 | 0.0722 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1339 | 4983.079 | 44265.979 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 199.1345 | 0:240:120 | 0:00 | 0.056 | 7 | 0.0028 | 0.066 | 0.0688 | 0.0676 | 0.001 | 0 | 3 | 0.056 | 0.0694 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1342 | 4986.594 | 44265.979 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 203.1172 | 0:240:120 | 0:00 | 0.0538 | 7 | 0.0041 | 0.0627 | 0.0668 | 0.0654 | 0.0015 | 0 | 3 | 0.0538 | 0.0666 | P | NP | 0-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1345 | 4990.243 | 44265.979 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 207.1796 | 0:240:120 | 0:00 | 0.0517 | 7 | 0.0034 | 0.0614 | 0.0648 | 0.063 | 0.0011 | 0 | 3 | 0.0517 | 0.064 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1348 | 4993.845 | 44265.9791 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 211.3231 | 0:240:120 | 0:00 | 0.0497 | 7 | 0.0036 | 0.0581 | 0.0617 | 0.0604 | 0.0015 | 0 | 3 | 0.0497 | 0.0615 | P | NP | 1-1-1-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1351 | 4997.415 | 44265.9791 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 215.5496 | 0:240:120 | 0:00 | 0.0478 | 7 | 0.0041 | 0.0556 | 0.0597 | 0.058 | 0.0015 | 0 | 3 | 0.0478 | 0.0591 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1354 | 5001.373 | 44265.9792 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 219.8606 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0038 | 0.0528 | 0.0566 | 0.0553 | 0.0016 | 0 | 3 | 0.0459 | 0.0568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1357 | 5004.843 | 44265.9792 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 224.2578 | 0:240:120 | 0:00 | 0.0441 | 7 | 0.0041 | 0.0509 | 0.055 | 0.0533 | 0.0015 | 0 | 3 | 0.0441 | 0.0545 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1360 | 5008.506 | 44265.9792 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 228.743 | 0:240:120 | 0:00 | 0.0424 | 7 | 0.0027 | 0.0497 | 0.0524 | 0.0514 | 0.0009 | 0 | 3 | 0.0424 | 0.0524 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1363 | 5012.137 | 44265.9793 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 233.3178 | 0:240:120 | 0:00 | 0.0407 | 7 | 0.0034 | 0.0471 | 0.0505 | 0.0491 | 0.0013 | 0 | 3 | 0.0407 | 0.0507 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1366 | 5015.964 | 44265.9793 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.9842 | 0:240:120 | 0:00 | 0.0391 | 7 | 0.0038 | 0.0463 | 0.0501 | 0.0484 | 0.0012 | 0 | 3 | 0.0391 | 0.0491 | P | NP | 1-1-1-1-1-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1369 | 5019.536 | 44265.9794 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 242.7439 | 0:240:120 | 0:00 | 0.0376 | 7 | 0.0035 | 0.0438 | 0.0473 | 0.046 | 0.0012 | 0 | 3 | 0.0376 | 0.0476 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1372 | 5023.146 | 44265.9794 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 247.5987 | 0:240:120 | 0:00 | 0.0361 | 7 | 0.0034 | 0.0422 | 0.0456 | 0.0443 | 0.0011 | 0 | 3 | 0.0361 | 0.0461 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1375 | 5026.6 | 44265.9795 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 252.5507 | 0:240:120 | 0:00 | 0.0347 | 7 | 0.0034 | 0.0407 | 0.0441 | 0.0428 | 0.0013 | 0 | 3 | 0.0347 | 0.0447 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1378 | 5030.263 | 44265.9795 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 257.6017 | 0:240:120 | 0:00 | 0.0334 | 7 | 0.0039 | 0.0394 | 0.0433 | 0.0413 | 0.0014 | 0 | 3 | 0.0334 | 0.0434 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1381 | 5033.979 | 44265.9795 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 262.7538 | 0:240:120 | 0:00 | 0.0321 | 7 | 0.0023 | 0.0385 | 0.0408 | 0.0396 | 0.0008 | 0 | 3 | 0.0321 | 0.0421 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1384 | 5037.444 | 44265.9796 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 268.0088 | 0:240:120 | 0:00 | 0.0308 | 7 | 0.0032 | 0.0363 | 0.0395 | 0.0381 | 0.0012 | 0 | 3 | 0.0308 | 0.0408 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1387 | 5040.974 | 44265.9796 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 273.369 | 0:240:120 | 0:00 | 0.0296 | 7 | 0.0029 | 0.0355 | 0.0384 | 0.0368 | 0.001 | 0 | 3 | 0.0296 | 0.0396 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1390 | 5044.372 | 44265.9797 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 278.8364 | 0:240:120 | 0:00 | 0.0284 | 7 | 0.0028 | 0.0336 | 0.0364 | 0.0353 | 0.0011 | 0 | 3 | 0.0284 | 0.0384 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1393 | 5048.356 | 44265.9797 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 284.4131 | 0:240:120 | 0:00 | 0.0273 | 7 | 0.0036 | 0.0322 | 0.0358 | 0.0344 | 0.0012 | 0 | 3 | 0.0273 | 0.0373 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1396 | 5051.995 | 44265.9798 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 290.1014 | 0:240:120 | 0:00 | 0.0263 | 7 | 0.0035 | 0.0308 | 0.0343 | 0.0329 | 0.0012 | 0 | 3 | 0.0263 | 0.0363 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1399 | 5055.573 | 44265.9798 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 295.9034 | 0:240:120 | 0:00 | 0.0252 | 7 | 0.0028 | 0.0301 | 0.0329 | 0.0319 | 0.0011 | 0 | 3 | 0.0252 | 0.0352 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1402 | 5059.123 | 44265.9798 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 301.8215 | 0:240:120 | 0:00 | 0.0243 | 7 | 0.0028 | 0.0297 | 0.0325 | 0.031 | 0.001 | 0 | 3 | 0.0243 | 0.0343 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1405 | 5062.503 | 44265.9799 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 307.8579 | 0:240:120 | 0:00 | 0.0233 | 7 | 0.004 | 0.0276 | 0.0316 | 0.0298 | 0.0014 | 0 | 3 | 0.0233 | 0.0333 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1408 | 5066.003 | 44265.9799 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 314.0151 | 0:240:120 | 0:00 | 0.0224 | 7 | 0.0039 | 0.0265 | 0.0304 | 0.0287 | 0.0015 | 0 | 3 | 0.0224 | 0.0324 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1411 | 5069.556 | 44265.98 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 320.2954 | 0:240:120 | 0:00 | 0.0215 | 7 | 0.0033 | 0.0265 | 0.0298 | 0.0281 | 0.0012 | 0 | 3 | 0.0215 | 0.0315 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1414 | 5072.95 | 44265.98 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 326.7013 | 0:240:120 | 0:00 | 0.0207 | 7 | 0.0027 | 0.0255 | 0.0282 | 0.0268 | 0.001 | 0 | 3 | 0.0207 | 0.0307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1417 | 5076.352 | 44265.98 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 333.2353 | 0:240:120 | 0:00 | 0.0199 | 7 | 0.0025 | 0.0247 | 0.0272 | 0.0264 | 0.001 | 0 | 3 | 0.0199 | 0.0299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1420 | 5079.865 | 44265.9801 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 339.9 | 0:240:120 | 0:00 | 0.0191 | 7 | 0.0034 | 0.0235 | 0.0269 | 0.0253 | 0.0012 | 0 | 3 | 0.0191 | 0.0291 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1423 | 5083.376 | 44265.9801 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 346.698 | 0:240:120 | 0:00 | 0.0184 | 7 | 0.0025 | 0.0226 | 0.0251 | 0.0242 | 0.0011 | 0 | 3 | 0.0184 | 0.0284 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1426 | 5086.905 | 44265.9802 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 353.632 | 0:240:120 | 0:00 | 0.0176 | 7 | 0.0038 | 0.0215 | 0.0253 | 0.0236 | 0.0014 | 0 | 3 | 0.0176 | 0.0276 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1429 | 5090.541 | 44265.9802 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 360.7046 | 0:240:120 | 0:00 | 0.017 | 7 | 0.0032 | 0.0209 | 0.0241 | 0.0229 | 0.0012 | 0 | 3 | 0.017 | 0.027 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1432 | 5093.898 | 44265.9802 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 367.9187 | 0:240:120 | 0:00 | 0.0163 | 7 | 0.0028 | 0.0205 | 0.0233 | 0.0224 | 0.0011 | 0 | 3 | 0.0163 | 0.0263 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1435 | 5097.35 | 44265.9803 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 375.2771 | 0:240:120 | 0:00 | 0.0157 | 7 | 0.0029 | 0.0203 | 0.0232 | 0.0221 | 0.0012 | 0 | 3 | 0.0157 | 0.0257 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1438 | 5100.883 | 44265.9803 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 382.7826 | 0:240:120 | 0:00 | 0.0151 | 7 | 0.0043 | 0.0192 | 0.0235 | 0.0213 | 0.0016 | 0 | 3 | 0.0151 | 0.0251 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1441 | 5104.432 | 44265.9804 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 390.4383 | 0:240:120 | 0:00 | 0.0145 | 7 | 0.0037 | 0.0189 | 0.0226 | 0.0208 | 0.0014 | 0 | 3 | 0.0145 | 0.0245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1444 | 5107.848 | 44265.9804 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 398.2471 | 0:240:120 | 0:00 | 0.0139 | 7 | 0.0038 | 0.0184 | 0.0222 | 0.0206 | 0.0014 | 0 | 3 | 0.0139 | 0.0239 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1447 | 5111.318 | 44265.9804 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 406.212 | 0:240:120 | 0:00 | 0.0134 | 7 | 0.0041 | 0.018 | 0.0221 | 0.0202 | 0.0015 | 0 | 3 | 0.0134 | 0.0234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1450 | 5114.623 | 44265.9805 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 414.3362 | 0:240:120 | 0:00 | 0.0128 | 7 | 0.003 | 0.0182 | 0.0212 | 0.0198 | 0.001 | 0 | 3 | 0.0128 | 0.0228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1453 | 5118.095 | 44265.9805 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 422.623 | 0:240:120 | 0:00 | 0.0123 | 7 | 0.0034 | 0.0177 | 0.0211 | 0.019 | 0.0013 | 0 | 3 | 0.0123 | 0.0223 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1456 | 5121.542 | 44265.9806 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 431.0754 | 0:240:120 | 0:00 | 0.0119 | 7 | 0.0017 | 0.0185 | 0.0202 | 0.0193 | 0.0007 | 0 | 3 | 0.0119 | 0.0219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1459 | 5124.969 | 44265.9806 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 439.6969 | 0:240:120 | 0:00 | 0.0114 | 7 | 0.0021 | 0.0173 | 0.0194 | 0.0182 | 0.0008 | 0 | 3 | 0.0114 | 0.0214 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1462 | 5128.539 | 44265.9806 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 448.4909 | 0:240:120 | 0:00 | 0.011 | 7 | 0.0019 | 0.0176 | 0.0195 | 0.0182 | 0.0007 | 0 | 3 | 0.011 | 0.021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1465 | 5132.023 | 44265.9807 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 457.4607 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0011 | 0.0169 | 0.018 | 0.0176 | 0.0004 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1468 | 5135.544 | 44265.9807 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 466.6099 | 0:240:120 | 0:00 | 0.0101 | 7 | 0.0013 | 0.0169 | 0.0182 | 0.0171 | 0.0004 | 0 | 3 | 0.0101 | 0.0201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1471 | 5139.022 | 44265.9808 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 469.4678 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0019 | 0.0159 | 0.0178 | 0.0173 | 0.0007 | 0 | 3 | 0.01 | 0.016 | NP | NP | 1-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1474 | 5142.461 | 44265.9808 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 478.8571 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0025 | 0.0152 | 0.0177 | 0.0167 | 0.0009 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 1-0-0-1-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1477 | 5145.811 | 44265.9808 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 488.4343 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0016 | 0.0159 | 0.0175 | 0.0166 | 0.0007 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 1-1-0-0-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
1480 | 5149.102 | 44265.9809 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 498.203 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0025 | 0.0149 | 0.0174 | 0.016 | 0.0008 | 0 | 3 | 0.0089 | 0.016 | P | NP | 1-0-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1483 | 5152.601 | 44265.9809 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 508.167 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0025 | 0.0149 | 0.0174 | 0.0157 | 0.001 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1486 | 5156.115 | 44265.981 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 518.3304 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0037 | 0.0133 | 0.017 | 0.015 | 0.0013 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1489 | 5159.538 | 44265.981 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 528.697 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0033 | 0.0131 | 0.0164 | 0.0149 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1492 | 5163.201 | 44265.981 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 539.2709 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0041 | 0.0129 | 0.017 | 0.0147 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1495 | 5166.778 | 44265.9811 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 550.0563 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0049 | 0.0121 | 0.017 | 0.0146 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1498 | 5170.295 | 44265.9811 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 561.0575 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0051 | 0.0118 | 0.0169 | 0.0144 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1501 | 5173.738 | 44265.9812 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 572.2786 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0043 | 0.0119 | 0.0162 | 0.0143 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1504 | 5177.056 | 44265.9812 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 583.7242 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0042 | 0.0121 | 0.0163 | 0.0142 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1507 | 5180.776 | 44265.9812 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 595.3987 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0053 | 0.012 | 0.0173 | 0.0141 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1510 | 5184.489 | 44265.9813 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 607.3066 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0047 | 0.0117 | 0.0164 | 0.0141 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1513 | 5187.943 | 44265.9813 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 619.4528 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0049 | 0.0112 | 0.0161 | 0.014 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1516 | 5191.3 | 44265.9814 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 631.8418 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0055 | 0.0111 | 0.0166 | 0.0136 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1519 | 5194.694 | 44265.9814 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 644.4787 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0052 | 0.0108 | 0.016 | 0.0134 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1522 | 5198.179 | 44265.9814 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 657.3682 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0045 | 0.0107 | 0.0152 | 0.0133 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1525 | 5201.628 | 44265.9815 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 670.5156 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.004 | 0.0108 | 0.0148 | 0.0132 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1528 | 5205.161 | 44265.9815 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 683.9259 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0056 | 0.0108 | 0.0164 | 0.0132 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1531 | 5208.982 | 44265.9816 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 697.6044 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0054 | 0.011 | 0.0164 | 0.0133 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1534 | 5212.591 | 44265.9816 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 711.5565 | 0:240:120 | 0:00 | 0.0043 | 7 | 0.0053 | 0.0105 | 0.0158 | 0.0131 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1537 | 5216.075 | 44265.9817 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 725.7876 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0053 | 0.0106 | 0.0159 | 0.0129 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1540 | 5219.55 | 44265.9817 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 740.3034 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0037 | 0.0113 | 0.015 | 0.0132 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1543 | 5223.234 | 44265.9817 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 755.1095 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0049 | 0.0102 | 0.0151 | 0.0129 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1546 | 5226.579 | 44265.9818 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 770.2117 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0051 | 0.0108 | 0.0159 | 0.013 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1549 | 5230.011 | 44265.9818 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 785.6159 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0038 | 0.01 | 0.0138 | 0.0121 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1552 | 5233.462 | 44265.9819 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 801.3282 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0029 | 0.0108 | 0.0137 | 0.0123 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1555 | 5236.828 | 44265.9819 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 817.3548 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0033 | 0.0105 | 0.0138 | 0.0117 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1558 | 5240.286 | 44265.9819 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 833.7019 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0027 | 0.0102 | 0.0129 | 0.0112 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1561 | 5243.756 | 44265.982 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 850.3759 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0053 | 0.0099 | 0.0152 | 0.0117 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1564 | 5247.071 | 44265.982 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 867.3834 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0041 | 0.0094 | 0.0135 | 0.0111 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1567 | 5250.482 | 44265.982 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 884.7311 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0053 | 0.0099 | 0.0152 | 0.0114 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1570 | 5254.256 | 44265.9821 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 902.4257 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0047 | 0.0094 | 0.0141 | 0.0114 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1573 | 5258.032 | 44265.9821 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 920.4742 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0028 | 0.0098 | 0.0126 | 0.0111 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1576 | 5261.794 | 44265.9822 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 938.8837 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0026 | 0.01 | 0.0126 | 0.0108 | 0.0009 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1579 | 5265.17 | 44265.9822 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 938.9356 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0041 | 0.0091 | 0.0132 | 0.0108 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1582 | 5268.678 | 44265.9823 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 957.7143 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0051 | 0.009 | 0.0141 | 0.0111 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1585 | 5272.464 | 44265.9823 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 976.8686 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0027 | 0.0095 | 0.0122 | 0.0105 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1588 | 5275.913 | 44265.9823 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 996.4059 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0032 | 0.0092 | 0.0124 | 0.0107 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1591 | 5280.445 | 44265.9824 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1016.3341 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.003 | 0.01 | 0.013 | 0.0111 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1594 | 5283.857 | 44265.9824 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1036.6607 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0026 | 0.0089 | 0.0115 | 0.0102 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1597 | 5287.228 | 44265.9825 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1057.3939 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0018 | 0.0102 | 0.012 | 0.0109 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1600 | 5290.761 | 44265.9825 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1078.5418 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0025 | 0.0093 | 0.0118 | 0.0107 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1603 | 5294.235 | 44265.9826 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1100.1127 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0028 | 0.009 | 0.0118 | 0.0106 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1606 | 5297.797 | 44265.9826 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1122.1149 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0025 | 0.009 | 0.0115 | 0.0104 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1609 | 5301.318 | 44265.9826 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1144.5572 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0018 | 0.0096 | 0.0114 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1612 | 5304.774 | 44265.9827 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1167.4484 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1615 | 5308.7 | 44265.9827 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1190.7973 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1618 | 5312.327 | 44265.9828 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1214.6133 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0017 | 0.01 | 0.0117 | 0.0108 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1621 | 5315.731 | 44265.9828 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1238.9055 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0013 | 0.0095 | 0.0108 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1624 | 5319.184 | 44265.9828 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1263.6837 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1627 | 5322.52 | 44265.9829 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1288.9573 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1630 | 5326.304 | 44265.9829 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1314.7365 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0013 | 0.0095 | 0.0108 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1633 | 5329.966 | 44265.983 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1341.0312 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1636 | 5333.455 | 44265.983 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1367.8518 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1639 | 5336.903 | 44265.983 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1395.2089 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1642 | 5340.591 | 44265.9831 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1423.113 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0011 | 0.0094 | 0.0105 | 0.0099 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1645 | 5344.252 | 44265.9831 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1451.5753 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0013 | 0.0096 | 0.0109 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1648 | 5347.749 | 44265.9832 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1480.6068 | 0:240:120 | 0:00 | 0.001 | 7 | 0.002 | 0.0094 | 0.0114 | 0.0103 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1651 | 5351.126 | 44265.9832 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1510.2189 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0023 | 0.0091 | 0.0114 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1654 | 5354.613 | 44265.9833 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1540.4233 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0024 | 0.0091 | 0.0115 | 0.0102 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1657 | 5357.944 | 44265.9833 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1571.2318 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1660 | 5361.335 | 44265.9833 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1602.6564 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0019 | 0.0096 | 0.0115 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1663 | 5364.755 | 44265.9834 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1634.7096 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0011 | 0.0091 | 0.0102 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1666 | 5368.436 | 44265.9834 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1667.4037 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.002 | 0.0093 | 0.0113 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1669 | 5371.815 | 44265.9835 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1700.7518 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0016 | 0.0098 | 0.0114 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1672 | 5375.134 | 44265.9835 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1734.7669 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1675 | 5378.501 | 44265.9835 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1769.4622 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1678 | 5382.09 | 44265.9836 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1804.8514 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0023 | 0.009 | 0.0113 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1681 | 5385.808 | 44265.9836 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1840.9485 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1684 | 5389.247 | 44265.9837 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1877.7674 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0007 | 0.0099 | 0.0106 | 0.0103 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1687 | 5392.656 | 44265.9837 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1915.3228 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0018 | 0.0095 | 0.0113 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1690 | 5396.325 | 44265.9837 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1953.6292 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1693 | 5399.709 | 44265.9838 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1992.7018 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0015 | 0.0093 | 0.0108 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1696 | 5403.337 | 44265.9838 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2032.5559 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0021 | 0.009 | 0.0111 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1699 | 5406.869 | 44265.9839 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2073.207 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1702 | 5410.17 | 44265.9839 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2114.6711 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.001 | 0.0099 | 0.0109 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1705 | 5413.527 | 44265.9839 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2156.9645 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0012 | 0.009 | 0.0102 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1708 | 5416.967 | 44265.984 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2200.1038 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1711 | 5420.579 | 44265.984 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2244.1059 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0018 | 0.009 | 0.0108 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1714 | 5423.922 | 44265.9841 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2288.988 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0016 | 0.0094 | 0.011 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1717 | 5427.334 | 44265.9841 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2334.7678 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1720 | 5430.775 | 44265.9841 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2381.4631 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0013 | 0.0101 | 0.0114 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1723 | 5434.371 | 44265.9842 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2429.0924 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1726 | 5437.74 | 44265.9842 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2477.6742 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0016 | 0.0097 | 0.0113 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1729 | 5441.175 | 44265.9843 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2527.2277 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0015 | 0.0096 | 0.0111 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1732 | 5444.734 | 44265.9843 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2577.7723 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0014 | 0.0095 | 0.0109 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1735 | 5448.379 | 44265.9843 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2629.3277 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1738 | 5451.7 | 44265.9844 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2681.9143 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0014 | 0.0095 | 0.0109 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1741 | 5455.175 | 44265.9844 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2735.5526 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0018 | 0.0095 | 0.0113 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1744 | 5458.665 | 44265.9845 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2790.2636 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0005 | 0.0101 | 0.0106 | 0.0103 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1747 | 5462.332 | 44265.9845 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2846.0689 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.001 | 0.01 | 0.011 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1750 | 5466.076 | 44265.9845 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2902.9903 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1753 | 5470.039 | 44265.9846 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2961.0501 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0022 | 0.0088 | 0.011 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1756 | 5473.783 | 44265.9846 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3020.2711 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1759 | 5477.154 | 44265.9847 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3080.6765 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1762 | 5480.5 | 44265.9847 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3142.29 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0009 | 0.0099 | 0.0108 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1765 | 5483.914 | 44265.9848 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3205.1358 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0011 | 0.01 | 0.0111 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1768 | 5487.461 | 44265.9848 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3269.2386 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0009 | 0.0096 | 0.0105 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1771 | 5491.031 | 44265.9848 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3334.6233 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0003 | 0.0101 | 0.0104 | 0.0103 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1774 | 5494.359 | 44265.9849 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3401.3158 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1777 | 5497.849 | 44265.9849 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3469.3421 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0015 | 0.0098 | 0.0113 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1780 | 5501.426 | 44265.985 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3538.7289 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1783 | 5505.006 | 44265.985 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3609.5035 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0011 | 0.0091 | 0.0102 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1786 | 5508.508 | 44265.985 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3681.6936 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0015 | 0.0092 | 0.0107 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1789 | 5512.333 | 44265.9851 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3755.3275 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0024 | 0.0088 | 0.0112 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1792 | 5515.827 | 44265.9851 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3830.434 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0022 | 0.0089 | 0.0111 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1795 | 5519.147 | 44265.9852 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3907.0427 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.002 | 0.0093 | 0.0113 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1798 | 5522.819 | 44265.9852 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3985.1836 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0021 | 0.0091 | 0.0112 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1801 | 5526.548 | 44265.9852 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4064.8872 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0002 | 0.0096 | 0.0098 | 0.0097 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1804 | 5530.11 | 44265.9853 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4146.185 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0088 | 0.0099 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1807 | 5533.499 | 44265.9853 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4229.1087 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0009 | 0.0095 | 0.0104 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1810 | 5537.079 | 44265.9854 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4313.6908 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0014 | 0.0089 | 0.0103 | 0.0094 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1813 | 5540.368 | 44265.9854 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4399.9647 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0018 | 0.0094 | 0.0112 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1816 | 5543.736 | 44265.9854 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4487.964 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1819 | 5547.193 | 44265.9855 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4577.7232 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0014 | 0.0091 | 0.0105 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1822 | 5550.793 | 44265.9855 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4669.2777 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1825 | 5554.646 | 44265.9856 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4762.6632 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0088 | 0.0107 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1828 | 5558.068 | 44265.9856 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4857.9165 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1831 | 5561.551 | 44265.9856 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4955.0748 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1834 | 5564.944 | 44265.9857 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5054.1763 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0097 | 0.0109 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1837 | 5568.607 | 44265.9857 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5155.2599 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1840 | 5571.956 | 44265.9858 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5258.3651 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1843 | 5575.467 | 44265.9858 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5363.5324 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.002 | 0.0089 | 0.0109 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1846 | 5578.774 | 44265.9858 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5470.803 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.001 | 0.0098 | 0.0108 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1849 | 5582.348 | 44265.9859 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5580.2191 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0095 | 0.0107 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1852 | 5585.807 | 44265.9859 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5691.8235 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.002 | 0.0092 | 0.0112 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1855 | 5589.282 | 44265.986 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5805.6599 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1858 | 5592.804 | 44265.986 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5921.7731 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0018 | 0.009 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1861 | 5596.041 | 44265.986 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6040.2086 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0007 | 0.0094 | 0.0101 | 0.0098 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1864 | 5599.418 | 44265.9861 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6161.0128 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0095 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1867 | 5602.951 | 44265.9861 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6284.233 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1870 | 5606.4 | 44265.9862 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6409.9177 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.01 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1873 | 5609.76 | 44265.9862 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6538.116 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1876 | 5613.503 | 44265.9863 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6668.8783 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.0097 | 0.0109 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1879 | 5616.945 | 44265.9863 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6802.2559 | 0:240:120 | 0:00 | 0 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1882 | 5620.613 | 44265.9863 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6938.301 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1885 | 5624.089 | 44265.9864 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7077.0671 | 0:240:120 | 0:00 | 0 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1888 | 5627.591 | 44265.9864 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7218.6084 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1891 | 5631.12 | 44265.9865 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7362.9806 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0093 | 0.011 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1894 | 5634.45 | 44265.9865 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7510.2402 | 0:240:120 | 0:00 | 0 | 7 | 0.002 | 0.0089 | 0.0109 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1897 | 5638.53 | 44265.9865 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7660.445 | 0:240:120 | 0:00 | 0 | 7 | 0.0015 | 0.0089 | 0.0104 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1900 | 5641.858 | 44265.9866 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7813.6539 | 0:240:120 | 0:00 | 0 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1903 | 5645.524 | 44265.9866 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7969.927 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1906 | 5649.173 | 44265.9867 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8129.3255 | 0:240:120 | 0:00 | 0 | 7 | 0.0004 | 0.0102 | 0.0106 | 0.0104 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1909 | 5652.764 | 44265.9867 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8291.912 | 0:240:120 | 0:00 | 0 | 7 | 0.0007 | 0.0094 | 0.0101 | 0.0097 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1912 | 5656.467 | 44265.9867 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8457.7502 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1915 | 5659.881 | 44265.9868 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8626.9052 | 0:240:120 | 0:00 | 0 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1918 | 5663.38 | 44265.9868 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8799.4434 | 0:240:120 | 0:00 | 0 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1921 | 5666.831 | 44265.9869 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8975.4322 | 0:240:120 | 0:00 | 0 | 7 | 0.0015 | 0.0087 | 0.0102 | 0.0095 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1924 | 5670.653 | 44265.9869 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9154.9409 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1927 | 5674.012 | 44265.987 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9338.0397 | 0:240:120 | 0:00 | 0 | 7 | 0.0015 | 0.0088 | 0.0103 | 0.0094 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1930 | 5677.313 | 44265.987 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9524.8005 | 0:240:120 | 0:00 | 0 | 7 | 0.0007 | 0.0098 | 0.0105 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1933 | 5680.693 | 44265.987 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9715.2965 | 0:240:120 | 0:00 | 0 | 7 | 0.0009 | 0.0095 | 0.0104 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1936 | 5684.055 | 44265.9871 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9909.6024 | 0:240:120 | 0:00 | 0 | 7 | 0.0019 | 0.0089 | 0.0108 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1939 | 5687.609 | 44265.9871 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10107.7945 | 0:240:120 | 0:00 | 0 | 7 | 0.0014 | 0.0091 | 0.0105 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1942 | 5691.283 | 44265.9872 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10309.9503 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1945 | 5694.961 | 44265.9872 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10516.1494 | 0:240:120 | 0:00 | 0 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1948 | 5698.373 | 44265.9872 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10726.4724 | 0:240:120 | 0:00 | 0 | 7 | 0.002 | 0.009 | 0.011 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1951 | 5702.165 | 44265.9873 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10941.0018 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1954 | 5705.889 | 44265.9873 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11159.8218 | 0:240:120 | 0:00 | 0 | 7 | 0.0022 | 0.0088 | 0.011 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1957 | 5709.544 | 44265.9874 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11383.0183 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0094 | 0.0105 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1960 | 5713.24 | 44265.9874 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11610.6786 | 0:240:120 | 0:00 | 0 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1963 | 5716.535 | 44265.9874 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11842.8922 | 0:240:120 | 0:00 | 0 | 7 | 0.0014 | 0.0088 | 0.0102 | 0.0093 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1966 | 5823.517 | 44265.9887 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.7 | 0:240:120 | 0:00 | 13.6063 | 7 | 51.2947 | 55.8872 | 107.1819 | 78.7416 | 21.0424 | 442.7829 | 3 | 13.6063 | 77.2201 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1969 | 6088.215 | 44265.9917 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.2 | 0:240:120 | 0:00 | 11.8509 | 7 | 24.663 | 24.9462 | 49.6092 | 33.1186 | 11.7009 | 136.9107 | 3 | 11.8509 | 44.4984 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1972 | 6213.682 | 44265.9932 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.7 | 0:240:120 | 0:00 | 10.4717 | 7 | 2.2236 | 21.8968 | 24.1204 | 22.7021 | 1.0255 | 1.0516 | 3 | 10.4717 | 31.034 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1975 | 6286.773 | 44265.994 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.1 | 0:240:120 | 0:00 | 9.5648 | 7 | 2.6033 | 19.1362 | 21.7395 | 20.1159 | 1.2196 | 1.4875 | 3 | 9.5648 | 24.8841 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1978 | 6351.54 | 44265.9948 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.6 | 0:240:120 | 0:00 | 8.6153 | 7 | 2.5636 | 15.5731 | 18.1367 | 16.7346 | 1.1128 | 1.2382 | 3 | 8.6153 | 19.8628 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1981 | 6405.031 | 44265.9954 | Vista Speed | E | 10E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.2 | 0:240:120 | 0:00 | 7.6805 | 7 | 1.9695 | 12.1576 | 14.1271 | 12.925 | 0.8855 | 0.7842 | 3 | 7.6805 | 15.9144 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1984 | 6670.945 | 44265.9985 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29 | 0:240:120 | 0:00 | 22.5333 | 7 | 41.7801 | 192.2555 | 234.0356 | 210.1668 | 18.2762 | 334.0194 | 3 | 22.5333 | Inf | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1987 | 7320.02 | 44266.006 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.58 | 0:240:120 | 0:00 | 18.6856 | 7 | 36.3858 | 141.7634 | 178.1492 | 156.824 | 16.16 | 261.1453 | 3 | 18.6856 | 121.916 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1990 | 7804.996 | 44266.0116 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.1716 | 0:240:120 | 0:00 | 15.8668 | 7 | 43.5395 | 82.2629 | 125.8024 | 102.8628 | 18.482 | 341.5854 | 3 | 15.8668 | 60.5897 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1993 | 8133.818 | 44266.0154 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.775 | 0:240:120 | 0:00 | 13.7144 | 7 | 46.0904 | 28.3527 | 74.4431 | 50.1073 | 19.6671 | 386.7946 | 3 | 13.7144 | 40.7885 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1996 | 8311.038 | 44266.0175 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.3905 | 0:240:120 | 0:00 | 12.0181 | 7 | 2.5974 | 23.4392 | 26.0366 | 24.6222 | 1.1201 | 1.2547 | 3 | 12.0181 | 30.439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1999 | 8389.409 | 44266.0184 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.0183 | 0:240:120 | 0:00 | 10.648 | 7 | 2.356 | 20.5788 | 22.9348 | 21.4307 | 1.1037 | 1.2182 | 3 | 10.648 | 24.0817 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2002 | 8458.123 | 44266.0192 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.6587 | 0:240:120 | 0:00 | 9.5189 | 7 | 2.1813 | 17.3897 | 19.571 | 18.3186 | 0.9525 | 0.9073 | 3 | 9.5189 | 19.783 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2005 | 8517.46 | 44266.0199 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.3119 | 0:240:120 | 0:00 | 8.5731 | 7 | 2.5952 | 14.032 | 16.6272 | 15.1553 | 1.1431 | 1.3067 | 3 | 8.5731 | 16.6845 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2008 | 8567.75 | 44266.0204 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.9781 | 0:240:120 | 0:00 | 7.7699 | 7 | 1.6905 | 12.0167 | 13.7072 | 12.6092 | 0.8129 | 0.6607 | 3 | 7.7699 | 14.3466 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2011 | 8610.052 | 44266.0209 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.6577 | 0:240:120 | 0:00 | 7.0798 | 7 | 0.8738 | 10.8337 | 11.7075 | 11.2227 | 0.3676 | 0.1351 | 3 | 7.0798 | 12.5212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2014 | 8647.377 | 44266.0214 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.3508 | 0:240:120 | 0:00 | 6.4809 | 7 | 0.911 | 9.7797 | 10.6907 | 10.1266 | 0.4278 | 0.183 | 3 | 6.4809 | 11.0575 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2017 | 8681.439 | 44266.0218 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.0579 | 0:240:120 | 0:00 | 5.9567 | 7 | 0.8229 | 8.6651 | 9.488 | 8.9961 | 0.3585 | 0.1285 | 3 | 5.9567 | 9.8585 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2020 | 8712.272 | 44266.0221 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.779 | 0:240:120 | 0:00 | 5.4943 | 7 | 0.6836 | 7.7337 | 8.4173 | 7.981 | 0.3225 | 0.104 | 3 | 5.4943 | 8.8591 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2023 | 8740.106 | 44266.0224 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.5146 | 0:240:120 | 0:00 | 5.0838 | 7 | 0.4267 | 7.1341 | 7.5608 | 7.3189 | 0.1827 | 0.0334 | 3 | 5.0838 | 8.0138 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2026 | 8765.423 | 44266.0227 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.2649 | 0:240:120 | 0:00 | 4.7171 | 7 | 0.4513 | 6.5745 | 7.0258 | 6.7476 | 0.2095 | 0.0439 | 3 | 4.7171 | 7.2902 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2029 | 8789.42 | 44266.023 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.0302 | 0:240:120 | 0:00 | 4.3878 | 7 | 0.4553 | 5.9526 | 6.4079 | 6.126 | 0.2124 | 0.0451 | 3 | 4.3878 | 6.6641 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2032 | 8811.377 | 44266.0233 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.8108 | 0:240:120 | 0:00 | 4.0907 | 7 | 0.2896 | 5.4915 | 5.7811 | 5.6071 | 0.1264 | 0.016 | 3 | 4.0907 | 6.1175 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2035 | 8831.42 | 44266.0235 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.607 | 0:240:120 | 0:00 | 3.8215 | 7 | 0.2916 | 5.1096 | 5.4012 | 5.2266 | 0.1285 | 0.0165 | 3 | 3.8215 | 5.6365 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2038 | 8850.26 | 44266.0237 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.4191 | 0:240:120 | 0:00 | 3.5766 | 7 | 0.2767 | 4.7602 | 5.0369 | 4.859 | 0.1325 | 0.0175 | 3 | 3.5766 | 5.2103 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2041 | 8868.515 | 44266.0239 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.2475 | 0:240:120 | 0:00 | 3.353 | 7 | 0.2809 | 4.3735 | 4.6544 | 4.4781 | 0.13 | 0.0169 | 3 | 3.353 | 4.8303 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2044 | 8885.356 | 44266.0241 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.0925 | 0:240:120 | 0:00 | 3.1483 | 7 | 0.2034 | 4.1093 | 4.3127 | 4.189 | 0.0922 | 0.0085 | 3 | 3.1483 | 4.4896 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2047 | 8901.216 | 44266.0243 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.9543 | 0:240:120 | 0:00 | 2.9602 | 7 | 0.1968 | 3.8512 | 4.048 | 3.9247 | 0.0918 | 0.0084 | 3 | 2.9602 | 4.1827 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2050 | 8916.751 | 44266.0245 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.8334 | 0:240:120 | 0:00 | 2.787 | 7 | 0.1936 | 3.5736 | 3.7672 | 3.6459 | 0.0896 | 0.008 | 3 | 2.787 | 3.9049 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2053 | 8931.208 | 44266.0247 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.7301 | 0:240:120 | 0:00 | 2.6271 | 7 | 0.1479 | 3.3576 | 3.5055 | 3.4133 | 0.0687 | 0.0047 | 3 | 2.6271 | 3.6526 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2056 | 8944.943 | 44266.0248 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.6447 | 0:240:120 | 0:00 | 2.4791 | 7 | 0.1411 | 3.1597 | 3.3008 | 3.2092 | 0.0674 | 0.0045 | 3 | 2.4791 | 3.4225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2059 | 8958.139 | 44266.025 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.5776 | 0:240:120 | 0:00 | 2.3419 | 7 | 0.135 | 2.9648 | 3.0998 | 3.0124 | 0.0648 | 0.0042 | 3 | 2.3419 | 3.212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2062 | 8970.468 | 44266.0251 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.5291 | 0:240:120 | 0:00 | 2.2143 | 7 | 0.1242 | 2.7846 | 2.9088 | 2.8332 | 0.0565 | 0.0032 | 3 | 2.2143 | 3.0188 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2065 | 8982.215 | 44266.0252 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.4997 | 0:240:120 | 0:00 | 2.0956 | 7 | 0.1078 | 2.6368 | 2.7446 | 2.6743 | 0.0509 | 0.0026 | 3 | 2.0956 | 2.841 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2068 | 8993.456 | 44266.0254 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.4897 | 0:240:120 | 0:00 | 1.9848 | 7 | 0.1093 | 2.4852 | 2.5945 | 2.5241 | 0.0518 | 0.0027 | 3 | 1.9848 | 2.677 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2071 | 9004.338 | 44266.0255 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.4995 | 0:240:120 | 0:00 | 1.8814 | 7 | 0.0776 | 2.3521 | 2.4297 | 2.379 | 0.0375 | 0.0014 | 3 | 1.8814 | 2.5253 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2074 | 9014.859 | 44266.0256 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.5295 | 0:240:120 | 0:00 | 1.7846 | 7 | 0.0986 | 2.2176 | 2.3162 | 2.2559 | 0.0448 | 0.002 | 3 | 1.7846 | 2.3848 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2077 | 9024.997 | 44266.0257 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.5801 | 0:240:120 | 0:00 | 1.694 | 7 | 0.088 | 2.092 | 2.18 | 2.1267 | 0.0401 | 0.0016 | 3 | 1.694 | 2.2542 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2080 | 9034.731 | 44266.0258 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.6517 | 0:240:120 | 0:00 | 1.609 | 7 | 0.0704 | 1.9908 | 2.0612 | 2.0175 | 0.0321 | 0.001 | 3 | 1.609 | 2.1327 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2083 | 9044.054 | 44266.026 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.7447 | 0:240:120 | 0:00 | 1.5291 | 7 | 0.0702 | 1.8869 | 1.9571 | 1.912 | 0.0323 | 0.001 | 3 | 1.5291 | 2.0195 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2086 | 9053.079 | 44266.0261 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.8596 | 0:240:120 | 0:00 | 1.454 | 7 | 0.0609 | 1.7897 | 1.8506 | 1.8111 | 0.0291 | 0.0008 | 3 | 1.454 | 1.9138 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2089 | 9061.938 | 44266.0262 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.9968 | 0:240:120 | 0:00 | 1.3834 | 7 | 0.0577 | 1.7035 | 1.7612 | 1.7232 | 0.0282 | 0.0008 | 3 | 1.3834 | 1.815 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2092 | 9070.507 | 44266.0263 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.1567 | 0:240:120 | 0:00 | 1.3168 | 7 | 0.0575 | 1.6115 | 1.669 | 1.6313 | 0.0277 | 0.0008 | 3 | 1.3168 | 1.7224 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2095 | 9078.799 | 44266.0264 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.3399 | 0:240:120 | 0:00 | 1.254 | 7 | 0.0442 | 1.5375 | 1.5817 | 1.5541 | 0.0206 | 0.0004 | 3 | 1.254 | 1.6356 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2098 | 9086.991 | 44266.0265 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.5467 | 0:240:120 | 0:00 | 1.1947 | 7 | 0.0525 | 1.4563 | 1.5088 | 1.4753 | 0.0243 | 0.0006 | 3 | 1.1947 | 1.5542 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2101 | 9094.884 | 44266.0265 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.7776 | 0:240:120 | 0:00 | 1.1387 | 7 | 0.0451 | 1.3878 | 1.4329 | 1.4035 | 0.0215 | 0.0005 | 3 | 1.1387 | 1.4776 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2104 | 9102.414 | 44266.0266 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.0332 | 0:240:120 | 0:00 | 1.0858 | 7 | 0.0446 | 1.3174 | 1.362 | 1.3359 | 0.0194 | 0.0004 | 3 | 1.0858 | 1.4056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2107 | 9109.834 | 44266.0267 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.3138 | 0:240:120 | 0:00 | 1.0357 | 7 | 0.0396 | 1.2591 | 1.2987 | 1.2729 | 0.0193 | 0.0004 | 3 | 1.0357 | 1.3377 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2110 | 9117.099 | 44266.0268 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.6201 | 0:240:120 | 0:00 | 0.9882 | 7 | 0.0375 | 1.1986 | 1.2361 | 1.2126 | 0.0173 | 0.0003 | 3 | 0.9882 | 1.2737 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2113 | 9124.075 | 44266.0269 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.9525 | 0:240:120 | 0:00 | 0.9433 | 7 | 0.0374 | 1.1419 | 1.1793 | 1.1552 | 0.0171 | 0.0003 | 3 | 0.9433 | 1.2134 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2116 | 9130.909 | 44266.027 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.3115 | 0:240:120 | 0:00 | 0.9007 | 7 | 0.034 | 1.0902 | 1.1242 | 1.1023 | 0.0162 | 0.0003 | 3 | 0.9007 | 1.1563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2119 | 9137.847 | 44266.027 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.6978 | 0:240:120 | 0:00 | 0.8602 | 7 | 0.0337 | 1.0391 | 1.0728 | 1.0509 | 0.0156 | 0.0002 | 3 | 0.8602 | 1.1024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2122 | 9144.293 | 44266.0271 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.1117 | 0:240:120 | 0:00 | 0.8218 | 7 | 0.0301 | 0.9933 | 1.0234 | 1.0039 | 0.0142 | 0.0002 | 3 | 0.8218 | 1.0514 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2125 | 9151.172 | 44266.0272 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.554 | 0:240:120 | 0:00 | 0.7854 | 7 | 0.031 | 0.9454 | 0.9764 | 0.9571 | 0.0142 | 0.0002 | 3 | 0.7854 | 1.0032 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2128 | 9157.404 | 44266.0273 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.025 | 0:240:120 | 0:00 | 0.7507 | 7 | 0.0273 | 0.9033 | 0.9306 | 0.9136 | 0.0124 | 0.0002 | 3 | 0.7507 | 0.9574 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2131 | 9163.523 | 44266.0273 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.5255 | 0:240:120 | 0:00 | 0.7177 | 7 | 0.0265 | 0.8614 | 0.8879 | 0.8709 | 0.0118 | 0.0001 | 3 | 0.7177 | 0.9141 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2134 | 9169.423 | 44266.0274 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.0561 | 0:240:120 | 0:00 | 0.6864 | 7 | 0.0231 | 0.8251 | 0.8482 | 0.8333 | 0.0109 | 0.0001 | 3 | 0.6864 | 0.8729 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2137 | 9174.978 | 44266.0275 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.6172 | 0:240:120 | 0:00 | 0.6566 | 7 | 0.024 | 0.7861 | 0.8101 | 0.7953 | 0.0107 | 0.0001 | 3 | 0.6566 | 0.8339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2140 | 9180.582 | 44266.0275 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.2095 | 0:240:120 | 0:00 | 0.6281 | 7 | 0.0228 | 0.7518 | 0.7746 | 0.761 | 0.01 | 0.0001 | 3 | 0.6281 | 0.7968 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2143 | 9186.279 | 44266.0276 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.8337 | 0:240:120 | 0:00 | 0.6011 | 7 | 0.019 | 0.72 | 0.739 | 0.7271 | 0.0089 | 0.0001 | 3 | 0.6011 | 0.7616 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2146 | 9192.068 | 44266.0277 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.4904 | 0:240:120 | 0:00 | 0.5753 | 7 | 0.0222 | 0.6871 | 0.7093 | 0.6956 | 0.0094 | 0.0001 | 3 | 0.5753 | 0.7281 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2149 | 9197.377 | 44266.0277 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.1802 | 0:240:120 | 0:00 | 0.5507 | 7 | 0.0193 | 0.6591 | 0.6784 | 0.6659 | 0.0089 | 0.0001 | 3 | 0.5507 | 0.6963 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2152 | 9203.093 | 44266.0278 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.9038 | 0:240:120 | 0:00 | 0.5273 | 7 | 0.0164 | 0.6309 | 0.6473 | 0.6367 | 0.0075 | 0.0001 | 3 | 0.5273 | 0.666 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2155 | 9208.414 | 44266.0279 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.6619 | 0:240:120 | 0:00 | 0.5049 | 7 | 0.0162 | 0.6035 | 0.6197 | 0.6092 | 0.0077 | 0.0001 | 3 | 0.5049 | 0.6371 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2158 | 9213.563 | 44266.0279 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.4551 | 0:240:120 | 0:00 | 0.4836 | 7 | 0.0163 | 0.5772 | 0.5935 | 0.5833 | 0.0076 | 0.0001 | 3 | 0.4836 | 0.6096 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2161 | 9218.485 | 44266.028 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.2842 | 0:240:120 | 0:00 | 0.4632 | 7 | 0.0148 | 0.5528 | 0.5676 | 0.5583 | 0.0067 | 0 | 3 | 0.4632 | 0.5834 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2164 | 9223.387 | 44266.028 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.1499 | 0:240:120 | 0:00 | 0.4438 | 7 | 0.0143 | 0.53 | 0.5443 | 0.5346 | 0.0067 | 0 | 3 | 0.4438 | 0.5585 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2167 | 9228.681 | 44266.0281 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.0529 | 0:240:120 | 0:00 | 0.4252 | 7 | 0.0125 | 0.5077 | 0.5202 | 0.5123 | 0.0058 | 0 | 3 | 0.4252 | 0.5347 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2170 | 9233.499 | 44266.0281 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.9939 | 0:240:120 | 0:00 | 0.4075 | 7 | 0.0125 | 0.4863 | 0.4988 | 0.4906 | 0.0059 | 0 | 3 | 0.4075 | 0.512 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2173 | 9238.16 | 44266.0282 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.9738 | 0:240:120 | 0:00 | 0.3906 | 7 | 0.0126 | 0.4648 | 0.4774 | 0.4698 | 0.0058 | 0 | 3 | 0.3906 | 0.4903 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2176 | 9242.704 | 44266.0283 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.9933 | 0:240:120 | 0:00 | 0.3744 | 7 | 0.0131 | 0.4453 | 0.4584 | 0.4504 | 0.0057 | 0 | 3 | 0.3744 | 0.4697 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2179 | 9247.506 | 44266.0283 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.0532 | 0:240:120 | 0:00 | 0.3589 | 7 | 0.0115 | 0.4265 | 0.438 | 0.4307 | 0.005 | 0 | 3 | 0.3589 | 0.4499 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2182 | 9251.988 | 44266.0284 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.1542 | 0:240:120 | 0:00 | 0.3441 | 7 | 0.0124 | 0.408 | 0.4204 | 0.4127 | 0.0054 | 0 | 3 | 0.3441 | 0.4311 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2185 | 9256.417 | 44266.0284 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.2973 | 0:240:120 | 0:00 | 0.3299 | 7 | 0.0111 | 0.3921 | 0.4032 | 0.3962 | 0.0048 | 0 | 3 | 0.3299 | 0.4131 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2188 | 9261.206 | 44266.0285 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.4833 | 0:240:120 | 0:00 | 0.3164 | 7 | 0.0089 | 0.3765 | 0.3854 | 0.3795 | 0.0041 | 0 | 3 | 0.3164 | 0.3959 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2191 | 9265.784 | 44266.0285 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.7129 | 0:240:120 | 0:00 | 0.3034 | 7 | 0.0092 | 0.361 | 0.3702 | 0.3645 | 0.0041 | 0 | 3 | 0.3034 | 0.3795 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2194 | 9270.094 | 44266.0286 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 115.9872 | 0:240:120 | 0:00 | 0.291 | 7 | 0.0087 | 0.3466 | 0.3553 | 0.3497 | 0.004 | 0 | 3 | 0.291 | 0.3638 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2197 | 9274.578 | 44266.0286 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.3069 | 0:240:120 | 0:00 | 0.2791 | 7 | 0.0098 | 0.3306 | 0.3404 | 0.3348 | 0.0039 | 0 | 3 | 0.2791 | 0.3487 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2200 | 9278.968 | 44266.0287 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.6731 | 0:240:120 | 0:00 | 0.2678 | 7 | 0.0095 | 0.3173 | 0.3268 | 0.3208 | 0.0041 | 0 | 3 | 0.2678 | 0.3344 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2203 | 9283.324 | 44266.0287 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.0865 | 0:240:120 | 0:00 | 0.2569 | 7 | 0.0087 | 0.3045 | 0.3132 | 0.3081 | 0.0034 | 0 | 3 | 0.2569 | 0.3206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2206 | 9287.849 | 44266.0288 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.5483 | 0:240:120 | 0:00 | 0.2464 | 7 | 0.0073 | 0.2927 | 0.3 | 0.2956 | 0.0031 | 0 | 3 | 0.2464 | 0.3075 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2209 | 9291.906 | 44266.0288 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.0592 | 0:240:120 | 0:00 | 0.2365 | 7 | 0.0075 | 0.2797 | 0.2872 | 0.2832 | 0.0029 | 0 | 3 | 0.2365 | 0.2949 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2212 | 9296.472 | 44266.0289 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.6204 | 0:240:120 | 0:00 | 0.2269 | 7 | 0.0078 | 0.2697 | 0.2775 | 0.2728 | 0.0031 | 0 | 3 | 0.2269 | 0.2829 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2215 | 9300.635 | 44266.0289 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.2328 | 0:240:120 | 0:00 | 0.2177 | 7 | 0.0079 | 0.2579 | 0.2658 | 0.2612 | 0.0033 | 0 | 3 | 0.2177 | 0.2713 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2218 | 9304.525 | 44266.029 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 135.8975 | 0:240:120 | 0:00 | 0.209 | 7 | 0.0076 | 0.2476 | 0.2552 | 0.2504 | 0.0034 | 0 | 3 | 0.209 | 0.2603 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2221 | 9308.602 | 44266.029 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.6154 | 0:240:120 | 0:00 | 0.2006 | 7 | 0.0076 | 0.2368 | 0.2444 | 0.2402 | 0.0031 | 0 | 3 | 0.2006 | 0.2497 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2224 | 9312.726 | 44266.0291 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.3877 | 0:240:120 | 0:00 | 0.1925 | 7 | 0.0057 | 0.2281 | 0.2338 | 0.2303 | 0.0023 | 0 | 3 | 0.1925 | 0.2396 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2227 | 9316.611 | 44266.0291 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.2155 | 0:240:120 | 0:00 | 0.1848 | 7 | 0.0052 | 0.2194 | 0.2246 | 0.2216 | 0.0021 | 0 | 3 | 0.1848 | 0.2299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2230 | 9320.767 | 44266.0292 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.0998 | 0:240:120 | 0:00 | 0.1774 | 7 | 0.0052 | 0.2101 | 0.2153 | 0.2122 | 0.0022 | 0 | 3 | 0.1774 | 0.2206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2233 | 9325.047 | 44266.0292 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.0418 | 0:240:120 | 0:00 | 0.1703 | 7 | 0.0064 | 0.2015 | 0.2079 | 0.2041 | 0.0025 | 0 | 3 | 0.1703 | 0.2117 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2236 | 9328.922 | 44266.0293 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.0426 | 0:240:120 | 0:00 | 0.1635 | 7 | 0.0063 | 0.1927 | 0.199 | 0.1955 | 0.0025 | 0 | 3 | 0.1635 | 0.2032 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2239 | 9332.878 | 44266.0293 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.1035 | 0:240:120 | 0:00 | 0.1569 | 7 | 0.0053 | 0.1855 | 0.1908 | 0.1878 | 0.0021 | 0 | 3 | 0.1569 | 0.195 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2242 | 9336.693 | 44266.0293 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 159.2256 | 0:240:120 | 0:00 | 0.1507 | 7 | 0.0039 | 0.1787 | 0.1826 | 0.1806 | 0.0015 | 0 | 3 | 0.1507 | 0.1872 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2245 | 9340.566 | 44266.0294 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 162.4101 | 0:240:120 | 0:00 | 0.1447 | 7 | 0.005 | 0.171 | 0.176 | 0.1736 | 0.002 | 0 | 3 | 0.1447 | 0.1797 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2248 | 9344.316 | 44266.0294 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.6583 | 0:240:120 | 0:00 | 0.1389 | 7 | 0.0041 | 0.165 | 0.1691 | 0.1669 | 0.0016 | 0 | 3 | 0.1389 | 0.1725 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2251 | 9348.219 | 44266.0295 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 168.9714 | 0:240:120 | 0:00 | 0.1334 | 7 | 0.0048 | 0.1577 | 0.1625 | 0.16 | 0.0018 | 0 | 3 | 0.1334 | 0.1656 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2254 | 9351.989 | 44266.0295 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 172.3509 | 0:240:120 | 0:00 | 0.1281 | 7 | 0.0054 | 0.1505 | 0.1559 | 0.1534 | 0.002 | 0 | 3 | 0.1281 | 0.159 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2257 | 9355.86 | 44266.0296 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175.7979 | 0:240:120 | 0:00 | 0.123 | 7 | 0.004 | 0.1455 | 0.1495 | 0.1474 | 0.0015 | 0 | 3 | 0.123 | 0.1526 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2260 | 9359.669 | 44266.0296 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 179.3138 | 0:240:120 | 0:00 | 0.1181 | 7 | 0.0041 | 0.1389 | 0.143 | 0.1412 | 0.0015 | 0 | 3 | 0.1181 | 0.1466 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2263 | 9363.409 | 44266.0297 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 182.9001 | 0:240:120 | 0:00 | 0.1134 | 7 | 0.0043 | 0.1338 | 0.1381 | 0.136 | 0.0015 | 0 | 3 | 0.1134 | 0.1407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2266 | 9367.515 | 44266.0297 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 186.5581 | 0:240:120 | 0:00 | 0.1089 | 7 | 0.0035 | 0.1283 | 0.1318 | 0.1303 | 0.0014 | 0 | 3 | 0.1089 | 0.1351 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2269 | 9371.269 | 44266.0297 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 190.2893 | 0:240:120 | 0:00 | 0.1046 | 7 | 0.0042 | 0.1235 | 0.1277 | 0.1255 | 0.0014 | 0 | 3 | 0.1046 | 0.1298 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2272 | 9375.019 | 44266.0298 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.0951 | 0:240:120 | 0:00 | 0.1005 | 7 | 0.0042 | 0.1188 | 0.123 | 0.1207 | 0.0016 | 0 | 3 | 0.1005 | 0.1246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2275 | 9378.729 | 44266.0298 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 197.977 | 0:240:120 | 0:00 | 0.0965 | 7 | 0.0041 | 0.1141 | 0.1182 | 0.1164 | 0.0014 | 0 | 3 | 0.0965 | 0.1197 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2278 | 9382.532 | 44266.0299 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 201.9365 | 0:240:120 | 0:00 | 0.0927 | 7 | 0.003 | 0.1094 | 0.1124 | 0.1112 | 0.0012 | 0 | 3 | 0.0927 | 0.1149 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2281 | 9386.474 | 44266.0299 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 205.9752 | 0:240:120 | 0:00 | 0.0891 | 7 | 0.003 | 0.1052 | 0.1082 | 0.1069 | 0.0009 | 0 | 3 | 0.0891 | 0.1104 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2284 | 9390.223 | 44266.03 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 210.0947 | 0:240:120 | 0:00 | 0.0855 | 7 | 0.003 | 0.1013 | 0.1043 | 0.1027 | 0.001 | 0 | 3 | 0.0855 | 0.106 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2287 | 9393.834 | 44266.03 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 214.2966 | 0:240:120 | 0:00 | 0.0822 | 7 | 0.0038 | 0.0969 | 0.1007 | 0.0987 | 0.0015 | 0 | 3 | 0.0822 | 0.1018 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2290 | 9397.529 | 44266.03 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 218.5826 | 0:240:120 | 0:00 | 0.0789 | 7 | 0.0036 | 0.0927 | 0.0963 | 0.0946 | 0.0013 | 0 | 3 | 0.0789 | 0.0978 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2293 | 9401.315 | 44266.0301 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 222.9542 | 0:240:120 | 0:00 | 0.0758 | 7 | 0.0026 | 0.0906 | 0.0932 | 0.0917 | 0.0009 | 0 | 3 | 0.0758 | 0.0939 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2296 | 9405.163 | 44266.0301 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 227.4133 | 0:240:120 | 0:00 | 0.0728 | 7 | 0.0027 | 0.0859 | 0.0886 | 0.0874 | 0.0008 | 0 | 3 | 0.0728 | 0.0902 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2299 | 9408.84 | 44266.0302 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 231.9616 | 0:240:120 | 0:00 | 0.07 | 7 | 0.0039 | 0.0816 | 0.0855 | 0.084 | 0.0015 | 0 | 3 | 0.07 | 0.0867 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2302 | 9412.481 | 44266.0302 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 236.6008 | 0:240:120 | 0:00 | 0.0672 | 7 | 0.0028 | 0.0797 | 0.0825 | 0.0812 | 0.0011 | 0 | 3 | 0.0672 | 0.0832 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2305 | 9416.108 | 44266.0303 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 241.3328 | 0:240:120 | 0:00 | 0.0646 | 7 | 0.0031 | 0.076 | 0.0791 | 0.0777 | 0.0011 | 0 | 3 | 0.0646 | 0.08 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2308 | 9419.871 | 44266.0303 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.1595 | 0:240:120 | 0:00 | 0.0621 | 7 | 0.0034 | 0.0733 | 0.0767 | 0.0751 | 0.0011 | 0 | 3 | 0.0621 | 0.0768 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2311 | 9423.695 | 44266.0304 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 251.0827 | 0:240:120 | 0:00 | 0.0596 | 7 | 0.0037 | 0.07 | 0.0737 | 0.0718 | 0.0013 | 0 | 3 | 0.0596 | 0.0738 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2314 | 9427.354 | 44266.0304 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.1043 | 0:240:120 | 0:00 | 0.0573 | 7 | 0.0023 | 0.0681 | 0.0704 | 0.0696 | 0.001 | 0 | 3 | 0.0573 | 0.0709 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2317 | 9430.945 | 44266.0304 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 261.2264 | 0:240:120 | 0:00 | 0.055 | 7 | 0.003 | 0.0645 | 0.0675 | 0.0667 | 0.001 | 0 | 3 | 0.055 | 0.0681 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2320 | 9434.515 | 44266.0305 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 266.4509 | 0:240:120 | 0:00 | 0.0529 | 7 | 0.0035 | 0.0621 | 0.0656 | 0.064 | 0.0014 | 0 | 3 | 0.0529 | 0.0654 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2323 | 9438.129 | 44266.0305 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 271.7799 | 0:240:120 | 0:00 | 0.0508 | 7 | 0.0033 | 0.0593 | 0.0626 | 0.0614 | 0.0013 | 0 | 3 | 0.0508 | 0.0629 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2326 | 9441.71 | 44266.0306 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 277.2155 | 0:240:120 | 0:00 | 0.0488 | 7 | 0.003 | 0.0576 | 0.0606 | 0.0596 | 0.001 | 0 | 3 | 0.0488 | 0.0604 | P | NP | 0-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2329 | 9445.336 | 44266.0306 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 282.7599 | 0:240:120 | 0:00 | 0.0469 | 7 | 0.0027 | 0.0554 | 0.0581 | 0.0573 | 0.0011 | 0 | 3 | 0.0469 | 0.058 | P | NP | 1-1-1-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2332 | 9449.187 | 44266.0306 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 288.4151 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0017 | 0.0538 | 0.0555 | 0.0548 | 0.0006 | 0 | 3 | 0.0451 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2335 | 9453.318 | 44266.0307 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.1834 | 0:240:120 | 0:00 | 0.0433 | 7 | 0.0015 | 0.0517 | 0.0532 | 0.0526 | 0.0006 | 0 | 3 | 0.0433 | 0.0536 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2338 | 9456.959 | 44266.0307 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 300.067 | 0:240:120 | 0:00 | 0.0416 | 7 | 0.003 | 0.0493 | 0.0523 | 0.0508 | 0.0013 | 0 | 3 | 0.0416 | 0.0516 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2341 | 9460.469 | 44266.0308 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 306.0684 | 0:240:120 | 0:00 | 0.04 | 7 | 0.003 | 0.0477 | 0.0507 | 0.0492 | 0.001 | 0 | 3 | 0.04 | 0.05 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2344 | 9464.038 | 44266.0308 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 312.1897 | 0:240:120 | 0:00 | 0.0384 | 7 | 0.0034 | 0.0452 | 0.0486 | 0.0472 | 0.0011 | 0 | 3 | 0.0384 | 0.0484 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2347 | 9467.554 | 44266.0309 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 318.4335 | 0:240:120 | 0:00 | 0.0369 | 7 | 0.0025 | 0.044 | 0.0465 | 0.0453 | 0.0008 | 0 | 3 | 0.0369 | 0.0469 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2350 | 9471.231 | 44266.0309 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 324.8022 | 0:240:120 | 0:00 | 0.0355 | 7 | 0.003 | 0.0419 | 0.0449 | 0.0436 | 0.001 | 0 | 3 | 0.0355 | 0.0455 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2353 | 9474.848 | 44266.0309 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 331.2982 | 0:240:120 | 0:00 | 0.0341 | 7 | 0.003 | 0.0397 | 0.0427 | 0.0416 | 0.0013 | 0 | 3 | 0.0341 | 0.0441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2356 | 9478.369 | 44266.031 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 337.9242 | 0:240:120 | 0:00 | 0.0328 | 7 | 0.0032 | 0.0385 | 0.0417 | 0.0404 | 0.0013 | 0 | 3 | 0.0328 | 0.0428 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2359 | 9481.964 | 44266.031 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 344.6827 | 0:240:120 | 0:00 | 0.0315 | 7 | 0.0018 | 0.0381 | 0.0399 | 0.0391 | 0.0006 | 0 | 3 | 0.0315 | 0.0415 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2362 | 9485.647 | 44266.0311 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 351.5763 | 0:240:120 | 0:00 | 0.0302 | 7 | 0.003 | 0.0361 | 0.0391 | 0.0375 | 0.001 | 0 | 3 | 0.0302 | 0.0402 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2365 | 9489.284 | 44266.0311 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 358.6079 | 0:240:120 | 0:00 | 0.0291 | 7 | 0.0023 | 0.0347 | 0.037 | 0.0361 | 0.0011 | 0 | 3 | 0.0291 | 0.0391 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2368 | 9492.682 | 44266.0311 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 365.78 | 0:240:120 | 0:00 | 0.0279 | 7 | 0.0023 | 0.0339 | 0.0362 | 0.0349 | 0.0008 | 0 | 3 | 0.0279 | 0.0379 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2371 | 9496.178 | 44266.0312 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 373.0956 | 0:240:120 | 0:00 | 0.0268 | 7 | 0.0034 | 0.0318 | 0.0352 | 0.0337 | 0.0012 | 0 | 3 | 0.0268 | 0.0368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2374 | 9499.726 | 44266.0312 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 380.5575 | 0:240:120 | 0:00 | 0.0258 | 7 | 0.0038 | 0.0302 | 0.034 | 0.0323 | 0.0011 | 0 | 3 | 0.0258 | 0.0358 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2377 | 9503.166 | 44266.0313 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 388.1687 | 0:240:120 | 0:00 | 0.0248 | 7 | 0.0027 | 0.0298 | 0.0325 | 0.0313 | 0.0011 | 0 | 3 | 0.0248 | 0.0348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2380 | 9506.62 | 44266.0313 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 395.9321 | 0:240:120 | 0:00 | 0.0238 | 7 | 0.003 | 0.0289 | 0.0319 | 0.0306 | 0.0012 | 0 | 3 | 0.0238 | 0.0338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2383 | 9510.119 | 44266.0314 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 403.8507 | 0:240:120 | 0:00 | 0.0229 | 7 | 0.0028 | 0.0276 | 0.0304 | 0.029 | 0.001 | 0 | 3 | 0.0229 | 0.0329 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2386 | 9513.842 | 44266.0314 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 411.9277 | 0:240:120 | 0:00 | 0.022 | 7 | 0.0029 | 0.0265 | 0.0294 | 0.0282 | 0.0011 | 0 | 3 | 0.022 | 0.032 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2389 | 9517.18 | 44266.0314 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 420.1663 | 0:240:120 | 0:00 | 0.0211 | 7 | 0.0041 | 0.0251 | 0.0292 | 0.0275 | 0.0013 | 0 | 3 | 0.0211 | 0.0311 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2392 | 9520.537 | 44266.0315 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 428.5696 | 0:240:120 | 0:00 | 0.0203 | 7 | 0.003 | 0.025 | 0.028 | 0.0268 | 0.0012 | 0 | 3 | 0.0203 | 0.0303 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2395 | 9524.259 | 44266.0315 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 437.141 | 0:240:120 | 0:00 | 0.0195 | 7 | 0.0032 | 0.0239 | 0.0271 | 0.0259 | 0.0013 | 0 | 3 | 0.0195 | 0.0295 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2398 | 9527.585 | 44266.0316 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 445.8838 | 0:240:120 | 0:00 | 0.0188 | 7 | 0.0038 | 0.0226 | 0.0264 | 0.0248 | 0.0014 | 0 | 3 | 0.0188 | 0.0288 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2401 | 9531.317 | 44266.0316 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 454.8015 | 0:240:120 | 0:00 | 0.018 | 7 | 0.0029 | 0.0226 | 0.0255 | 0.024 | 0.001 | 0 | 3 | 0.018 | 0.028 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2404 | 9534.724 | 44266.0316 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 463.8975 | 0:240:120 | 0:00 | 0.0173 | 7 | 0.0029 | 0.0218 | 0.0247 | 0.0235 | 0.0011 | 0 | 3 | 0.0173 | 0.0273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2407 | 9538.264 | 44266.0317 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 473.1755 | 0:240:120 | 0:00 | 0.0167 | 7 | 0.0038 | 0.0204 | 0.0242 | 0.0229 | 0.0014 | 0 | 3 | 0.0167 | 0.0267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2410 | 9541.835 | 44266.0317 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 482.639 | 0:240:120 | 0:00 | 0.016 | 7 | 0.004 | 0.0199 | 0.0239 | 0.0223 | 0.0013 | 0 | 3 | 0.016 | 0.026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2413 | 9545.36 | 44266.0318 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 492.2918 | 0:240:120 | 0:00 | 0.0154 | 7 | 0.0037 | 0.0195 | 0.0232 | 0.0216 | 0.0014 | 0 | 3 | 0.0154 | 0.0254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2416 | 9548.618 | 44266.0318 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 502.1376 | 0:240:120 | 0:00 | 0.0148 | 7 | 0.0033 | 0.0192 | 0.0225 | 0.0213 | 0.0013 | 0 | 3 | 0.0148 | 0.0248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2419 | 9552.271 | 44266.0318 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 512.1803 | 0:240:120 | 0:00 | 0.0142 | 7 | 0.003 | 0.0192 | 0.0222 | 0.0208 | 0.0011 | 0 | 3 | 0.0142 | 0.0242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2422 | 9555.755 | 44266.0319 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 522.4239 | 0:240:120 | 0:00 | 0.0137 | 7 | 0.0032 | 0.0184 | 0.0216 | 0.0202 | 0.0012 | 0 | 3 | 0.0137 | 0.0237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2425 | 9559.194 | 44266.0319 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 532.8724 | 0:240:120 | 0:00 | 0.0131 | 7 | 0.0029 | 0.0182 | 0.0211 | 0.0197 | 0.0009 | 0 | 3 | 0.0131 | 0.0231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2428 | 9562.618 | 44266.032 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 543.5299 | 0:240:120 | 0:00 | 0.0126 | 7 | 0.0034 | 0.0178 | 0.0212 | 0.019 | 0.0013 | 0 | 3 | 0.0126 | 0.0226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2431 | 9565.799 | 44266.032 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 554.4005 | 0:240:120 | 0:00 | 0.0121 | 7 | 0.0034 | 0.0179 | 0.0213 | 0.019 | 0.0012 | 0 | 3 | 0.0121 | 0.0221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2434 | 9569.212 | 44266.032 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 565.4885 | 0:240:120 | 0:00 | 0.0117 | 7 | 0.0022 | 0.0176 | 0.0198 | 0.0186 | 0.0008 | 0 | 3 | 0.0117 | 0.0217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2437 | 9572.591 | 44266.0321 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 576.7983 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.002 | 0.0178 | 0.0198 | 0.0186 | 0.0007 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2440 | 9576.064 | 44266.0321 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 588.3342 | 0:240:120 | 0:00 | 0.0108 | 7 | 0.0012 | 0.0169 | 0.0181 | 0.0177 | 0.0006 | 0 | 3 | 0.0108 | 0.0208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2443 | 9579.434 | 44266.0322 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 600.1009 | 0:240:120 | 0:00 | 0.0103 | 7 | 0.002 | 0.0166 | 0.0186 | 0.0176 | 0.0005 | 0 | 3 | 0.0103 | 0.0203 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2446 | 9583.109 | 44266.0322 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 610.3081 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0013 | 0.0163 | 0.0176 | 0.0172 | 0.0004 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2449 | 9586.562 | 44266.0322 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 622.5143 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0029 | 0.0156 | 0.0185 | 0.0168 | 0.0009 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 1-0-0-0-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
2452 | 9590.182 | 44266.0323 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 634.9646 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0031 | 0.015 | 0.0181 | 0.0164 | 0.0013 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 1-0-0-1-0-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2455 | 9593.513 | 44266.0323 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 647.6639 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0029 | 0.0146 | 0.0175 | 0.016 | 0.0009 | 0 | 3 | 0.0089 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2458 | 9596.958 | 44266.0324 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 660.6171 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0041 | 0.0136 | 0.0177 | 0.0153 | 0.0014 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2461 | 9600.7 | 44266.0324 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 673.8295 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0041 | 0.0128 | 0.0169 | 0.0152 | 0.0013 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2464 | 9604.202 | 44266.0324 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 687.3061 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0041 | 0.0128 | 0.0169 | 0.0149 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2467 | 9607.658 | 44266.0325 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 701.0522 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0042 | 0.0125 | 0.0167 | 0.0147 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2470 | 9611.146 | 44266.0325 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 715.0732 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0041 | 0.0124 | 0.0165 | 0.0147 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2473 | 9614.508 | 44266.0326 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 729.3747 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0039 | 0.0126 | 0.0165 | 0.0145 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2476 | 9618.171 | 44266.0326 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 743.9622 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0052 | 0.012 | 0.0172 | 0.0143 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2479 | 9621.556 | 44266.0326 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 758.8414 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.006 | 0.0114 | 0.0174 | 0.0143 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2482 | 9625.339 | 44266.0327 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 774.0183 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0051 | 0.012 | 0.0171 | 0.0141 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2485 | 9629.139 | 44266.0327 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 789.4986 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0045 | 0.0116 | 0.0161 | 0.0137 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2488 | 9632.876 | 44266.0328 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 805.2886 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0054 | 0.0116 | 0.017 | 0.014 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2491 | 9636.453 | 44266.0328 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 821.3944 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0056 | 0.011 | 0.0166 | 0.0136 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2494 | 9640.183 | 44266.0329 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 837.8223 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0047 | 0.0107 | 0.0154 | 0.0132 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2497 | 9643.881 | 44266.0329 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 854.5787 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0052 | 0.0108 | 0.016 | 0.0134 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2500 | 9647.741 | 44266.0329 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 871.6703 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0052 | 0.0106 | 0.0158 | 0.0131 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2503 | 9651.205 | 44266.033 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 889.1037 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0042 | 0.0113 | 0.0155 | 0.0137 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2506 | 9654.472 | 44266.033 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 906.8858 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0051 | 0.0105 | 0.0156 | 0.0131 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2509 | 9657.932 | 44266.0331 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 925.0235 | 0:240:120 | 0:00 | 0.0043 | 7 | 0.0058 | 0.0103 | 0.0161 | 0.013 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2512 | 9661.212 | 44266.0331 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 943.5239 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0059 | 0.0102 | 0.0161 | 0.0131 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2515 | 9664.835 | 44266.0331 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 962.3944 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0042 | 0.011 | 0.0152 | 0.0133 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2518 | 9668.495 | 44266.0332 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 981.6423 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.005 | 0.0103 | 0.0153 | 0.013 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2521 | 9671.839 | 44266.0332 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1001.2752 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0044 | 0.0106 | 0.015 | 0.0128 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2524 | 9675.459 | 44266.0333 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1021.3007 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0048 | 0.0103 | 0.0151 | 0.0123 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2527 | 9678.796 | 44266.0333 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1041.7267 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0041 | 0.0103 | 0.0144 | 0.0122 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2530 | 9682.273 | 44266.0333 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1062.5612 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0039 | 0.0103 | 0.0142 | 0.0119 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2533 | 9685.795 | 44266.0334 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1083.8124 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0042 | 0.0097 | 0.0139 | 0.0113 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2536 | 9689.262 | 44266.0334 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1105.4887 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0029 | 0.0105 | 0.0134 | 0.0113 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2539 | 9692.632 | 44266.0335 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1127.5985 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0038 | 0.0095 | 0.0133 | 0.0112 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2542 | 9696.054 | 44266.0335 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1150.1504 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0029 | 0.0097 | 0.0126 | 0.0109 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2545 | 9699.89 | 44266.0335 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1173.1534 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0028 | 0.0102 | 0.013 | 0.0111 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2548 | 9703.28 | 44266.0336 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1196.6165 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0047 | 0.0103 | 0.015 | 0.0115 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2551 | 9706.723 | 44266.0336 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1220.5488 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0058 | 0.0093 | 0.0151 | 0.0112 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2554 | 9710.08 | 44266.0337 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1220.6162 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0036 | 0.0092 | 0.0128 | 0.0107 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2557 | 9713.803 | 44266.0337 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1245.0286 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0051 | 0.01 | 0.0151 | 0.0113 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2560 | 9717.349 | 44266.0337 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1269.9291 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0052 | 0.0099 | 0.0151 | 0.0114 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2563 | 9721.049 | 44266.0338 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1295.3277 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0031 | 0.0094 | 0.0125 | 0.0107 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2566 | 9724.756 | 44266.0338 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1321.2343 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0054 | 0.0091 | 0.0145 | 0.0112 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2569 | 9728.2 | 44266.0339 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1347.659 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0025 | 0.0094 | 0.0119 | 0.0105 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2572 | 9731.787 | 44266.0339 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1374.6121 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0035 | 0.0089 | 0.0124 | 0.0104 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2575 | 9735.45 | 44266.034 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1402.1044 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0029 | 0.0093 | 0.0122 | 0.0104 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2578 | 9738.714 | 44266.034 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1430.1465 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0026 | 0.0094 | 0.012 | 0.0107 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2581 | 9742.284 | 44266.034 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1458.7494 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0025 | 0.0091 | 0.0116 | 0.01 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2584 | 9745.714 | 44266.0341 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1487.9244 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0012 | 0.0098 | 0.011 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2587 | 9749.172 | 44266.0341 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1517.6829 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0018 | 0.0099 | 0.0117 | 0.0105 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2590 | 9752.666 | 44266.0342 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1548.0365 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.002 | 0.0097 | 0.0117 | 0.0105 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2593 | 9756.009 | 44266.0342 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1578.9973 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2596 | 9759.783 | 44266.0342 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1610.5772 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0022 | 0.0094 | 0.0116 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2599 | 9763.299 | 44266.0343 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1642.7887 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0012 | 0.0099 | 0.0111 | 0.0105 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2602 | 9766.64 | 44266.0343 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1675.6445 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0015 | 0.0095 | 0.011 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2605 | 9770.215 | 44266.0344 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1709.1574 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.002 | 0.0094 | 0.0114 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2608 | 9773.933 | 44266.0344 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1743.3406 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2611 | 9777.514 | 44266.0344 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1778.2074 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0026 | 0.009 | 0.0116 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2614 | 9781.006 | 44266.0345 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1813.7715 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0012 | 0.0091 | 0.0103 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2617 | 9784.55 | 44266.0345 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1850.0469 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0018 | 0.0095 | 0.0113 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2620 | 9788.435 | 44266.0346 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1887.0479 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0011 | 0.0104 | 0.0115 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2623 | 9791.813 | 44266.0346 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1924.7888 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0019 | 0.0094 | 0.0113 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2626 | 9795.336 | 44266.0347 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1963.2846 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0013 | 0.0099 | 0.0112 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2629 | 9798.672 | 44266.0347 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2002.5503 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0095 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2632 | 9801.958 | 44266.0347 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2042.6013 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2635 | 9805.455 | 44266.0348 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2083.4533 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2638 | 9808.786 | 44266.0348 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2125.1224 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0026 | 0.0089 | 0.0115 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2641 | 9812.144 | 44266.0348 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2167.6249 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2644 | 9815.699 | 44266.0349 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2210.9774 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0011 | 0.0093 | 0.0104 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2647 | 9819.156 | 44266.0349 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2255.1969 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0017 | 0.0098 | 0.0115 | 0.0105 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2650 | 9822.622 | 44266.035 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2300.3008 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2653 | 9825.943 | 44266.035 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2346.3069 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0106 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2656 | 9829.474 | 44266.035 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2393.233 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2659 | 9833.391 | 44266.0351 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2441.0977 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2662 | 9836.846 | 44266.0351 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2489.9196 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0001 | 0.0097 | 0.0098 | 0.0097 | 0 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2665 | 9840.112 | 44266.0352 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2539.718 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.001 | 0.0099 | 0.0109 | 0.01 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2668 | 9843.679 | 44266.0352 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2590.5124 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.002 | 0.0093 | 0.0113 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2671 | 9847.024 | 44266.0352 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2642.3226 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0008 | 0.0098 | 0.0106 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2674 | 9850.439 | 44266.0353 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2695.1691 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.002 | 0.0091 | 0.0111 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2677 | 9854.023 | 44266.0353 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2749.0724 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2680 | 9857.454 | 44266.0354 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2804.0539 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2683 | 9860.804 | 44266.0354 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2860.135 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2686 | 9864.259 | 44266.0354 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2917.3377 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2689 | 9867.733 | 44266.0355 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2975.6844 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0004 | 0.0105 | 0.0109 | 0.0107 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2692 | 9871.213 | 44266.0355 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3035.1981 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.001 | 0.0098 | 0.0108 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2695 | 9874.633 | 44266.0356 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3095.9021 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0015 | 0.0098 | 0.0113 | 0.0105 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2698 | 9878.057 | 44266.0356 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3157.8201 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0018 | 0.009 | 0.0108 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2701 | 9881.329 | 44266.0356 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3220.9765 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2704 | 9884.762 | 44266.0357 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3285.3961 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2707 | 9888.227 | 44266.0357 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3351.104 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2710 | 9891.642 | 44266.0358 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3418.1261 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0019 | 0.0089 | 0.0108 | 0.0096 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2713 | 9895.443 | 44266.0358 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3486.4886 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2716 | 9898.931 | 44266.0359 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3556.2183 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0009 | 0.0097 | 0.0106 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2719 | 9902.275 | 44266.0359 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3627.3427 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0018 | 0.0089 | 0.0107 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2722 | 9905.732 | 44266.0359 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3699.8896 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0097 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2725 | 9909.168 | 44266.036 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3773.8874 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2728 | 9912.773 | 44266.036 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3849.3651 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.002 | 0.0088 | 0.0108 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2731 | 9916.19 | 44266.0361 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3926.3524 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2734 | 9919.559 | 44266.0361 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4004.8795 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0098 | 0.0114 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2737 | 9923.243 | 44266.0361 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4084.977 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2740 | 9926.736 | 44266.0362 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4166.6766 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0023 | 0.009 | 0.0113 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2743 | 9930.229 | 44266.0362 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4250.0101 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2746 | 9933.674 | 44266.0363 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4335.0103 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0012 | 0.0096 | 0.0108 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2749 | 9936.909 | 44266.0363 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4421.7105 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0021 | 0.0091 | 0.0112 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2752 | 9940.374 | 44266.0363 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4510.1447 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2755 | 9943.933 | 44266.0364 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4600.3476 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0011 | 0.01 | 0.0111 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2758 | 9947.376 | 44266.0364 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4692.3546 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2761 | 9950.703 | 44266.0364 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4786.2017 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2764 | 9954.43 | 44266.0365 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4881.9257 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0097 | 0.0113 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2767 | 9957.918 | 44266.0365 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4979.5642 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0093 | 0.011 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2770 | 9961.63 | 44266.0366 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5079.1555 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2773 | 9965.295 | 44266.0366 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5180.7386 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0018 | 0.0094 | 0.0112 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2776 | 9968.824 | 44266.0367 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5284.3534 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.001 | 0.0094 | 0.0104 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2779 | 9972.261 | 44266.0367 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5390.0405 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0024 | 0.0088 | 0.0112 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2782 | 9975.795 | 44266.0367 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5497.8413 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.009 | 0.0101 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2785 | 9979.072 | 44266.0368 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5607.7981 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.002 | 0.0092 | 0.0112 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2788 | 9982.453 | 44266.0368 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5719.9541 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2791 | 9985.897 | 44266.0369 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5834.3531 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0094 | 0.0113 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2794 | 9989.413 | 44266.0369 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5951.0402 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2797 | 9992.76 | 44266.0369 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6070.061 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0005 | 0.01 | 0.0105 | 0.0103 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2800 | 9996.225 | 44266.037 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6191.4622 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0002 | 0.0096 | 0.0098 | 0.0096 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2803 | 9999.553 | 44266.037 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6315.2915 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0101 | 0.0113 | 0.0105 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2806 | 10003.104 | 44266.0371 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6441.5973 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0021 | 0.009 | 0.0111 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2809 | 10006.495 | 44266.0371 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6570.4292 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0018 | 0.0092 | 0.011 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2812 | 10009.813 | 44266.0371 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6701.8378 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0014 | 0.0097 | 0.0111 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2815 | 10013.434 | 44266.0372 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6835.8746 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2818 | 10016.826 | 44266.0372 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6972.5921 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2821 | 10020.11 | 44266.0373 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7112.0439 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2824 | 10023.391 | 44266.0373 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7254.2848 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0008 | 0.0092 | 0.01 | 0.0096 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2827 | 10026.719 | 44266.0373 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7399.3705 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0021 | 0.0091 | 0.0112 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2830 | 10030.047 | 44266.0374 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7547.3579 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2833 | 10033.362 | 44266.0374 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7698.3051 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2836 | 10036.717 | 44266.0374 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7852.2712 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2839 | 10040.485 | 44266.0375 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8009.3166 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2842 | 10044.141 | 44266.0375 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8169.5029 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.002 | 0.0089 | 0.0109 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2845 | 10047.895 | 44266.0376 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8332.893 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0004 | 0.0094 | 0.0098 | 0.0096 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2848 | 10051.542 | 44266.0376 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8499.5508 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.01 | 0.0111 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2851 | 10054.873 | 44266.0377 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8669.5419 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2854 | 10058.192 | 44266.0377 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8842.9327 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2857 | 10061.957 | 44266.0377 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9019.7913 | 0:240:120 | 0:00 | 0 | 7 | 0.001 | 0.0089 | 0.0099 | 0.0094 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2860 | 10065.491 | 44266.0378 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9200.1872 | 0:240:120 | 0:00 | 0 | 7 | 0.0015 | 0.0095 | 0.011 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2863 | 10069.026 | 44266.0378 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9384.1909 | 0:240:120 | 0:00 | 0 | 7 | 0.0009 | 0.0093 | 0.0102 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2866 | 10072.488 | 44266.0379 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9571.8747 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2869 | 10076.108 | 44266.0379 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9763.3122 | 0:240:120 | 0:00 | 0 | 7 | 0.0022 | 0.0087 | 0.0109 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2872 | 10079.487 | 44266.0379 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9958.5785 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.0095 | 0.0107 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2875 | 10082.846 | 44266.038 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10157.75 | 0:240:120 | 0:00 | 0 | 7 | 0.0024 | 0.0088 | 0.0112 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2878 | 10086.272 | 44266.038 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10360.905 | 0:240:120 | 0:00 | 0 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2881 | 10089.644 | 44266.0381 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10568.1231 | 0:240:120 | 0:00 | 0 | 7 | 0.0009 | 0.0096 | 0.0105 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2884 | 10093.058 | 44266.0381 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10779.4856 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.0096 | 0.0109 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2887 | 10096.455 | 44266.0381 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10995.0753 | 0:240:120 | 0:00 | 0 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2890 | 10100.045 | 44266.0382 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11214.9768 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2893 | 10103.606 | 44266.0382 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11439.2764 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2896 | 10107.406 | 44266.0383 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11668.0619 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0097 | 0.0108 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2899 | 10110.597 | 44266.0383 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11901.4231 | 0:240:120 | 0:00 | 0 | 7 | 0.0004 | 0.0097 | 0.0101 | 0.01 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2902 | 10262.634 | 44266.0401 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.9 | 0:240:120 | 0:00 | 17.0543 | 7 | 49.3838 | 100.6719 | 150.0557 | 124.7526 | 20.3403 | 413.7267 | 3 | 17.0543 | 78.0928 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2905 | 10665.144 | 44266.0447 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.5 | 0:240:120 | 0:00 | 14.6234 | 7 | 48.0402 | 51.4159 | 99.4561 | 72.7675 | 21.1309 | 446.5155 | 3 | 14.6234 | 47.9726 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2908 | 10915.727 | 44266.0476 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.1 | 0:240:120 | 0:00 | 12.7674 | 7 | 24.5486 | 24.8428 | 49.3914 | 33.2335 | 11.7984 | 139.2032 | 3 | 12.7674 | 34.6053 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2911 | 11042.165 | 44266.0491 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.7 | 0:240:120 | 0:00 | 11.3047 | 7 | 2.6776 | 21.9204 | 24.598 | 23.1237 | 1.1443 | 1.3095 | 3 | 11.3047 | 26.9497 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2914 | 11116.106 | 44266.0499 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.3 | 0:240:120 | 0:00 | 10.1228 | 7 | 2.2125 | 19.2766 | 21.4891 | 20.1089 | 1.0397 | 1.081 | 3 | 10.1228 | 21.9916 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2917 | 11180.391 | 44266.0507 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33 | 0:240:120 | 0:00 | 9.0024 | 7 | 2.4653 | 15.56 | 18.0253 | 16.7444 | 1.0284 | 1.0576 | 3 | 9.0024 | 18.0407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2920 | 11234.789 | 44266.0513 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.6 | 0:240:120 | 0:00 | 8.2082 | 7 | 2.6354 | 12.6166 | 15.252 | 13.8163 | 1.1463 | 1.3139 | 3 | 8.2082 | 15.5919 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2923 | 11280.785 | 44266.0518 | Vista Speed | E | 13E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.3 | 0:240:120 | 0:00 | 7.4287 | 7 | 0.8811 | 11.463 | 12.3441 | 11.8233 | 0.3883 | 0.1508 | 3 | 7.4287 | 13.4245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2926 | 11577.526 | 44266.0553 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33 | 0:240:120 | 0:00 | 26.1905 | 7 | 42.5758 | 224.6596 | 267.2354 | 242.2518 | 19.1685 | 367.4306 | 3 | 26.1905 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2929 | 12335.418 | 44266.0641 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.66 | 0:240:120 | 0:00 | 21.245 | 7 | 45.5094 | 174.6257 | 220.1351 | 192.7346 | 20.3594 | 414.5033 | 3 | 21.245 | 279.2439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2932 | 12943.478 | 44266.0711 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.3332 | 0:240:120 | 0:00 | 17.7567 | 7 | 42.797 | 124.6526 | 167.4496 | 140.0733 | 20.398 | 416.0767 | 3 | 17.7567 | 90.3242 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2935 | 13394.014 | 44266.0763 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.0199 | 0:240:120 | 0:00 | 15.1659 | 7 | 40.0048 | 73.5744 | 113.5792 | 88.1259 | 18.7856 | 352.8988 | 3 | 15.1659 | 53.0111 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2938 | 13679.619 | 44266.0796 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.7203 | 0:240:120 | 0:00 | 13.1671 | 7 | 30.4115 | 25.9227 | 56.3342 | 36.2289 | 14.9522 | 223.5683 | 3 | 13.1671 | 37.0762 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2941 | 13820.505 | 44266.0812 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.4347 | 0:240:120 | 0:00 | 11.5794 | 7 | 2.31 | 22.6628 | 24.9728 | 23.6982 | 0.9845 | 0.9692 | 3 | 11.5794 | 28.2433 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2944 | 13895.804 | 44266.0821 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.1634 | 0:240:120 | 0:00 | 10.2886 | 7 | 2.4662 | 19.6265 | 22.0927 | 20.6905 | 1.0888 | 1.1854 | 3 | 10.2886 | 22.6334 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2947 | 13962.461 | 44266.0829 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.9066 | 0:240:120 | 0:00 | 9.2194 | 7 | 2.6431 | 16.6269 | 19.27 | 17.5762 | 1.263 | 1.5951 | 3 | 9.2194 | 18.7572 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2950 | 14019.96 | 44266.0835 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.6648 | 0:240:120 | 0:00 | 8.3198 | 7 | 2.217 | 13.5642 | 15.7812 | 14.4176 | 1.0198 | 1.0399 | 3 | 8.3198 | 15.9205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2953 | 14067.464 | 44266.0841 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.4381 | 0:240:120 | 0:00 | 7.5531 | 7 | 0.8082 | 11.7058 | 12.514 | 12.0261 | 0.3685 | 0.1358 | 3 | 7.5531 | 13.756 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2956 | 14107.347 | 44266.0846 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.2268 | 0:240:120 | 0:00 | 6.8923 | 7 | 0.8561 | 10.6621 | 11.5182 | 10.9629 | 0.4103 | 0.1683 | 3 | 6.8923 | 12.0514 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2959 | 14143.81 | 44266.085 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.0314 | 0:240:120 | 0:00 | 6.3172 | 7 | 0.7903 | 9.4797 | 10.27 | 9.842 | 0.3316 | 0.11 | 3 | 6.3172 | 10.6752 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2962 | 14176.964 | 44266.0854 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.852 | 0:240:120 | 0:00 | 5.8127 | 7 | 0.9017 | 8.4037 | 9.3054 | 8.7173 | 0.4327 | 0.1872 | 3 | 5.8127 | 9.5415 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2965 | 14206.975 | 44266.0857 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.689 | 0:240:120 | 0:00 | 5.3667 | 7 | 0.4375 | 7.58 | 8.0175 | 7.7587 | 0.1919 | 0.0368 | 3 | 5.3667 | 8.5922 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2968 | 14233.555 | 44266.086 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.5428 | 0:240:120 | 0:00 | 4.97 | 7 | 0.425 | 7.0475 | 7.4725 | 7.1994 | 0.1997 | 0.0399 | 3 | 4.97 | 7.7862 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2971 | 14258.9 | 44266.0863 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.4137 | 0:240:120 | 0:00 | 4.6151 | 7 | 0.4524 | 6.4053 | 6.8577 | 6.5635 | 0.2197 | 0.0483 | 3 | 4.6151 | 7.0939 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2974 | 14282.259 | 44266.0866 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.3019 | 0:240:120 | 0:00 | 4.2959 | 7 | 0.4224 | 5.8001 | 6.2225 | 5.9525 | 0.2019 | 0.0408 | 3 | 4.2959 | 6.4932 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2977 | 14303.684 | 44266.0868 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.208 | 0:240:120 | 0:00 | 4.0075 | 7 | 0.249 | 5.4378 | 5.6868 | 5.5241 | 0.1172 | 0.0137 | 3 | 4.0075 | 5.9675 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2980 | 14323.841 | 44266.0871 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.1321 | 0:240:120 | 0:00 | 3.7459 | 7 | 0.2818 | 5.0482 | 5.33 | 5.1507 | 0.1335 | 0.0178 | 3 | 3.7459 | 5.5039 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2983 | 14343.144 | 44266.0873 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.0748 | 0:240:120 | 0:00 | 3.5077 | 7 | 0.2725 | 4.6636 | 4.9361 | 4.7577 | 0.1326 | 0.0176 | 3 | 3.5077 | 5.0923 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2986 | 14361.018 | 44266.0875 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.0363 | 0:240:120 | 0:00 | 3.29 | 7 | 0.2246 | 4.312 | 4.5366 | 4.3893 | 0.1099 | 0.0121 | 3 | 3.29 | 4.7247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2989 | 14377.327 | 44266.0877 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.017 | 0:240:120 | 0:00 | 3.0905 | 7 | 0.1803 | 4.0509 | 4.2312 | 4.1124 | 0.0883 | 0.0078 | 3 | 3.0905 | 4.3946 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2992 | 14392.987 | 44266.0879 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.0173 | 0:240:120 | 0:00 | 2.907 | 7 | 0.1829 | 3.7839 | 3.9668 | 3.8489 | 0.0882 | 0.0078 | 3 | 2.907 | 4.0969 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2995 | 14407.749 | 44266.088 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.0377 | 0:240:120 | 0:00 | 2.738 | 7 | 0.1875 | 3.516 | 3.7035 | 3.5831 | 0.0898 | 0.0081 | 3 | 2.738 | 3.8271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2998 | 14421.908 | 44266.0882 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.0784 | 0:240:120 | 0:00 | 2.5817 | 7 | 0.1388 | 3.3192 | 3.458 | 3.3727 | 0.0625 | 0.0039 | 3 | 2.5817 | 3.5817 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3001 | 14435.441 | 44266.0884 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.14 | 0:240:120 | 0:00 | 2.4371 | 7 | 0.1434 | 3.101 | 3.2444 | 3.1615 | 0.062 | 0.0038 | 3 | 2.4371 | 3.3577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3004 | 14448.22 | 44266.0885 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.2228 | 0:240:120 | 0:00 | 2.3028 | 7 | 0.1274 | 2.9123 | 3.0397 | 2.9553 | 0.0627 | 0.0039 | 3 | 2.3028 | 3.1526 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3007 | 14460.883 | 44266.0887 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.3273 | 0:240:120 | 0:00 | 2.178 | 7 | 0.1119 | 2.7541 | 2.866 | 2.7976 | 0.051 | 0.0026 | 3 | 2.178 | 2.9642 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3010 | 14472.585 | 44266.0888 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.4538 | 0:240:120 | 0:00 | 2.0617 | 7 | 0.1028 | 2.595 | 2.6978 | 2.6314 | 0.0485 | 0.0023 | 3 | 2.0617 | 2.7907 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3013 | 14483.735 | 44266.0889 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.6029 | 0:240:120 | 0:00 | 1.9532 | 7 | 0.1079 | 2.4409 | 2.5488 | 2.483 | 0.0493 | 0.0024 | 3 | 1.9532 | 2.6305 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3016 | 14494.414 | 44266.089 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.7749 | 0:240:120 | 0:00 | 1.8518 | 7 | 0.0767 | 2.3178 | 2.3945 | 2.345 | 0.0367 | 0.0013 | 3 | 1.8518 | 2.4822 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3019 | 14504.731 | 44266.0892 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.9704 | 0:240:120 | 0:00 | 1.7569 | 7 | 0.0947 | 2.1806 | 2.2753 | 2.2193 | 0.041 | 0.0017 | 3 | 1.7569 | 2.3448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3022 | 14514.831 | 44266.0893 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.1898 | 0:240:120 | 0:00 | 1.668 | 7 | 0.0735 | 2.0711 | 2.1446 | 2.0985 | 0.0344 | 0.0012 | 3 | 1.668 | 2.217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3025 | 14524.493 | 44266.0894 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.4336 | 0:240:120 | 0:00 | 1.5846 | 7 | 0.0683 | 1.9604 | 2.0287 | 1.9874 | 0.0308 | 0.0009 | 3 | 1.5846 | 2.0981 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3028 | 14533.892 | 44266.0895 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.7023 | 0:240:120 | 0:00 | 1.5062 | 7 | 0.0658 | 1.8584 | 1.9242 | 1.8824 | 0.0307 | 0.0009 | 3 | 1.5062 | 1.9872 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3031 | 14542.657 | 44266.0896 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.9964 | 0:240:120 | 0:00 | 1.4325 | 7 | 0.053 | 1.7683 | 1.8213 | 1.7867 | 0.0246 | 0.0006 | 3 | 1.4325 | 1.8836 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3034 | 14551.146 | 44266.0897 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.3163 | 0:240:120 | 0:00 | 1.3631 | 7 | 0.0537 | 1.6782 | 1.7319 | 1.6975 | 0.0255 | 0.0007 | 3 | 1.3631 | 1.7867 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3037 | 14559.63 | 44266.0898 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.6626 | 0:240:120 | 0:00 | 1.2977 | 7 | 0.0504 | 1.5904 | 1.6408 | 1.6092 | 0.0234 | 0.0005 | 3 | 1.2977 | 1.6959 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3040 | 14567.93 | 44266.0899 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.0359 | 0:240:120 | 0:00 | 1.2359 | 7 | 0.0524 | 1.5092 | 1.5616 | 1.5302 | 0.0233 | 0.0005 | 3 | 1.2359 | 1.6108 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3043 | 14575.723 | 44266.09 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.4366 | 0:240:120 | 0:00 | 1.1777 | 7 | 0.053 | 1.4351 | 1.4881 | 1.454 | 0.0254 | 0.0006 | 3 | 1.1777 | 1.5308 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3046 | 14583.382 | 44266.0901 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.8653 | 0:240:120 | 0:00 | 1.1226 | 7 | 0.0383 | 1.371 | 1.4093 | 1.3849 | 0.018 | 0.0003 | 3 | 1.1226 | 1.4556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3049 | 14590.843 | 44266.0902 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.3226 | 0:240:120 | 0:00 | 1.0705 | 7 | 0.0438 | 1.301 | 1.3448 | 1.3169 | 0.0205 | 0.0004 | 3 | 1.0705 | 1.3849 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3052 | 14598.342 | 44266.0902 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.8091 | 0:240:120 | 0:00 | 1.0212 | 7 | 0.0342 | 1.2432 | 1.2774 | 1.2555 | 0.0162 | 0.0003 | 3 | 1.0212 | 1.3182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3055 | 14605.388 | 44266.0903 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.3252 | 0:240:120 | 0:00 | 0.9746 | 7 | 0.0393 | 1.1815 | 1.2208 | 1.1951 | 0.0188 | 0.0004 | 3 | 0.9746 | 1.2553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3058 | 14612.266 | 44266.0904 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.8718 | 0:240:120 | 0:00 | 0.9303 | 7 | 0.0315 | 1.1264 | 1.1579 | 1.1376 | 0.0151 | 0.0002 | 3 | 0.9303 | 1.196 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3061 | 14618.881 | 44266.0905 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.4492 | 0:240:120 | 0:00 | 0.8884 | 7 | 0.0313 | 1.0739 | 1.1052 | 1.086 | 0.0144 | 0.0002 | 3 | 0.8884 | 1.1399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3064 | 14625.289 | 44266.0906 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.0582 | 0:240:120 | 0:00 | 0.8485 | 7 | 0.03 | 1.0252 | 1.0552 | 1.0364 | 0.0135 | 0.0002 | 3 | 0.8485 | 1.0869 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3067 | 14631.729 | 44266.0906 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.6993 | 0:240:120 | 0:00 | 0.8107 | 7 | 0.029 | 0.9776 | 1.0066 | 0.9881 | 0.0138 | 0.0002 | 3 | 0.8107 | 1.0368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3070 | 14637.964 | 44266.0907 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.3733 | 0:240:120 | 0:00 | 0.7748 | 7 | 0.0266 | 0.9329 | 0.9595 | 0.9426 | 0.0118 | 0.0001 | 3 | 0.7748 | 0.9893 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3073 | 14644.372 | 44266.0908 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.0808 | 0:240:120 | 0:00 | 0.7407 | 7 | 0.025 | 0.8924 | 0.9174 | 0.9009 | 0.0121 | 0.0001 | 3 | 0.7407 | 0.9442 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3076 | 14650.713 | 44266.0908 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.8224 | 0:240:120 | 0:00 | 0.7082 | 7 | 0.0233 | 0.8526 | 0.8759 | 0.8603 | 0.0112 | 0.0001 | 3 | 0.7082 | 0.9016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3079 | 14656.582 | 44266.0909 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.5989 | 0:240:120 | 0:00 | 0.6773 | 7 | 0.0239 | 0.8129 | 0.8368 | 0.8212 | 0.0109 | 0.0001 | 3 | 0.6773 | 0.8611 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3082 | 14662.456 | 44266.091 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.4108 | 0:240:120 | 0:00 | 0.6479 | 7 | 0.0213 | 0.7786 | 0.7999 | 0.786 | 0.01 | 0.0001 | 3 | 0.6479 | 0.8226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3085 | 14668.039 | 44266.091 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.259 | 0:240:120 | 0:00 | 0.6199 | 7 | 0.0223 | 0.7425 | 0.7648 | 0.7499 | 0.0101 | 0.0001 | 3 | 0.6199 | 0.7861 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3088 | 14673.54 | 44266.0911 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.1442 | 0:240:120 | 0:00 | 0.5933 | 7 | 0.0201 | 0.7118 | 0.7319 | 0.7188 | 0.0095 | 0.0001 | 3 | 0.5933 | 0.7514 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3091 | 14678.893 | 44266.0912 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.0671 | 0:240:120 | 0:00 | 0.5678 | 7 | 0.0192 | 0.681 | 0.7002 | 0.6878 | 0.0087 | 0.0001 | 3 | 0.5678 | 0.7184 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3094 | 14684.36 | 44266.0912 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.0285 | 0:240:120 | 0:00 | 0.5436 | 7 | 0.0178 | 0.6516 | 0.6694 | 0.6578 | 0.0086 | 0.0001 | 3 | 0.5436 | 0.6871 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3097 | 14689.656 | 44266.0913 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.029 | 0:240:120 | 0:00 | 0.5205 | 7 | 0.0172 | 0.6232 | 0.6404 | 0.6295 | 0.0075 | 0.0001 | 3 | 0.5205 | 0.6572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3100 | 14694.751 | 44266.0914 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.0696 | 0:240:120 | 0:00 | 0.4985 | 7 | 0.0168 | 0.5948 | 0.6116 | 0.6011 | 0.0076 | 0.0001 | 3 | 0.4985 | 0.6288 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3103 | 14699.936 | 44266.0914 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.151 | 0:240:120 | 0:00 | 0.4774 | 7 | 0.0157 | 0.5704 | 0.5861 | 0.5761 | 0.0071 | 0.0001 | 3 | 0.4774 | 0.6017 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3106 | 14705.059 | 44266.0915 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 108.274 | 0:240:120 | 0:00 | 0.4573 | 7 | 0.0141 | 0.5466 | 0.5607 | 0.5518 | 0.0066 | 0 | 3 | 0.4573 | 0.5759 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3109 | 14709.878 | 44266.0915 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.4395 | 0:240:120 | 0:00 | 0.4382 | 7 | 0.0136 | 0.5229 | 0.5365 | 0.5278 | 0.0062 | 0 | 3 | 0.4382 | 0.5513 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3112 | 14714.625 | 44266.0916 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.6483 | 0:240:120 | 0:00 | 0.4199 | 7 | 0.0144 | 0.5001 | 0.5145 | 0.5058 | 0.0062 | 0 | 3 | 0.4199 | 0.5278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3115 | 14719.339 | 44266.0916 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.9013 | 0:240:120 | 0:00 | 0.4024 | 7 | 0.0118 | 0.4801 | 0.4919 | 0.4843 | 0.0053 | 0 | 3 | 0.4024 | 0.5054 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3118 | 14723.994 | 44266.0917 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.1993 | 0:240:120 | 0:00 | 0.3856 | 7 | 0.0122 | 0.4592 | 0.4714 | 0.4636 | 0.0054 | 0 | 3 | 0.3856 | 0.4841 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3121 | 14728.501 | 44266.0917 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.5433 | 0:240:120 | 0:00 | 0.3697 | 7 | 0.0116 | 0.4408 | 0.4524 | 0.4448 | 0.0051 | 0 | 3 | 0.3697 | 0.4637 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3124 | 14733.171 | 44266.0918 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.9341 | 0:240:120 | 0:00 | 0.3544 | 7 | 0.0111 | 0.4214 | 0.4325 | 0.4255 | 0.005 | 0 | 3 | 0.3544 | 0.4442 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3127 | 14737.732 | 44266.0919 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.3728 | 0:240:120 | 0:00 | 0.3398 | 7 | 0.01 | 0.4044 | 0.4144 | 0.408 | 0.0047 | 0 | 3 | 0.3398 | 0.4256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3130 | 14742.331 | 44266.0919 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.8603 | 0:240:120 | 0:00 | 0.3258 | 7 | 0.0104 | 0.3868 | 0.3972 | 0.3907 | 0.0046 | 0 | 3 | 0.3258 | 0.4079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3133 | 14746.911 | 44266.092 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 129.3975 | 0:240:120 | 0:00 | 0.3124 | 7 | 0.0087 | 0.3714 | 0.3801 | 0.3746 | 0.0039 | 0 | 3 | 0.3124 | 0.3909 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3136 | 14751.205 | 44266.092 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131.9854 | 0:240:120 | 0:00 | 0.2996 | 7 | 0.0104 | 0.3559 | 0.3663 | 0.3601 | 0.0042 | 0 | 3 | 0.2996 | 0.3747 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3139 | 14755.681 | 44266.0921 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.6251 | 0:240:120 | 0:00 | 0.2874 | 7 | 0.0078 | 0.3419 | 0.3497 | 0.3451 | 0.0035 | 0 | 3 | 0.2874 | 0.3592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3142 | 14760.168 | 44266.0921 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.3176 | 0:240:120 | 0:00 | 0.2757 | 7 | 0.0087 | 0.3278 | 0.3365 | 0.3311 | 0.0039 | 0 | 3 | 0.2757 | 0.3444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3145 | 14764.596 | 44266.0922 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 140.064 | 0:240:120 | 0:00 | 0.2645 | 7 | 0.0091 | 0.3134 | 0.3225 | 0.3169 | 0.0038 | 0 | 3 | 0.2645 | 0.3302 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3148 | 14768.891 | 44266.0922 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.8653 | 0:240:120 | 0:00 | 0.2537 | 7 | 0.0064 | 0.302 | 0.3084 | 0.3043 | 0.0028 | 0 | 3 | 0.2537 | 0.3166 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3151 | 14773.082 | 44266.0923 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 145.7226 | 0:240:120 | 0:00 | 0.2434 | 7 | 0.008 | 0.2895 | 0.2975 | 0.2923 | 0.0032 | 0 | 3 | 0.2434 | 0.3037 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3154 | 14777.475 | 44266.0923 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.637 | 0:240:120 | 0:00 | 0.2336 | 7 | 0.0072 | 0.2775 | 0.2847 | 0.2802 | 0.0031 | 0 | 3 | 0.2336 | 0.2913 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3157 | 14781.639 | 44266.0924 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 151.6098 | 0:240:120 | 0:00 | 0.2241 | 7 | 0.0073 | 0.2659 | 0.2732 | 0.2686 | 0.0031 | 0 | 3 | 0.2241 | 0.2794 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3160 | 14785.78 | 44266.0924 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 154.642 | 0:240:120 | 0:00 | 0.2151 | 7 | 0.0053 | 0.256 | 0.2613 | 0.258 | 0.0022 | 0 | 3 | 0.2151 | 0.268 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3163 | 14789.816 | 44266.0925 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 157.7348 | 0:240:120 | 0:00 | 0.2064 | 7 | 0.0053 | 0.2454 | 0.2507 | 0.2477 | 0.0023 | 0 | 3 | 0.2064 | 0.2571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3166 | 14793.951 | 44266.0925 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.8895 | 0:240:120 | 0:00 | 0.1981 | 7 | 0.0055 | 0.2347 | 0.2402 | 0.2371 | 0.0023 | 0 | 3 | 0.1981 | 0.2467 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3169 | 14798.022 | 44266.0926 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.1073 | 0:240:120 | 0:00 | 0.1902 | 7 | 0.005 | 0.2257 | 0.2307 | 0.2278 | 0.002 | 0 | 3 | 0.1902 | 0.2367 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3172 | 14802.012 | 44266.0926 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 167.3894 | 0:240:120 | 0:00 | 0.1825 | 7 | 0.0051 | 0.216 | 0.2211 | 0.2186 | 0.0019 | 0 | 3 | 0.1825 | 0.2271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3175 | 14805.775 | 44266.0926 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.7372 | 0:240:120 | 0:00 | 0.1752 | 7 | 0.0058 | 0.2066 | 0.2124 | 0.2094 | 0.002 | 0 | 3 | 0.1752 | 0.2179 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3178 | 14809.693 | 44266.0927 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 174.152 | 0:240:120 | 0:00 | 0.1682 | 7 | 0.0049 | 0.1996 | 0.2045 | 0.2016 | 0.0018 | 0 | 3 | 0.1682 | 0.2092 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3181 | 14813.42 | 44266.0927 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 177.635 | 0:240:120 | 0:00 | 0.1615 | 7 | 0.0044 | 0.1919 | 0.1963 | 0.1936 | 0.0017 | 0 | 3 | 0.1615 | 0.2007 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3184 | 14817.281 | 44266.0928 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 181.1877 | 0:240:120 | 0:00 | 0.155 | 7 | 0.0045 | 0.1837 | 0.1882 | 0.1859 | 0.0017 | 0 | 3 | 0.155 | 0.1927 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3187 | 14821.105 | 44266.0928 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 184.8115 | 0:240:120 | 0:00 | 0.1488 | 7 | 0.005 | 0.1762 | 0.1812 | 0.1787 | 0.0021 | 0 | 3 | 0.1488 | 0.1849 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3190 | 14825.173 | 44266.0929 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 188.5077 | 0:240:120 | 0:00 | 0.1429 | 7 | 0.0046 | 0.1697 | 0.1743 | 0.1719 | 0.0017 | 0 | 3 | 0.1429 | 0.1775 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3193 | 14828.921 | 44266.0929 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 192.2778 | 0:240:120 | 0:00 | 0.1372 | 7 | 0.0035 | 0.163 | 0.1665 | 0.1649 | 0.0012 | 0 | 3 | 0.1372 | 0.1704 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3196 | 14832.786 | 44266.093 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 196.1234 | 0:240:120 | 0:00 | 0.1318 | 7 | 0.0052 | 0.1556 | 0.1608 | 0.1579 | 0.0019 | 0 | 3 | 0.1318 | 0.1636 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3199 | 14836.575 | 44266.093 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 200.0459 | 0:240:120 | 0:00 | 0.1265 | 7 | 0.0041 | 0.1499 | 0.154 | 0.1516 | 0.0015 | 0 | 3 | 0.1265 | 0.1571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3202 | 14840.585 | 44266.093 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 204.0468 | 0:240:120 | 0:00 | 0.1215 | 7 | 0.004 | 0.1432 | 0.1472 | 0.1453 | 0.0014 | 0 | 3 | 0.1215 | 0.1508 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3205 | 14844.387 | 44266.0931 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.1277 | 0:240:120 | 0:00 | 0.1167 | 7 | 0.0035 | 0.1383 | 0.1418 | 0.1402 | 0.0012 | 0 | 3 | 0.1167 | 0.1448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3208 | 14848.259 | 44266.0931 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 212.2903 | 0:240:120 | 0:00 | 0.1121 | 7 | 0.0036 | 0.1327 | 0.1363 | 0.1344 | 0.0014 | 0 | 3 | 0.1121 | 0.139 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3211 | 14852.24 | 44266.0932 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 216.5361 | 0:240:120 | 0:00 | 0.1076 | 7 | 0.003 | 0.1271 | 0.1301 | 0.1286 | 0.0013 | 0 | 3 | 0.1076 | 0.1335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3214 | 14856.135 | 44266.0932 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 220.8668 | 0:240:120 | 0:00 | 0.1034 | 7 | 0.0038 | 0.1223 | 0.1261 | 0.1243 | 0.0016 | 0 | 3 | 0.1034 | 0.1282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3217 | 14859.897 | 44266.0933 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 225.2841 | 0:240:120 | 0:00 | 0.0993 | 7 | 0.0042 | 0.1175 | 0.1217 | 0.1196 | 0.0017 | 0 | 3 | 0.0993 | 0.1231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3220 | 14863.643 | 44266.0933 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 229.7898 | 0:240:120 | 0:00 | 0.0954 | 7 | 0.004 | 0.1124 | 0.1164 | 0.1146 | 0.0014 | 0 | 3 | 0.0954 | 0.1182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3223 | 14867.266 | 44266.0934 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.3856 | 0:240:120 | 0:00 | 0.0916 | 7 | 0.0035 | 0.1078 | 0.1113 | 0.1097 | 0.0012 | 0 | 3 | 0.0916 | 0.1135 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3226 | 14870.989 | 44266.0934 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 239.0733 | 0:240:120 | 0:00 | 0.088 | 7 | 0.0029 | 0.1041 | 0.107 | 0.1056 | 0.001 | 0 | 3 | 0.088 | 0.109 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3229 | 14874.969 | 44266.0934 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 243.8548 | 0:240:120 | 0:00 | 0.0845 | 7 | 0.0041 | 0.0998 | 0.1039 | 0.1021 | 0.0012 | 0 | 3 | 0.0845 | 0.1047 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3232 | 14878.996 | 44266.0935 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 248.7319 | 0:240:120 | 0:00 | 0.0812 | 7 | 0.0035 | 0.0959 | 0.0994 | 0.0978 | 0.0012 | 0 | 3 | 0.0812 | 0.1006 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3235 | 14882.694 | 44266.0935 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 253.7065 | 0:240:120 | 0:00 | 0.078 | 7 | 0.0037 | 0.0916 | 0.0953 | 0.0938 | 0.0013 | 0 | 3 | 0.078 | 0.0966 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3238 | 14886.455 | 44266.0936 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 258.7807 | 0:240:120 | 0:00 | 0.0749 | 7 | 0.0032 | 0.0887 | 0.0919 | 0.0906 | 0.0012 | 0 | 3 | 0.0749 | 0.0928 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3241 | 14889.961 | 44266.0936 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 263.9563 | 0:240:120 | 0:00 | 0.072 | 7 | 0.0023 | 0.0855 | 0.0878 | 0.0868 | 0.0008 | 0 | 3 | 0.072 | 0.0891 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3244 | 14893.636 | 44266.0937 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 269.2354 | 0:240:120 | 0:00 | 0.0691 | 7 | 0.0025 | 0.0815 | 0.084 | 0.083 | 0.0009 | 0 | 3 | 0.0691 | 0.0856 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3247 | 14897.292 | 44266.0937 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 274.6201 | 0:240:120 | 0:00 | 0.0664 | 7 | 0.0029 | 0.0784 | 0.0813 | 0.0801 | 0.0012 | 0 | 3 | 0.0664 | 0.0822 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3250 | 14900.942 | 44266.0937 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 280.1125 | 0:240:120 | 0:00 | 0.0638 | 7 | 0.0029 | 0.075 | 0.0779 | 0.0768 | 0.0011 | 0 | 3 | 0.0638 | 0.079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3253 | 14904.588 | 44266.0938 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 285.7147 | 0:240:120 | 0:00 | 0.0613 | 7 | 0.0038 | 0.072 | 0.0758 | 0.0741 | 0.0014 | 0 | 3 | 0.0613 | 0.0759 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3256 | 14908.229 | 44266.0938 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 291.429 | 0:240:120 | 0:00 | 0.0589 | 7 | 0.0026 | 0.0696 | 0.0722 | 0.0711 | 0.001 | 0 | 3 | 0.0589 | 0.0729 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3259 | 14912.089 | 44266.0939 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 297.2576 | 0:240:120 | 0:00 | 0.0566 | 7 | 0.0034 | 0.0663 | 0.0697 | 0.0685 | 0.0013 | 0 | 3 | 0.0566 | 0.07 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3262 | 14915.613 | 44266.0939 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 303.2028 | 0:240:120 | 0:00 | 0.0544 | 7 | 0.0021 | 0.0647 | 0.0668 | 0.0657 | 0.0007 | 0 | 3 | 0.0544 | 0.0673 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3265 | 14919.237 | 44266.094 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 309.2668 | 0:240:120 | 0:00 | 0.0522 | 7 | 0.003 | 0.0618 | 0.0648 | 0.0635 | 0.0012 | 0 | 3 | 0.0522 | 0.0646 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3268 | 14922.967 | 44266.094 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 315.4522 | 0:240:120 | 0:00 | 0.0502 | 7 | 0.0032 | 0.0595 | 0.0627 | 0.061 | 0.0012 | 0 | 3 | 0.0502 | 0.0621 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3271 | 14926.505 | 44266.094 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 321.7612 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0028 | 0.0569 | 0.0597 | 0.0588 | 0.0011 | 0 | 3 | 0.0482 | 0.0597 | P | NP | 0-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3274 | 14930.225 | 44266.0941 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 328.1964 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0022 | 0.0552 | 0.0574 | 0.0563 | 0.0007 | 0 | 3 | 0.0463 | 0.0573 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3277 | 14933.766 | 44266.0941 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 334.7604 | 0:240:120 | 0:00 | 0.0445 | 7 | 0.0028 | 0.0522 | 0.055 | 0.0537 | 0.0012 | 0 | 3 | 0.0445 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3280 | 14937.266 | 44266.0942 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 341.4556 | 0:240:120 | 0:00 | 0.0428 | 7 | 0.004 | 0.0501 | 0.0541 | 0.0524 | 0.0014 | 0 | 3 | 0.0428 | 0.0529 | P | NP | 0-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3283 | 14940.836 | 44266.0942 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 348.2847 | 0:240:120 | 0:00 | 0.0411 | 7 | 0.0027 | 0.0485 | 0.0512 | 0.0501 | 0.001 | 0 | 3 | 0.0411 | 0.0511 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3286 | 14944.36 | 44266.0942 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 355.2504 | 0:240:120 | 0:00 | 0.0395 | 7 | 0.0022 | 0.0472 | 0.0494 | 0.0484 | 0.0007 | 0 | 3 | 0.0395 | 0.0495 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3289 | 14947.836 | 44266.0943 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 362.3554 | 0:240:120 | 0:00 | 0.038 | 7 | 0.0017 | 0.0455 | 0.0472 | 0.0466 | 0.0006 | 0 | 3 | 0.038 | 0.048 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3292 | 14951.218 | 44266.0943 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 369.6025 | 0:240:120 | 0:00 | 0.0365 | 7 | 0.0028 | 0.0427 | 0.0455 | 0.0447 | 0.0011 | 0 | 3 | 0.0365 | 0.0465 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3295 | 14954.973 | 44266.0944 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 376.9945 | 0:240:120 | 0:00 | 0.0351 | 7 | 0.0027 | 0.0419 | 0.0446 | 0.0435 | 0.001 | 0 | 3 | 0.0351 | 0.0451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3298 | 14958.475 | 44266.0944 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 384.5344 | 0:240:120 | 0:00 | 0.0337 | 7 | 0.0038 | 0.039 | 0.0428 | 0.0411 | 0.0013 | 0 | 3 | 0.0337 | 0.0437 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3301 | 14962.013 | 44266.0945 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 392.2251 | 0:240:120 | 0:00 | 0.0324 | 7 | 0.0022 | 0.0386 | 0.0408 | 0.0398 | 0.0006 | 0 | 3 | 0.0324 | 0.0424 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3304 | 14965.387 | 44266.0945 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 400.0696 | 0:240:120 | 0:00 | 0.0311 | 7 | 0.0035 | 0.0366 | 0.0401 | 0.0387 | 0.0011 | 0 | 3 | 0.0311 | 0.0411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3307 | 14968.914 | 44266.0945 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 408.071 | 0:240:120 | 0:00 | 0.0299 | 7 | 0.0032 | 0.0355 | 0.0387 | 0.0373 | 0.0011 | 0 | 3 | 0.0299 | 0.0399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3310 | 14972.326 | 44266.0946 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 416.2324 | 0:240:120 | 0:00 | 0.0287 | 7 | 0.0031 | 0.0337 | 0.0368 | 0.0359 | 0.0012 | 0 | 3 | 0.0287 | 0.0387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3313 | 14975.915 | 44266.0946 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 424.5571 | 0:240:120 | 0:00 | 0.0276 | 7 | 0.0033 | 0.0329 | 0.0362 | 0.0346 | 0.0011 | 0 | 3 | 0.0276 | 0.0376 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3316 | 14979.41 | 44266.0947 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 433.0482 | 0:240:120 | 0:00 | 0.0265 | 7 | 0.003 | 0.0318 | 0.0348 | 0.0335 | 0.001 | 0 | 3 | 0.0265 | 0.0365 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3319 | 14982.811 | 44266.0947 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 441.7092 | 0:240:120 | 0:00 | 0.0255 | 7 | 0.0035 | 0.03 | 0.0335 | 0.0321 | 0.0013 | 0 | 3 | 0.0255 | 0.0355 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3322 | 14986.362 | 44266.0947 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 450.5434 | 0:240:120 | 0:00 | 0.0245 | 7 | 0.0028 | 0.0293 | 0.0321 | 0.0307 | 0.0011 | 0 | 3 | 0.0245 | 0.0345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3325 | 14990.139 | 44266.0948 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 459.5542 | 0:240:120 | 0:00 | 0.0235 | 7 | 0.0038 | 0.0275 | 0.0313 | 0.0296 | 0.0013 | 0 | 3 | 0.0235 | 0.0335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3328 | 14993.538 | 44266.0948 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 468.7453 | 0:240:120 | 0:00 | 0.0226 | 7 | 0.003 | 0.0273 | 0.0303 | 0.0288 | 0.0009 | 0 | 3 | 0.0226 | 0.0326 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3331 | 14997.069 | 44266.0949 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 478.1202 | 0:240:120 | 0:00 | 0.0217 | 7 | 0.003 | 0.0261 | 0.0291 | 0.028 | 0.0012 | 0 | 3 | 0.0217 | 0.0317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3334 | 15000.404 | 44266.0949 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 487.6826 | 0:240:120 | 0:00 | 0.0209 | 7 | 0.0032 | 0.0252 | 0.0284 | 0.027 | 0.0012 | 0 | 3 | 0.0209 | 0.0309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3337 | 15003.854 | 44266.0949 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 497.4363 | 0:240:120 | 0:00 | 0.0201 | 7 | 0.0026 | 0.0249 | 0.0275 | 0.0263 | 0.001 | 0 | 3 | 0.0201 | 0.0301 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3340 | 15007.363 | 44266.095 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 507.385 | 0:240:120 | 0:00 | 0.0193 | 7 | 0.0036 | 0.0232 | 0.0268 | 0.0253 | 0.0012 | 0 | 3 | 0.0193 | 0.0293 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3343 | 15010.951 | 44266.095 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 517.5327 | 0:240:120 | 0:00 | 0.0185 | 7 | 0.0032 | 0.0227 | 0.0259 | 0.0244 | 0.0011 | 0 | 3 | 0.0185 | 0.0285 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3346 | 15014.419 | 44266.0951 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 527.8834 | 0:240:120 | 0:00 | 0.0178 | 7 | 0.0037 | 0.0219 | 0.0256 | 0.0241 | 0.0014 | 0 | 3 | 0.0178 | 0.0278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3349 | 15017.86 | 44266.0951 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 538.441 | 0:240:120 | 0:00 | 0.0171 | 7 | 0.0032 | 0.022 | 0.0252 | 0.0236 | 0.0012 | 0 | 3 | 0.0171 | 0.0271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3352 | 15021.395 | 44266.0951 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 549.2099 | 0:240:120 | 0:00 | 0.0165 | 7 | 0.0041 | 0.02 | 0.0241 | 0.0227 | 0.0013 | 0 | 3 | 0.0165 | 0.0265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3355 | 15025.023 | 44266.0952 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 560.1941 | 0:240:120 | 0:00 | 0.0158 | 7 | 0.0031 | 0.0199 | 0.023 | 0.0219 | 0.0013 | 0 | 3 | 0.0158 | 0.0258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3358 | 15028.477 | 44266.0952 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 571.3979 | 0:240:120 | 0:00 | 0.0152 | 7 | 0.0041 | 0.0192 | 0.0233 | 0.0214 | 0.0016 | 0 | 3 | 0.0152 | 0.0252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3361 | 15031.953 | 44266.0953 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 582.8259 | 0:240:120 | 0:00 | 0.0146 | 7 | 0.0041 | 0.0193 | 0.0234 | 0.0214 | 0.0013 | 0 | 3 | 0.0146 | 0.0246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3364 | 15035.66 | 44266.0953 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 594.4824 | 0:240:120 | 0:00 | 0.014 | 7 | 0.0037 | 0.0187 | 0.0224 | 0.0209 | 0.0014 | 0 | 3 | 0.014 | 0.024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3367 | 15039.014 | 44266.0953 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 606.3721 | 0:240:120 | 0:00 | 0.0135 | 7 | 0.0031 | 0.0185 | 0.0216 | 0.0203 | 0.0012 | 0 | 3 | 0.0135 | 0.0235 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3370 | 15042.705 | 44266.0954 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 618.4995 | 0:240:120 | 0:00 | 0.013 | 7 | 0.0041 | 0.0178 | 0.0219 | 0.0198 | 0.0015 | 0 | 3 | 0.013 | 0.023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3373 | 15046.251 | 44266.0954 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 630.8695 | 0:240:120 | 0:00 | 0.0125 | 7 | 0.0025 | 0.018 | 0.0205 | 0.019 | 0.0011 | 0 | 3 | 0.0125 | 0.0225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3376 | 15049.729 | 44266.0955 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 643.4869 | 0:240:120 | 0:00 | 0.012 | 7 | 0.0021 | 0.018 | 0.0201 | 0.0189 | 0.0008 | 0 | 3 | 0.012 | 0.022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3379 | 15053.099 | 44266.0955 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 656.3566 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0013 | 0.0181 | 0.0194 | 0.0187 | 0.0005 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3382 | 15056.527 | 44266.0955 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 669.4838 | 0:240:120 | 0:00 | 0.0111 | 7 | 0.0023 | 0.0172 | 0.0195 | 0.0185 | 0.0006 | 0 | 3 | 0.0111 | 0.0211 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3385 | 15059.946 | 44266.0956 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 682.8734 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0015 | 0.0169 | 0.0184 | 0.0177 | 0.0006 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3388 | 15063.582 | 44266.0956 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 696.5309 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.0021 | 0.0163 | 0.0184 | 0.0174 | 0.0005 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3391 | 15067.107 | 44266.0957 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 704.2017 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0014 | 0.0162 | 0.0176 | 0.0168 | 0.0005 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3394 | 15070.539 | 44266.0957 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 718.2857 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0012 | 0.0163 | 0.0175 | 0.017 | 0.0003 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3397 | 15074.18 | 44266.0957 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 732.6514 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0023 | 0.015 | 0.0173 | 0.0164 | 0.0008 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 1-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3400 | 15077.512 | 44266.0958 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 747.3045 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0025 | 0.0148 | 0.0173 | 0.016 | 0.001 | 0 | 3 | 0.0089 | 0.016 | P | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3403 | 15080.826 | 44266.0958 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 762.2505 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0024 | 0.0145 | 0.0169 | 0.0157 | 0.0009 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3406 | 15084.221 | 44266.0959 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 777.4956 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.003 | 0.0139 | 0.0169 | 0.0152 | 0.0012 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3409 | 15087.615 | 44266.0959 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 793.0455 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0041 | 0.0129 | 0.017 | 0.015 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3412 | 15091.301 | 44266.0959 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 808.9064 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0041 | 0.013 | 0.0171 | 0.0147 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3415 | 15094.906 | 44266.096 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 825.0845 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0027 | 0.0134 | 0.0161 | 0.0147 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3418 | 15098.171 | 44266.096 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 841.5862 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0052 | 0.0121 | 0.0173 | 0.0146 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3421 | 15101.847 | 44266.0961 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 858.4179 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0052 | 0.0117 | 0.0169 | 0.0141 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3424 | 15105.846 | 44266.0961 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 875.5863 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0053 | 0.012 | 0.0173 | 0.0143 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3427 | 15109.095 | 44266.0962 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 893.098 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0051 | 0.0115 | 0.0166 | 0.014 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3430 | 15112.541 | 44266.0962 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 910.96 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0044 | 0.0113 | 0.0157 | 0.0138 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3433 | 15116.159 | 44266.0962 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 929.1792 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0041 | 0.0116 | 0.0157 | 0.0138 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3436 | 15119.515 | 44266.0963 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 947.7627 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0052 | 0.0113 | 0.0165 | 0.0138 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3439 | 15122.832 | 44266.0963 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 966.718 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0053 | 0.0109 | 0.0162 | 0.0134 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3442 | 15126.116 | 44266.0964 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 986.0524 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0052 | 0.011 | 0.0162 | 0.0135 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3445 | 15129.787 | 44266.0964 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1005.7734 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0051 | 0.0109 | 0.016 | 0.0134 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3448 | 15133.721 | 44266.0964 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1025.8889 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.004 | 0.0111 | 0.0151 | 0.0132 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3451 | 15137.54 | 44266.0965 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1046.4066 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0044 | 0.0109 | 0.0153 | 0.0133 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3454 | 15140.917 | 44266.0965 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1067.3348 | 0:240:120 | 0:00 | 0.0043 | 7 | 0.005 | 0.0104 | 0.0154 | 0.013 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3457 | 15144.485 | 44266.0966 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1088.6815 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0043 | 0.0106 | 0.0149 | 0.0129 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3460 | 15147.959 | 44266.0966 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1110.4551 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0038 | 0.0109 | 0.0147 | 0.013 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3463 | 15151.543 | 44266.0966 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1132.6642 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0052 | 0.0103 | 0.0155 | 0.0127 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3466 | 15155.441 | 44266.0967 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1155.3175 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0045 | 0.0104 | 0.0149 | 0.0127 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3469 | 15158.709 | 44266.0967 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1178.4238 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0044 | 0.0107 | 0.0151 | 0.0129 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3472 | 15162.171 | 44266.0968 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1201.9923 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0034 | 0.0105 | 0.0139 | 0.0119 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3475 | 15166.082 | 44266.0968 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1226.0322 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0045 | 0.01 | 0.0145 | 0.0119 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3478 | 15169.462 | 44266.0969 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1250.5528 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0054 | 0.0098 | 0.0152 | 0.0119 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3481 | 15172.854 | 44266.0969 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1275.5639 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0029 | 0.0105 | 0.0134 | 0.0114 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3484 | 15176.19 | 44266.0969 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1301.0751 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0035 | 0.0107 | 0.0142 | 0.0115 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3487 | 15179.476 | 44266.097 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1327.0966 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0029 | 0.0098 | 0.0127 | 0.0108 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3490 | 15182.981 | 44266.097 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1353.6386 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0041 | 0.0091 | 0.0132 | 0.0108 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3493 | 15186.329 | 44266.097 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1380.7113 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0055 | 0.0097 | 0.0152 | 0.0113 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3496 | 15189.875 | 44266.0971 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1408.3256 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.004 | 0.0093 | 0.0133 | 0.011 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3499 | 15193.344 | 44266.0971 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1408.4034 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0025 | 0.0094 | 0.0119 | 0.0105 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3502 | 15197.127 | 44266.0972 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1436.5714 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0021 | 0.01 | 0.0121 | 0.0109 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3505 | 15200.918 | 44266.0972 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1465.3028 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0038 | 0.0107 | 0.0145 | 0.0115 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3508 | 15204.482 | 44266.0973 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1494.6089 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0027 | 0.0094 | 0.0121 | 0.0109 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3511 | 15207.776 | 44266.0973 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1524.5011 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0061 | 0.0091 | 0.0152 | 0.011 | 0.0019 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3514 | 15211.373 | 44266.0973 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1554.9911 | 0:240:120 | 0:00 | 0.002 | 7 | 0.003 | 0.0095 | 0.0125 | 0.0107 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3517 | 15214.725 | 44266.0974 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1586.0909 | 0:240:120 | 0:00 | 0.002 | 7 | 0.004 | 0.0091 | 0.0131 | 0.011 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3520 | 15218.604 | 44266.0974 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1617.8127 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.003 | 0.0094 | 0.0124 | 0.0105 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3523 | 15221.907 | 44266.0975 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1650.169 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0032 | 0.0091 | 0.0123 | 0.0104 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3526 | 15225.365 | 44266.0975 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1683.1724 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.003 | 0.009 | 0.012 | 0.0106 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3529 | 15228.866 | 44266.0975 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1716.8358 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0028 | 0.0095 | 0.0123 | 0.0105 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3532 | 15232.425 | 44266.0976 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1751.1725 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0036 | 0.0089 | 0.0125 | 0.0105 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3535 | 15235.682 | 44266.0976 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1786.196 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0034 | 0.0094 | 0.0128 | 0.0105 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3538 | 15239.239 | 44266.0977 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1821.9199 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.003 | 0.0095 | 0.0125 | 0.0106 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3541 | 15242.544 | 44266.0977 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1858.3583 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0027 | 0.0089 | 0.0116 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3544 | 15245.903 | 44266.0977 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1895.5255 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3547 | 15249.43 | 44266.0978 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1933.436 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3550 | 15252.835 | 44266.0978 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1972.1047 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3553 | 15256.19 | 44266.0979 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2011.5468 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3556 | 15259.865 | 44266.0979 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2051.7777 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3559 | 15263.312 | 44266.0979 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2092.8133 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0024 | 0.0092 | 0.0116 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3562 | 15266.98 | 44266.098 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2134.6696 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0018 | 0.0094 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3565 | 15270.428 | 44266.098 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2177.3629 | 0:240:120 | 0:00 | 0.001 | 7 | 0.002 | 0.0095 | 0.0115 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3568 | 15273.796 | 44266.0981 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2220.9102 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3571 | 15277.266 | 44266.0981 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2265.3284 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0019 | 0.0094 | 0.0113 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3574 | 15280.639 | 44266.0981 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2310.635 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3577 | 15283.959 | 44266.0982 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2356.8477 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.002 | 0.0092 | 0.0112 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3580 | 15287.715 | 44266.0982 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2403.9846 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0017 | 0.0089 | 0.0106 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3583 | 15291.265 | 44266.0983 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2452.0643 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3586 | 15294.566 | 44266.0983 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2501.1056 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3589 | 15297.967 | 44266.0983 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2551.1277 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3592 | 15301.316 | 44266.0984 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2602.1503 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3595 | 15304.717 | 44266.0984 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2654.1933 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0015 | 0.0098 | 0.0113 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3598 | 15308.138 | 44266.0985 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2707.2772 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0018 | 0.0091 | 0.0109 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3601 | 15311.551 | 44266.0985 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2761.4227 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0026 | 0.0088 | 0.0114 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3604 | 15315.014 | 44266.0985 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2816.6511 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3607 | 15318.456 | 44266.0986 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2872.9842 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.001 | 0.0095 | 0.0105 | 0.01 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3610 | 15321.774 | 44266.0986 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2930.4439 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3613 | 15325.207 | 44266.0987 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2989.0527 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3616 | 15328.819 | 44266.0987 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3048.8338 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0015 | 0.0093 | 0.0108 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3619 | 15332.093 | 44266.0987 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3109.8105 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0015 | 0.0099 | 0.0114 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3622 | 15335.725 | 44266.0988 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3172.0067 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0013 | 0.0096 | 0.0109 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3625 | 15339.399 | 44266.0988 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3235.4468 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3628 | 15343.002 | 44266.0989 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3300.1557 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3631 | 15346.391 | 44266.0989 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3366.1589 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3634 | 15350.401 | 44266.0989 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3433.482 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0019 | 0.0089 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3637 | 15353.585 | 44266.099 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3502.1517 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3640 | 15356.887 | 44266.099 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3572.1947 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0018 | 0.0095 | 0.0113 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3643 | 15360.312 | 44266.0991 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3643.6386 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0018 | 0.0095 | 0.0113 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3646 | 15363.652 | 44266.0991 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3716.5114 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3649 | 15367.021 | 44266.0991 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3790.8416 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3652 | 15370.366 | 44266.0992 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3866.6584 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3655 | 15373.868 | 44266.0992 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3943.9916 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0009 | 0.0095 | 0.0104 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3658 | 15377.225 | 44266.0993 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4022.8714 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3661 | 15380.714 | 44266.0993 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4103.3289 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0023 | 0.0091 | 0.0114 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3664 | 15384.439 | 44266.0993 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4185.3954 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3667 | 15388.086 | 44266.0994 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4269.1033 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0005 | 0.0096 | 0.0101 | 0.0098 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3670 | 15391.372 | 44266.0994 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4354.4854 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3673 | 15394.736 | 44266.0995 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4441.5751 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.009 | 0.0106 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3676 | 15398.286 | 44266.0995 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4530.4066 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0008 | 0.0096 | 0.0104 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3679 | 15401.625 | 44266.0995 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4621.0148 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.001 | 0.0098 | 0.0108 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3682 | 15404.971 | 44266.0996 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4713.4351 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3685 | 15408.577 | 44266.0996 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4807.7038 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0021 | 0.0089 | 0.011 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3688 | 15411.933 | 44266.0997 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4903.8578 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3691 | 15415.621 | 44266.0997 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5001.935 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0024 | 0.0089 | 0.0113 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3694 | 15419.022 | 44266.0997 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5101.9737 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3697 | 15422.434 | 44266.0998 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5204.0132 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3700 | 15425.985 | 44266.0998 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5308.0934 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3703 | 15429.527 | 44266.0999 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5414.2553 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0005 | 0.0096 | 0.0101 | 0.0099 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3706 | 15433.294 | 44266.0999 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5522.5404 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0011 | 0.0097 | 0.0108 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3709 | 15436.948 | 44266.0999 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5632.9912 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3712 | 15440.617 | 44266.1 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5745.651 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3715 | 15443.928 | 44266.1 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5860.564 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3718 | 15447.351 | 44266.1001 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5977.7753 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0001 | 0.0098 | 0.0099 | 0.0099 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3721 | 15450.709 | 44266.1001 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6097.3308 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3724 | 15454.198 | 44266.1001 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6219.2775 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.001 | 0.0095 | 0.0105 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3727 | 15457.488 | 44266.1002 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6343.663 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0024 | 0.0088 | 0.0112 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3730 | 15460.995 | 44266.1002 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6470.5363 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.0097 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3733 | 15464.343 | 44266.1003 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6599.947 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.001 | 0.0097 | 0.0107 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3736 | 15467.935 | 44266.1003 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6731.9459 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0005 | 0.0096 | 0.0101 | 0.0099 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3739 | 15471.461 | 44266.1003 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6866.5848 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3742 | 15474.732 | 44266.1004 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7003.9165 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3745 | 15478.031 | 44266.1004 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7143.9949 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0088 | 0.0101 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3748 | 15481.505 | 44266.1005 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7286.8748 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3751 | 15485.164 | 44266.1005 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7432.6123 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3754 | 15488.602 | 44266.1005 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7581.2645 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0007 | 0.0099 | 0.0106 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3757 | 15492.009 | 44266.1006 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7732.8898 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0008 | 0.0092 | 0.01 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3760 | 15495.64 | 44266.1006 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7887.5476 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.001 | 0.01 | 0.011 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3763 | 15499.542 | 44266.1007 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8045.2986 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.0097 | 0.0112 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3766 | 15503.11 | 44266.1007 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8206.2045 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0097 | 0.011 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3769 | 15506.394 | 44266.1008 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8370.3286 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.002 | 0.0091 | 0.0111 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3772 | 15510.008 | 44266.1008 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8537.7352 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0006 | 0.0096 | 0.0102 | 0.0098 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3775 | 15513.492 | 44266.1008 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8708.4899 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0097 | 0.0108 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3778 | 15516.802 | 44266.1009 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8882.6597 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0005 | 0.01 | 0.0105 | 0.0102 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3781 | 15520.188 | 44266.1009 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9060.3129 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0089 | 0.0106 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3784 | 15523.98 | 44266.101 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9241.5191 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3787 | 15527.431 | 44266.101 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9426.3495 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0004 | 0.0098 | 0.0102 | 0.01 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3790 | 15531.034 | 44266.101 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9614.8765 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3793 | 15534.359 | 44266.1011 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9807.174 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.0093 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3796 | 15537.986 | 44266.1011 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10003.3175 | 0:240:120 | 0:00 | 0 | 7 | 0.0015 | 0.0097 | 0.0112 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3799 | 15541.471 | 44266.1012 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10203.3839 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.0105 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3802 | 15545.08 | 44266.1012 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10407.4515 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.009 | 0.0102 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3805 | 15548.543 | 44266.1012 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10615.6006 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0088 | 0.0105 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3808 | 15552.202 | 44266.1013 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10827.9126 | 0:240:120 | 0:00 | 0 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3811 | 15555.542 | 44266.1013 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11044.4708 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0089 | 0.0106 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3814 | 15559.09 | 44266.1014 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11265.3603 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3817 | 15562.454 | 44266.1014 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11490.6675 | 0:240:120 | 0:00 | 0 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3820 | 15565.738 | 44266.1014 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11720.4808 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3823 | 15569.452 | 44266.1015 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11954.8904 | 0:240:120 | 0:00 | 0 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3826 | 15699.887 | 44266.103 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.7 | 0:240:120 | 0:00 | 16.2781 | 7 | 45.7051 | 86.1431 | 131.8482 | 107.4053 | 17.0527 | 290.7955 | 3 | 16.2781 | 65.7258 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3829 | 16041.455 | 44266.1069 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.4 | 0:240:120 | 0:00 | 14.0163 | 7 | 39.4917 | 39.365 | 78.8567 | 56.4173 | 16.467 | 271.1609 | 3 | 14.0163 | 43.0212 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3832 | 16227.216 | 44266.1091 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.1 | 0:240:120 | 0:00 | 12.2765 | 7 | 2.3795 | 24.1752 | 26.5547 | 25.1545 | 1.0371 | 1.0757 | 3 | 12.2765 | 31.8123 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3835 | 16306.84 | 44266.11 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.8 | 0:240:120 | 0:00 | 10.8973 | 7 | 2.4638 | 21.0026 | 23.4664 | 22.1235 | 1.0528 | 1.1084 | 3 | 10.8973 | 25.1353 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3838 | 16377.821 | 44266.1108 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.5 | 0:240:120 | 0:00 | 9.7778 | 7 | 2.5757 | 18.1374 | 20.7131 | 19.214 | 1.1451 | 1.3113 | 3 | 9.7778 | 20.7059 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3841 | 16439.653 | 44266.1116 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.3 | 0:240:120 | 0:00 | 8.7319 | 7 | 2.1647 | 15.0783 | 17.243 | 15.8588 | 1.0199 | 1.0401 | 3 | 8.7319 | 17.1767 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3844 | 16491.231 | 44266.1122 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.1 | 0:240:120 | 0:00 | 7.872 | 7 | 1.7326 | 12.157 | 13.8896 | 12.8236 | 0.8032 | 0.6452 | 3 | 7.872 | 14.6304 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3847 | 16534.202 | 44266.1126 | Vista Speed | E | 15E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.8 | 0:240:120 | 0:00 | 7.2364 | 7 | 0.8716 | 11.1844 | 12.056 | 11.5234 | 0.4025 | 0.162 | 3 | 7.2364 | 12.9218 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3850 | 16836.226 | 44266.1161 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44 | 0:240:120 | 0:00 | 26.1905 | 7 | 42.2956 | 231.1654 | 273.461 | 247.2617 | 19.7465 | 389.9244 | 3 | 26.1905 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3853 | 17610.037 | 44266.1251 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.88 | 0:240:120 | 0:00 | 21.245 | 7 | 42.9927 | 180.6814 | 223.6741 | 196.5109 | 20.3845 | 415.5295 | 3 | 21.245 | 279.2439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3856 | 18234.506 | 44266.1323 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.7776 | 0:240:120 | 0:00 | 17.7567 | 7 | 47.1039 | 126.9461 | 174.05 | 145.3678 | 21.6074 | 466.8791 | 3 | 17.7567 | 90.3242 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3859 | 18708.174 | 44266.1378 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.6932 | 0:240:120 | 0:00 | 15.1659 | 7 | 46.4872 | 76.4024 | 122.8896 | 92.2477 | 22.8261 | 521.0303 | 3 | 15.1659 | 53.0111 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3862 | 19021.363 | 44266.1414 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.627 | 0:240:120 | 0:00 | 13.1671 | 7 | 38.926 | 26.2156 | 65.1416 | 39.0916 | 19.1276 | 365.8656 | 3 | 13.1671 | 37.0761 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3865 | 19179.211 | 44266.1433 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.5796 | 0:240:120 | 0:00 | 11.5794 | 7 | 1.703 | 23.4065 | 25.1095 | 23.9923 | 0.823 | 0.6773 | 3 | 11.5794 | 28.2433 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3868 | 19254.816 | 44266.1441 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.5511 | 0:240:120 | 0:00 | 10.2886 | 7 | 1.6681 | 20.4305 | 22.0986 | 21.0939 | 0.7557 | 0.5711 | 3 | 10.2886 | 22.6334 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3871 | 19321.459 | 44266.1449 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.5422 | 0:240:120 | 0:00 | 9.2194 | 7 | 2.5638 | 16.7888 | 19.3526 | 17.7901 | 1.1768 | 1.3848 | 3 | 9.2194 | 18.7572 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3874 | 19379.653 | 44266.1456 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.553 | 0:240:120 | 0:00 | 8.3198 | 7 | 2.3728 | 13.879 | 16.2518 | 14.6651 | 1.1586 | 1.3424 | 3 | 8.3198 | 15.9205 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3877 | 19427.879 | 44266.1461 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.5841 | 0:240:120 | 0:00 | 7.5531 | 7 | 0.5646 | 11.9836 | 12.5482 | 12.1989 | 0.2572 | 0.0661 | 3 | 7.5531 | 13.756 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3880 | 19467.68 | 44266.1466 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.6358 | 0:240:120 | 0:00 | 6.8923 | 7 | 0.8868 | 10.7124 | 11.5992 | 11.0135 | 0.4389 | 0.1927 | 3 | 6.8923 | 12.0514 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3883 | 19504.505 | 44266.147 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.7085 | 0:240:120 | 0:00 | 6.3172 | 7 | 0.6255 | 9.7634 | 10.3889 | 9.9776 | 0.3003 | 0.0902 | 3 | 6.3172 | 10.6752 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3886 | 19537.999 | 44266.1474 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.8026 | 0:240:120 | 0:00 | 5.8127 | 7 | 0.885 | 8.452 | 9.337 | 8.795 | 0.4086 | 0.1669 | 3 | 5.8127 | 9.5415 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3889 | 19567.858 | 44266.1478 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.9187 | 0:240:120 | 0:00 | 5.3667 | 7 | 0.3153 | 7.728 | 8.0433 | 7.8384 | 0.1472 | 0.0217 | 3 | 5.3667 | 8.5922 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3892 | 19594.406 | 44266.1481 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.0571 | 0:240:120 | 0:00 | 4.97 | 7 | 0.4439 | 7.0794 | 7.5233 | 7.2307 | 0.2183 | 0.0476 | 3 | 4.97 | 7.7862 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3895 | 19619.548 | 44266.1484 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.2182 | 0:240:120 | 0:00 | 4.6151 | 7 | 0.4398 | 6.4169 | 6.8567 | 6.6006 | 0.1965 | 0.0386 | 3 | 4.6151 | 7.0939 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3898 | 19642.849 | 44266.1486 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.4026 | 0:240:120 | 0:00 | 4.2959 | 7 | 0.4188 | 5.8206 | 6.2394 | 6.0227 | 0.1642 | 0.027 | 3 | 4.2959 | 6.4932 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3901 | 19664.441 | 44266.1489 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.6106 | 0:240:120 | 0:00 | 4.0075 | 7 | 0.2467 | 5.467 | 5.7137 | 5.5499 | 0.1219 | 0.0149 | 3 | 4.0075 | 5.9675 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3904 | 19684.429 | 44266.1491 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.8428 | 0:240:120 | 0:00 | 3.7459 | 7 | 0.267 | 5.0684 | 5.3354 | 5.1616 | 0.13 | 0.0169 | 3 | 3.7459 | 5.5039 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3907 | 19703.348 | 44266.1493 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.0997 | 0:240:120 | 0:00 | 3.5077 | 7 | 0.2674 | 4.6692 | 4.9366 | 4.7692 | 0.1261 | 0.0159 | 3 | 3.5077 | 5.0923 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3910 | 19721.044 | 44266.1495 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.3817 | 0:240:120 | 0:00 | 3.29 | 7 | 0.2205 | 4.3167 | 4.5372 | 4.3966 | 0.1057 | 0.0112 | 3 | 3.29 | 4.7247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3913 | 19737.625 | 44266.1497 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.6893 | 0:240:120 | 0:00 | 3.0905 | 7 | 0.1736 | 4.0564 | 4.23 | 4.1213 | 0.0818 | 0.0067 | 3 | 3.0905 | 4.3946 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3916 | 19753.368 | 44266.1499 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.0231 | 0:240:120 | 0:00 | 2.907 | 7 | 0.1743 | 3.7941 | 3.9684 | 3.8547 | 0.0845 | 0.0071 | 3 | 2.907 | 4.0969 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3919 | 19768.274 | 44266.1501 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.3836 | 0:240:120 | 0:00 | 2.738 | 7 | 0.1758 | 3.5284 | 3.7042 | 3.5876 | 0.0869 | 0.0076 | 3 | 2.738 | 3.8271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3922 | 19782.417 | 44266.1502 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.7712 | 0:240:120 | 0:00 | 2.5817 | 7 | 0.1329 | 3.3313 | 3.4642 | 3.381 | 0.0623 | 0.0039 | 3 | 2.5817 | 3.5817 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3925 | 19795.875 | 44266.1504 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.1867 | 0:240:120 | 0:00 | 2.4371 | 7 | 0.1521 | 3.1038 | 3.2559 | 3.1702 | 0.0648 | 0.0042 | 3 | 2.4371 | 3.3577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3928 | 19808.679 | 44266.1505 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.6304 | 0:240:120 | 0:00 | 2.3028 | 7 | 0.1268 | 2.913 | 3.0398 | 2.9574 | 0.0613 | 0.0038 | 3 | 2.3028 | 3.1526 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3931 | 19820.904 | 44266.1507 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.103 | 0:240:120 | 0:00 | 2.178 | 7 | 0.0926 | 2.7742 | 2.8668 | 2.8063 | 0.0453 | 0.0021 | 3 | 2.178 | 2.9642 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3934 | 19832.747 | 44266.1508 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.6051 | 0:240:120 | 0:00 | 2.0617 | 7 | 0.099 | 2.5976 | 2.6966 | 2.6333 | 0.0466 | 0.0022 | 3 | 2.0617 | 2.7907 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3937 | 19843.867 | 44266.151 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.1372 | 0:240:120 | 0:00 | 1.9532 | 7 | 0.0943 | 2.4546 | 2.5489 | 2.487 | 0.0462 | 0.0021 | 3 | 1.9532 | 2.6305 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3940 | 19854.612 | 44266.1511 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.6999 | 0:240:120 | 0:00 | 1.8518 | 7 | 0.0738 | 2.3194 | 2.3932 | 2.3448 | 0.0356 | 0.0013 | 3 | 1.8518 | 2.4822 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3943 | 19864.972 | 44266.1512 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.2939 | 0:240:120 | 0:00 | 1.7569 | 7 | 0.0951 | 2.1856 | 2.2807 | 2.2228 | 0.0429 | 0.0018 | 3 | 1.7569 | 2.3448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3946 | 19874.887 | 44266.1513 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.9198 | 0:240:120 | 0:00 | 1.668 | 7 | 0.0712 | 2.0735 | 2.1447 | 2.1005 | 0.0328 | 0.0011 | 3 | 1.668 | 2.217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3949 | 19884.216 | 44266.1514 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.5782 | 0:240:120 | 0:00 | 1.5846 | 7 | 0.0583 | 1.971 | 2.0293 | 1.9911 | 0.028 | 0.0008 | 3 | 1.5846 | 2.0981 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3952 | 19893.486 | 44266.1515 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.2697 | 0:240:120 | 0:00 | 1.5062 | 7 | 0.0597 | 1.8619 | 1.9216 | 1.8826 | 0.0287 | 0.0008 | 3 | 1.5062 | 1.9872 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3955 | 19902.393 | 44266.1516 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.9951 | 0:240:120 | 0:00 | 1.4325 | 7 | 0.0501 | 1.769 | 1.8191 | 1.7857 | 0.0241 | 0.0006 | 3 | 1.4325 | 1.8836 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3958 | 19910.978 | 44266.1517 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.755 | 0:240:120 | 0:00 | 1.3631 | 7 | 0.0475 | 1.6809 | 1.7284 | 1.6971 | 0.023 | 0.0005 | 3 | 1.3631 | 1.7867 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3961 | 19919.745 | 44266.1518 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.5501 | 0:240:120 | 0:00 | 1.2977 | 7 | 0.0439 | 1.5961 | 1.64 | 1.6108 | 0.0211 | 0.0004 | 3 | 1.2977 | 1.6959 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3964 | 19928.001 | 44266.1519 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.3811 | 0:240:120 | 0:00 | 1.2359 | 7 | 0.0424 | 1.5194 | 1.5618 | 1.5348 | 0.0197 | 0.0004 | 3 | 1.2359 | 1.6108 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3967 | 19936.022 | 44266.152 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.2488 | 0:240:120 | 0:00 | 1.1777 | 7 | 0.0532 | 1.4356 | 1.4888 | 1.4559 | 0.0242 | 0.0006 | 3 | 1.1777 | 1.5308 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3970 | 19943.709 | 44266.1521 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.1537 | 0:240:120 | 0:00 | 1.1226 | 7 | 0.0386 | 1.3722 | 1.4108 | 1.3861 | 0.0178 | 0.0003 | 3 | 1.1226 | 1.4556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3973 | 19951.008 | 44266.1522 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.0968 | 0:240:120 | 0:00 | 1.0705 | 7 | 0.0409 | 1.3032 | 1.3441 | 1.3194 | 0.0184 | 0.0003 | 3 | 1.0705 | 1.3849 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3976 | 19958.434 | 44266.1523 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.0788 | 0:240:120 | 0:00 | 1.0212 | 7 | 0.0328 | 1.2446 | 1.2774 | 1.2561 | 0.0159 | 0.0003 | 3 | 1.0212 | 1.3182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3979 | 19965.507 | 44266.1524 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.1003 | 0:240:120 | 0:00 | 0.9746 | 7 | 0.0386 | 1.1832 | 1.2218 | 1.1972 | 0.018 | 0.0003 | 3 | 0.9746 | 1.2553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3982 | 19972.404 | 44266.1524 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.1623 | 0:240:120 | 0:00 | 0.9303 | 7 | 0.0294 | 1.1283 | 1.1577 | 1.1398 | 0.0131 | 0.0002 | 3 | 0.9303 | 1.196 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3985 | 19979.174 | 44266.1525 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.2656 | 0:240:120 | 0:00 | 0.8884 | 7 | 0.0288 | 1.077 | 1.1058 | 1.0885 | 0.0123 | 0.0002 | 3 | 0.8884 | 1.1399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3988 | 19985.629 | 44266.1526 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.4109 | 0:240:120 | 0:00 | 0.8485 | 7 | 0.024 | 1.0294 | 1.0534 | 1.038 | 0.0114 | 0.0001 | 3 | 0.8485 | 1.0869 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3991 | 19992.347 | 44266.1527 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.5991 | 0:240:120 | 0:00 | 0.8107 | 7 | 0.0263 | 0.9808 | 1.0071 | 0.9904 | 0.0124 | 0.0002 | 3 | 0.8107 | 1.0368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3994 | 19998.764 | 44266.1527 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.8311 | 0:240:120 | 0:00 | 0.7748 | 7 | 0.025 | 0.9346 | 0.9596 | 0.9447 | 0.0105 | 0.0001 | 3 | 0.7748 | 0.9893 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3997 | 20004.859 | 44266.1528 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.1077 | 0:240:120 | 0:00 | 0.7407 | 7 | 0.0233 | 0.8942 | 0.9175 | 0.9026 | 0.0107 | 0.0001 | 3 | 0.7407 | 0.9442 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4000 | 20011.092 | 44266.1529 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.4299 | 0:240:120 | 0:00 | 0.7082 | 7 | 0.0223 | 0.8532 | 0.8755 | 0.8614 | 0.0104 | 0.0001 | 3 | 0.7082 | 0.9016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4003 | 20017.083 | 44266.153 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.7985 | 0:240:120 | 0:00 | 0.6773 | 7 | 0.0218 | 0.8136 | 0.8354 | 0.8226 | 0.0093 | 0.0001 | 3 | 0.6773 | 0.8611 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4006 | 20022.937 | 44266.153 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.2144 | 0:240:120 | 0:00 | 0.6479 | 7 | 0.0201 | 0.7797 | 0.7998 | 0.7869 | 0.0093 | 0.0001 | 3 | 0.6479 | 0.8226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4009 | 20028.85 | 44266.1531 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.6787 | 0:240:120 | 0:00 | 0.6199 | 7 | 0.019 | 0.7438 | 0.7628 | 0.7511 | 0.0088 | 0.0001 | 3 | 0.6199 | 0.7861 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4012 | 20034.28 | 44266.1532 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.1923 | 0:240:120 | 0:00 | 0.5933 | 7 | 0.0189 | 0.712 | 0.7309 | 0.7187 | 0.0086 | 0.0001 | 3 | 0.5933 | 0.7514 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4015 | 20039.693 | 44266.1532 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.7561 | 0:240:120 | 0:00 | 0.5678 | 7 | 0.0181 | 0.6815 | 0.6996 | 0.6884 | 0.0081 | 0.0001 | 3 | 0.5678 | 0.7184 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4018 | 20045.358 | 44266.1533 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.3713 | 0:240:120 | 0:00 | 0.5436 | 7 | 0.0185 | 0.6512 | 0.6697 | 0.6584 | 0.0082 | 0.0001 | 3 | 0.5436 | 0.6871 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4021 | 20050.696 | 44266.1533 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.0387 | 0:240:120 | 0:00 | 0.5205 | 7 | 0.0156 | 0.6236 | 0.6392 | 0.6293 | 0.0071 | 0.0001 | 3 | 0.5205 | 0.6572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4024 | 20055.787 | 44266.1534 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.7595 | 0:240:120 | 0:00 | 0.4985 | 7 | 0.0143 | 0.5969 | 0.6112 | 0.6026 | 0.0064 | 0 | 3 | 0.4985 | 0.6288 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4027 | 20060.855 | 44266.1535 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.5347 | 0:240:120 | 0:00 | 0.4774 | 7 | 0.0146 | 0.5713 | 0.5859 | 0.5769 | 0.0065 | 0 | 3 | 0.4774 | 0.6017 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4030 | 20066.064 | 44266.1535 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.3654 | 0:240:120 | 0:00 | 0.4573 | 7 | 0.0115 | 0.5482 | 0.5597 | 0.5521 | 0.0055 | 0 | 3 | 0.4573 | 0.5759 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4033 | 20071.213 | 44266.1536 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.2527 | 0:240:120 | 0:00 | 0.4382 | 7 | 0.0129 | 0.5236 | 0.5365 | 0.5286 | 0.0057 | 0 | 3 | 0.4382 | 0.5513 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4036 | 20076.216 | 44266.1536 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.1977 | 0:240:120 | 0:00 | 0.4199 | 7 | 0.0115 | 0.5029 | 0.5144 | 0.5068 | 0.0051 | 0 | 3 | 0.4199 | 0.5278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4039 | 20080.811 | 44266.1537 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.2017 | 0:240:120 | 0:00 | 0.4024 | 7 | 0.0096 | 0.4825 | 0.4921 | 0.4857 | 0.0045 | 0 | 3 | 0.4024 | 0.5054 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4042 | 20085.578 | 44266.1538 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.2657 | 0:240:120 | 0:00 | 0.3856 | 7 | 0.0117 | 0.4602 | 0.4719 | 0.4647 | 0.0051 | 0 | 3 | 0.3856 | 0.4841 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4045 | 20090.392 | 44266.1538 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 159.391 | 0:240:120 | 0:00 | 0.3697 | 7 | 0.0104 | 0.4412 | 0.4516 | 0.445 | 0.0048 | 0 | 3 | 0.3697 | 0.4637 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4048 | 20095.06 | 44266.1539 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 162.5788 | 0:240:120 | 0:00 | 0.3544 | 7 | 0.0093 | 0.4229 | 0.4322 | 0.4265 | 0.0041 | 0 | 3 | 0.3544 | 0.4442 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4051 | 20099.639 | 44266.1539 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.8304 | 0:240:120 | 0:00 | 0.3398 | 7 | 0.0075 | 0.4067 | 0.4142 | 0.4092 | 0.0035 | 0 | 3 | 0.3398 | 0.4256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4054 | 20104.266 | 44266.154 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.147 | 0:240:120 | 0:00 | 0.3258 | 7 | 0.0089 | 0.3885 | 0.3974 | 0.3918 | 0.004 | 0 | 3 | 0.3258 | 0.4079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4057 | 20108.691 | 44266.154 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 172.53 | 0:240:120 | 0:00 | 0.3124 | 7 | 0.0093 | 0.3725 | 0.3818 | 0.3761 | 0.0035 | 0 | 3 | 0.3124 | 0.3909 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4060 | 20113.203 | 44266.1541 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175.9806 | 0:240:120 | 0:00 | 0.2996 | 7 | 0.0081 | 0.3574 | 0.3655 | 0.3604 | 0.0036 | 0 | 3 | 0.2996 | 0.3747 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4063 | 20117.374 | 44266.1541 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 179.5002 | 0:240:120 | 0:00 | 0.2874 | 7 | 0.0073 | 0.3424 | 0.3497 | 0.3454 | 0.0029 | 0 | 3 | 0.2874 | 0.3592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4066 | 20121.857 | 44266.1542 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.0902 | 0:240:120 | 0:00 | 0.2757 | 7 | 0.0079 | 0.3287 | 0.3366 | 0.3319 | 0.0032 | 0 | 3 | 0.2757 | 0.3444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4069 | 20126.328 | 44266.1542 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 186.752 | 0:240:120 | 0:00 | 0.2645 | 7 | 0.0079 | 0.3144 | 0.3223 | 0.3175 | 0.0033 | 0 | 3 | 0.2645 | 0.3302 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4072 | 20130.624 | 44266.1543 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 190.487 | 0:240:120 | 0:00 | 0.2537 | 7 | 0.0065 | 0.3018 | 0.3083 | 0.3047 | 0.0026 | 0 | 3 | 0.2537 | 0.3166 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4075 | 20134.762 | 44266.1543 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.2968 | 0:240:120 | 0:00 | 0.2434 | 7 | 0.0055 | 0.2908 | 0.2963 | 0.2928 | 0.0025 | 0 | 3 | 0.2434 | 0.3037 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4078 | 20139.193 | 44266.1544 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 198.1827 | 0:240:120 | 0:00 | 0.2336 | 7 | 0.0063 | 0.2781 | 0.2844 | 0.2808 | 0.0025 | 0 | 3 | 0.2336 | 0.2913 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4081 | 20143.243 | 44266.1544 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 202.1463 | 0:240:120 | 0:00 | 0.2241 | 7 | 0.0056 | 0.2667 | 0.2723 | 0.2688 | 0.0025 | 0 | 3 | 0.2241 | 0.2794 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4084 | 20147.469 | 44266.1545 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 206.1893 | 0:240:120 | 0:00 | 0.2151 | 7 | 0.0052 | 0.2558 | 0.261 | 0.2583 | 0.0019 | 0 | 3 | 0.2151 | 0.268 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4087 | 20151.433 | 44266.1545 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 210.3131 | 0:240:120 | 0:00 | 0.2064 | 7 | 0.0044 | 0.2463 | 0.2507 | 0.2477 | 0.002 | 0 | 3 | 0.2064 | 0.2571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4090 | 20155.373 | 44266.1546 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 214.5193 | 0:240:120 | 0:00 | 0.1981 | 7 | 0.0057 | 0.2347 | 0.2404 | 0.2372 | 0.0022 | 0 | 3 | 0.1981 | 0.2467 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4093 | 20159.34 | 44266.1546 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 218.8097 | 0:240:120 | 0:00 | 0.1902 | 7 | 0.0051 | 0.2262 | 0.2313 | 0.2284 | 0.0018 | 0 | 3 | 0.1902 | 0.2367 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4096 | 20163.607 | 44266.1547 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.1859 | 0:240:120 | 0:00 | 0.1825 | 7 | 0.0051 | 0.2167 | 0.2218 | 0.219 | 0.0016 | 0 | 3 | 0.1825 | 0.2271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4099 | 20167.512 | 44266.1547 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 227.6496 | 0:240:120 | 0:00 | 0.1752 | 7 | 0.0036 | 0.2083 | 0.2119 | 0.2099 | 0.0015 | 0 | 3 | 0.1752 | 0.2179 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4102 | 20171.241 | 44266.1547 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 232.2026 | 0:240:120 | 0:00 | 0.1682 | 7 | 0.0044 | 0.1997 | 0.2041 | 0.2015 | 0.0017 | 0 | 3 | 0.1682 | 0.2092 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4105 | 20175.045 | 44266.1548 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 236.8467 | 0:240:120 | 0:00 | 0.1615 | 7 | 0.0041 | 0.1917 | 0.1958 | 0.1935 | 0.0013 | 0 | 3 | 0.1615 | 0.2007 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4108 | 20179.005 | 44266.1548 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 241.5836 | 0:240:120 | 0:00 | 0.155 | 7 | 0.004 | 0.1841 | 0.1881 | 0.186 | 0.0015 | 0 | 3 | 0.155 | 0.1927 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4111 | 20182.875 | 44266.1549 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.4153 | 0:240:120 | 0:00 | 0.1488 | 7 | 0.0041 | 0.1769 | 0.181 | 0.1788 | 0.0016 | 0 | 3 | 0.1488 | 0.1849 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4114 | 20186.624 | 44266.1549 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 251.3436 | 0:240:120 | 0:00 | 0.1429 | 7 | 0.0038 | 0.1696 | 0.1734 | 0.1719 | 0.0013 | 0 | 3 | 0.1429 | 0.1775 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4117 | 20190.319 | 44266.155 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.3704 | 0:240:120 | 0:00 | 0.1372 | 7 | 0.0038 | 0.1635 | 0.1673 | 0.1652 | 0.0014 | 0 | 3 | 0.1372 | 0.1704 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4120 | 20194.085 | 44266.155 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 261.4979 | 0:240:120 | 0:00 | 0.1318 | 7 | 0.0048 | 0.1556 | 0.1604 | 0.1577 | 0.0016 | 0 | 3 | 0.1318 | 0.1636 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4123 | 20197.849 | 44266.1551 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 266.7278 | 0:240:120 | 0:00 | 0.1265 | 7 | 0.0028 | 0.1502 | 0.153 | 0.1516 | 0.0009 | 0 | 3 | 0.1265 | 0.1571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4126 | 20201.478 | 44266.1551 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 272.0624 | 0:240:120 | 0:00 | 0.1215 | 7 | 0.0041 | 0.1435 | 0.1476 | 0.1458 | 0.0013 | 0 | 3 | 0.1215 | 0.1508 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4129 | 20205.448 | 44266.1551 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 277.5036 | 0:240:120 | 0:00 | 0.1167 | 7 | 0.0029 | 0.1384 | 0.1413 | 0.1404 | 0.001 | 0 | 3 | 0.1167 | 0.1448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4132 | 20208.98 | 44266.1552 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 283.0537 | 0:240:120 | 0:00 | 0.1121 | 7 | 0.0038 | 0.1322 | 0.136 | 0.1342 | 0.0013 | 0 | 3 | 0.1121 | 0.139 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4135 | 20212.703 | 44266.1552 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 288.7148 | 0:240:120 | 0:00 | 0.1076 | 7 | 0.0039 | 0.1268 | 0.1307 | 0.1292 | 0.0014 | 0 | 3 | 0.1076 | 0.1335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4138 | 20216.43 | 44266.1553 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.4891 | 0:240:120 | 0:00 | 0.1034 | 7 | 0.0023 | 0.1231 | 0.1254 | 0.1244 | 0.0008 | 0 | 3 | 0.1034 | 0.1282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4141 | 20220.076 | 44266.1553 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 300.3788 | 0:240:120 | 0:00 | 0.0993 | 7 | 0.003 | 0.1179 | 0.1209 | 0.1194 | 0.0011 | 0 | 3 | 0.0993 | 0.1231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4144 | 20223.778 | 44266.1554 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 306.3864 | 0:240:120 | 0:00 | 0.0954 | 7 | 0.0031 | 0.113 | 0.1161 | 0.1148 | 0.0009 | 0 | 3 | 0.0954 | 0.1182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4147 | 20227.853 | 44266.1554 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 312.5141 | 0:240:120 | 0:00 | 0.0916 | 7 | 0.0027 | 0.1089 | 0.1116 | 0.1101 | 0.001 | 0 | 3 | 0.0916 | 0.1135 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4150 | 20231.981 | 44266.1554 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 318.7644 | 0:240:120 | 0:00 | 0.088 | 7 | 0.0024 | 0.1043 | 0.1067 | 0.1055 | 0.001 | 0 | 3 | 0.088 | 0.109 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4153 | 20235.84 | 44266.1555 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 325.1397 | 0:240:120 | 0:00 | 0.0845 | 7 | 0.0029 | 0.1 | 0.1029 | 0.102 | 0.001 | 0 | 3 | 0.0845 | 0.1047 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4156 | 20239.474 | 44266.1555 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 331.6425 | 0:240:120 | 0:00 | 0.0812 | 7 | 0.0028 | 0.0964 | 0.0992 | 0.0983 | 0.0013 | 0 | 3 | 0.0812 | 0.1006 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4159 | 20243.257 | 44266.1556 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 338.2754 | 0:240:120 | 0:00 | 0.078 | 7 | 0.0041 | 0.092 | 0.0961 | 0.0941 | 0.0014 | 0 | 3 | 0.078 | 0.0966 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4162 | 20247.026 | 44266.1556 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 345.0409 | 0:240:120 | 0:00 | 0.0749 | 7 | 0.0038 | 0.0886 | 0.0924 | 0.0906 | 0.0014 | 0 | 3 | 0.0749 | 0.0928 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4165 | 20250.714 | 44266.1557 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 351.9417 | 0:240:120 | 0:00 | 0.072 | 7 | 0.0024 | 0.086 | 0.0884 | 0.087 | 0.001 | 0 | 3 | 0.072 | 0.0891 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4168 | 20254.437 | 44266.1557 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 358.9805 | 0:240:120 | 0:00 | 0.0691 | 7 | 0.003 | 0.0817 | 0.0847 | 0.0836 | 0.001 | 0 | 3 | 0.0691 | 0.0856 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4171 | 20258.026 | 44266.1557 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 366.1601 | 0:240:120 | 0:00 | 0.0664 | 7 | 0.003 | 0.0786 | 0.0816 | 0.0804 | 0.0012 | 0 | 3 | 0.0664 | 0.0822 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4174 | 20261.593 | 44266.1558 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 373.4833 | 0:240:120 | 0:00 | 0.0638 | 7 | 0.0042 | 0.0745 | 0.0787 | 0.0766 | 0.0014 | 0 | 3 | 0.0638 | 0.079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4177 | 20265.522 | 44266.1558 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 380.953 | 0:240:120 | 0:00 | 0.0613 | 7 | 0.0022 | 0.0729 | 0.0751 | 0.0743 | 0.0008 | 0 | 3 | 0.0613 | 0.0759 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4180 | 20269.199 | 44266.1559 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 388.5721 | 0:240:120 | 0:00 | 0.0589 | 7 | 0.0035 | 0.069 | 0.0725 | 0.0712 | 0.0014 | 0 | 3 | 0.0589 | 0.0729 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4183 | 20272.88 | 44266.1559 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 396.3435 | 0:240:120 | 0:00 | 0.0566 | 7 | 0.0025 | 0.0672 | 0.0697 | 0.0684 | 0.0009 | 0 | 3 | 0.0566 | 0.07 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4186 | 20276.514 | 44266.156 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 404.2704 | 0:240:120 | 0:00 | 0.0544 | 7 | 0.0031 | 0.0645 | 0.0676 | 0.066 | 0.0012 | 0 | 3 | 0.0544 | 0.0673 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4189 | 20280.432 | 44266.156 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 412.3558 | 0:240:120 | 0:00 | 0.0522 | 7 | 0.0029 | 0.0618 | 0.0647 | 0.0634 | 0.0011 | 0 | 3 | 0.0522 | 0.0646 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4192 | 20284.222 | 44266.1561 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 420.6029 | 0:240:120 | 0:00 | 0.0502 | 7 | 0.0033 | 0.0595 | 0.0628 | 0.0606 | 0.001 | 0 | 3 | 0.0502 | 0.0621 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4195 | 20287.864 | 44266.1561 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 429.015 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0031 | 0.0574 | 0.0605 | 0.0588 | 0.0011 | 0 | 3 | 0.0482 | 0.0597 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4198 | 20291.651 | 44266.1561 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 437.5953 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0019 | 0.0555 | 0.0574 | 0.0569 | 0.0007 | 0 | 3 | 0.0463 | 0.0573 | P | NP | 1-1-1-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4201 | 20295.321 | 44266.1562 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 446.3472 | 0:240:120 | 0:00 | 0.0445 | 7 | 0.003 | 0.0524 | 0.0554 | 0.0538 | 0.001 | 0 | 3 | 0.0445 | 0.0551 | P | NP | 0-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4204 | 20299.324 | 44266.1562 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 455.2741 | 0:240:120 | 0:00 | 0.0428 | 7 | 0.0025 | 0.0503 | 0.0528 | 0.0521 | 0.0009 | 0 | 3 | 0.0428 | 0.0529 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4207 | 20302.656 | 44266.1563 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 464.3796 | 0:240:120 | 0:00 | 0.0411 | 7 | 0.0028 | 0.0483 | 0.0511 | 0.0496 | 0.0011 | 0 | 3 | 0.0411 | 0.0511 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4210 | 20306.186 | 44266.1563 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 473.6672 | 0:240:120 | 0:00 | 0.0395 | 7 | 0.0024 | 0.0474 | 0.0498 | 0.0487 | 0.0008 | 0 | 3 | 0.0395 | 0.0495 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4213 | 20309.619 | 44266.1563 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 483.1405 | 0:240:120 | 0:00 | 0.038 | 7 | 0.0026 | 0.0451 | 0.0477 | 0.0467 | 0.001 | 0 | 3 | 0.038 | 0.048 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4216 | 20313.217 | 44266.1564 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 492.8033 | 0:240:120 | 0:00 | 0.0365 | 7 | 0.0028 | 0.0431 | 0.0459 | 0.0447 | 0.001 | 0 | 3 | 0.0365 | 0.0465 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4219 | 20316.604 | 44266.1564 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 502.6594 | 0:240:120 | 0:00 | 0.0351 | 7 | 0.0038 | 0.041 | 0.0448 | 0.0434 | 0.0015 | 0 | 3 | 0.0351 | 0.0451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4222 | 20320.089 | 44266.1565 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 512.7126 | 0:240:120 | 0:00 | 0.0337 | 7 | 0.003 | 0.0397 | 0.0427 | 0.0413 | 0.0011 | 0 | 3 | 0.0337 | 0.0437 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4225 | 20323.719 | 44266.1565 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 522.9668 | 0:240:120 | 0:00 | 0.0324 | 7 | 0.0028 | 0.0387 | 0.0415 | 0.0401 | 0.0009 | 0 | 3 | 0.0324 | 0.0424 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4228 | 20327.083 | 44266.1565 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 533.4262 | 0:240:120 | 0:00 | 0.0311 | 7 | 0.0029 | 0.0371 | 0.04 | 0.0388 | 0.0011 | 0 | 3 | 0.0311 | 0.0411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4231 | 20330.777 | 44266.1566 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 544.0947 | 0:240:120 | 0:00 | 0.0299 | 7 | 0.0024 | 0.0355 | 0.0379 | 0.0371 | 0.0009 | 0 | 3 | 0.0299 | 0.0399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4234 | 20334.457 | 44266.1566 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 554.9766 | 0:240:120 | 0:00 | 0.0287 | 7 | 0.003 | 0.0343 | 0.0373 | 0.0357 | 0.001 | 0 | 3 | 0.0287 | 0.0387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4237 | 20338.247 | 44266.1567 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 566.0761 | 0:240:120 | 0:00 | 0.0276 | 7 | 0.0025 | 0.0331 | 0.0356 | 0.0344 | 0.0008 | 0 | 3 | 0.0276 | 0.0376 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4240 | 20341.813 | 44266.1567 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 577.3976 | 0:240:120 | 0:00 | 0.0265 | 7 | 0.0029 | 0.0318 | 0.0347 | 0.0334 | 0.0009 | 0 | 3 | 0.0265 | 0.0365 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4243 | 20345.449 | 44266.1568 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 588.9456 | 0:240:120 | 0:00 | 0.0255 | 7 | 0.0029 | 0.0304 | 0.0333 | 0.0324 | 0.001 | 0 | 3 | 0.0255 | 0.0355 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4246 | 20349.097 | 44266.1568 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 600.7245 | 0:240:120 | 0:00 | 0.0245 | 7 | 0.0028 | 0.0292 | 0.032 | 0.031 | 0.001 | 0 | 3 | 0.0245 | 0.0345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4249 | 20352.543 | 44266.1568 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 612.739 | 0:240:120 | 0:00 | 0.0235 | 7 | 0.0031 | 0.0278 | 0.0309 | 0.0299 | 0.0012 | 0 | 3 | 0.0235 | 0.0335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4252 | 20356.059 | 44266.1569 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 624.9938 | 0:240:120 | 0:00 | 0.0226 | 7 | 0.0037 | 0.0276 | 0.0313 | 0.0294 | 0.0012 | 0 | 3 | 0.0226 | 0.0326 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4255 | 20359.455 | 44266.1569 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 637.4937 | 0:240:120 | 0:00 | 0.0217 | 7 | 0.0031 | 0.0261 | 0.0292 | 0.0282 | 0.001 | 0 | 3 | 0.0217 | 0.0317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4258 | 20362.852 | 44266.157 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 650.2435 | 0:240:120 | 0:00 | 0.0209 | 7 | 0.0029 | 0.0256 | 0.0285 | 0.0273 | 0.001 | 0 | 3 | 0.0209 | 0.0309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4261 | 20366.216 | 44266.157 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 663.2484 | 0:240:120 | 0:00 | 0.0201 | 7 | 0.0033 | 0.0244 | 0.0277 | 0.0266 | 0.0015 | 0 | 3 | 0.0201 | 0.0301 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4264 | 20369.619 | 44266.157 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 676.5134 | 0:240:120 | 0:00 | 0.0193 | 7 | 0.0025 | 0.0238 | 0.0263 | 0.0254 | 0.001 | 0 | 3 | 0.0193 | 0.0293 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4267 | 20373.114 | 44266.1571 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 690.0436 | 0:240:120 | 0:00 | 0.0185 | 7 | 0.0027 | 0.0231 | 0.0258 | 0.025 | 0.001 | 0 | 3 | 0.0185 | 0.0285 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4270 | 20376.605 | 44266.1571 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 703.8445 | 0:240:120 | 0:00 | 0.0178 | 7 | 0.0031 | 0.0221 | 0.0252 | 0.0241 | 0.0013 | 0 | 3 | 0.0178 | 0.0278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4273 | 20380.051 | 44266.1572 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 717.9214 | 0:240:120 | 0:00 | 0.0171 | 7 | 0.0033 | 0.0211 | 0.0244 | 0.0232 | 0.0014 | 0 | 3 | 0.0171 | 0.0271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4276 | 20383.419 | 44266.1572 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 732.2798 | 0:240:120 | 0:00 | 0.0165 | 7 | 0.0028 | 0.0211 | 0.0239 | 0.0228 | 0.0012 | 0 | 3 | 0.0165 | 0.0265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4279 | 20386.988 | 44266.1572 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 746.9254 | 0:240:120 | 0:00 | 0.0158 | 7 | 0.0036 | 0.0197 | 0.0233 | 0.0218 | 0.0013 | 0 | 3 | 0.0158 | 0.0258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4282 | 20390.428 | 44266.1573 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 761.8639 | 0:240:120 | 0:00 | 0.0152 | 7 | 0.0042 | 0.0189 | 0.0231 | 0.0216 | 0.0016 | 0 | 3 | 0.0152 | 0.0252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4285 | 20393.701 | 44266.1573 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 777.1012 | 0:240:120 | 0:00 | 0.0146 | 7 | 0.0036 | 0.0189 | 0.0225 | 0.0211 | 0.0014 | 0 | 3 | 0.0146 | 0.0246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4288 | 20397.017 | 44266.1574 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 792.6432 | 0:240:120 | 0:00 | 0.014 | 7 | 0.0035 | 0.0188 | 0.0223 | 0.021 | 0.0014 | 0 | 3 | 0.014 | 0.024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4291 | 20400.568 | 44266.1574 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 808.4961 | 0:240:120 | 0:00 | 0.0135 | 7 | 0.0042 | 0.018 | 0.0222 | 0.02 | 0.0015 | 0 | 3 | 0.0135 | 0.0235 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4294 | 20403.848 | 44266.1574 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 824.666 | 0:240:120 | 0:00 | 0.013 | 7 | 0.0032 | 0.0185 | 0.0217 | 0.0196 | 0.0012 | 0 | 3 | 0.013 | 0.023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4297 | 20407.174 | 44266.1575 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 841.1593 | 0:240:120 | 0:00 | 0.0125 | 7 | 0.0037 | 0.0179 | 0.0216 | 0.0195 | 0.0013 | 0 | 3 | 0.0125 | 0.0225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4300 | 20410.626 | 44266.1575 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 857.9825 | 0:240:120 | 0:00 | 0.012 | 7 | 0.0021 | 0.0179 | 0.02 | 0.0189 | 0.0009 | 0 | 3 | 0.012 | 0.022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4303 | 20413.944 | 44266.1576 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 875.1422 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0021 | 0.0176 | 0.0197 | 0.0187 | 0.0008 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4306 | 20417.508 | 44266.1576 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 892.645 | 0:240:120 | 0:00 | 0.0111 | 7 | 0.0013 | 0.0179 | 0.0192 | 0.0183 | 0.0004 | 0 | 3 | 0.0111 | 0.0211 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4309 | 20420.712 | 44266.1576 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 910.4979 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0017 | 0.0169 | 0.0186 | 0.0176 | 0.0005 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4312 | 20424.044 | 44266.1577 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 928.7079 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.0017 | 0.0161 | 0.0178 | 0.0172 | 0.0007 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4315 | 20427.458 | 44266.1577 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 938.9356 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0022 | 0.0161 | 0.0183 | 0.0171 | 0.0008 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4318 | 20431.102 | 44266.1578 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 957.7143 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0021 | 0.016 | 0.0181 | 0.0168 | 0.0008 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-1-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4321 | 20434.564 | 44266.1578 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 976.8686 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0018 | 0.0156 | 0.0174 | 0.0165 | 0.0008 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 1-1-0-1-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
4324 | 20438.041 | 44266.1578 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 996.4059 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0016 | 0.0155 | 0.0171 | 0.0161 | 0.0006 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 1-1-0-1-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4327 | 20441.403 | 44266.1579 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1016.3341 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0029 | 0.0145 | 0.0174 | 0.0156 | 0.0009 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4330 | 20444.722 | 44266.1579 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1036.6607 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0053 | 0.0126 | 0.0179 | 0.015 | 0.002 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4333 | 20448.491 | 44266.158 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1057.3939 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0041 | 0.0126 | 0.0167 | 0.0149 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4336 | 20451.858 | 44266.158 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1078.5418 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0042 | 0.0124 | 0.0166 | 0.0148 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4339 | 20455.308 | 44266.158 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1100.1127 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0034 | 0.0127 | 0.0161 | 0.0145 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4342 | 20458.687 | 44266.1581 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1122.1149 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0046 | 0.012 | 0.0166 | 0.0144 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4345 | 20462.357 | 44266.1581 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1144.5572 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0043 | 0.0123 | 0.0166 | 0.0146 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4348 | 20465.719 | 44266.1582 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1167.4484 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0035 | 0.0124 | 0.0159 | 0.0139 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4351 | 20469.156 | 44266.1582 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1190.7973 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0038 | 0.0123 | 0.0161 | 0.0139 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4354 | 20472.774 | 44266.1582 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1214.6133 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0044 | 0.0119 | 0.0163 | 0.0142 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4357 | 20476.255 | 44266.1583 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1238.9055 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0052 | 0.0113 | 0.0165 | 0.0141 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4360 | 20479.583 | 44266.1583 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1263.6837 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0047 | 0.0112 | 0.0159 | 0.0137 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4363 | 20483.233 | 44266.1584 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1288.9573 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0047 | 0.0113 | 0.016 | 0.0135 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4366 | 20486.675 | 44266.1584 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1314.7365 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0052 | 0.0112 | 0.0164 | 0.0137 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4369 | 20490.186 | 44266.1584 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1341.0312 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0041 | 0.0114 | 0.0155 | 0.0135 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4372 | 20493.469 | 44266.1585 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1367.8518 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0047 | 0.0108 | 0.0155 | 0.0134 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4375 | 20496.995 | 44266.1585 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1395.2089 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0042 | 0.011 | 0.0152 | 0.013 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4378 | 20500.371 | 44266.1586 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1423.113 | 0:240:120 | 0:00 | 0.0043 | 7 | 0.0041 | 0.0112 | 0.0153 | 0.0133 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4381 | 20503.792 | 44266.1586 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1451.5753 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0052 | 0.0106 | 0.0158 | 0.013 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4384 | 20507.165 | 44266.1586 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1480.6068 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0051 | 0.0102 | 0.0153 | 0.0129 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4387 | 20510.974 | 44266.1587 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1510.2189 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0042 | 0.0106 | 0.0148 | 0.0129 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4390 | 20514.452 | 44266.1587 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1540.4233 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0046 | 0.0105 | 0.0151 | 0.0128 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4393 | 20518.007 | 44266.1588 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1571.2318 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0041 | 0.0107 | 0.0148 | 0.0127 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4396 | 20521.45 | 44266.1588 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1602.6564 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0036 | 0.01 | 0.0136 | 0.012 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4399 | 20524.923 | 44266.1588 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1634.7096 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0031 | 0.0108 | 0.0139 | 0.0122 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4402 | 20528.477 | 44266.1589 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1667.4037 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0044 | 0.0102 | 0.0146 | 0.0118 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4405 | 20531.776 | 44266.1589 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1700.7518 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0042 | 0.009 | 0.0132 | 0.0112 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4408 | 20535.129 | 44266.159 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1734.7669 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0033 | 0.0092 | 0.0125 | 0.0108 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4411 | 20538.653 | 44266.159 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1769.4622 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0036 | 0.0093 | 0.0129 | 0.011 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4414 | 20542.004 | 44266.159 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1804.8514 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0041 | 0.0093 | 0.0134 | 0.0113 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4417 | 20545.34 | 44266.1591 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1840.9485 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0042 | 0.0093 | 0.0135 | 0.011 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4420 | 20548.849 | 44266.1591 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1877.7674 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0035 | 0.0096 | 0.0131 | 0.0112 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4423 | 20552.564 | 44266.1592 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1877.8711 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0036 | 0.0093 | 0.0129 | 0.011 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4426 | 20555.989 | 44266.1592 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1915.4286 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0041 | 0.0092 | 0.0133 | 0.0109 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4429 | 20559.336 | 44266.1592 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1953.7371 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0036 | 0.0093 | 0.0129 | 0.011 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4432 | 20562.727 | 44266.1593 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1992.8119 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0048 | 0.0096 | 0.0144 | 0.0115 | 0.0017 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4435 | 20565.983 | 44266.1593 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2032.6681 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0028 | 0.0097 | 0.0125 | 0.0112 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4438 | 20569.416 | 44266.1594 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2073.3215 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0054 | 0.0096 | 0.015 | 0.0114 | 0.0017 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4441 | 20573.112 | 44266.1594 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2114.7879 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0055 | 0.0096 | 0.0151 | 0.0117 | 0.0019 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4444 | 20576.446 | 44266.1594 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2157.0837 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0025 | 0.0094 | 0.0119 | 0.0107 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4447 | 20579.893 | 44266.1595 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2200.2253 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0024 | 0.0092 | 0.0116 | 0.0103 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4450 | 20583.405 | 44266.1595 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2244.2298 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0055 | 0.0089 | 0.0144 | 0.0108 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4453 | 20586.978 | 44266.1596 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2289.1144 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0018 | 0.0097 | 0.0115 | 0.0107 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4456 | 20590.546 | 44266.1596 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2334.8967 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4459 | 20594.062 | 44266.1596 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2381.5947 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4462 | 20597.331 | 44266.1597 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2429.2266 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0021 | 0.0094 | 0.0115 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4465 | 20600.915 | 44266.1597 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2477.8111 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4468 | 20604.564 | 44266.1598 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2527.3673 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0011 | 0.0102 | 0.0113 | 0.0106 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4471 | 20607.953 | 44266.1598 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2577.9147 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4474 | 20611.733 | 44266.1598 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2629.4729 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0005 | 0.0103 | 0.0108 | 0.0105 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4477 | 20615.132 | 44266.1599 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2682.0624 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0047 | 0.0094 | 0.0141 | 0.0107 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4480 | 20618.595 | 44266.1599 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2735.7036 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0013 | 0.0099 | 0.0112 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4483 | 20621.871 | 44266.16 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2790.4177 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0006 | 0.0096 | 0.0102 | 0.0099 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4486 | 20625.729 | 44266.16 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2846.2261 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0027 | 0.0089 | 0.0116 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4489 | 20629.13 | 44266.16 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2903.1506 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0018 | 0.009 | 0.0108 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4492 | 20632.471 | 44266.1601 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2961.2136 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0056 | 0.0095 | 0.0151 | 0.0106 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4495 | 20635.786 | 44266.1601 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3020.4379 | 0:240:120 | 0:00 | 0.001 | 7 | 0.002 | 0.0094 | 0.0114 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4498 | 20639.452 | 44266.1602 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3080.8466 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0013 | 0.0097 | 0.011 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4501 | 20642.875 | 44266.1602 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3142.4636 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0009 | 0.0096 | 0.0105 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4504 | 20646.616 | 44266.1602 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3205.3128 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4507 | 20650.079 | 44266.1603 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3269.4191 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0023 | 0.0091 | 0.0114 | 0.0103 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4510 | 20653.62 | 44266.1603 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3334.8075 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0013 | 0.0097 | 0.011 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4513 | 20656.958 | 44266.1604 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3401.5036 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4516 | 20660.362 | 44266.1604 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3469.5337 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0022 | 0.0092 | 0.0114 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4519 | 20664.255 | 44266.1604 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3538.9244 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0005 | 0.0095 | 0.01 | 0.0098 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4522 | 20667.635 | 44266.1605 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3609.7029 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0011 | 0.0093 | 0.0104 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4525 | 20671.168 | 44266.1605 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3681.8969 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4528 | 20674.499 | 44266.1606 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3755.5349 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4531 | 20677.899 | 44266.1606 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3830.6456 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0008 | 0.0099 | 0.0107 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4534 | 20681.243 | 44266.1606 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3907.2585 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0019 | 0.0095 | 0.0114 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4537 | 20684.662 | 44266.1607 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3985.4036 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4540 | 20688.278 | 44266.1607 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4065.1117 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0022 | 0.0093 | 0.0115 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4543 | 20691.956 | 44266.1608 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4146.4139 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.001 | 0.0099 | 0.0109 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4546 | 20695.323 | 44266.1608 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4229.3422 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4549 | 20698.867 | 44266.1608 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4313.9291 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0005 | 0.01 | 0.0105 | 0.0102 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4552 | 20702.52 | 44266.1609 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4400.2077 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0022 | 0.0089 | 0.0111 | 0.0097 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4555 | 20705.801 | 44266.1609 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4488.2118 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0048 | 0.0095 | 0.0143 | 0.0104 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4558 | 20709.586 | 44266.161 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4577.976 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0048 | 0.0093 | 0.0141 | 0.0106 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4561 | 20712.992 | 44266.161 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4669.5356 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0041 | 0.01 | 0.0141 | 0.0108 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4564 | 20716.275 | 44266.1611 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4762.9263 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4567 | 20719.728 | 44266.1611 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4858.1848 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0007 | 0.0094 | 0.0101 | 0.0099 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4570 | 20723.004 | 44266.1611 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4955.3485 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0018 | 0.0096 | 0.0114 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4573 | 20726.442 | 44266.1612 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5054.4555 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.002 | 0.0092 | 0.0112 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4576 | 20730.127 | 44266.1612 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5155.5446 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4579 | 20733.563 | 44266.1613 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5258.6555 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4582 | 20736.834 | 44266.1613 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5363.8286 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0011 | 0.0102 | 0.0113 | 0.0106 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4585 | 20740.503 | 44266.1613 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5471.1051 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0014 | 0.0098 | 0.0112 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4588 | 20743.843 | 44266.1614 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5580.5273 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0006 | 0.0095 | 0.0101 | 0.0099 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4591 | 20747.148 | 44266.1614 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5692.1378 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4594 | 20750.59 | 44266.1614 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5805.9806 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0013 | 0.0099 | 0.0112 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4597 | 20753.999 | 44266.1615 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5922.1002 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4600 | 20757.536 | 44266.1615 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6040.5422 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0012 | 0.0088 | 0.01 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4603 | 20760.891 | 44266.1616 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6161.353 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4606 | 20764.466 | 44266.1616 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6284.5801 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0005 | 0.0097 | 0.0102 | 0.0099 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4609 | 20767.786 | 44266.1616 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6410.2717 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4612 | 20771.627 | 44266.1617 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6538.4771 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.001 | 0.0094 | 0.0104 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4615 | 20774.899 | 44266.1617 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6669.2466 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0012 | 0.0091 | 0.0103 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4618 | 20778.44 | 44266.1618 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6802.6316 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0015 | 0.0089 | 0.0104 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4621 | 20781.706 | 44266.1618 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6938.6842 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.001 | 0.01 | 0.011 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4624 | 20785.107 | 44266.1618 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7077.4579 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0009 | 0.0095 | 0.0104 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4627 | 20788.417 | 44266.1619 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7219.0071 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0022 | 0.0089 | 0.0111 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4630 | 20791.662 | 44266.1619 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7363.3872 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0022 | 0.009 | 0.0112 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4633 | 20794.967 | 44266.162 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7510.6549 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0005 | 0.0099 | 0.0104 | 0.0102 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4636 | 20798.274 | 44266.162 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7660.868 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0095 | 0.0106 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4639 | 20801.569 | 44266.162 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7814.0854 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4642 | 20804.968 | 44266.1621 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7970.3671 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0021 | 0.0091 | 0.0112 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4645 | 20808.641 | 44266.1621 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8129.7744 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.002 | 0.009 | 0.011 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4648 | 20811.997 | 44266.1622 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8292.3699 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0008 | 0.0097 | 0.0105 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4651 | 20815.341 | 44266.1622 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8458.2173 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0018 | 0.0093 | 0.0111 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4654 | 20818.877 | 44266.1622 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8627.3817 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4657 | 20822.218 | 44266.1623 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8799.9293 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0091 | 0.0103 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4660 | 20825.743 | 44266.1623 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8975.9279 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4663 | 20828.852 | 44266.1624 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9155.4465 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4666 | 20832.375 | 44266.1624 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9338.5554 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4669 | 20835.67 | 44266.1624 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9525.3265 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.0092 | 0.0107 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4672 | 20839.004 | 44266.1625 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9715.833 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.0093 | 0.0108 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4675 | 20842.308 | 44266.1625 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9910.1497 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0088 | 0.0107 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4678 | 20845.99 | 44266.1626 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10108.3527 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0096 | 0.0107 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4681 | 20849.539 | 44266.1626 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10310.5197 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0024 | 0.0099 | 0.0123 | 0.0107 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4684 | 20853.211 | 44266.1626 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10516.7301 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4687 | 20856.677 | 44266.1627 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10727.0647 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0097 | 0.0109 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4690 | 20860.373 | 44266.1627 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10941.606 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0018 | 0.0093 | 0.0111 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4693 | 20864.176 | 44266.1628 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11160.4381 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0097 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4696 | 20867.625 | 44266.1628 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11383.6469 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4699 | 20871.014 | 44266.1628 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11611.3198 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4702 | 20874.338 | 44266.1629 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11843.5462 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0006 | 0.0096 | 0.0102 | 0.0099 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4705 | 21014.078 | 44266.1645 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.2 | 0:240:120 | 0:00 | 16.4658 | 7 | 46.5251 | 100.4765 | 147.0016 | 115.1974 | 20.6986 | 428.4317 | 3 | 16.4658 | 68.2719 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4708 | 21395.584 | 44266.1689 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.2 | 0:240:120 | 0:00 | 14.0163 | 7 | 36.3947 | 50.6618 | 87.0565 | 62.9121 | 18.0624 | 326.2511 | 3 | 14.0163 | 43.0212 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4711 | 21604.248 | 44266.1713 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.1 | 0:240:120 | 0:00 | 12.3317 | 7 | 6.8334 | 24.8204 | 31.6538 | 27.003 | 3.2657 | 10.6646 | 3 | 12.3317 | 32.114 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4714 | 21693.943 | 44266.1724 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.1 | 0:240:120 | 0:00 | 10.8533 | 7 | 1.8035 | 21.6859 | 23.4894 | 22.4291 | 0.7924 | 0.6279 | 3 | 10.8533 | 24.9464 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4717 | 21764.954 | 44266.1732 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50 | 0:240:120 | 0:00 | 9.7778 | 7 | 1.9653 | 18.7683 | 20.7336 | 19.5255 | 0.9072 | 0.823 | 3 | 9.7778 | 20.7059 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4720 | 21827.737 | 44266.1739 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51 | 0:240:120 | 0:00 | 8.7912 | 7 | 2.6449 | 15.3292 | 17.9741 | 16.3255 | 1.2371 | 1.5304 | 3 | 8.7912 | 17.3635 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4723 | 21880.955 | 44266.1745 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.1 | 0:240:120 | 0:00 | 7.8966 | 7 | 1.605 | 12.4739 | 14.0789 | 13.0173 | 0.7888 | 0.6221 | 3 | 7.8966 | 14.6992 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4726 | 21924.337 | 44266.175 | Vista Speed | E | 20E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.1 | 0:240:120 | 0:00 | 7.2154 | 7 | 0.7563 | 11.2999 | 12.0562 | 11.6241 | 0.3318 | 0.1101 | 3 | 7.2154 | 12.8677 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4729 | 21977.581 | 44266.1756 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55 | 0:240:120 | 0:00 | 12.4738 | 7 | 1.7525 | 22.7572 | 24.5097 | 23.5673 | 0.7213 | 0.5203 | 3 | 12.4738 | 26.9855 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4732 | 22053.242 | 44266.1765 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.659 | 0:240:120 | 0:00 | 11.6834 | 7 | 2.2572 | 20.9753 | 23.2325 | 21.8955 | 1.0013 | 1.0027 | 3 | 11.6834 | 24.0848 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4735 | 22123.986 | 44266.1773 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.5567 | 0:240:120 | 0:00 | 10.7448 | 7 | 1.3294 | 19.5733 | 20.9027 | 20.0674 | 0.6267 | 0.3927 | 3 | 10.7448 | 20.9766 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4738 | 22187.46 | 44266.1781 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.584 | 0:240:120 | 0:00 | 9.8282 | 7 | 1.2334 | 17.2632 | 18.4966 | 17.6894 | 0.6044 | 0.3653 | 3 | 9.8282 | 18.2432 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4741 | 22243.777 | 44266.1787 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.6885 | 0:240:120 | 0:00 | 8.9905 | 7 | 1.2416 | 14.8532 | 16.0948 | 15.2811 | 0.6094 | 0.3714 | 3 | 8.9905 | 15.9702 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4744 | 22293.551 | 44266.1793 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.5754 | 0:240:120 | 0:00 | 8.4067 | 7 | 1.8933 | 12.4819 | 14.3752 | 13.1235 | 0.8972 | 0.8049 | 3 | 8.4067 | 14.4986 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4747 | 22337.96 | 44266.1798 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.9616 | 0:240:120 | 0:00 | 7.6208 | 7 | 0.6462 | 11.4031 | 12.0493 | 11.7103 | 0.2596 | 0.0674 | 3 | 7.6208 | 12.6475 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4750 | 22375.763 | 44266.1803 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.8811 | 0:240:120 | 0:00 | 6.7293 | 7 | 0.6654 | 9.888 | 10.5534 | 10.1136 | 0.3217 | 0.1035 | 3 | 6.7293 | 10.7098 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4753 | 22409.413 | 44266.1806 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.5373 | 0:240:120 | 0:00 | 6.0987 | 7 | 0.6688 | 8.5878 | 9.2566 | 8.8057 | 0.3212 | 0.1032 | 3 | 6.0987 | 9.4324 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4756 | 22439.379 | 44266.181 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.3699 | 0:240:120 | 0:00 | 5.5137 | 7 | 0.3 | 7.6376 | 7.9376 | 7.7684 | 0.1287 | 0.0166 | 3 | 5.5137 | 8.3102 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4759 | 22465.594 | 44266.1813 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.5281 | 0:240:120 | 0:00 | 4.9411 | 7 | 0.3222 | 6.7309 | 7.0531 | 6.8775 | 0.1353 | 0.0183 | 3 | 4.9411 | 7.2659 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4762 | 22489.035 | 44266.1816 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.0401 | 0:240:120 | 0:00 | 4.3943 | 7 | 0.3025 | 5.8106 | 6.1131 | 5.9101 | 0.1475 | 0.0218 | 3 | 4.3943 | 6.315 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4765 | 22509.965 | 44266.1818 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.6441 | 0:240:120 | 0:00 | 3.9295 | 7 | 0.2675 | 5.1457 | 5.4132 | 5.2378 | 0.1305 | 0.017 | 3 | 3.9295 | 5.5401 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4768 | 22529.027 | 44266.182 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.3436 | 0:240:120 | 0:00 | 3.5304 | 7 | 0.2212 | 4.5233 | 4.7445 | 4.5999 | 0.1085 | 0.0118 | 3 | 3.5304 | 4.8977 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4771 | 22545.659 | 44266.1822 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.7408 | 0:240:120 | 0:00 | 3.0121 | 7 | 0.1794 | 3.8121 | 3.9915 | 3.8725 | 0.0885 | 0.0078 | 3 | 3.0121 | 4.0936 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4774 | 22560.086 | 44266.1824 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.1355 | 0:240:120 | 0:00 | 2.6109 | 7 | 0.1276 | 3.2803 | 3.4079 | 3.3237 | 0.0628 | 0.0039 | 3 | 2.6109 | 3.4932 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4777 | 22573.205 | 44266.1825 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.8592 | 0:240:120 | 0:00 | 2.2706 | 7 | 0.0925 | 2.8134 | 2.9059 | 2.8493 | 0.0427 | 0.0018 | 3 | 2.2706 | 2.9985 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4780 | 22584.948 | 44266.1827 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.3395 | 0:240:120 | 0:00 | 2.0645 | 7 | 0.0743 | 2.5505 | 2.6248 | 2.5764 | 0.0363 | 0.0013 | 3 | 2.0645 | 2.7051 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4783 | 22595.823 | 44266.1828 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.0123 | 0:240:120 | 0:00 | 1.7887 | 7 | 0.0701 | 2.1812 | 2.2513 | 2.2109 | 0.0301 | 0.0009 | 3 | 1.7887 | 2.3194 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4786 | 22605.599 | 44266.1829 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.7152 | 0:240:120 | 0:00 | 1.5676 | 7 | 0.0489 | 1.9078 | 1.9567 | 1.9254 | 0.0232 | 0.0005 | 3 | 1.5676 | 2.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4789 | 22614.461 | 44266.183 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.9739 | 0:240:120 | 0:00 | 1.4007 | 7 | 0.0437 | 1.6938 | 1.7375 | 1.7121 | 0.019 | 0.0004 | 3 | 1.4007 | 1.7903 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4792 | 22622.845 | 44266.1831 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.8904 | 0:240:120 | 0:00 | 1.2214 | 7 | 0.0454 | 1.4672 | 1.5126 | 1.4864 | 0.0201 | 0.0004 | 3 | 1.2214 | 1.5509 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4795 | 22630.431 | 44266.1832 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.1296 | 0:240:120 | 0:00 | 1.0895 | 7 | 0.03 | 1.3084 | 1.3384 | 1.3191 | 0.0139 | 0.0002 | 3 | 1.0895 | 1.3766 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4798 | 22637.684 | 44266.1833 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131.3994 | 0:240:120 | 0:00 | 0.9469 | 7 | 0.022 | 1.1328 | 1.1548 | 1.1411 | 0.01 | 0.0001 | 3 | 0.9469 | 1.1903 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4801 | 22644.348 | 44266.1834 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 140.9265 | 0:240:120 | 0:00 | 0.8166 | 7 | 0.0269 | 0.9703 | 0.9972 | 0.9812 | 0.0119 | 0.0001 | 3 | 0.8166 | 1.0216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4804 | 22650.437 | 44266.1834 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.843 | 0:240:120 | 0:00 | 0.7089 | 7 | 0.0205 | 0.8429 | 0.8634 | 0.8504 | 0.0091 | 0.0001 | 3 | 0.7089 | 0.8835 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4807 | 22656.336 | 44266.1835 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 161.6186 | 0:240:120 | 0:00 | 0.6154 | 7 | 0.0155 | 0.7291 | 0.7446 | 0.7353 | 0.0067 | 0 | 3 | 0.6154 | 0.7644 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4810 | 22661.673 | 44266.1836 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175.6051 | 0:240:120 | 0:00 | 0.5204 | 7 | 0.0127 | 0.6148 | 0.6275 | 0.6194 | 0.0055 | 0 | 3 | 0.5204 | 0.6441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4813 | 22666.991 | 44266.1836 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 192.335 | 0:240:120 | 0:00 | 0.434 | 7 | 0.0103 | 0.5122 | 0.5225 | 0.5165 | 0.0045 | 0 | 3 | 0.434 | 0.5356 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4816 | 22671.924 | 44266.1837 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 212.564 | 0:240:120 | 0:00 | 0.3565 | 7 | 0.0074 | 0.4191 | 0.4265 | 0.4221 | 0.0033 | 0 | 3 | 0.3565 | 0.4387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4819 | 22676.147 | 44266.1837 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 241.5897 | 0:240:120 | 0:00 | 0.2779 | 7 | 0.005 | 0.3267 | 0.3317 | 0.3287 | 0.0021 | 0 | 3 | 0.2779 | 0.341 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4822 | 22680.375 | 44266.1838 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 261.9727 | 0:240:120 | 0:00 | 0.2377 | 7 | 0.0054 | 0.2787 | 0.2841 | 0.2809 | 0.0023 | 0 | 3 | 0.2377 | 0.2913 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4825 | 22684.373 | 44266.1838 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 286.3575 | 0:240:120 | 0:00 | 0.2004 | 7 | 0.0029 | 0.2361 | 0.239 | 0.2375 | 0.0011 | 0 | 3 | 0.2004 | 0.2453 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4828 | 22688.166 | 44266.1839 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 310.8281 | 0:240:120 | 0:00 | 0.1714 | 7 | 0.0041 | 0.2003 | 0.2044 | 0.2024 | 0.0014 | 0 | 3 | 0.1714 | 0.2096 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4831 | 22692.017 | 44266.1839 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 333.6993 | 0:240:120 | 0:00 | 0.1498 | 7 | 0.0038 | 0.1755 | 0.1793 | 0.1773 | 0.0014 | 0 | 3 | 0.1498 | 0.183 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4834 | 22695.987 | 44266.184 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 354.6895 | 0:240:120 | 0:00 | 0.1335 | 7 | 0.004 | 0.1563 | 0.1603 | 0.1582 | 0.0014 | 0 | 3 | 0.1335 | 0.163 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4837 | 22699.767 | 44266.184 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 390.8179 | 0:240:120 | 0:00 | 0.1112 | 7 | 0.0035 | 0.1293 | 0.1328 | 0.1311 | 0.0013 | 0 | 3 | 0.1112 | 0.1356 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4840 | 22703.513 | 44266.1841 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 421.256 | 0:240:120 | 0:00 | 0.0965 | 7 | 0.0029 | 0.1125 | 0.1154 | 0.114 | 0.0009 | 0 | 3 | 0.0965 | 0.1177 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4843 | 22707.186 | 44266.1841 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 454.0657 | 0:240:120 | 0:00 | 0.0839 | 7 | 0.0028 | 0.0978 | 0.1006 | 0.0995 | 0.001 | 0 | 3 | 0.0839 | 0.1022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4846 | 22711.257 | 44266.1841 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 494.3488 | 0:240:120 | 0:00 | 0.0715 | 7 | 0.002 | 0.084 | 0.086 | 0.0851 | 0.0008 | 0 | 3 | 0.0715 | 0.0871 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4849 | 22714.951 | 44266.1842 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 540.9041 | 0:240:120 | 0:00 | 0.0604 | 7 | 0.003 | 0.07 | 0.073 | 0.0717 | 0.001 | 0 | 3 | 0.0604 | 0.0736 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4852 | 22718.401 | 44266.1842 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 606.2188 | 0:240:120 | 0:00 | 0.0489 | 7 | 0.0033 | 0.0569 | 0.0602 | 0.059 | 0.0013 | 0 | 3 | 0.0489 | 0.0595 | P | NP | 0-1-0-0-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4855 | 22722.068 | 44266.1843 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 656.0532 | 0:240:120 | 0:00 | 0.0422 | 7 | 0.003 | 0.0489 | 0.0519 | 0.0506 | 0.001 | 0 | 3 | 0.0422 | 0.0522 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4858 | 22725.858 | 44266.1843 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 708.565 | 0:240:120 | 0:00 | 0.0365 | 7 | 0.0023 | 0.0432 | 0.0455 | 0.0443 | 0.0007 | 0 | 3 | 0.0365 | 0.0465 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4861 | 22729.481 | 44266.1844 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 715 | 0:240:120 | 0:00 | 0.0359 | 7 | 0.0028 | 0.0415 | 0.0443 | 0.0431 | 0.001 | 0 | 3 | 0.0359 | 0.0459 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4864 | 22732.912 | 44266.1844 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 775 | 0:240:120 | 0:00 | 0.0309 | 7 | 0.0034 | 0.0356 | 0.039 | 0.0375 | 0.0013 | 0 | 3 | 0.0309 | 0.0409 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4867 | 22736.369 | 44266.1844 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 829.589 | 0:240:120 | 0:00 | 0.0272 | 7 | 0.0028 | 0.031 | 0.0338 | 0.033 | 0.0011 | 0 | 3 | 0.0272 | 0.0372 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4870 | 22739.777 | 44266.1845 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 897.785 | 0:240:120 | 0:00 | 0.0235 | 7 | 0.003 | 0.028 | 0.031 | 0.0295 | 0.0011 | 0 | 3 | 0.0235 | 0.0335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4873 | 22743.368 | 44266.1845 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 980.371 | 0:240:120 | 0:00 | 0.02 | 7 | 0.0035 | 0.0236 | 0.0271 | 0.0258 | 0.0011 | 0 | 3 | 0.02 | 0.03 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4876 | 22746.64 | 44266.1846 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1053.56 | 0:240:120 | 0:00 | 0.0175 | 7 | 0.0025 | 0.0219 | 0.0244 | 0.0233 | 0.0008 | 0 | 3 | 0.0175 | 0.0275 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4879 | 22750.633 | 44266.1846 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1151.62 | 0:240:120 | 0:00 | 0.0148 | 7 | 0.0029 | 0.0197 | 0.0226 | 0.0211 | 0.001 | 0 | 3 | 0.0148 | 0.0248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4882 | 22753.997 | 44266.1846 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1222.83 | 0:240:120 | 0:00 | 0.0133 | 7 | 0.0028 | 0.018 | 0.0208 | 0.0194 | 0.0011 | 0 | 3 | 0.0133 | 0.0233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4885 | 22757.436 | 44266.1847 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1295.86 | 0:240:120 | 0:00 | 0.0119 | 7 | 0.0029 | 0.0172 | 0.0201 | 0.0184 | 0.0012 | 0 | 3 | 0.0119 | 0.0219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4888 | 22761.105 | 44266.1847 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1326.01 | 0:240:120 | 0:00 | 0.0114 | 7 | 0.0017 | 0.0174 | 0.0191 | 0.0181 | 0.0006 | 0 | 3 | 0.0114 | 0.0214 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4891 | 22764.449 | 44266.1848 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1391.7843 | 0:240:120 | 0:00 | 0.0104 | 7 | 0.001 | 0.0158 | 0.0168 | 0.0164 | 0.0003 | 0 | 3 | 0.0104 | 0.0204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4894 | 22767.979 | 44266.1848 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1565.7574 | 0:240:120 | 0:00 | 0.0084 | 7 | 0.0041 | 0.0122 | 0.0163 | 0.0148 | 0.0015 | 0 | 3 | 0.0084 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4897 | 22771.403 | 44266.1848 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1739.7304 | 0:240:120 | 0:00 | 0.0069 | 7 | 0.0051 | 0.0113 | 0.0164 | 0.0136 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4900 | 22774.781 | 44266.1849 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1948.4981 | 0:240:120 | 0:00 | 0.0056 | 7 | 0.0041 | 0.0106 | 0.0147 | 0.0131 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4903 | 22778.143 | 44266.1849 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2652.0451 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0028 | 0.0092 | 0.012 | 0.0102 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4906 | 22801.416 | 44266.1852 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.1 | 0:240:120 | 0:00 | 10.2415 | 7 | 1.2847 | 18.4143 | 19.699 | 18.8686 | 0.6229 | 0.388 | 3 | 10.2415 | 19.4416 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4909 | 22861.634 | 44266.1859 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.1 | 0:240:120 | 0:00 | 9.4199 | 7 | 1.2585 | 16.0813 | 17.3398 | 16.5035 | 0.6242 | 0.3896 | 3 | 9.4199 | 17.1104 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4912 | 22914.847 | 44266.1865 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.1 | 0:240:120 | 0:00 | 8.7108 | 7 | 1.5722 | 13.6812 | 15.2534 | 14.198 | 0.7679 | 0.5896 | 3 | 8.7108 | 15.2543 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4915 | 22961.07 | 44266.187 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.3 | 0:240:120 | 0:00 | 7.9786 | 7 | 0.4638 | 12.032 | 12.4958 | 12.1937 | 0.2242 | 0.0503 | 3 | 7.9786 | 13.4726 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4918 | 23000.559 | 44266.1875 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.9 | 0:240:120 | 0:00 | 7.1602 | 7 | 0.479 | 10.7473 | 11.2263 | 10.9086 | 0.2379 | 0.0566 | 3 | 7.1602 | 11.6261 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4921 | 23036.229 | 44266.1879 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.7 | 0:240:120 | 0:00 | 6.4037 | 7 | 0.7202 | 9.1686 | 9.8888 | 9.5054 | 0.2995 | 0.0897 | 3 | 6.4037 | 10.0412 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4924 | 23067.812 | 44266.1883 | Vista Speed | E | 25E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.5 | 0:240:120 | 0:00 | 5.7784 | 7 | 0.65 | 7.9354 | 8.5854 | 8.1711 | 0.3116 | 0.0971 | 3 | 5.7784 | 8.8109 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4927 | 23336.172 | 44266.1914 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66 | 0:240:120 | 0:00 | 23.6749 | 7 | 24.9706 | 221.3362 | 246.3068 | 230.9814 | 11.5198 | 132.705 | 3 | 23.6749 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4930 | 24078.162 | 44266.2 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.1712 | 0:240:120 | 0:00 | 22.9902 | 7 | 43.1294 | 202.9209 | 246.0503 | 221.7213 | 18.9431 | 358.8421 | 3 | 22.9902 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4933 | 24802.447 | 44266.2083 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.3699 | 0:240:120 | 0:00 | 22.2414 | 7 | 27.1184 | 201.7682 | 228.8866 | 210.8401 | 13.277 | 176.2789 | 3 | 22.2414 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4936 | 25483.534 | 44266.2162 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.903 | 0:240:120 | 0:00 | 20.4464 | 7 | 41.5564 | 179.5693 | 221.1257 | 195.7348 | 19.2256 | 369.6233 | 3 | 20.4464 | 696.7135 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4939 | 26130.745 | 44266.2237 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.373 | 0:240:120 | 0:00 | 19.0794 | 7 | 28.923 | 172.8516 | 201.7746 | 184.6867 | 13.0131 | 169.3409 | 3 | 19.0794 | 232.3625 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4942 | 26717.149 | 44266.2305 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.9141 | 0:240:120 | 0:00 | 17.7074 | 7 | 22.3766 | 157.1361 | 179.5127 | 164.6285 | 11.1624 | 124.6 | 3 | 17.7074 | 131.097 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4945 | 27236.745 | 44266.2365 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.5281 | 0:240:120 | 0:00 | 16.362 | 7 | 22.2856 | 134.974 | 157.2596 | 142.4092 | 11.1367 | 124.0267 | 3 | 16.362 | 87.4945 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4948 | 27689.584 | 44266.2418 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.2168 | 0:240:120 | 0:00 | 15.0669 | 7 | 22.395 | 112.5988 | 134.9938 | 120.1016 | 11.1668 | 124.6966 | 3 | 15.0669 | 63.5741 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4951 | 28075.362 | 44266.2462 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.8426 | 0:240:120 | 0:00 | 14.0478 | 7 | 22.312 | 90.4221 | 112.7341 | 97.8719 | 11.1446 | 124.2023 | 3 | 14.0478 | 50.837 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4954 | 28394.45 | 44266.2499 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.474 | 0:240:120 | 0:00 | 13.1436 | 7 | 22.3399 | 68.1402 | 90.4801 | 75.6168 | 11.1462 | 124.2385 | 3 | 13.1436 | 42.2308 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4957 | 28647.244 | 44266.2528 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.3962 | 0:240:120 | 0:00 | 12.004 | 7 | 42.3604 | 25.7705 | 68.1309 | 42.8157 | 19.2922 | 372.189 | 3 | 12.004 | 33.7926 | NP | NP | 0-0-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4960 | 28832.564 | 44266.255 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.0416 | 0:240:120 | 0:00 | 11.3106 | 7 | 23.154 | 22.7515 | 45.9055 | 30.6852 | 11.406 | 130.096 | 3 | 11.3106 | 29.61 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4963 | 28950.092 | 44266.2564 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.9842 | 0:240:120 | 0:00 | 10.4228 | 7 | 1.3562 | 21.2168 | 22.573 | 21.662 | 0.6641 | 0.441 | 3 | 10.4228 | 25.0393 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4966 | 29018.673 | 44266.2571 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.6824 | 0:240:120 | 0:00 | 9.113 | 7 | 2.2674 | 17.7172 | 19.9846 | 18.5527 | 1.0766 | 1.1591 | 3 | 9.113 | 19.5214 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4969 | 29078.031 | 44266.2578 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.573 | 0:240:120 | 0:00 | 7.9731 | 7 | 2.0421 | 14.2475 | 16.2896 | 15.091 | 0.91 | 0.8281 | 3 | 7.9731 | 15.6085 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4972 | 29126.458 | 44266.2584 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.6686 | 0:240:120 | 0:00 | 6.9821 | 7 | 1.6188 | 10.9555 | 12.5743 | 11.5089 | 0.7985 | 0.6377 | 3 | 6.9821 | 12.7162 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4975 | 29164.954 | 44266.2588 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.8216 | 0:240:120 | 0:00 | 6.1743 | 7 | 0.5385 | 9.725 | 10.2635 | 9.8967 | 0.2558 | 0.0654 | 3 | 6.1743 | 10.6406 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4978 | 29197.757 | 44266.2592 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.3662 | 0:240:120 | 0:00 | 5.4143 | 7 | 0.7228 | 8.0929 | 8.8157 | 8.3332 | 0.3583 | 0.1283 | 3 | 5.4143 | 8.8819 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4981 | 29226.09 | 44266.2595 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.4767 | 0:240:120 | 0:00 | 4.9012 | 7 | 0.2677 | 7.0744 | 7.3421 | 7.1599 | 0.1264 | 0.016 | 3 | 4.9012 | 7.7872 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4984 | 29250.322 | 44266.2598 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.168 | 0:240:120 | 0:00 | 4.3607 | 7 | 0.2541 | 6.2193 | 6.4734 | 6.3221 | 0.113 | 0.0128 | 3 | 4.3607 | 6.7062 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4987 | 29272.254 | 44266.2601 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.5809 | 0:240:120 | 0:00 | 3.959 | 7 | 0.3549 | 5.4571 | 5.812 | 5.5755 | 0.1744 | 0.0304 | 3 | 3.959 | 5.9466 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4990 | 29292.222 | 44266.2603 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.2462 | 0:240:120 | 0:00 | 3.5849 | 7 | 0.1912 | 4.8928 | 5.084 | 4.9571 | 0.0936 | 0.0088 | 3 | 3.5849 | 5.2703 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4993 | 29310.074 | 44266.2605 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.1821 | 0:240:120 | 0:00 | 3.2385 | 7 | 0.2375 | 4.2976 | 4.5351 | 4.3976 | 0.106 | 0.0112 | 3 | 3.2385 | 4.6694 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4996 | 29326.126 | 44266.2607 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.8075 | 0:240:120 | 0:00 | 2.8838 | 7 | 0.1356 | 3.8148 | 3.9504 | 3.8594 | 0.0653 | 0.0043 | 3 | 2.8838 | 4.0774 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4999 | 29340.713 | 44266.2609 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.6732 | 0:240:120 | 0:00 | 2.5729 | 7 | 0.1546 | 3.3405 | 3.4951 | 3.3917 | 0.0756 | 0.0057 | 3 | 2.5729 | 3.5772 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5002 | 29354.003 | 44266.261 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 108.1202 | 0:240:120 | 0:00 | 2.2799 | 7 | 0.1132 | 2.9256 | 3.0388 | 2.9642 | 0.0555 | 0.0031 | 3 | 2.2799 | 3.1207 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5005 | 29365.915 | 44266.2612 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.0965 | 0:240:120 | 0:00 | 2.013 | 7 | 0.0825 | 2.5411 | 2.6236 | 2.5758 | 0.0372 | 0.0014 | 3 | 2.013 | 2.7171 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5008 | 29376.956 | 44266.2613 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.7758 | 0:240:120 | 0:00 | 1.7668 | 7 | 0.068 | 2.2202 | 2.2882 | 2.2451 | 0.0313 | 0.001 | 3 | 1.7668 | 2.3546 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5011 | 29386.917 | 44266.2614 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.4914 | 0:240:120 | 0:00 | 1.5656 | 7 | 0.0596 | 1.9457 | 2.0053 | 1.9662 | 0.0289 | 0.0008 | 3 | 1.5656 | 2.0651 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5014 | 29395.864 | 44266.2615 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.7438 | 0:240:120 | 0:00 | 1.3854 | 7 | 0.0503 | 1.7035 | 1.7538 | 1.7224 | 0.0234 | 0.0005 | 3 | 1.3854 | 1.8107 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5017 | 29404.275 | 44266.2616 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.0358 | 0:240:120 | 0:00 | 1.2359 | 7 | 0.0473 | 1.515 | 1.5623 | 1.5333 | 0.0216 | 0.0005 | 3 | 1.2359 | 1.6033 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5020 | 29412.177 | 44266.2617 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 145.3639 | 0:240:120 | 0:00 | 1.0749 | 7 | 0.0302 | 1.3124 | 1.3426 | 1.3236 | 0.0139 | 0.0002 | 3 | 1.0749 | 1.3832 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5023 | 29419.137 | 44266.2618 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.89 | 0:240:120 | 0:00 | 0.9424 | 7 | 0.0257 | 1.1458 | 1.1715 | 1.1551 | 0.012 | 0.0001 | 3 | 0.9424 | 1.2049 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5026 | 29425.751 | 44266.2619 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 163.8978 | 0:240:120 | 0:00 | 0.8176 | 7 | 0.0251 | 0.9864 | 1.0115 | 0.9961 | 0.0113 | 0.0001 | 3 | 0.8176 | 1.0389 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5029 | 29432.039 | 44266.2619 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 173.5107 | 0:240:120 | 0:00 | 0.7208 | 7 | 0.0167 | 0.8695 | 0.8862 | 0.8757 | 0.0078 | 0.0001 | 3 | 0.7208 | 0.9116 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5032 | 29437.868 | 44266.262 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 188.716 | 0:240:120 | 0:00 | 0.6009 | 7 | 0.0166 | 0.7194 | 0.736 | 0.7259 | 0.0074 | 0.0001 | 3 | 0.6009 | 0.7555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5035 | 29443.223 | 44266.2621 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 211.5036 | 0:240:120 | 0:00 | 0.4721 | 7 | 0.01 | 0.5641 | 0.5741 | 0.568 | 0.0043 | 0 | 3 | 0.4721 | 0.5899 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5038 | 29448.108 | 44266.2621 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 231.1903 | 0:240:120 | 0:00 | 0.3925 | 7 | 0.0078 | 0.4673 | 0.4751 | 0.471 | 0.0032 | 0 | 3 | 0.3925 | 0.4886 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5041 | 29452.67 | 44266.2622 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 253.7227 | 0:240:120 | 0:00 | 0.3246 | 7 | 0.0058 | 0.3872 | 0.393 | 0.3893 | 0.0026 | 0 | 3 | 0.3246 | 0.4027 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5044 | 29457.171 | 44266.2622 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 274.3048 | 0:240:120 | 0:00 | 0.2772 | 7 | 0.0064 | 0.3285 | 0.3349 | 0.3311 | 0.0024 | 0 | 3 | 0.2772 | 0.3432 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5047 | 29461.537 | 44266.2623 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 303.1545 | 0:240:120 | 0:00 | 0.2269 | 7 | 0.0041 | 0.2695 | 0.2736 | 0.271 | 0.0017 | 0 | 3 | 0.2269 | 0.2802 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5050 | 29465.459 | 44266.2623 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 323.8378 | 0:240:120 | 0:00 | 0.1991 | 7 | 0.0043 | 0.2355 | 0.2398 | 0.2376 | 0.0016 | 0 | 3 | 0.1991 | 0.2455 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5053 | 29469.603 | 44266.2624 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 351.1596 | 0:240:120 | 0:00 | 0.1696 | 7 | 0.0038 | 0.2006 | 0.2044 | 0.2023 | 0.0014 | 0 | 3 | 0.1696 | 0.2089 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5056 | 29473.57 | 44266.2624 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 374.7436 | 0:240:120 | 0:00 | 0.1493 | 7 | 0.0025 | 0.1771 | 0.1796 | 0.1782 | 0.0009 | 0 | 3 | 0.1493 | 0.1837 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5059 | 29477.243 | 44266.2625 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 404.7384 | 0:240:120 | 0:00 | 0.1284 | 7 | 0.0023 | 0.1518 | 0.1541 | 0.1527 | 0.0011 | 0 | 3 | 0.1284 | 0.1578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5062 | 29481.031 | 44266.2625 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 437.1345 | 0:240:120 | 0:00 | 0.1105 | 7 | 0.0025 | 0.1306 | 0.1331 | 0.1318 | 0.0009 | 0 | 3 | 0.1105 | 0.1357 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5065 | 29484.657 | 44266.2625 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 473.5423 | 0:240:120 | 0:00 | 0.0946 | 7 | 0.0023 | 0.1119 | 0.1142 | 0.1128 | 0.0008 | 0 | 3 | 0.0946 | 0.1161 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5068 | 29488.291 | 44266.2626 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 512.9828 | 0:240:120 | 0:00 | 0.0811 | 7 | 0.0028 | 0.0954 | 0.0982 | 0.0969 | 0.0009 | 0 | 3 | 0.0811 | 0.0994 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5071 | 29492.04 | 44266.2626 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 547.9815 | 0:240:120 | 0:00 | 0.0714 | 7 | 0.0035 | 0.0841 | 0.0876 | 0.0858 | 0.0011 | 0 | 3 | 0.0714 | 0.0875 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5074 | 29495.584 | 44266.2627 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 600.1875 | 0:240:120 | 0:00 | 0.0599 | 7 | 0.0035 | 0.0699 | 0.0734 | 0.0716 | 0.0011 | 0 | 3 | 0.0599 | 0.0734 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5077 | 29499.317 | 44266.2627 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 641.7774 | 0:240:120 | 0:00 | 0.0526 | 7 | 0.0031 | 0.0612 | 0.0643 | 0.0632 | 0.001 | 0 | 3 | 0.0526 | 0.0645 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5080 | 29502.921 | 44266.2627 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 686.9357 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0026 | 0.0549 | 0.0575 | 0.0564 | 0.0008 | 0 | 3 | 0.0462 | 0.0566 | P | NP | 1-1-0-0-1-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5083 | 29506.646 | 44266.2628 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 753.8861 | 0:240:120 | 0:00 | 0.0387 | 7 | 0.004 | 0.0447 | 0.0487 | 0.0471 | 0.0016 | 0 | 3 | 0.0387 | 0.0487 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5086 | 29510.049 | 44266.2628 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 830.6771 | 0:240:120 | 0:00 | 0.0321 | 7 | 0.0032 | 0.0375 | 0.0407 | 0.0393 | 0.0013 | 0 | 3 | 0.0321 | 0.0421 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5089 | 29513.689 | 44266.2629 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 898.683 | 0:240:120 | 0:00 | 0.0276 | 7 | 0.0028 | 0.033 | 0.0358 | 0.0343 | 0.0009 | 0 | 3 | 0.0276 | 0.0376 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5092 | 29517.186 | 44266.2629 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 962.882 | 0:240:120 | 0:00 | 0.0242 | 7 | 0.0028 | 0.0287 | 0.0315 | 0.0306 | 0.001 | 0 | 3 | 0.0242 | 0.0342 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5095 | 29520.601 | 44266.263 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1042.03 | 0:240:120 | 0:00 | 0.0208 | 7 | 0.0022 | 0.0249 | 0.0271 | 0.0266 | 0.0008 | 0 | 3 | 0.0208 | 0.0308 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5098 | 29523.803 | 44266.263 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1120.94 | 0:240:120 | 0:00 | 0.0181 | 7 | 0.0029 | 0.0221 | 0.025 | 0.024 | 0.0011 | 0 | 3 | 0.0181 | 0.0281 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5101 | 29527.27 | 44266.263 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1197.42 | 0:240:120 | 0:00 | 0.016 | 7 | 0.0028 | 0.02 | 0.0228 | 0.0219 | 0.0011 | 0 | 3 | 0.016 | 0.026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5104 | 29530.754 | 44266.2631 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1277.84 | 0:240:120 | 0:00 | 0.0141 | 7 | 0.0041 | 0.0183 | 0.0224 | 0.0205 | 0.0016 | 0 | 3 | 0.0141 | 0.0241 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5107 | 29534.305 | 44266.2631 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1343.36 | 0:240:120 | 0:00 | 0.0128 | 7 | 0.0025 | 0.0177 | 0.0202 | 0.0192 | 0.0011 | 0 | 3 | 0.0128 | 0.0228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5110 | 29537.693 | 44266.2632 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1396.78 | 0:240:120 | 0:00 | 0.0119 | 7 | 0.0021 | 0.0174 | 0.0195 | 0.0182 | 0.0008 | 0 | 3 | 0.0119 | 0.0219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5113 | 29541.057 | 44266.2632 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1436.45 | 0:240:120 | 0:00 | 0.0113 | 7 | 0.0017 | 0.017 | 0.0187 | 0.0179 | 0.0005 | 0 | 3 | 0.0113 | 0.0213 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5116 | 29544.631 | 44266.2632 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1462.54 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0013 | 0.0164 | 0.0177 | 0.0173 | 0.0005 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5119 | 29548.21 | 44266.2633 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1535.0867 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0019 | 0.0155 | 0.0174 | 0.0166 | 0.0006 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-1-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
5122 | 29551.476 | 44266.2633 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1726.9725 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0044 | 0.0123 | 0.0167 | 0.0144 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5125 | 29554.945 | 44266.2634 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1918.8583 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0052 | 0.0109 | 0.0161 | 0.0137 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5128 | 29558.402 | 44266.2634 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2149.1213 | 0:240:120 | 0:00 | 0.0052 | 7 | 0.0046 | 0.0105 | 0.0151 | 0.0129 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5131 | 29562.107 | 44266.2634 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2925.1076 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0061 | 0.0089 | 0.015 | 0.0116 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5134 | 29744.419 | 44266.2655 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.2 | 0:240:120 | 0:00 | 17.0558 | 7 | 43.0382 | 135.3964 | 178.4346 | 153.2132 | 19.3595 | 374.7897 | 3 | 17.0558 | 106.4506 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5137 | 30257.979 | 44266.2715 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.9 | 0:240:120 | 0:00 | 15.6377 | 7 | 40.9268 | 112.8495 | 153.7763 | 127.6655 | 19.5779 | 383.2931 | 3 | 15.6377 | 72.7459 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5140 | 30702.752 | 44266.2766 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.5 | 0:240:120 | 0:00 | 14.5891 | 7 | 42.8619 | 91.39 | 134.2519 | 107.693 | 20.0429 | 401.7178 | 3 | 14.5891 | 57.1136 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5143 | 31084.291 | 44266.2811 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.2 | 0:240:120 | 0:00 | 13.5222 | 7 | 41.7528 | 68.2553 | 110.0081 | 83.0964 | 20.1813 | 407.2843 | 3 | 13.5222 | 45.5879 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5146 | 31390.846 | 44266.2846 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.9 | 0:240:120 | 0:00 | 12.5931 | 7 | 37.4688 | 45.9453 | 83.4141 | 58.7409 | 18.3551 | 336.9092 | 3 | 12.5931 | 37.8756 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5149 | 31607.861 | 44266.2871 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.7 | 0:240:120 | 0:00 | 11.668 | 7 | 23.0854 | 23.6827 | 46.7681 | 31.3152 | 11.4396 | 130.8636 | 3 | 11.668 | 31.69 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5152 | 31728.051 | 44266.2885 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.5 | 0:240:120 | 0:00 | 10.8621 | 7 | 1.2531 | 22.4302 | 23.6833 | 22.8566 | 0.62 | 0.3844 | 3 | 10.8621 | 27.2026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5155 | 31799.863 | 44266.2893 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.8 | 0:240:120 | 0:00 | 9.753 | 7 | 1.2495 | 19.9716 | 21.2211 | 20.3906 | 0.6216 | 0.3864 | 3 | 9.753 | 22.06 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5158 | 31863.489 | 44266.2901 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.6 | 0:240:120 | 0:00 | 8.5248 | 7 | 1.499 | 16.2873 | 17.7863 | 16.7717 | 0.7246 | 0.525 | 3 | 8.5248 | 17.4147 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5161 | 31915.952 | 44266.2907 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.6 | 0:240:120 | 0:00 | 7.4575 | 7 | 1.3172 | 12.5901 | 13.9073 | 13.0288 | 0.6553 | 0.4294 | 3 | 7.4575 | 14.0518 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5164 | 31957.894 | 44266.2912 | Vista Speed | E | 30E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.7 | 0:240:120 | 0:00 | 6.5727 | 7 | 0.471 | 10.4836 | 10.9546 | 10.6653 | 0.2167 | 0.047 | 3 | 6.5727 | 11.6358 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5167 | 32258.096 | 44266.2946 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88 | 0:240:120 | 0:00 | 26.1905 | 7 | 24.7466 | 248.9301 | 273.6767 | 257.1808 | 12.3693 | 153 | 3 | 26.1905 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5170 | 33057.566 | 44266.3039 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.86 | 0:240:120 | 0:00 | 23.5279 | 7 | 24.7631 | 224.1696 | 248.9327 | 232.4255 | 12.3799 | 153.2619 | 3 | 23.5279 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5173 | 33782.793 | 44266.3123 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.7531 | 0:240:120 | 0:00 | 21.261 | 7 | 24.7539 | 199.4226 | 224.1765 | 207.6747 | 12.3748 | 153.1361 | 3 | 21.261 | 281.4942 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5176 | 34433.703 | 44266.3198 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.7399 | 0:240:120 | 0:00 | 19.1959 | 7 | 25.8011 | 173.6271 | 199.4282 | 182.6204 | 12.6083 | 158.97 | 3 | 19.1959 | 130.7006 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5179 | 34988.55 | 44266.3262 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.0419 | 0:240:120 | 0:00 | 16.9907 | 7 | 27.9889 | 125.1862 | 153.1751 | 134.4932 | 13.8886 | 192.8919 | 3 | 16.9907 | 76.175 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5182 | 35423.109 | 44266.3313 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.06 | 0:240:120 | 0:00 | 15.5741 | 7 | 24.7829 | 100.431 | 125.2139 | 108.6926 | 12.3848 | 153.3831 | 3 | 15.5741 | 57.2607 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5185 | 35777.638 | 44266.3354 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.9013 | 0:240:120 | 0:00 | 14.5608 | 7 | 24.8136 | 75.687 | 100.5006 | 83.9575 | 12.3986 | 153.7249 | 3 | 14.5608 | 47.4307 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5188 | 36057.643 | 44266.3386 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.0348 | 0:240:120 | 0:00 | 13.3758 | 7 | 25.8372 | 49.8559 | 75.6931 | 58.8887 | 12.6089 | 158.9832 | 3 | 13.3758 | 38.4443 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5191 | 36263.803 | 44266.341 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.7982 | 0:240:120 | 0:00 | 12.6742 | 7 | 24.7509 | 26.1966 | 50.9475 | 34.4477 | 12.3743 | 153.1225 | 3 | 12.6742 | 34.0553 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5194 | 36395.027 | 44266.3425 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.0517 | 0:240:120 | 0:00 | 11.6594 | 7 | 2.6684 | 23.5183 | 26.1867 | 24.7054 | 1.1712 | 1.3717 | 3 | 11.6594 | 28.6315 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5197 | 36474.504 | 44266.3434 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.1252 | 0:240:120 | 0:00 | 10.9027 | 7 | 1.9064 | 22.091 | 23.9974 | 22.7232 | 0.9382 | 0.8802 | 3 | 10.9027 | 25.1586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5200 | 36548.13 | 44266.3443 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.5085 | 0:240:120 | 0:00 | 10.0515 | 7 | 1.9933 | 20.0978 | 22.0911 | 20.9883 | 0.857 | 0.7344 | 3 | 10.0515 | 21.7207 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5203 | 36613.397 | 44266.345 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.0276 | 0:240:120 | 0:00 | 8.7788 | 7 | 1.4137 | 16.5702 | 17.9839 | 17.0596 | 0.6929 | 0.4801 | 3 | 8.7788 | 17.3245 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5206 | 36667.878 | 44266.3457 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.9848 | 0:240:120 | 0:00 | 7.9767 | 7 | 2.6823 | 12.5632 | 15.2455 | 13.7531 | 1.18 | 1.3925 | 3 | 7.9767 | 14.9254 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5209 | 36713.964 | 44266.3462 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.8734 | 0:240:120 | 0:00 | 7.3194 | 7 | 0.8568 | 11.6015 | 12.4583 | 11.918 | 0.4054 | 0.1644 | 3 | 7.3194 | 13.1371 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5212 | 36753.543 | 44266.3467 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 108.0122 | 0:240:120 | 0:00 | 6.6836 | 7 | 0.4574 | 10.692 | 11.1494 | 10.8457 | 0.2273 | 0.0516 | 3 | 6.6836 | 11.5411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5215 | 36789.401 | 44266.3471 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.0836 | 0:240:120 | 0:00 | 6.1556 | 7 | 0.8973 | 9.3447 | 10.242 | 9.7618 | 0.3886 | 0.151 | 3 | 6.1556 | 10.3047 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5218 | 36821.865 | 44266.3475 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.6444 | 0:240:120 | 0:00 | 5.5973 | 7 | 0.8693 | 8.0145 | 8.8838 | 8.4143 | 0.3764 | 0.1417 | 3 | 5.5973 | 9.0771 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5221 | 36850.844 | 44266.3478 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.3472 | 0:240:120 | 0:00 | 5.2732 | 7 | 0.4175 | 7.5596 | 7.9771 | 7.7628 | 0.1778 | 0.0316 | 3 | 5.2732 | 8.399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5224 | 36877.437 | 44266.3481 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.2424 | 0:240:120 | 0:00 | 4.7919 | 7 | 0.4378 | 6.8542 | 7.292 | 7.001 | 0.2142 | 0.0459 | 3 | 4.7919 | 7.4354 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5227 | 36901.976 | 44266.3484 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.7306 | 0:240:120 | 0:00 | 4.4358 | 7 | 0.4481 | 6.1836 | 6.6317 | 6.349 | 0.2133 | 0.0455 | 3 | 4.4358 | 6.7541 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5230 | 36924.267 | 44266.3486 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 122.3937 | 0:240:120 | 0:00 | 4.1025 | 7 | 0.3573 | 5.6014 | 5.9587 | 5.7342 | 0.1691 | 0.0286 | 3 | 4.1025 | 6.1388 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5233 | 36944.628 | 44266.3489 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.2405 | 0:240:120 | 0:00 | 3.791 | 7 | 0.2065 | 5.2006 | 5.4071 | 5.2694 | 0.1009 | 0.0102 | 3 | 3.791 | 5.5829 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5236 | 36963.729 | 44266.3491 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.7968 | 0:240:120 | 0:00 | 3.4548 | 7 | 0.165 | 4.6681 | 4.8331 | 4.7223 | 0.079 | 0.0062 | 3 | 3.4548 | 5.0023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5239 | 36980.872 | 44266.3493 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.3221 | 0:240:120 | 0:00 | 3.0234 | 7 | 0.1598 | 3.983 | 4.1428 | 4.062 | 0.0657 | 0.0043 | 3 | 3.0234 | 4.2852 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5242 | 36995.89 | 44266.3495 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 139.6637 | 0:240:120 | 0:00 | 2.6858 | 7 | 0.1477 | 3.4702 | 3.6179 | 3.532 | 0.0663 | 0.0044 | 3 | 2.6858 | 3.7448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5245 | 37009.681 | 44266.3496 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.7831 | 0:240:120 | 0:00 | 2.4172 | 7 | 0.1138 | 3.1082 | 3.222 | 3.1644 | 0.047 | 0.0022 | 3 | 2.4172 | 3.3272 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5248 | 37022.105 | 44266.3498 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.3909 | 0:240:120 | 0:00 | 2.1705 | 7 | 0.0928 | 2.7752 | 2.868 | 2.8073 | 0.0453 | 0.0021 | 3 | 2.1705 | 2.953 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5251 | 37033.632 | 44266.3499 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 155.2815 | 0:240:120 | 0:00 | 1.9873 | 7 | 0.0908 | 2.5052 | 2.596 | 2.5501 | 0.0385 | 0.0015 | 3 | 1.9873 | 2.6807 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5254 | 37044.489 | 44266.35 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.4911 | 0:240:120 | 0:00 | 1.8184 | 7 | 0.0689 | 2.2842 | 2.3531 | 2.3184 | 0.0292 | 0.0009 | 3 | 1.8184 | 2.4337 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5257 | 37054.776 | 44266.3502 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.2134 | 0:240:120 | 0:00 | 1.6846 | 7 | 0.0716 | 2.1085 | 2.1801 | 2.1342 | 0.0342 | 0.0012 | 3 | 1.6846 | 2.2407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5260 | 37064.617 | 44266.3503 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.9279 | 0:240:120 | 0:00 | 1.5428 | 7 | 0.0533 | 1.9199 | 1.9732 | 1.9465 | 0.0216 | 0.0005 | 3 | 1.5428 | 2.0388 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5263 | 37073.893 | 44266.3504 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176.3091 | 0:240:120 | 0:00 | 1.426 | 7 | 0.0431 | 1.7704 | 1.8135 | 1.7889 | 0.0191 | 0.0004 | 3 | 1.426 | 1.8745 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5266 | 37082.332 | 44266.3505 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.1379 | 0:240:120 | 0:00 | 1.297 | 7 | 0.039 | 1.5986 | 1.6376 | 1.6169 | 0.0164 | 0.0003 | 3 | 1.297 | 1.695 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5269 | 37090.508 | 44266.3506 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 190.4221 | 0:240:120 | 0:00 | 1.1788 | 7 | 0.0362 | 1.4535 | 1.4897 | 1.4667 | 0.017 | 0.0003 | 3 | 1.1788 | 1.5324 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5272 | 37098.079 | 44266.3507 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 198.5896 | 0:240:120 | 0:00 | 1.0654 | 7 | 0.0307 | 1.3116 | 1.3423 | 1.322 | 0.0135 | 0.0002 | 3 | 1.0654 | 1.378 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5275 | 37105.017 | 44266.3507 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.3543 | 0:240:120 | 0:00 | 0.9511 | 7 | 0.0233 | 1.1616 | 1.1849 | 1.1719 | 0.0097 | 0.0001 | 3 | 0.9511 | 1.2238 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5278 | 37111.584 | 44266.3508 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 221.4597 | 0:240:120 | 0:00 | 0.8254 | 7 | 0.0187 | 1.0046 | 1.0233 | 1.0133 | 0.0078 | 0.0001 | 3 | 0.8254 | 1.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5281 | 37118.072 | 44266.3509 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.6839 | 0:240:120 | 0:00 | 0.7231 | 7 | 0.0174 | 0.8759 | 0.8933 | 0.8841 | 0.007 | 0 | 3 | 0.7231 | 0.9212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5284 | 37124.024 | 44266.351 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.9632 | 0:240:120 | 0:00 | 0.6448 | 7 | 0.0125 | 0.7817 | 0.7942 | 0.7875 | 0.0052 | 0 | 3 | 0.6448 | 0.8186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5287 | 37129.451 | 44266.351 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 257.8147 | 0:240:120 | 0:00 | 0.586 | 7 | 0.0123 | 0.71 | 0.7223 | 0.715 | 0.0052 | 0 | 3 | 0.586 | 0.742 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5290 | 37135 | 44266.3511 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 267.2648 | 0:240:120 | 0:00 | 0.5413 | 7 | 0.0108 | 0.6557 | 0.6665 | 0.6595 | 0.0047 | 0 | 3 | 0.5413 | 0.684 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5293 | 37140.389 | 44266.3511 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 278.1724 | 0:240:120 | 0:00 | 0.4959 | 7 | 0.0102 | 0.597 | 0.6072 | 0.6014 | 0.0036 | 0 | 3 | 0.4959 | 0.6255 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5296 | 37145.373 | 44266.3512 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.195 | 0:240:120 | 0:00 | 0.4392 | 7 | 0.0074 | 0.529 | 0.5364 | 0.5323 | 0.003 | 0 | 3 | 0.4392 | 0.5525 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5299 | 37150.591 | 44266.3513 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 305.5888 | 0:240:120 | 0:00 | 0.4047 | 7 | 0.0065 | 0.4877 | 0.4942 | 0.4904 | 0.0027 | 0 | 3 | 0.4047 | 0.5084 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5302 | 37155.336 | 44266.3513 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 320.6148 | 0:240:120 | 0:00 | 0.3652 | 7 | 0.0051 | 0.4399 | 0.445 | 0.4419 | 0.0022 | 0 | 3 | 0.3652 | 0.458 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5305 | 37159.939 | 44266.3514 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 337.3909 | 0:240:120 | 0:00 | 0.3276 | 7 | 0.0066 | 0.3927 | 0.3993 | 0.3955 | 0.0027 | 0 | 3 | 0.3276 | 0.4102 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5308 | 37164.213 | 44266.3514 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 362.9417 | 0:240:120 | 0:00 | 0.2809 | 7 | 0.0052 | 0.3383 | 0.3435 | 0.3401 | 0.0023 | 0 | 3 | 0.2809 | 0.351 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5311 | 37168.529 | 44266.3515 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 390.0369 | 0:240:120 | 0:00 | 0.2415 | 7 | 0.004 | 0.2902 | 0.2942 | 0.292 | 0.0017 | 0 | 3 | 0.2415 | 0.3013 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5314 | 37172.471 | 44266.3515 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 442.4123 | 0:240:120 | 0:00 | 0.1859 | 7 | 0.0048 | 0.222 | 0.2268 | 0.2239 | 0.0019 | 0 | 3 | 0.1859 | 0.2314 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5317 | 37176.343 | 44266.3516 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 485.5301 | 0:240:120 | 0:00 | 0.1535 | 7 | 0.004 | 0.1832 | 0.1872 | 0.1847 | 0.0018 | 0 | 3 | 0.1535 | 0.1907 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5320 | 37179.981 | 44266.3516 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 533.918 | 0:240:120 | 0:00 | 0.1263 | 7 | 0.0039 | 0.1506 | 0.1545 | 0.1523 | 0.0014 | 0 | 3 | 0.1263 | 0.1568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5323 | 37184.102 | 44266.3517 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 583.6149 | 0:240:120 | 0:00 | 0.1053 | 7 | 0.0021 | 0.1263 | 0.1284 | 0.1269 | 0.0008 | 0 | 3 | 0.1053 | 0.1306 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5326 | 37187.767 | 44266.3517 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 642.4198 | 0:240:120 | 0:00 | 0.0866 | 7 | 0.0041 | 0.1029 | 0.107 | 0.1045 | 0.0013 | 0 | 3 | 0.0866 | 0.1074 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5329 | 37191.613 | 44266.3517 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 712.8286 | 0:240:120 | 0:00 | 0.0702 | 7 | 0.0038 | 0.0827 | 0.0865 | 0.0848 | 0.0014 | 0 | 3 | 0.0702 | 0.0869 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5332 | 37195.652 | 44266.3518 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 779.1795 | 0:240:120 | 0:00 | 0.0586 | 7 | 0.003 | 0.0694 | 0.0724 | 0.0713 | 0.0013 | 0 | 3 | 0.0586 | 0.0725 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5335 | 37199.07 | 44266.3518 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 856.8318 | 0:240:120 | 0:00 | 0.0484 | 7 | 0.0032 | 0.0571 | 0.0603 | 0.0591 | 0.0013 | 0 | 3 | 0.0484 | 0.0598 | P | NP | 0-1-0-0-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5338 | 37202.933 | 44266.3519 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 932.8473 | 0:240:120 | 0:00 | 0.0407 | 7 | 0.0028 | 0.0482 | 0.051 | 0.0496 | 0.0011 | 0 | 3 | 0.0407 | 0.0507 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5341 | 37206.557 | 44266.3519 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1019.6769 | 0:240:120 | 0:00 | 0.0341 | 7 | 0.0032 | 0.0401 | 0.0433 | 0.042 | 0.0012 | 0 | 3 | 0.0341 | 0.0441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5344 | 37209.877 | 44266.3519 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1100 | 0:240:120 | 0:00 | 0.0292 | 7 | 0.0025 | 0.0351 | 0.0376 | 0.0369 | 0.0009 | 0 | 3 | 0.0292 | 0.0392 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5347 | 37213.07 | 44266.352 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1185.51 | 0:240:120 | 0:00 | 0.0252 | 7 | 0.0033 | 0.03 | 0.0333 | 0.032 | 0.0011 | 0 | 3 | 0.0252 | 0.0352 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5350 | 37217.208 | 44266.352 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1298.45 | 0:240:120 | 0:00 | 0.021 | 7 | 0.0036 | 0.0253 | 0.0289 | 0.0272 | 0.0014 | 0 | 3 | 0.021 | 0.031 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5353 | 37220.939 | 44266.3521 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1453.79 | 0:240:120 | 0:00 | 0.0167 | 7 | 0.004 | 0.0201 | 0.0241 | 0.0227 | 0.0015 | 0 | 3 | 0.0167 | 0.0267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5356 | 37224.203 | 44266.3521 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1559.2 | 0:240:120 | 0:00 | 0.0145 | 7 | 0.0045 | 0.0182 | 0.0227 | 0.0205 | 0.0016 | 0 | 3 | 0.0145 | 0.0245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5359 | 37227.604 | 44266.3522 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1649.01 | 0:240:120 | 0:00 | 0.013 | 7 | 0.0042 | 0.0171 | 0.0213 | 0.0192 | 0.0015 | 0 | 3 | 0.013 | 0.023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5362 | 37231.063 | 44266.3522 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1724.91 | 0:240:120 | 0:00 | 0.0119 | 7 | 0.0021 | 0.0179 | 0.02 | 0.0186 | 0.0007 | 0 | 3 | 0.0119 | 0.0219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5365 | 37234.394 | 44266.3522 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1798.89 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0015 | 0.017 | 0.0185 | 0.0175 | 0.0006 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5368 | 37237.923 | 44266.3523 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1849.98 | 0:240:120 | 0:00 | 0.0103 | 7 | 0.0019 | 0.0165 | 0.0184 | 0.0174 | 0.0007 | 0 | 3 | 0.0103 | 0.0203 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5371 | 37241.237 | 44266.3523 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1877.93 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0021 | 0.0156 | 0.0177 | 0.0166 | 0.0006 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
5374 | 37244.61 | 44266.3524 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1971.0813 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.0024 | 0.0146 | 0.017 | 0.0162 | 0.0009 | 0 | 3 | 0.0091 | 0.016 | NP | NP | 1-0-0-1-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
5377 | 37247.848 | 44266.3524 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2217.4665 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0052 | 0.0118 | 0.017 | 0.0143 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5380 | 37251.374 | 44266.3524 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2463.8517 | 0:240:120 | 0:00 | 0.0058 | 7 | 0.0053 | 0.0111 | 0.0164 | 0.0135 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5383 | 37254.659 | 44266.3525 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2759.5139 | 0:240:120 | 0:00 | 0.0046 | 7 | 0.0046 | 0.0106 | 0.0152 | 0.0131 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5386 | 37258.708 | 44266.3525 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3755.8955 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0028 | 0.0094 | 0.0122 | 0.0106 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5389 | 37436.67 | 44266.3546 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.4 | 0:240:120 | 0:00 | 18.0147 | 7 | 24.7542 | 149.9302 | 174.6844 | 158.1827 | 12.3751 | 153.1423 | 3 | 18.0147 | 95.9893 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5392 | 37939.203 | 44266.3604 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.6 | 0:240:120 | 0:00 | 16.1857 | 7 | 38.5576 | 111.3635 | 149.9211 | 128.2772 | 16.7707 | 281.257 | 3 | 16.1857 | 64.5214 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5395 | 38367.281 | 44266.3653 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.5 | 0:240:120 | 0:00 | 15.0283 | 7 | 43.8353 | 81.3268 | 125.1621 | 100.8096 | 18.9374 | 358.6239 | 3 | 15.0283 | 51.6718 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5398 | 38718.645 | 44266.3694 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.5 | 0:240:120 | 0:00 | 13.9117 | 7 | 46.9889 | 50.9864 | 97.9753 | 67.7933 | 22.3244 | 498.3788 | 3 | 13.9117 | 42.2314 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5401 | 38986.942 | 44266.3725 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.4 | 0:240:120 | 0:00 | 13.0314 | 7 | 44.9526 | 26.2093 | 71.1619 | 41.6532 | 21.6868 | 470.3186 | 3 | 13.0314 | 36.2162 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5404 | 39161.729 | 44266.3745 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.4 | 0:240:120 | 0:00 | 12.1675 | 7 | 5.3704 | 24.8298 | 30.2002 | 26.4794 | 2.487 | 6.1853 | 3 | 12.1675 | 31.2251 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5407 | 39248.704 | 44266.3755 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.6 | 0:240:120 | 0:00 | 11.2613 | 7 | 1.3778 | 23.453 | 24.8308 | 23.9159 | 0.6858 | 0.4704 | 3 | 11.2613 | 26.7505 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5410 | 39324.992 | 44266.3764 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.8 | 0:240:120 | 0:00 | 10.4717 | 7 | 2.7134 | 20.736 | 23.4494 | 21.8207 | 1.2354 | 1.5262 | 3 | 10.4717 | 23.3613 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5413 | 39395.018 | 44266.3772 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.8 | 0:240:120 | 0:00 | 9.3601 | 7 | 1.6809 | 17.9833 | 19.6642 | 18.5229 | 0.8089 | 0.6543 | 3 | 9.3601 | 19.2337 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5416 | 39453.857 | 44266.3779 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103 | 0:240:120 | 0:00 | 8.363 | 7 | 2.1038 | 14.5111 | 16.6149 | 15.4816 | 0.886 | 0.7851 | 3 | 8.363 | 16.0489 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5419 | 39504.158 | 44266.3785 | Vista Speed | E | 40E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.9 | 0:240:120 | 0:00 | 7.6455 | 7 | 1.8177 | 12.0569 | 13.8746 | 12.7167 | 0.8696 | 0.7561 | 3 | 7.6455 | 14.0058 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5422 | 39809.919 | 44266.382 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110 | 0:240:120 | 0:00 | 26.1905 | 7 | 24.7422 | 248.9312 | 273.6734 | 257.1797 | 12.3692 | 152.9971 | 3 | 26.1905 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5425 | 40634.236 | 44266.3916 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.3036 | 0:240:120 | 0:00 | 25.3821 | 7 | 27.9919 | 245.6817 | 273.6736 | 256.1942 | 13.1698 | 173.4437 | 3 | 25.3821 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5428 | 41433.88 | 44266.4008 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.7458 | 0:240:120 | 0:00 | 24.2865 | 7 | 25.094 | 224.1752 | 249.2692 | 232.7546 | 12.3704 | 153.0273 | 3 | 24.2865 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5431 | 42184.637 | 44266.4095 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.3013 | 0:240:120 | 0:00 | 23.032 | 7 | 24.8266 | 224.1055 | 248.9321 | 232.4053 | 12.3939 | 153.6098 | 3 | 23.032 | 1605.2161 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5434 | 42927.371 | 44266.4181 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.6357 | 0:240:120 | 0:00 | 22.3348 | 7 | 42.1969 | 199.6938 | 241.8907 | 218.2844 | 18.6561 | 348.0487 | 3 | 22.3348 | 581.0949 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5437 | 43638.165 | 44266.4264 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.5322 | 0:240:120 | 0:00 | 20.6496 | 7 | 35.1598 | 189.0001 | 224.1599 | 204.4655 | 15.2908 | 233.8075 | 3 | 20.6496 | 213.6488 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5440 | 44288.979 | 44266.4339 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.0965 | 0:240:120 | 0:00 | 19.7075 | 7 | 24.7507 | 174.6796 | 199.4303 | 182.9303 | 12.3733 | 153.0994 | 3 | 19.7075 | 152.5393 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5443 | 44866.303 | 44266.4406 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.0051 | 0:240:120 | 0:00 | 18.3507 | 7 | 25.449 | 149.9305 | 175.3795 | 158.5204 | 12.5591 | 157.7318 | 3 | 18.3507 | 104.2255 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5446 | 45387.189 | 44266.4466 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.9203 | 0:240:120 | 0:00 | 17.1517 | 7 | 41.8885 | 125.3271 | 167.2156 | 143.6936 | 18.4414 | 340.0839 | 3 | 17.1517 | 78.8636 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5449 | 45850.343 | 44266.452 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.1919 | 0:240:120 | 0:00 | 15.7118 | 7 | 25.3326 | 100.4358 | 125.7684 | 109.0026 | 12.5541 | 157.6065 | 3 | 15.7118 | 58.7951 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5452 | 46206.772 | 44266.4561 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.2424 | 0:240:120 | 0:00 | 14.6832 | 7 | 26.5343 | 75.69 | 102.2243 | 84.5239 | 13.0648 | 170.6903 | 3 | 14.6832 | 48.4974 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5455 | 46490.199 | 44266.4594 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.4205 | 0:240:120 | 0:00 | 13.67 | 7 | 24.9354 | 50.9453 | 75.8807 | 59.2412 | 12.4228 | 154.3269 | 3 | 13.67 | 40.4719 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5458 | 46696.03 | 44266.4617 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.9693 | 0:240:120 | 0:00 | 12.521 | 7 | 24.7601 | 26.1862 | 50.9463 | 34.4456 | 12.3751 | 153.1437 | 3 | 12.521 | 33.1718 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5461 | 46827.006 | 44266.4633 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.418 | 0:240:120 | 0:00 | 11.5977 | 7 | 2.5847 | 23.474 | 26.0587 | 24.6594 | 1.1138 | 1.2406 | 3 | 11.5977 | 28.3317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5464 | 46905.706 | 44266.4642 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.2528 | 0:240:120 | 0:00 | 10.5947 | 7 | 1.4106 | 22.0511 | 23.4617 | 22.5397 | 0.6905 | 0.4768 | 3 | 10.5947 | 23.8621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5467 | 46976.452 | 44266.465 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.9908 | 0:240:120 | 0:00 | 9.7818 | 7 | 1.3788 | 19.3486 | 20.7274 | 19.8099 | 0.6868 | 0.4717 | 3 | 9.7818 | 20.7204 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5470 | 47040.57 | 44266.4657 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.6265 | 0:240:120 | 0:00 | 9.1146 | 7 | 1.8964 | 17.4573 | 19.3537 | 18.3083 | 0.803 | 0.6449 | 3 | 9.1146 | 18.4084 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5473 | 47099.181 | 44266.4664 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.5405 | 0:240:120 | 0:00 | 8.4321 | 7 | 1.3738 | 15.2412 | 16.615 | 15.7009 | 0.6853 | 0.4696 | 3 | 8.4321 | 16.2561 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5476 | 47149.529 | 44266.467 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.6129 | 0:240:120 | 0:00 | 7.7907 | 7 | 1.3725 | 12.5046 | 13.8771 | 12.9629 | 0.6851 | 0.4693 | 3 | 7.7907 | 14.404 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5479 | 47192.528 | 44266.4675 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 132.5874 | 0:240:120 | 0:00 | 7.2565 | 7 | 0.4759 | 11.5997 | 12.0756 | 11.7585 | 0.236 | 0.0557 | 3 | 7.2565 | 12.9738 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5482 | 47231.148 | 44266.4679 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 135.1306 | 0:240:120 | 0:00 | 6.6584 | 7 | 0.4565 | 10.6923 | 11.1488 | 10.8455 | 0.2273 | 0.0517 | 3 | 6.6584 | 11.4803 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5485 | 47266.938 | 44266.4684 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.5847 | 0:240:120 | 0:00 | 6.1593 | 7 | 0.8039 | 9.4396 | 10.2435 | 9.8229 | 0.3427 | 0.1174 | 3 | 6.1593 | 10.3133 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5488 | 47300.167 | 44266.4687 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 139.9442 | 0:240:120 | 0:00 | 5.7385 | 7 | 0.905 | 8.4298 | 9.3348 | 8.8188 | 0.4092 | 0.1674 | 3 | 5.7385 | 9.3803 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5491 | 47330.3 | 44266.4691 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.3433 | 0:240:120 | 0:00 | 5.3598 | 7 | 0.4342 | 7.7505 | 8.1847 | 7.8903 | 0.207 | 0.0429 | 3 | 5.3598 | 8.5778 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5494 | 47357.32 | 44266.4694 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.7831 | 0:240:120 | 0:00 | 5.0173 | 7 | 0.2263 | 7.302 | 7.5283 | 7.3785 | 0.1121 | 0.0126 | 3 | 5.0173 | 7.8804 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5497 | 47382.925 | 44266.4697 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.5606 | 0:240:120 | 0:00 | 4.6713 | 7 | 0.449 | 6.6321 | 7.0811 | 6.8424 | 0.1953 | 0.0381 | 3 | 4.6713 | 7.2017 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5500 | 47406.817 | 44266.47 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.5416 | 0:240:120 | 0:00 | 4.3434 | 7 | 0.3137 | 6.0942 | 6.4079 | 6.2318 | 0.1359 | 0.0185 | 3 | 4.3434 | 6.5814 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5503 | 47428.848 | 44266.4702 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 154.8162 | 0:240:120 | 0:00 | 3.9376 | 7 | 0.1438 | 5.4582 | 5.602 | 5.5113 | 0.0678 | 0.0046 | 3 | 3.9376 | 5.8423 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5506 | 47448.177 | 44266.4704 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.171 | 0:240:120 | 0:00 | 3.5133 | 7 | 0.1353 | 4.8013 | 4.9366 | 4.8472 | 0.0665 | 0.0044 | 3 | 3.5133 | 5.1019 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5509 | 47465.544 | 44266.4706 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.2078 | 0:240:120 | 0:00 | 3.1206 | 7 | 0.174 | 4.1421 | 4.3161 | 4.2049 | 0.0835 | 0.007 | 3 | 3.1206 | 4.444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5512 | 47480.922 | 44266.4708 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 173.5107 | 0:240:120 | 0:00 | 2.7355 | 7 | 0.1661 | 3.5391 | 3.7052 | 3.6216 | 0.0696 | 0.0048 | 3 | 2.7355 | 3.8232 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5515 | 47494.973 | 44266.471 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 181.6793 | 0:240:120 | 0:00 | 2.3905 | 7 | 0.0834 | 3.0969 | 3.1803 | 3.1239 | 0.0385 | 0.0015 | 3 | 2.3905 | 3.2863 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5518 | 47507.275 | 44266.4711 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 189.8512 | 0:240:120 | 0:00 | 2.1119 | 7 | 0.0801 | 2.6987 | 2.7788 | 2.736 | 0.0339 | 0.0011 | 3 | 2.1119 | 2.8653 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5521 | 47518.502 | 44266.4713 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 196.8109 | 0:240:120 | 0:00 | 1.9141 | 7 | 0.0746 | 2.4244 | 2.499 | 2.4494 | 0.0356 | 0.0013 | 3 | 1.9141 | 2.5731 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5524 | 47528.747 | 44266.4714 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 204.6374 | 0:240:120 | 0:00 | 1.7254 | 7 | 0.0388 | 2.1775 | 2.2163 | 2.1919 | 0.018 | 0.0003 | 3 | 1.7254 | 2.2993 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5527 | 47538.777 | 44266.4715 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 212.7763 | 0:240:120 | 0:00 | 1.5592 | 7 | 0.0544 | 1.947 | 2.0014 | 1.9731 | 0.0229 | 0.0005 | 3 | 1.5592 | 2.0621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5530 | 47547.666 | 44266.4716 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.685 | 0:240:120 | 0:00 | 1.3738 | 7 | 0.0442 | 1.7036 | 1.7478 | 1.7256 | 0.018 | 0.0003 | 3 | 1.3738 | 1.8016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5533 | 47555.78 | 44266.4717 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 232.8139 | 0:240:120 | 0:00 | 1.2443 | 7 | 0.0329 | 1.5434 | 1.5763 | 1.5561 | 0.0144 | 0.0002 | 3 | 1.2443 | 1.6222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5536 | 47563.392 | 44266.4718 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 244.7511 | 0:240:120 | 0:00 | 1.1021 | 7 | 0.0286 | 1.3598 | 1.3884 | 1.3701 | 0.0126 | 0.0002 | 3 | 1.1021 | 1.4278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5539 | 47570.762 | 44266.4719 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.7851 | 0:240:120 | 0:00 | 0.9832 | 7 | 0.0206 | 1.2091 | 1.2297 | 1.2165 | 0.0095 | 0.0001 | 3 | 0.9832 | 1.267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5542 | 47577.516 | 44266.4719 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 268.873 | 0:240:120 | 0:00 | 0.8829 | 7 | 0.0125 | 1.0826 | 1.0951 | 1.0875 | 0.0056 | 0 | 3 | 0.8829 | 1.1327 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5545 | 47583.748 | 44266.472 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 284.0761 | 0:240:120 | 0:00 | 0.7779 | 7 | 0.0117 | 0.9494 | 0.9611 | 0.9537 | 0.0049 | 0 | 3 | 0.7779 | 0.9934 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5548 | 47589.792 | 44266.4721 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 298.0439 | 0:240:120 | 0:00 | 0.6977 | 7 | 0.0138 | 0.8477 | 0.8615 | 0.8542 | 0.0057 | 0 | 3 | 0.6977 | 0.8878 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5551 | 47595.579 | 44266.4722 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 314.2667 | 0:240:120 | 0:00 | 0.6196 | 7 | 0.0125 | 0.7503 | 0.7628 | 0.7562 | 0.0052 | 0 | 3 | 0.6196 | 0.7857 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5554 | 47601.158 | 44266.4722 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 330.3795 | 0:240:120 | 0:00 | 0.5547 | 7 | 0.0095 | 0.6708 | 0.6803 | 0.6753 | 0.0039 | 0 | 3 | 0.5547 | 0.7014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5557 | 47606.813 | 44266.4723 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 343.8622 | 0:240:120 | 0:00 | 0.5081 | 7 | 0.0089 | 0.615 | 0.6239 | 0.6186 | 0.0038 | 0 | 3 | 0.5081 | 0.6412 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5560 | 47612.166 | 44266.4723 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 361.493 | 0:240:120 | 0:00 | 0.4558 | 7 | 0.0075 | 0.5498 | 0.5573 | 0.5535 | 0.0031 | 0 | 3 | 0.4558 | 0.5738 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5563 | 47617.158 | 44266.4724 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 381.931 | 0:240:120 | 0:00 | 0.4048 | 7 | 0.0074 | 0.4877 | 0.4951 | 0.4905 | 0.0029 | 0 | 3 | 0.4048 | 0.5085 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5566 | 47621.959 | 44266.4725 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 409.6246 | 0:240:120 | 0:00 | 0.3486 | 7 | 0.0069 | 0.4186 | 0.4255 | 0.4217 | 0.0027 | 0 | 3 | 0.3486 | 0.4368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5569 | 47626.265 | 44266.4725 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 457.2546 | 0:240:120 | 0:00 | 0.2763 | 7 | 0.0074 | 0.3311 | 0.3385 | 0.334 | 0.0032 | 0 | 3 | 0.2763 | 0.3451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5572 | 47630.394 | 44266.4726 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 504.3357 | 0:240:120 | 0:00 | 0.2251 | 7 | 0.0055 | 0.2688 | 0.2743 | 0.2716 | 0.0021 | 0 | 3 | 0.2251 | 0.2806 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5575 | 47634.913 | 44266.4726 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 577.808 | 0:240:120 | 0:00 | 0.1698 | 7 | 0.0041 | 0.2026 | 0.2067 | 0.2043 | 0.0017 | 0 | 3 | 0.1698 | 0.2112 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5578 | 47638.582 | 44266.4727 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 667.3007 | 0:240:120 | 0:00 | 0.1264 | 7 | 0.0029 | 0.1509 | 0.1538 | 0.1522 | 0.0011 | 0 | 3 | 0.1264 | 0.1568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5581 | 47642.146 | 44266.4727 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 725.7756 | 0:240:120 | 0:00 | 0.1064 | 7 | 0.0033 | 0.1268 | 0.1301 | 0.1283 | 0.0012 | 0 | 3 | 0.1064 | 0.132 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5584 | 47645.956 | 44266.4727 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 788.5856 | 0:240:120 | 0:00 | 0.0899 | 7 | 0.0027 | 0.1069 | 0.1096 | 0.1082 | 0.001 | 0 | 3 | 0.0899 | 0.1114 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5587 | 47649.533 | 44266.4728 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 840.7047 | 0:240:120 | 0:00 | 0.0789 | 7 | 0.003 | 0.0931 | 0.0961 | 0.0948 | 0.0012 | 0 | 3 | 0.0789 | 0.0978 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5590 | 47653.18 | 44266.4728 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 902.5654 | 0:240:120 | 0:00 | 0.0684 | 7 | 0.0042 | 0.0808 | 0.085 | 0.0825 | 0.0015 | 0 | 3 | 0.0684 | 0.0846 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5593 | 47656.719 | 44266.4729 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 991.5224 | 0:240:120 | 0:00 | 0.0565 | 7 | 0.0027 | 0.0669 | 0.0696 | 0.0687 | 0.001 | 0 | 3 | 0.0565 | 0.0699 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5596 | 47660.291 | 44266.4729 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1049.6805 | 0:240:120 | 0:00 | 0.0504 | 7 | 0.0037 | 0.0593 | 0.063 | 0.0614 | 0.0012 | 0 | 3 | 0.0504 | 0.0623 | P | NP | 1-1-0-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5599 | 47664.29 | 44266.4729 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1117.93 | 0:240:120 | 0:00 | 0.0444 | 7 | 0.0029 | 0.0524 | 0.0553 | 0.0538 | 0.001 | 0 | 3 | 0.0444 | 0.0549 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5602 | 47667.807 | 44266.473 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1181.147 | 0:240:120 | 0:00 | 0.0397 | 7 | 0.003 | 0.0474 | 0.0504 | 0.0491 | 0.001 | 0 | 3 | 0.0397 | 0.0497 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5605 | 47671.175 | 44266.473 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1240.459 | 0:240:120 | 0:00 | 0.036 | 7 | 0.0027 | 0.0429 | 0.0456 | 0.0444 | 0.001 | 0 | 3 | 0.036 | 0.046 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5608 | 47674.982 | 44266.4731 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1335 | 0:240:120 | 0:00 | 0.031 | 7 | 0.0027 | 0.0367 | 0.0394 | 0.0385 | 0.0011 | 0 | 3 | 0.031 | 0.041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5611 | 47678.617 | 44266.4731 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1393.99 | 0:240:120 | 0:00 | 0.0285 | 7 | 0.0042 | 0.0334 | 0.0376 | 0.0354 | 0.0013 | 0 | 3 | 0.0285 | 0.0385 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5614 | 47682.208 | 44266.4732 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1496.56 | 0:240:120 | 0:00 | 0.0247 | 7 | 0.0023 | 0.0296 | 0.0319 | 0.0306 | 0.0008 | 0 | 3 | 0.0247 | 0.0347 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5617 | 47685.766 | 44266.4732 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1576.44 | 0:240:120 | 0:00 | 0.0222 | 7 | 0.0042 | 0.0261 | 0.0303 | 0.0283 | 0.0015 | 0 | 3 | 0.0222 | 0.0322 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5620 | 47689.348 | 44266.4732 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1685.69 | 0:240:120 | 0:00 | 0.0194 | 7 | 0.0028 | 0.024 | 0.0268 | 0.0254 | 0.001 | 0 | 3 | 0.0194 | 0.0294 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5623 | 47692.675 | 44266.4733 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1781 | 0:240:120 | 0:00 | 0.0174 | 7 | 0.0042 | 0.0208 | 0.025 | 0.0233 | 0.0015 | 0 | 3 | 0.0174 | 0.0274 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5626 | 47695.899 | 44266.4733 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1893.02 | 0:240:120 | 0:00 | 0.0154 | 7 | 0.0042 | 0.0187 | 0.0229 | 0.0215 | 0.0014 | 0 | 3 | 0.0154 | 0.0254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5629 | 47699.505 | 44266.4734 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1984.11 | 0:240:120 | 0:00 | 0.014 | 7 | 0.0046 | 0.0183 | 0.0229 | 0.0204 | 0.0015 | 0 | 3 | 0.014 | 0.024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5632 | 47703.339 | 44266.4734 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2060.96 | 0:240:120 | 0:00 | 0.013 | 7 | 0.0042 | 0.0175 | 0.0217 | 0.0196 | 0.0014 | 0 | 3 | 0.013 | 0.023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5635 | 47706.749 | 44266.4734 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2138.65 | 0:240:120 | 0:00 | 0.0121 | 7 | 0.0033 | 0.0175 | 0.0208 | 0.0185 | 0.0014 | 0 | 3 | 0.0121 | 0.0221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5638 | 47710.082 | 44266.4735 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2208.19 | 0:240:120 | 0:00 | 0.0113 | 7 | 0.0016 | 0.0176 | 0.0192 | 0.0182 | 0.0007 | 0 | 3 | 0.0113 | 0.0213 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5641 | 47713.587 | 44266.4735 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2261.83 | 0:240:120 | 0:00 | 0.0108 | 7 | 0.0016 | 0.017 | 0.0186 | 0.0178 | 0.0007 | 0 | 3 | 0.0108 | 0.0208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5644 | 47717 | 44266.4736 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2289.13 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0016 | 0.0164 | 0.018 | 0.0173 | 0.0006 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5647 | 47720.335 | 44266.4736 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2402.6782 | 0:240:120 | 0:00 | 0.0095 | 7 | 0.0029 | 0.0149 | 0.0178 | 0.0165 | 0.001 | 0 | 3 | 0.0095 | 0.016 | NP | NP | 1-0-0-1-1-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
5650 | 47723.67 | 44266.4736 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2703.0129 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0052 | 0.012 | 0.0172 | 0.0143 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5653 | 47727.043 | 44266.4737 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3003.3477 | 0:240:120 | 0:00 | 0.0061 | 7 | 0.0055 | 0.0114 | 0.0169 | 0.0139 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5656 | 47730.292 | 44266.4737 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3363.7494 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0044 | 0.0108 | 0.0152 | 0.0133 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5659 | 47733.53 | 44266.4738 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4578.3032 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0046 | 0.0093 | 0.0139 | 0.0109 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5662 | 47936.587 | 44266.4761 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.6 | 0:240:120 | 0:00 | 18.9331 | 7 | 33.7549 | 165.6698 | 199.4247 | 179.9371 | 15.1019 | 228.0675 | 3 | 18.9331 | 121.4081 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5665 | 48513.178 | 44266.4828 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.5 | 0:240:120 | 0:00 | 17.6835 | 7 | 24.7634 | 149.9179 | 174.6813 | 158.176 | 12.3784 | 153.2258 | 3 | 17.6835 | 88.8096 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5668 | 49015.759 | 44266.4886 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 115.6 | 0:240:120 | 0:00 | 16.3527 | 7 | 24.806 | 125.1277 | 149.9337 | 133.4236 | 12.3815 | 153.3016 | 3 | 16.3527 | 66.7215 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5671 | 49444.12 | 44266.4935 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.7 | 0:240:120 | 0:00 | 15.198 | 7 | 24.8504 | 100.3409 | 125.1913 | 108.6656 | 12.3919 | 153.5581 | 3 | 15.198 | 53.3307 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5674 | 49798.209 | 44266.4976 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.8 | 0:240:120 | 0:00 | 14.1868 | 7 | 25.0166 | 75.4206 | 100.4372 | 83.8969 | 12.4053 | 153.8916 | 3 | 14.1868 | 44.3462 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5677 | 50076.888 | 44266.5009 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.2 | 0:240:120 | 0:00 | 13.0684 | 7 | 47.5196 | 26.9579 | 74.4775 | 46.6553 | 21.7789 | 474.3218 | 3 | 13.0684 | 36.448 | NP | NP | 0-1-1-0-0-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5680 | 50255.067 | 44266.5029 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.7 | 0:240:120 | 0:00 | 12.039 | 7 | 1.3728 | 24.8265 | 26.1993 | 25.2852 | 0.6853 | 0.4696 | 3 | 12.039 | 30.5475 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5683 | 50335.308 | 44266.5039 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 122.3 | 0:240:120 | 0:00 | 11.0948 | 7 | 1.7149 | 23.1151 | 24.83 | 23.8311 | 0.7564 | 0.5721 | 3 | 11.0948 | 25.9998 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5686 | 50410.32 | 44266.5047 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.1 | 0:240:120 | 0:00 | 10.1837 | 7 | 1.3729 | 20.7188 | 22.0917 | 21.1774 | 0.685 | 0.4693 | 3 | 10.1837 | 22.2253 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5689 | 50478.256 | 44266.5055 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.8 | 0:240:120 | 0:00 | 9.441 | 7 | 2.5983 | 17.9854 | 20.5837 | 19.1415 | 1.1388 | 1.2968 | 3 | 9.441 | 19.5121 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5692 | 50540.637 | 44266.5062 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 127.6 | 0:240:120 | 0:00 | 8.7555 | 7 | 1.4066 | 16.5779 | 17.9845 | 17.0647 | 0.6887 | 0.4742 | 3 | 8.7555 | 17.251 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5695 | 50595.119 | 44266.5069 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 129.6 | 0:240:120 | 0:00 | 8.0928 | 7 | 1.3729 | 13.8728 | 15.2457 | 14.3319 | 0.6849 | 0.4691 | 3 | 8.0928 | 15.2571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5698 | 50641.573 | 44266.5074 | Vista Speed | E | 50E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131.6 | 0:240:120 | 0:00 | 7.5151 | 7 | 0.4552 | 12.052 | 12.5072 | 12.2049 | 0.2266 | 0.0514 | 3 | 7.5151 | 13.6543 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5701 | 50944.795 | 44266.5109 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 143 | 0:240:120 | 0:00 | 26.1905 | 7 | 24.7486 | 248.9288 | 273.6774 | 257.1798 | 12.3694 | 153.0025 | 3 | 26.1905 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5704 | 51744.293 | 44266.5202 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.0615 | 0:240:120 | 0:00 | 24.1196 | 7 | 24.7614 | 224.1754 | 248.9368 | 232.7901 | 12.1181 | 146.8473 | 3 | 24.1196 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5707 | 52494.301 | 44266.5289 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.9283 | 0:240:120 | 0:00 | 22.6475 | 7 | 25.9268 | 222.9781 | 248.9049 | 232.0531 | 12.645 | 159.8953 | 3 | 22.6475 | 819.5794 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5710 | 53219.321 | 44266.5372 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 146.2384 | 0:240:120 | 0:00 | 20.7215 | 7 | 24.7716 | 199.4039 | 224.1755 | 207.67 | 12.3785 | 153.2273 | 3 | 20.7215 | 220.056 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5713 | 53870.237 | 44266.5448 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.4132 | 0:240:120 | 0:00 | 19.2417 | 7 | 24.7511 | 174.6774 | 199.4285 | 182.9291 | 12.3739 | 153.1132 | 3 | 19.2417 | 132.4399 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5716 | 54446.975 | 44266.5515 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.5968 | 0:240:120 | 0:00 | 17.9405 | 7 | 24.7535 | 149.9278 | 174.6813 | 158.1802 | 12.375 | 153.1412 | 3 | 17.9405 | 94.3064 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5719 | 54949.454 | 44266.5573 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.5416 | 0:240:120 | 0:00 | 16.1294 | 7 | 25.3544 | 124.5766 | 149.931 | 133.2843 | 12.4862 | 155.9053 | 3 | 16.1294 | 63.8022 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5722 | 55356.144 | 44266.562 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 152.3588 | 0:240:120 | 0:00 | 14.7231 | 7 | 28.2489 | 75.7099 | 103.9588 | 90.7788 | 12.2724 | 150.612 | 3 | 14.7231 | 48.8518 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5725 | 55642.484 | 44266.5653 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 154.198 | 0:240:120 | 0:00 | 13.516 | 7 | 24.7511 | 50.9417 | 75.6928 | 59.1939 | 12.3733 | 153.0977 | 3 | 13.516 | 39.3958 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5728 | 55847.897 | 44266.5677 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 155.9041 | 0:240:120 | 0:00 | 12.5505 | 7 | 24.7522 | 26.1952 | 50.9474 | 34.4471 | 12.374 | 153.1155 | 3 | 12.5505 | 33.3401 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5731 | 55979.361 | 44266.5692 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 157.6289 | 0:240:120 | 0:00 | 11.6964 | 7 | 1.4437 | 24.7552 | 26.1989 | 25.2677 | 0.6982 | 0.4875 | 3 | 11.6964 | 28.8131 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5734 | 56058.771 | 44266.5701 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 159.5308 | 0:240:120 | 0:00 | 10.8712 | 7 | 1.425 | 22.092 | 23.517 | 22.7127 | 0.6246 | 0.3901 | 3 | 10.8712 | 25.0231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5737 | 56131.129 | 44266.5709 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 161.4569 | 0:240:120 | 0:00 | 10.1382 | 7 | 1.373 | 20.7188 | 22.0918 | 21.178 | 0.6851 | 0.4693 | 3 | 10.1382 | 22.0504 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5740 | 56199.255 | 44266.5717 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 163.57 | 0:240:120 | 0:00 | 9.4316 | 7 | 2.4857 | 18.0116 | 20.4973 | 19.2592 | 1.0562 | 1.1156 | 3 | 9.4316 | 19.4796 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5743 | 56261.55 | 44266.5725 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.8756 | 0:240:120 | 0:00 | 8.7567 | 7 | 1.3742 | 16.6099 | 17.9841 | 17.0704 | 0.6849 | 0.4691 | 3 | 8.7567 | 17.2548 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5746 | 56315.89 | 44266.5731 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 168.047 | 0:240:120 | 0:00 | 8.1968 | 7 | 1.4727 | 13.8764 | 15.3491 | 14.5079 | 0.6397 | 0.4092 | 3 | 8.1968 | 15.5585 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5749 | 56362.585 | 44266.5736 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.7563 | 0:240:120 | 0:00 | 7.583 | 7 | 0.9984 | 12.0549 | 13.0533 | 12.4679 | 0.4095 | 0.1677 | 3 | 7.583 | 13.8365 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5752 | 56403.809 | 44266.5741 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 174.0321 | 0:240:120 | 0:00 | 6.9432 | 7 | 0.4578 | 11.1452 | 11.603 | 11.2989 | 0.2273 | 0.0517 | 3 | 6.9432 | 12.178 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5755 | 56440.972 | 44266.5745 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176.4862 | 0:240:120 | 0:00 | 6.524 | 7 | 0.5283 | 10.2436 | 10.7719 | 10.4779 | 0.2276 | 0.0518 | 3 | 6.524 | 11.1593 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5758 | 56475.593 | 44266.5749 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 180.0513 | 0:240:120 | 0:00 | 5.9896 | 7 | 0.4562 | 9.3331 | 9.7893 | 9.4862 | 0.2269 | 0.0515 | 3 | 5.9896 | 9.9317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5761 | 56507.152 | 44266.5753 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.5053 | 0:240:120 | 0:00 | 5.5412 | 7 | 0.6496 | 7.977 | 8.6266 | 8.3006 | 0.2758 | 0.0761 | 3 | 5.5412 | 8.9581 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5764 | 56535.549 | 44266.5756 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 187.3993 | 0:240:120 | 0:00 | 5.102 | 7 | 0.2978 | 7.4559 | 7.7537 | 7.5875 | 0.1263 | 0.0159 | 3 | 5.102 | 8.0504 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5767 | 56561.301 | 44266.5759 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 191.1844 | 0:240:120 | 0:00 | 4.7299 | 7 | 0.2276 | 6.8535 | 7.0811 | 6.9301 | 0.1128 | 0.0127 | 3 | 4.7299 | 7.315 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5770 | 56585.038 | 44266.5762 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 195.6328 | 0:240:120 | 0:00 | 4.3491 | 7 | 0.2263 | 6.1806 | 6.4069 | 6.257 | 0.1121 | 0.0126 | 3 | 4.3491 | 6.592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5773 | 56606.947 | 44266.5765 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 199.9844 | 0:240:120 | 0:00 | 4.0249 | 7 | 0.1352 | 5.6 | 5.7352 | 5.6459 | 0.0663 | 0.0044 | 3 | 4.0249 | 5.9987 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5776 | 56626.927 | 44266.5767 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 205.0477 | 0:240:120 | 0:00 | 3.6966 | 7 | 0.1341 | 5.0685 | 5.2026 | 5.1151 | 0.0656 | 0.0043 | 3 | 3.6966 | 5.4179 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5779 | 56645.302 | 44266.5769 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 209.6083 | 0:240:120 | 0:00 | 3.4381 | 7 | 0.1362 | 4.6688 | 4.805 | 4.7145 | 0.0666 | 0.0044 | 3 | 3.4381 | 4.9738 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5782 | 56662.476 | 44266.5771 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 216.4239 | 0:240:120 | 0:00 | 3.1046 | 7 | 0.0901 | 4.1412 | 4.2313 | 4.1718 | 0.0435 | 0.0019 | 3 | 3.1046 | 4.4178 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5785 | 56677.977 | 44266.5773 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 224.5815 | 0:240:120 | 0:00 | 2.7716 | 7 | 0.1336 | 3.6191 | 3.7527 | 3.6893 | 0.0562 | 0.0032 | 3 | 2.7716 | 3.8804 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5788 | 56693.006 | 44266.5774 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 231.6534 | 0:240:120 | 0:00 | 2.5283 | 7 | 0.0988 | 3.2839 | 3.3827 | 3.3365 | 0.0415 | 0.0017 | 3 | 2.5283 | 3.4987 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5791 | 56705.972 | 44266.5776 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 239.9045 | 0:240:120 | 0:00 | 2.2864 | 7 | 0.1018 | 2.9358 | 3.0376 | 2.9869 | 0.04 | 0.0016 | 3 | 2.2864 | 3.1276 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5794 | 56718.242 | 44266.5777 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.9632 | 0:240:120 | 0:00 | 2.1081 | 7 | 0.0635 | 2.7144 | 2.7779 | 2.7428 | 0.0262 | 0.0007 | 3 | 2.1081 | 2.8598 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5797 | 56729.28 | 44266.5779 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 254.7391 | 0:240:120 | 0:00 | 1.9368 | 7 | 0.0479 | 2.4564 | 2.5043 | 2.4733 | 0.0228 | 0.0005 | 3 | 1.9368 | 2.6064 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5800 | 56739.835 | 44266.578 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 263.2861 | 0:240:120 | 0:00 | 1.7732 | 7 | 0.0363 | 2.2484 | 2.2847 | 2.2612 | 0.0171 | 0.0003 | 3 | 1.7732 | 2.3682 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5803 | 56749.898 | 44266.5781 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 270.7628 | 0:240:120 | 0:00 | 1.6477 | 7 | 0.0301 | 2.0802 | 2.1103 | 2.0913 | 0.0136 | 0.0002 | 3 | 1.6477 | 2.1879 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5806 | 56759.69 | 44266.5782 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 282.3766 | 0:240:120 | 0:00 | 1.4792 | 7 | 0.0426 | 1.8481 | 1.8907 | 1.8675 | 0.0179 | 0.0003 | 3 | 1.4792 | 1.9492 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5809 | 56768.269 | 44266.5783 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 296.5578 | 0:240:120 | 0:00 | 1.3083 | 7 | 0.0395 | 1.6207 | 1.6602 | 1.6415 | 0.0147 | 0.0002 | 3 | 1.3083 | 1.7106 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5812 | 56776.207 | 44266.5784 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 310.2077 | 0:240:120 | 0:00 | 1.1717 | 7 | 0.0203 | 1.4518 | 1.4721 | 1.4596 | 0.0089 | 0.0001 | 3 | 1.1717 | 1.5226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5815 | 56783.696 | 44266.5785 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 327.4194 | 0:240:120 | 0:00 | 1.0293 | 7 | 0.0143 | 1.2703 | 1.2846 | 1.2757 | 0.0066 | 0 | 3 | 1.0293 | 1.3291 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5818 | 56790.45 | 44266.5786 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 347.666 | 0:240:120 | 0:00 | 0.894 | 7 | 0.021 | 1.0939 | 1.1149 | 1.1037 | 0.0089 | 0.0001 | 3 | 0.894 | 1.1474 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5821 | 56797.083 | 44266.5787 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 367.6904 | 0:240:120 | 0:00 | 0.7857 | 7 | 0.0194 | 0.9567 | 0.9761 | 0.966 | 0.008 | 0.0001 | 3 | 0.7857 | 1.0037 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5824 | 56803.091 | 44266.5787 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 389.6475 | 0:240:120 | 0:00 | 0.6889 | 7 | 0.0177 | 0.8343 | 0.852 | 0.8438 | 0.0072 | 0.0001 | 3 | 0.6889 | 0.8762 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5827 | 56808.8 | 44266.5788 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 417.8999 | 0:240:120 | 0:00 | 0.5893 | 7 | 0.0164 | 0.7118 | 0.7282 | 0.7203 | 0.0065 | 0 | 3 | 0.5893 | 0.7462 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5830 | 56813.975 | 44266.5788 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 440.6457 | 0:240:120 | 0:00 | 0.5243 | 7 | 0.0138 | 0.6325 | 0.6463 | 0.6392 | 0.0056 | 0 | 3 | 0.5243 | 0.6621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5833 | 56818.844 | 44266.5789 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 470.7098 | 0:240:120 | 0:00 | 0.4542 | 7 | 0.0104 | 0.5475 | 0.5579 | 0.5526 | 0.0043 | 0 | 3 | 0.4542 | 0.5718 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5836 | 56823.906 | 44266.579 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 489.9191 | 0:240:120 | 0:00 | 0.4166 | 7 | 0.0106 | 0.5005 | 0.5111 | 0.5055 | 0.0044 | 0 | 3 | 0.4166 | 0.5236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5839 | 56828.665 | 44266.579 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 509.4045 | 0:240:120 | 0:00 | 0.3832 | 7 | 0.0115 | 0.46 | 0.4715 | 0.4651 | 0.0045 | 0 | 3 | 0.3832 | 0.4809 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5842 | 56833.11 | 44266.5791 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 531.2549 | 0:240:120 | 0:00 | 0.3503 | 7 | 0.0092 | 0.4193 | 0.4285 | 0.4237 | 0.0034 | 0 | 3 | 0.3503 | 0.439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5845 | 56838.083 | 44266.5791 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 561.8536 | 0:240:120 | 0:00 | 0.3111 | 7 | 0.0075 | 0.3731 | 0.3806 | 0.3764 | 0.0031 | 0 | 3 | 0.3111 | 0.3892 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5848 | 56842.508 | 44266.5792 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 597.1933 | 0:240:120 | 0:00 | 0.2736 | 7 | 0.0068 | 0.3273 | 0.3341 | 0.3307 | 0.0027 | 0 | 3 | 0.2736 | 0.3418 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5851 | 56846.898 | 44266.5792 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 641.7774 | 0:240:120 | 0:00 | 0.2353 | 7 | 0.0065 | 0.2804 | 0.2869 | 0.2837 | 0.0026 | 0 | 3 | 0.2353 | 0.2935 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5854 | 56851.004 | 44266.5793 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 680.7812 | 0:240:120 | 0:00 | 0.2081 | 7 | 0.0059 | 0.2485 | 0.2544 | 0.2513 | 0.0023 | 0 | 3 | 0.2081 | 0.2593 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5857 | 56855.268 | 44266.5793 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 729.4133 | 0:240:120 | 0:00 | 0.1804 | 7 | 0.005 | 0.2152 | 0.2202 | 0.2174 | 0.0019 | 0 | 3 | 0.1804 | 0.2245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5860 | 56859.016 | 44266.5794 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 791.7459 | 0:240:120 | 0:00 | 0.1524 | 7 | 0.0031 | 0.1825 | 0.1856 | 0.1836 | 0.0012 | 0 | 3 | 0.1524 | 0.1894 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5863 | 56862.687 | 44266.5794 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 868.043 | 0:240:120 | 0:00 | 0.1262 | 7 | 0.0032 | 0.151 | 0.1542 | 0.1522 | 0.0014 | 0 | 3 | 0.1262 | 0.1566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5866 | 56866.477 | 44266.5795 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 952.644 | 0:240:120 | 0:00 | 0.1044 | 7 | 0.0035 | 0.1241 | 0.1276 | 0.126 | 0.0011 | 0 | 3 | 0.1044 | 0.1294 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5869 | 56869.983 | 44266.5795 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1093.6112 | 0:240:120 | 0:00 | 0.0788 | 7 | 0.0029 | 0.0932 | 0.0961 | 0.095 | 0.0009 | 0 | 3 | 0.0788 | 0.0977 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5872 | 56873.747 | 44266.5795 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1196.602 | 0:240:120 | 0:00 | 0.0657 | 7 | 0.0032 | 0.0783 | 0.0815 | 0.0797 | 0.0012 | 0 | 3 | 0.0657 | 0.0813 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5875 | 56877.389 | 44266.5796 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1309.286 | 0:240:120 | 0:00 | 0.0548 | 7 | 0.0035 | 0.0645 | 0.068 | 0.0663 | 0.0012 | 0 | 3 | 0.0548 | 0.0678 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5878 | 56881.311 | 44266.5796 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1428.295 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0037 | 0.0532 | 0.0569 | 0.0554 | 0.0013 | 0 | 3 | 0.0459 | 0.0568 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5881 | 56885.087 | 44266.5797 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1559.679 | 0:240:120 | 0:00 | 0.0385 | 7 | 0.0032 | 0.0454 | 0.0486 | 0.047 | 0.001 | 0 | 3 | 0.0385 | 0.0485 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5884 | 56888.591 | 44266.5797 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1750 | 0:240:120 | 0:00 | 0.0305 | 7 | 0.0029 | 0.0367 | 0.0396 | 0.0381 | 0.0011 | 0 | 3 | 0.0305 | 0.0405 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5887 | 56892.098 | 44266.5798 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1935 | 0:240:120 | 0:00 | 0.0249 | 7 | 0.0037 | 0.0297 | 0.0334 | 0.0315 | 0.0011 | 0 | 3 | 0.0249 | 0.0349 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5890 | 56895.925 | 44266.5798 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2125.85 | 0:240:120 | 0:00 | 0.0206 | 7 | 0.004 | 0.0248 | 0.0288 | 0.0266 | 0.0013 | 0 | 3 | 0.0206 | 0.0306 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5893 | 56899.674 | 44266.5798 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2296.01 | 0:240:120 | 0:00 | 0.0177 | 7 | 0.0029 | 0.0224 | 0.0253 | 0.0237 | 0.0011 | 0 | 3 | 0.0177 | 0.0277 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5896 | 56903.166 | 44266.5799 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2464.95 | 0:240:120 | 0:00 | 0.0153 | 7 | 0.0041 | 0.0189 | 0.023 | 0.0213 | 0.0017 | 0 | 3 | 0.0153 | 0.0253 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5899 | 56906.849 | 44266.5799 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2659.59 | 0:240:120 | 0:00 | 0.0132 | 7 | 0.0038 | 0.0182 | 0.022 | 0.0198 | 0.0014 | 0 | 3 | 0.0132 | 0.0232 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5902 | 56910.109 | 44266.58 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2762.6 | 0:240:120 | 0:00 | 0.0122 | 7 | 0.0026 | 0.0176 | 0.0202 | 0.0188 | 0.001 | 0 | 3 | 0.0122 | 0.0222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5905 | 56913.451 | 44266.58 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2875.35 | 0:240:120 | 0:00 | 0.0113 | 7 | 0.0015 | 0.0173 | 0.0188 | 0.0178 | 0.0006 | 0 | 3 | 0.0113 | 0.0213 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5908 | 56916.889 | 44266.58 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2980.74 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0019 | 0.0169 | 0.0188 | 0.0175 | 0.0007 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5911 | 56920.497 | 44266.5801 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3090.01 | 0:240:120 | 0:00 | 0.0098 | 7 | 0.0023 | 0.015 | 0.0173 | 0.0161 | 0.0006 | 0 | 3 | 0.0098 | 0.016 | NP | NP | 0-0-0-1-1-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
5914 | 56923.76 | 44266.5801 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3133.57 | 0:240:120 | 0:00 | 0.0095 | 7 | 0.0013 | 0.0156 | 0.0169 | 0.0164 | 0.0005 | 0 | 3 | 0.0095 | 0.016 | NP | NP | 0-0-0-1-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
5917 | 56927.404 | 44266.5802 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3289.0051 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0032 | 0.0137 | 0.0169 | 0.0156 | 0.001 | 0 | 3 | 0.0086 | 0.016 | P | NP | 1-0-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5920 | 56930.985 | 44266.5802 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3700.1307 | 0:240:120 | 0:00 | 0.0068 | 7 | 0.0052 | 0.0114 | 0.0166 | 0.0139 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5923 | 56934.454 | 44266.5802 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4111.2564 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0052 | 0.0107 | 0.0159 | 0.0134 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5926 | 56938.082 | 44266.5803 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4604.6071 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.0052 | 0.01 | 0.0152 | 0.0127 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5929 | 56941.568 | 44266.5803 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6267.1992 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0054 | 0.0098 | 0.0152 | 0.0111 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5932 | 57131.507 | 44266.5825 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148 | 0:240:120 | 0:00 | 18.5751 | 7 | 38.1376 | 151.2104 | 189.348 | 170.9076 | 16.071 | 258.278 | 3 | 18.5751 | 110.3605 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5935 | 57663.039 | 44266.5887 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 149.6 | 0:240:120 | 0:00 | 16.9612 | 7 | 25.2625 | 125.1899 | 150.4524 | 136.957 | 10.9906 | 120.7923 | 3 | 16.9612 | 75.6965 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5938 | 58092.074 | 44266.5936 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 151.5 | 0:240:120 | 0:00 | 15.3579 | 7 | 24.7572 | 100.4312 | 125.1884 | 108.6856 | 12.3761 | 153.1677 | 3 | 15.3579 | 54.957 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5941 | 58446.196 | 44266.5977 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.3 | 0:240:120 | 0:00 | 14.0814 | 7 | 24.7815 | 75.6587 | 100.4402 | 83.9326 | 12.3794 | 153.249 | 3 | 14.0814 | 43.5216 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5944 | 58716.167 | 44266.6009 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 155.1 | 0:240:120 | 0:00 | 12.9891 | 7 | 40.044 | 26.2431 | 66.2871 | 47.323 | 17.2908 | 298.9707 | 3 | 12.9891 | 35.9523 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
5947 | 58877.806 | 44266.6027 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.8 | 0:240:120 | 0:00 | 12.093 | 7 | 1.3898 | 24.8303 | 26.2201 | 25.3312 | 0.6606 | 0.4364 | 3 | 12.093 | 30.8307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5950 | 58958.296 | 44266.6037 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 158.6 | 0:240:120 | 0:00 | 11.2613 | 7 | 1.3741 | 23.4564 | 24.8305 | 23.9162 | 0.6854 | 0.4698 | 3 | 11.2613 | 26.7505 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5953 | 59034.478 | 44266.6045 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.5 | 0:240:120 | 0:00 | 10.4907 | 7 | 1.5301 | 21.9294 | 23.4595 | 22.5114 | 0.7125 | 0.5077 | 3 | 10.4907 | 23.4379 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5956 | 59105.309 | 44266.6054 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 162.5 | 0:240:120 | 0:00 | 9.7778 | 7 | 1.3701 | 19.3529 | 20.723 | 19.8304 | 0.6694 | 0.4481 | 3 | 9.7778 | 20.7059 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5959 | 59169.067 | 44266.6061 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.7 | 0:240:120 | 0:00 | 9.0895 | 7 | 1.3892 | 17.9642 | 19.3534 | 18.4337 | 0.6887 | 0.4744 | 3 | 9.0895 | 18.3256 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5962 | 59227.729 | 44266.6068 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 167 | 0:240:120 | 0:00 | 8.4585 | 7 | 1.3738 | 15.242 | 16.6158 | 15.7018 | 0.6847 | 0.4688 | 3 | 8.4585 | 16.3354 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5965 | 59278.462 | 44266.6074 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.4 | 0:240:120 | 0:00 | 7.8795 | 7 | 1.5965 | 12.508 | 14.1045 | 13.2383 | 0.6834 | 0.4671 | 3 | 7.8795 | 14.6515 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5968 | 59321.868 | 44266.6079 | Vista Speed | E | 65E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 172.4 | 0:240:120 | 0:00 | 7.2494 | 7 | 0.4553 | 11.6014 | 12.0567 | 11.7604 | 0.2223 | 0.0494 | 3 | 7.2494 | 12.9554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5971 | 59624.256 | 44266.6114 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176 | 0:240:120 | 0:00 | 26.1905 | 7 | 24.7474 | 248.93 | 273.6774 | 257.1806 | 12.37 | 153.0157 | 3 | 26.1905 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5974 | 60423.69 | 44266.6206 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 177.5477 | 0:240:120 | 0:00 | 23.771 | 7 | 24.7631 | 224.1719 | 248.935 | 232.4485 | 12.363 | 152.8442 | 3 | 23.771 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5977 | 61149.143 | 44266.629 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 178.7951 | 0:240:120 | 0:00 | 22.1116 | 7 | 23.4963 | 200.8015 | 224.2978 | 216.3517 | 11.4847 | 131.8991 | 3 | 22.1116 | 479.1934 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5980 | 61824.908 | 44266.6368 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 180.0513 | 0:240:120 | 0:00 | 20.6498 | 7 | 24.7479 | 199.4234 | 224.1713 | 207.6749 | 12.3713 | 153.0501 | 3 | 20.6498 | 213.6696 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5983 | 62475.987 | 44266.6444 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 181.3163 | 0:240:120 | 0:00 | 19.3524 | 7 | 24.7544 | 174.6761 | 199.4305 | 182.9302 | 12.374 | 153.1153 | 3 | 19.3524 | 136.8004 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5986 | 63052.877 | 44266.6511 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 182.7727 | 0:240:120 | 0:00 | 18.0377 | 7 | 24.7535 | 149.9308 | 174.6843 | 158.2095 | 12.3541 | 152.6235 | 3 | 18.0377 | 96.5212 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5989 | 63555.411 | 44266.6569 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 184.7934 | 0:240:120 | 0:00 | 16.4705 | 7 | 24.7493 | 125.1844 | 149.9337 | 133.4367 | 12.3725 | 153.0788 | 3 | 16.4705 | 68.3374 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5992 | 63960.861 | 44266.6616 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 187.3993 | 0:240:120 | 0:00 | 14.7923 | 7 | 19.807 | 83.9994 | 103.8064 | 96.3108 | 8.4129 | 70.7773 | 3 | 14.7923 | 49.4732 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5995 | 64246.99 | 44266.6649 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 189.8512 | 0:240:120 | 0:00 | 13.4821 | 7 | 24.7508 | 50.9408 | 75.6916 | 59.1931 | 12.3735 | 153.1039 | 3 | 13.4821 | 39.1631 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5998 | 64428.45 | 44266.667 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 192.72 | 0:240:120 | 0:00 | 12.2 | 7 | 1.6564 | 24.9917 | 26.6481 | 25.9001 | 0.6764 | 0.4575 | 3 | 12.2 | 31.3991 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6001 | 64509.34 | 44266.6679 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 195.8286 | 0:240:120 | 0:00 | 11.0441 | 7 | 1.3612 | 23.4574 | 24.8186 | 23.9116 | 0.6781 | 0.4599 | 3 | 11.0441 | 25.7755 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6004 | 64584.292 | 44266.6688 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 199.1869 | 0:240:120 | 0:00 | 10.0033 | 7 | 1.373 | 20.7188 | 22.0918 | 21.1779 | 0.6854 | 0.4697 | 3 | 10.0033 | 21.5386 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6007 | 64651.352 | 44266.6696 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 202.8037 | 0:240:120 | 0:00 | 9.0667 | 7 | 1.3657 | 17.9794 | 19.3451 | 18.4356 | 0.6792 | 0.4614 | 3 | 9.0667 | 18.2507 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6010 | 64709.277 | 44266.6702 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 206.4876 | 0:240:120 | 0:00 | 8.2643 | 7 | 0.8829 | 15.0303 | 15.9132 | 15.3965 | 0.38 | 0.1444 | 3 | 8.2643 | 15.7564 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6013 | 64757.125 | 44266.6708 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 210.87 | 0:240:120 | 0:00 | 7.4631 | 7 | 0.4551 | 12.0517 | 12.5068 | 12.2046 | 0.2265 | 0.0513 | 3 | 7.4631 | 13.5156 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6016 | 64796.545 | 44266.6712 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 215.5604 | 0:240:120 | 0:00 | 6.7477 | 7 | 0.455 | 10.6948 | 11.1498 | 10.9812 | 0.2128 | 0.0453 | 3 | 6.7477 | 11.6966 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6019 | 64832.318 | 44266.6717 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 219.9153 | 0:240:120 | 0:00 | 6.1855 | 7 | 0.4573 | 9.7869 | 10.2442 | 9.94 | 0.2273 | 0.0517 | 3 | 6.1855 | 10.3729 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6022 | 64864.931 | 44266.672 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 224.1338 | 0:240:120 | 0:00 | 5.7152 | 7 | 0.4558 | 8.4299 | 8.8857 | 8.7394 | 0.2128 | 0.0453 | 3 | 5.7152 | 9.33 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6025 | 64894.202 | 44266.6724 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 228.4326 | 0:240:120 | 0:00 | 5.2969 | 7 | 0.2282 | 7.75 | 7.9782 | 7.827 | 0.1125 | 0.0127 | 3 | 5.2969 | 8.4478 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6028 | 64920.585 | 44266.6727 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 232.8139 | 0:240:120 | 0:00 | 4.9227 | 7 | 0.236 | 7.0881 | 7.3241 | 7.2381 | 0.1043 | 0.0109 | 3 | 4.9227 | 7.6924 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6031 | 64945.474 | 44266.673 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.2799 | 0:240:120 | 0:00 | 4.5861 | 7 | 0.2265 | 6.6297 | 6.8562 | 6.7056 | 0.1122 | 0.0126 | 3 | 4.5861 | 7.0384 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6034 | 64968.321 | 44266.6732 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 243.287 | 0:240:120 | 0:00 | 4.1919 | 7 | 0.2251 | 5.7391 | 5.9642 | 5.8915 | 0.1013 | 0.0103 | 3 | 4.1919 | 6.3018 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6037 | 64988.865 | 44266.6735 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 248.4504 | 0:240:120 | 0:00 | 3.8973 | 7 | 0.0838 | 5.3996 | 5.4834 | 5.4521 | 0.0323 | 0.001 | 3 | 3.8973 | 5.7706 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6040 | 65008.824 | 44266.6737 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 252.9626 | 0:240:120 | 0:00 | 3.6676 | 7 | 0.1344 | 5.0681 | 5.2025 | 5.1132 | 0.0665 | 0.0044 | 3 | 3.6676 | 5.3675 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6043 | 65027.604 | 44266.6739 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 257.8147 | 0:240:120 | 0:00 | 3.4452 | 7 | 0.1349 | 4.6696 | 4.8045 | 4.7157 | 0.0663 | 0.0044 | 3 | 3.4452 | 4.9859 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6046 | 65045.029 | 44266.6741 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 264.077 | 0:240:120 | 0:00 | 3.1901 | 7 | 0.0511 | 4.2796 | 4.3307 | 4.3073 | 0.0208 | 0.0004 | 3 | 3.1901 | 4.5586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6049 | 65061.204 | 44266.6743 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 268.6046 | 0:240:120 | 0:00 | 3.0248 | 7 | 0.0895 | 4.0528 | 4.1423 | 4.0835 | 0.0438 | 0.0019 | 3 | 3.0248 | 4.2874 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6052 | 65076.417 | 44266.6745 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 277.6169 | 0:240:120 | 0:00 | 2.7355 | 7 | 0.089 | 3.6158 | 3.7048 | 3.6459 | 0.0438 | 0.0019 | 3 | 2.7355 | 3.8232 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6055 | 65090.423 | 44266.6746 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 284.3599 | 0:240:120 | 0:00 | 2.5479 | 7 | 0.0639 | 3.3429 | 3.4068 | 3.3652 | 0.0308 | 0.001 | 3 | 2.5479 | 3.5291 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6058 | 65103.276 | 44266.6748 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 295.9649 | 0:240:120 | 0:00 | 2.2711 | 7 | 0.0625 | 2.9128 | 2.9753 | 2.9516 | 0.029 | 0.0008 | 3 | 2.2711 | 3.1046 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6061 | 65115.31 | 44266.6749 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 304.9783 | 0:240:120 | 0:00 | 2.0887 | 7 | 0.0456 | 2.6865 | 2.7321 | 2.7024 | 0.022 | 0.0005 | 3 | 2.0887 | 2.8307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6064 | 65126.453 | 44266.6751 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 318.3785 | 0:240:120 | 0:00 | 1.8584 | 7 | 0.0352 | 2.354 | 2.3892 | 2.3772 | 0.0169 | 0.0003 | 3 | 1.8584 | 2.4918 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6067 | 65136.697 | 44266.6752 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 330.7095 | 0:240:120 | 0:00 | 1.6808 | 7 | 0.0348 | 2.1106 | 2.1454 | 2.1327 | 0.0165 | 0.0003 | 3 | 1.6808 | 2.2353 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6070 | 65146.305 | 44266.6753 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 342.1473 | 0:240:120 | 0:00 | 1.5394 | 7 | 0.0331 | 1.9393 | 1.9724 | 1.9531 | 0.0144 | 0.0002 | 3 | 1.5394 | 2.034 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6073 | 65155.539 | 44266.6754 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 354.6895 | 0:240:120 | 0:00 | 1.4051 | 7 | 0.0448 | 1.7475 | 1.7923 | 1.7692 | 0.0189 | 0.0004 | 3 | 1.4051 | 1.8453 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6076 | 65164.175 | 44266.6755 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 367.323 | 0:240:120 | 0:00 | 1.2879 | 7 | 0.0382 | 1.5984 | 1.6366 | 1.6156 | 0.015 | 0.0002 | 3 | 1.2879 | 1.6824 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6079 | 65172.299 | 44266.6756 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 382.3138 | 0:240:120 | 0:00 | 1.1678 | 7 | 0.0365 | 1.4348 | 1.4713 | 1.4528 | 0.0154 | 0.0002 | 3 | 1.1678 | 1.5174 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6082 | 65179.961 | 44266.6757 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 395.1409 | 0:240:120 | 0:00 | 1.0786 | 7 | 0.0292 | 1.3299 | 1.3591 | 1.3439 | 0.0126 | 0.0002 | 3 | 1.0786 | 1.3959 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6085 | 65187.315 | 44266.6758 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 407.99 | 0:240:120 | 0:00 | 0.9996 | 7 | 0.0179 | 1.2305 | 1.2484 | 1.241 | 0.0078 | 0.0001 | 3 | 0.9996 | 1.289 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6088 | 65194.073 | 44266.6758 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 424.215 | 0:240:120 | 0:00 | 0.9122 | 7 | 0.02 | 1.1161 | 1.1361 | 1.127 | 0.0086 | 0.0001 | 3 | 0.9122 | 1.1717 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6091 | 65200.475 | 44266.6759 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 439.3257 | 0:240:120 | 0:00 | 0.8411 | 7 | 0.0236 | 1.0253 | 1.0489 | 1.038 | 0.0097 | 0.0001 | 3 | 0.8411 | 1.077 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6094 | 65206.595 | 44266.676 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 461.3884 | 0:240:120 | 0:00 | 0.7518 | 7 | 0.0166 | 0.9166 | 0.9332 | 0.9245 | 0.0066 | 0 | 3 | 0.7518 | 0.9589 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6097 | 65212.633 | 44266.6761 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 490.4097 | 0:240:120 | 0:00 | 0.6552 | 7 | 0.0165 | 0.7939 | 0.8104 | 0.8026 | 0.0068 | 0 | 3 | 0.6552 | 0.8321 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6100 | 65218.088 | 44266.6761 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 521.2559 | 0:240:120 | 0:00 | 0.5721 | 7 | 0.0174 | 0.6896 | 0.707 | 0.6986 | 0.0072 | 0.0001 | 3 | 0.5721 | 0.724 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6103 | 65223.498 | 44266.6762 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 551.8304 | 0:240:120 | 0:00 | 0.5048 | 7 | 0.0165 | 0.6059 | 0.6224 | 0.6144 | 0.0068 | 0 | 3 | 0.5048 | 0.6369 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6106 | 65228.642 | 44266.6762 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 587.7146 | 0:240:120 | 0:00 | 0.4403 | 7 | 0.0115 | 0.5296 | 0.5411 | 0.5349 | 0.0045 | 0 | 3 | 0.4403 | 0.5539 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6109 | 65233.558 | 44266.6763 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 616.6127 | 0:240:120 | 0:00 | 0.3971 | 7 | 0.0121 | 0.4766 | 0.4887 | 0.4824 | 0.0047 | 0 | 3 | 0.3971 | 0.4986 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6112 | 65238.193 | 44266.6764 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 650.1748 | 0:240:120 | 0:00 | 0.3545 | 7 | 0.0083 | 0.4248 | 0.4331 | 0.4288 | 0.0033 | 0 | 3 | 0.3545 | 0.4444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6115 | 65242.712 | 44266.6764 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 686.2493 | 0:240:120 | 0:00 | 0.3162 | 7 | 0.0081 | 0.3786 | 0.3867 | 0.3822 | 0.0033 | 0 | 3 | 0.3162 | 0.3957 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6118 | 65247.078 | 44266.6765 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 727.9569 | 0:240:120 | 0:00 | 0.2792 | 7 | 0.0073 | 0.3345 | 0.3418 | 0.3376 | 0.0027 | 0 | 3 | 0.2792 | 0.3488 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6121 | 65251.365 | 44266.6765 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 795.7147 | 0:240:120 | 0:00 | 0.2317 | 7 | 0.0056 | 0.277 | 0.2826 | 0.2797 | 0.0022 | 0 | 3 | 0.2317 | 0.289 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6124 | 65255.501 | 44266.6766 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 886.4647 | 0:240:120 | 0:00 | 0.1852 | 7 | 0.0042 | 0.2215 | 0.2257 | 0.2232 | 0.0018 | 0 | 3 | 0.1852 | 0.2305 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6127 | 65259.383 | 44266.6766 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 977.7372 | 0:240:120 | 0:00 | 0.1513 | 7 | 0.0041 | 0.1813 | 0.1854 | 0.1829 | 0.0017 | 0 | 3 | 0.1513 | 0.1881 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6130 | 65263.291 | 44266.6766 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1097.9947 | 0:240:120 | 0:00 | 0.1193 | 7 | 0.0035 | 0.1419 | 0.1454 | 0.1436 | 0.0014 | 0 | 3 | 0.1193 | 0.1481 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6133 | 65267.171 | 44266.6767 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1212.255 | 0:240:120 | 0:00 | 0.0975 | 7 | 0.0026 | 0.1167 | 0.1193 | 0.1178 | 0.001 | 0 | 3 | 0.0975 | 0.1209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6136 | 65270.725 | 44266.6767 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1315.853 | 0:240:120 | 0:00 | 0.0825 | 7 | 0.0043 | 0.0978 | 0.1021 | 0.0997 | 0.0016 | 0 | 3 | 0.0825 | 0.1023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6139 | 65274.488 | 44266.6768 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1425.446 | 0:240:120 | 0:00 | 0.0702 | 7 | 0.0038 | 0.0831 | 0.0869 | 0.0851 | 0.0013 | 0 | 3 | 0.0702 | 0.0869 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6142 | 65278.166 | 44266.6768 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1565.938 | 0:240:120 | 0:00 | 0.058 | 7 | 0.0025 | 0.0682 | 0.0707 | 0.0701 | 0.0009 | 0 | 3 | 0.058 | 0.0718 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6145 | 65281.805 | 44266.6769 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1671.098 | 0:240:120 | 0:00 | 0.0509 | 7 | 0.0029 | 0.0602 | 0.0631 | 0.0617 | 0.0011 | 0 | 3 | 0.0509 | 0.063 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6148 | 65285.238 | 44266.6769 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1795.86 | 0:240:120 | 0:00 | 0.044 | 7 | 0.0024 | 0.0519 | 0.0543 | 0.0534 | 0.0009 | 0 | 3 | 0.044 | 0.0544 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6151 | 65288.832 | 44266.6769 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1964.985 | 0:240:120 | 0:00 | 0.0367 | 7 | 0.0024 | 0.0434 | 0.0458 | 0.045 | 0.0008 | 0 | 3 | 0.0367 | 0.0467 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6154 | 65292.187 | 44266.677 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2137.168 | 0:240:120 | 0:00 | 0.031 | 7 | 0.0032 | 0.0365 | 0.0397 | 0.0385 | 0.0011 | 0 | 3 | 0.031 | 0.041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6157 | 65295.713 | 44266.677 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2385 | 0:240:120 | 0:00 | 0.0249 | 7 | 0.0019 | 0.0302 | 0.0321 | 0.0314 | 0.0007 | 0 | 3 | 0.0249 | 0.0349 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6160 | 65299.377 | 44266.6771 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2542.56 | 0:240:120 | 0:00 | 0.0219 | 7 | 0.0029 | 0.0261 | 0.029 | 0.028 | 0.0011 | 0 | 3 | 0.0219 | 0.0319 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6163 | 65302.628 | 44266.6771 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2787.58 | 0:240:120 | 0:00 | 0.0182 | 7 | 0.0024 | 0.0226 | 0.025 | 0.0238 | 0.0009 | 0 | 3 | 0.0182 | 0.0282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6166 | 65305.86 | 44266.6771 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3025.79 | 0:240:120 | 0:00 | 0.0154 | 7 | 0.0029 | 0.0197 | 0.0226 | 0.0214 | 0.0013 | 0 | 3 | 0.0154 | 0.0254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6169 | 65309.324 | 44266.6772 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3258.19 | 0:240:120 | 0:00 | 0.0133 | 7 | 0.0029 | 0.0185 | 0.0214 | 0.0198 | 0.001 | 0 | 3 | 0.0133 | 0.0233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6172 | 65312.8 | 44266.6772 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3543.71 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.0018 | 0.0175 | 0.0193 | 0.0182 | 0.0007 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6175 | 65316.383 | 44266.6773 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3800.65 | 0:240:120 | 0:00 | 0.0098 | 7 | 0.0012 | 0.0156 | 0.0168 | 0.0162 | 0.0004 | 0 | 3 | 0.0098 | 0.016 | NP | NP | 0-0-0-0-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
6178 | 65319.813 | 44266.6773 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3916.4 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.003 | 0.0144 | 0.0174 | 0.0159 | 0.001 | 0 | 3 | 0.0092 | 0.016 | P | NP | 1-1-0-1-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6181 | 65323.671 | 44266.6773 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3967.65 | 0:240:120 | 0:00 | 0.009 | 7 | 0.0019 | 0.0146 | 0.0165 | 0.0155 | 0.0007 | 0 | 3 | 0.009 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6184 | 65327.172 | 44266.6774 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4164.4581 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0042 | 0.0122 | 0.0164 | 0.0147 | 0.0015 | 0 | 3 | 0.0081 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6187 | 65330.885 | 44266.6774 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4685.0154 | 0:240:120 | 0:00 | 0.0064 | 7 | 0.0049 | 0.011 | 0.0159 | 0.0136 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6190 | 65334.199 | 44266.6775 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5205.5727 | 0:240:120 | 0:00 | 0.0052 | 7 | 0.0053 | 0.0106 | 0.0159 | 0.0132 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6193 | 65337.563 | 44266.6775 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5830.2414 | 0:240:120 | 0:00 | 0.0041 | 7 | 0.0052 | 0.0103 | 0.0155 | 0.0128 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6196 | 65341.067 | 44266.6775 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7935.375 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0038 | 0.0103 | 0.0141 | 0.0114 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6199 | 65534.639 | 44266.6798 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 182 | 0:240:120 | 0:00 | 18.7135 | 7 | 23.4472 | 171.1892 | 194.6364 | 179.8638 | 9.7221 | 94.5191 | 3 | 18.7135 | 114.4306 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6202 | 66086.319 | 44266.6862 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.8 | 0:240:120 | 0:00 | 17.2076 | 7 | 15.7201 | 146.6614 | 162.3815 | 152.82 | 6.5944 | 43.4861 | 3 | 17.2076 | 79.8287 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6205 | 66538.524 | 44266.6914 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 186.1 | 0:240:120 | 0:00 | 15.5869 | 7 | 24.7531 | 100.439 | 125.1921 | 109.4689 | 11.8386 | 140.1526 | 3 | 15.5869 | 57.4014 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6208 | 66892.728 | 44266.6955 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 188.6 | 0:240:120 | 0:00 | 14.1224 | 7 | 24.7547 | 75.6851 | 100.4398 | 83.9399 | 12.3741 | 153.1184 | 3 | 14.1224 | 43.8402 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6211 | 67147.735 | 44266.6985 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 191.3 | 0:240:120 | 0:00 | 12.805 | 7 | 24.7492 | 26.1985 | 50.9477 | 35.7073 | 11.5497 | 133.3955 | 3 | 12.805 | 34.8299 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6214 | 67278.358 | 44266.7 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.3 | 0:240:120 | 0:00 | 11.5861 | 7 | 0.5968 | 24.6522 | 25.249 | 24.9084 | 0.2396 | 0.0574 | 3 | 11.5861 | 28.2758 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6217 | 67355.614 | 44266.7009 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 197.5 | 0:240:120 | 0:00 | 10.5026 | 7 | 1.3723 | 22.0875 | 23.4598 | 22.546 | 0.6847 | 0.4689 | 3 | 10.5026 | 23.486 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6220 | 67426.355 | 44266.7017 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 201 | 0:240:120 | 0:00 | 9.5129 | 7 | 1.3724 | 19.349 | 20.7214 | 19.8081 | 0.6845 | 0.4685 | 3 | 9.5129 | 19.7619 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6223 | 67489.302 | 44266.7024 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 204.6 | 0:240:120 | 0:00 | 8.6587 | 7 | 1.31 | 16.6111 | 17.9211 | 17.0406 | 0.6413 | 0.4113 | 3 | 8.6587 | 16.9485 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6226 | 67542.326 | 44266.703 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.7 | 0:240:120 | 0:00 | 7.8415 | 7 | 1.3702 | 12.5069 | 13.8771 | 13.1349 | 0.5998 | 0.3597 | 3 | 7.8415 | 14.5453 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6229 | 67585.272 | 44266.7035 | Vista Speed | E | 80E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 213.2 | 0:240:120 | 0:00 | 7.0917 | 7 | 0.4576 | 11.5986 | 12.0562 | 11.7524 | 0.2271 | 0.0516 | 3 | 7.0917 | 12.5513 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6232 | 67887.426 | 44266.707 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 220 | 0:240:120 | 0:00 | 26.1905 | 7 | 24.7438 | 248.9321 | 273.6759 | 257.1805 | 12.3686 | 152.9829 | 3 | 26.1905 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6235 | 68711.633 | 44266.7166 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 220.1353 | 0:240:120 | 0:00 | 26.0061 | 7 | 24.7444 | 248.9308 | 273.6752 | 257.1798 | 12.3697 | 153.0103 | 3 | 26.0061 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6238 | 69511.225 | 44266.7258 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 221.4597 | 0:240:120 | 0:00 | 24.3244 | 7 | 21.0896 | 227.8458 | 248.9354 | 242.0106 | 10.3673 | 107.4802 | 3 | 24.3244 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6241 | 70236.516 | 44266.7342 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.685 | 0:240:120 | 0:00 | 21.9233 | 7 | 22.8692 | 201.3066 | 224.1758 | 216.71 | 11.1736 | 124.8487 | 3 | 21.9233 | 416.4039 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6244 | 70887.513 | 44266.7417 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 225.9334 | 0:240:120 | 0:00 | 19.9169 | 7 | 24.354 | 175.0769 | 199.4309 | 191.2354 | 11.9557 | 142.9392 | 3 | 19.9169 | 163.3041 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6247 | 71464.24 | 44266.7484 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 228.2038 | 0:240:120 | 0:00 | 18.2165 | 7 | 24.7387 | 149.9418 | 174.6805 | 165.5122 | 11.7423 | 137.8824 | 3 | 18.2165 | 100.8088 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6250 | 71966.94 | 44266.7542 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 230.9593 | 0:240:120 | 0:00 | 16.489 | 7 | 24.75 | 125.1834 | 149.9334 | 133.4393 | 12.3694 | 153.001 | 3 | 16.489 | 68.5961 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6253 | 72395.322 | 44266.7592 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 233.5135 | 0:240:120 | 0:00 | 15.1426 | 7 | 24.7569 | 100.4315 | 125.1884 | 108.6862 | 12.3758 | 153.1604 | 3 | 15.1426 | 52.7815 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6256 | 72735.534 | 44266.7631 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 236.0963 | 0:240:120 | 0:00 | 13.9758 | 7 | 13.4647 | 75.6855 | 89.1502 | 79.6597 | 5.9969 | 35.9632 | 3 | 13.9758 | 42.7136 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6259 | 72966.231 | 44266.7658 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 239.1862 | 0:240:120 | 0:00 | 12.7832 | 7 | 24.7479 | 26.1986 | 50.9465 | 41.7774 | 11.7825 | 138.8282 | 3 | 12.7832 | 34.6996 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6262 | 73097.724 | 44266.7673 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 242.3157 | 0:240:120 | 0:00 | 11.7541 | 7 | 1.3721 | 24.8265 | 26.1986 | 25.285 | 0.6849 | 0.469 | 3 | 11.7541 | 29.0979 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6265 | 73176.751 | 44266.7682 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 245.2406 | 0:240:120 | 0:00 | 10.9219 | 7 | 0.2471 | 23.214 | 23.4611 | 23.4267 | 0.0809 | 0.0065 | 3 | 10.9219 | 25.2415 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6268 | 73249.096 | 44266.7691 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 248.2018 | 0:240:120 | 0:00 | 10.1832 | 7 | 1.3696 | 20.7225 | 22.0921 | 21.2365 | 0.65 | 0.4225 | 3 | 10.1832 | 22.2237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6271 | 73315.787 | 44266.7698 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 251.7009 | 0:240:120 | 0:00 | 9.4205 | 7 | 0.0677 | 19.2852 | 19.3529 | 19.3446 | 0.0223 | 0.0005 | 3 | 9.4205 | 19.4411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6274 | 73375.563 | 44266.7705 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 255.2495 | 0:240:120 | 0:00 | 8.7467 | 7 | 1.3741 | 16.6103 | 17.9844 | 17.0703 | 0.6851 | 0.4694 | 3 | 8.7467 | 17.2233 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6277 | 73430.258 | 44266.7712 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 258.8476 | 0:240:120 | 0:00 | 8.1475 | 7 | 1.3706 | 13.8759 | 15.2465 | 14.7214 | 0.6441 | 0.4149 | 3 | 8.1475 | 15.4151 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6280 | 73476.696 | 44266.7717 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 262.4974 | 0:240:120 | 0:00 | 7.6112 | 7 | 0.0067 | 12.5042 | 12.5109 | 12.5069 | 0.002 | 0 | 3 | 7.6112 | 13.9126 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6283 | 73516.679 | 44266.7722 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 268.0678 | 0:240:120 | 0:00 | 6.9051 | 7 | 0.4577 | 11.1458 | 11.6035 | 11.2996 | 0.2273 | 0.0517 | 3 | 6.9051 | 12.0833 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6286 | 73553.634 | 44266.7726 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 272.3919 | 0:240:120 | 0:00 | 6.4332 | 7 | 0.4566 | 10.2401 | 10.6967 | 10.3933 | 0.2267 | 0.0514 | 3 | 6.4332 | 10.9454 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6289 | 73588.363 | 44266.773 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 276.7853 | 0:240:120 | 0:00 | 6.0093 | 7 | 0.4563 | 9.3333 | 9.7896 | 9.4866 | 0.2269 | 0.0515 | 3 | 6.0093 | 9.9754 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6292 | 73620.12 | 44266.7734 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 281.5307 | 0:240:120 | 0:00 | 5.6037 | 7 | 0.4568 | 8.4277 | 8.8845 | 8.5805 | 0.2274 | 0.0517 | 3 | 5.6037 | 9.0908 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6295 | 73649.272 | 44266.7737 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 286.9306 | 0:240:120 | 0:00 | 5.1974 | 7 | 0.2248 | 7.5293 | 7.7541 | 7.6839 | 0.1028 | 0.0106 | 3 | 5.1974 | 8.2438 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6298 | 73675.221 | 44266.774 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 292.435 | 0:240:120 | 0:00 | 4.8332 | 7 | 0.2273 | 7.0777 | 7.305 | 7.1545 | 0.1124 | 0.0126 | 3 | 4.8332 | 7.5163 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6301 | 73699.693 | 44266.7743 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 298.0439 | 0:240:120 | 0:00 | 4.5054 | 7 | 0.225 | 6.4066 | 6.6316 | 6.5554 | 0.1114 | 0.0124 | 3 | 4.5054 | 6.8852 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6304 | 73722.246 | 44266.7745 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 304.9783 | 0:240:120 | 0:00 | 4.15 | 7 | 0.2255 | 5.7339 | 5.9594 | 5.818 | 0.1071 | 0.0115 | 3 | 4.15 | 6.2253 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6307 | 73742.846 | 44266.7748 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 311.1394 | 0:240:120 | 0:00 | 3.8727 | 7 | 0.134 | 5.3352 | 5.4692 | 5.4242 | 0.066 | 0.0044 | 3 | 3.8727 | 5.727 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6310 | 73762.542 | 44266.775 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 316.7912 | 0:240:120 | 0:00 | 3.645 | 7 | 0.12 | 5.0669 | 5.1869 | 5.1026 | 0.0518 | 0.0027 | 3 | 3.645 | 5.3283 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6313 | 73781.073 | 44266.7752 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 322.2219 | 0:240:120 | 0:00 | 3.4468 | 7 | 0.1343 | 4.6692 | 4.8035 | 4.7578 | 0.066 | 0.0044 | 3 | 3.4468 | 4.9887 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6316 | 73798.399 | 44266.7754 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 329.3895 | 0:240:120 | 0:00 | 3.2118 | 7 | 0.0903 | 4.3151 | 4.4054 | 4.3465 | 0.0436 | 0.0019 | 3 | 3.2118 | 4.5945 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6319 | 73814.468 | 44266.7756 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 336.38 | 0:240:120 | 0:00 | 3.0075 | 7 | 0.089 | 4.0538 | 4.1428 | 4.0835 | 0.0435 | 0.0019 | 3 | 3.0075 | 4.2592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6322 | 73830.145 | 44266.7758 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 343.519 | 0:240:120 | 0:00 | 2.8203 | 7 | 0.0888 | 3.704 | 3.7928 | 3.7628 | 0.0435 | 0.0019 | 3 | 2.8203 | 3.958 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6325 | 73844.227 | 44266.776 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 350.108 | 0:240:120 | 0:00 | 2.6642 | 7 | 0.0616 | 3.4678 | 3.5294 | 3.5086 | 0.0302 | 0.0009 | 3 | 2.6642 | 3.7108 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6328 | 73857.712 | 44266.7761 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 359.6901 | 0:240:120 | 0:00 | 2.4615 | 7 | 0.0617 | 3.2218 | 3.2835 | 3.26 | 0.0287 | 0.0008 | 3 | 2.4615 | 3.3953 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6331 | 73870.648 | 44266.7763 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 368.7948 | 0:240:120 | 0:00 | 2.2914 | 7 | 0.0636 | 2.9737 | 3.0373 | 2.9955 | 0.0309 | 0.001 | 3 | 2.2914 | 3.1353 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6334 | 73882.722 | 44266.7764 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 380.0269 | 0:240:120 | 0:00 | 2.1069 | 7 | 0.0893 | 2.6879 | 2.7772 | 2.7328 | 0.0367 | 0.0013 | 3 | 2.1069 | 2.8579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6337 | 73894.083 | 44266.7765 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 393.9573 | 0:240:120 | 0:00 | 1.9097 | 7 | 0.0338 | 2.4247 | 2.4585 | 2.4464 | 0.0161 | 0.0003 | 3 | 1.9097 | 2.5667 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6340 | 73904.465 | 44266.7767 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 407.1738 | 0:240:120 | 0:00 | 1.7489 | 7 | 0.0364 | 2.2151 | 2.2515 | 2.238 | 0.0169 | 0.0003 | 3 | 1.7489 | 2.3332 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6343 | 73914.583 | 44266.7768 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 421.256 | 0:240:120 | 0:00 | 1.6005 | 7 | 0.0551 | 2.0009 | 2.056 | 2.0299 | 0.0238 | 0.0006 | 3 | 1.6005 | 2.1207 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6346 | 73923.85 | 44266.7769 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 439.7657 | 0:240:120 | 0:00 | 1.4342 | 7 | 0.0437 | 1.7915 | 1.8352 | 1.8119 | 0.0172 | 0.0003 | 3 | 1.4342 | 1.886 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6349 | 73932.395 | 44266.777 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 456.3416 | 0:240:120 | 0:00 | 1.3076 | 7 | 0.0439 | 1.6159 | 1.6598 | 1.6372 | 0.0188 | 0.0004 | 3 | 1.3076 | 1.7097 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6352 | 73940.599 | 44266.7771 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 472.5963 | 0:240:120 | 0:00 | 1.1999 | 7 | 0.0354 | 1.4896 | 1.525 | 1.5065 | 0.015 | 0.0002 | 3 | 1.1999 | 1.5613 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6355 | 73948.399 | 44266.7772 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 486.0163 | 0:240:120 | 0:00 | 1.1212 | 7 | 0.0391 | 1.3758 | 1.4149 | 1.3984 | 0.0154 | 0.0002 | 3 | 1.1212 | 1.4538 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6358 | 73955.846 | 44266.7772 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 504.3357 | 0:240:120 | 0:00 | 1.0263 | 7 | 0.0252 | 1.2593 | 1.2845 | 1.2724 | 0.0108 | 0.0001 | 3 | 1.0263 | 1.3251 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6361 | 73962.909 | 44266.7773 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 530.7236 | 0:240:120 | 0:00 | 0.9103 | 7 | 0.0217 | 1.1157 | 1.1374 | 1.1256 | 0.0089 | 0.0001 | 3 | 0.9103 | 1.1693 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6364 | 73969.573 | 44266.7774 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 561.8536 | 0:240:120 | 0:00 | 0.798 | 7 | 0.0282 | 0.967 | 0.9952 | 0.982 | 0.0119 | 0.0001 | 3 | 0.798 | 1.0199 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6367 | 73975.486 | 44266.7775 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 597.7906 | 0:240:120 | 0:00 | 0.6932 | 7 | 0.0198 | 0.841 | 0.8608 | 0.8511 | 0.0078 | 0.0001 | 3 | 0.6932 | 0.8819 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6370 | 73981.116 | 44266.7775 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 626.5578 | 0:240:120 | 0:00 | 0.624 | 7 | 0.015 | 0.7553 | 0.7703 | 0.763 | 0.0058 | 0 | 3 | 0.624 | 0.7914 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6373 | 73986.648 | 44266.7776 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 669.9759 | 0:240:120 | 0:00 | 0.5381 | 7 | 0.018 | 0.6474 | 0.6654 | 0.656 | 0.0073 | 0.0001 | 3 | 0.5381 | 0.6799 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6376 | 73991.959 | 44266.7777 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 702.2158 | 0:240:120 | 0:00 | 0.4855 | 7 | 0.0103 | 0.5862 | 0.5965 | 0.5916 | 0.0044 | 0 | 3 | 0.4855 | 0.6121 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6379 | 73996.885 | 44266.7777 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 740.4375 | 0:240:120 | 0:00 | 0.4329 | 7 | 0.0112 | 0.519 | 0.5302 | 0.5249 | 0.0045 | 0 | 3 | 0.4329 | 0.5444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6382 | 74001.847 | 44266.7778 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 784.6531 | 0:240:120 | 0:00 | 0.3822 | 7 | 0.0084 | 0.4596 | 0.468 | 0.4634 | 0.0035 | 0 | 3 | 0.3822 | 0.4796 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6385 | 74006.406 | 44266.7778 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 832.3403 | 0:240:120 | 0:00 | 0.337 | 7 | 0.0084 | 0.404 | 0.4124 | 0.4077 | 0.0036 | 0 | 3 | 0.337 | 0.4221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6388 | 74010.795 | 44266.7779 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 881.1616 | 0:240:120 | 0:00 | 0.2987 | 7 | 0.0076 | 0.3576 | 0.3652 | 0.3615 | 0.0031 | 0 | 3 | 0.2987 | 0.3736 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6391 | 74015.409 | 44266.7779 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 952.644 | 0:240:120 | 0:00 | 0.2536 | 7 | 0.0058 | 0.3039 | 0.3097 | 0.3066 | 0.0022 | 0 | 3 | 0.2536 | 0.3165 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6394 | 74019.627 | 44266.778 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1005.5012 | 0:240:120 | 0:00 | 0.2266 | 7 | 0.0054 | 0.2714 | 0.2768 | 0.2736 | 0.0022 | 0 | 3 | 0.2266 | 0.2824 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6397 | 74024.028 | 44266.778 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1065.5447 | 0:240:120 | 0:00 | 0.2008 | 7 | 0.0052 | 0.2396 | 0.2448 | 0.2423 | 0.002 | 0 | 3 | 0.2008 | 0.2501 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6400 | 74027.959 | 44266.7781 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1129.172 | 0:240:120 | 0:00 | 0.1781 | 7 | 0.0058 | 0.2118 | 0.2176 | 0.2145 | 0.0022 | 0 | 3 | 0.1781 | 0.2216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6403 | 74031.799 | 44266.7781 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1198.989 | 0:240:120 | 0:00 | 0.1574 | 7 | 0.0041 | 0.1884 | 0.1925 | 0.19 | 0.0015 | 0 | 3 | 0.1574 | 0.1957 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6406 | 74035.547 | 44266.7782 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1301.454 | 0:240:120 | 0:00 | 0.133 | 7 | 0.0041 | 0.1583 | 0.1624 | 0.1602 | 0.0015 | 0 | 3 | 0.133 | 0.1652 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6409 | 74039.284 | 44266.7782 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1425.446 | 0:240:120 | 0:00 | 0.1104 | 7 | 0.0027 | 0.1312 | 0.1339 | 0.1322 | 0.001 | 0 | 3 | 0.1104 | 0.137 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6412 | 74043.109 | 44266.7783 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1578.511 | 0:240:120 | 0:00 | 0.0897 | 7 | 0.0029 | 0.1064 | 0.1093 | 0.1076 | 0.0011 | 0 | 3 | 0.0897 | 0.1112 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6415 | 74046.851 | 44266.7783 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1720.268 | 0:240:120 | 0:00 | 0.0754 | 7 | 0.0035 | 0.0892 | 0.0927 | 0.0909 | 0.0013 | 0 | 3 | 0.0754 | 0.0933 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6418 | 74050.785 | 44266.7783 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1880.395 | 0:240:120 | 0:00 | 0.0629 | 7 | 0.0027 | 0.0746 | 0.0773 | 0.0759 | 0.0009 | 0 | 3 | 0.0629 | 0.0779 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6421 | 74054.458 | 44266.7784 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2047.221 | 0:240:120 | 0:00 | 0.053 | 7 | 0.0018 | 0.0634 | 0.0652 | 0.0644 | 0.0006 | 0 | 3 | 0.053 | 0.0656 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6424 | 74057.819 | 44266.7784 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2273.865 | 0:240:120 | 0:00 | 0.0429 | 7 | 0.0028 | 0.0507 | 0.0535 | 0.052 | 0.0009 | 0 | 3 | 0.0429 | 0.053 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6427 | 74061.191 | 44266.7785 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2470.655 | 0:240:120 | 0:00 | 0.0363 | 7 | 0.003 | 0.0429 | 0.0459 | 0.0444 | 0.001 | 0 | 3 | 0.0363 | 0.0463 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6430 | 74064.615 | 44266.7785 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2760.692 | 0:240:120 | 0:00 | 0.029 | 7 | 0.0029 | 0.0345 | 0.0374 | 0.0357 | 0.0009 | 0 | 3 | 0.029 | 0.039 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6433 | 74067.993 | 44266.7785 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3045 | 0:240:120 | 0:00 | 0.0238 | 7 | 0.0019 | 0.0289 | 0.0308 | 0.0301 | 0.0007 | 0 | 3 | 0.0238 | 0.0338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6436 | 74071.353 | 44266.7786 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3261.45 | 0:240:120 | 0:00 | 0.0208 | 7 | 0.003 | 0.0251 | 0.0281 | 0.0269 | 0.001 | 0 | 3 | 0.0208 | 0.0308 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6439 | 74074.692 | 44266.7786 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3536.63 | 0:240:120 | 0:00 | 0.0176 | 7 | 0.0031 | 0.0215 | 0.0246 | 0.0234 | 0.0012 | 0 | 3 | 0.0176 | 0.0276 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6442 | 74078.046 | 44266.7787 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3789.27 | 0:240:120 | 0:00 | 0.0154 | 7 | 0.0044 | 0.0189 | 0.0233 | 0.0212 | 0.0017 | 0 | 3 | 0.0154 | 0.0254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6445 | 74081.258 | 44266.7787 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4141.98 | 0:240:120 | 0:00 | 0.0129 | 7 | 0.0029 | 0.0177 | 0.0206 | 0.0192 | 0.0013 | 0 | 3 | 0.0129 | 0.0229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6448 | 74085.115 | 44266.7787 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4354.34 | 0:240:120 | 0:00 | 0.0116 | 7 | 0.0025 | 0.0174 | 0.0199 | 0.0182 | 0.0009 | 0 | 3 | 0.0116 | 0.0216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6451 | 74088.768 | 44266.7788 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4573.02 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0006 | 0.0172 | 0.0178 | 0.0174 | 0.0003 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6454 | 74092.041 | 44266.7788 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4731.17 | 0:240:120 | 0:00 | 0.0098 | 7 | 0.0016 | 0.0156 | 0.0172 | 0.0165 | 0.0006 | 0 | 3 | 0.0098 | 0.016 | NP | NP | 0-0-0-1-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
6457 | 74095.925 | 44266.7789 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4855.8 | 0:240:120 | 0:00 | 0.0093 | 7 | 0.0018 | 0.0154 | 0.0172 | 0.0162 | 0.0007 | 0 | 3 | 0.0093 | 0.016 | NP | NP | 1-1-0-1-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6460 | 74099.31 | 44266.7789 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4929.18 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.003 | 0.0146 | 0.0176 | 0.0159 | 0.0009 | 0 | 3 | 0.0091 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6463 | 74102.704 | 44266.7789 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5173.6831 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0052 | 0.0123 | 0.0175 | 0.0148 | 0.0018 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6466 | 74106.184 | 44266.779 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5820.3935 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0052 | 0.011 | 0.0162 | 0.0137 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6469 | 74109.723 | 44266.779 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6467.1039 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0047 | 0.0105 | 0.0152 | 0.0131 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6472 | 74113.099 | 44266.7791 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7243.1563 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0052 | 0.0102 | 0.0154 | 0.0128 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6475 | 74116.312 | 44266.7791 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9858.4531 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0052 | 0.0103 | 0.0155 | 0.0121 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6478 | 74270.831 | 44266.7809 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 229.6 | 0:240:120 | 0:00 | 17.3008 | 7 | 6.6168 | 149.8872 | 156.504 | 151.4394 | 2.6991 | 7.2851 | 3 | 17.3008 | 81.4788 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6481 | 74711.435 | 44266.786 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 232.2 | 0:240:120 | 0:00 | 15.8082 | 7 | 12.1271 | 113.0607 | 125.1878 | 122.0282 | 5.0507 | 25.5098 | 3 | 15.8082 | 59.9024 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6484 | 75065.909 | 44266.7901 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.8 | 0:240:120 | 0:00 | 14.5396 | 7 | 24.7495 | 75.6921 | 100.4416 | 91.7057 | 12.0264 | 144.6335 | 3 | 14.5396 | 47.2494 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6487 | 75345.822 | 44266.7933 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.6 | 0:240:120 | 0:00 | 13.3708 | 7 | 24.7509 | 50.9416 | 75.6925 | 59.1938 | 12.3737 | 153.1093 | 3 | 13.3708 | 38.4109 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6490 | 75526.7 | 44266.7954 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 240.8 | 0:240:120 | 0:00 | 12.2327 | 7 | 0.0056 | 26.1935 | 26.1991 | 26.1969 | 0.0019 | 0 | 3 | 12.2327 | 31.5749 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6493 | 75607.31 | 44266.7964 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 243.8 | 0:240:120 | 0:00 | 11.3178 | 7 | 1.3705 | 23.4599 | 24.8304 | 24.049 | 0.629 | 0.3956 | 3 | 11.3178 | 27.01 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6496 | 75683.611 | 44266.7972 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.7 | 0:240:120 | 0:00 | 10.5461 | 7 | 1.3717 | 22.0888 | 23.4605 | 22.5473 | 0.6847 | 0.4688 | 3 | 10.5461 | 23.6627 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6499 | 75754.439 | 44266.7981 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 250 | 0:240:120 | 0:00 | 9.7778 | 7 | 1.3694 | 19.3534 | 20.7228 | 20.2615 | 0.6808 | 0.4635 | 3 | 9.7778 | 20.7059 | P | NP | 0-0-1-0-0-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6502 | 75818.18 | 44266.7988 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 253.5 | 0:240:120 | 0:00 | 9.0676 | 7 | 0.908 | 17.9809 | 18.8889 | 18.2635 | 0.4234 | 0.1792 | 3 | 9.0676 | 18.2536 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6505 | 75875.911 | 44266.7995 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 257 | 0:240:120 | 0:00 | 8.4456 | 7 | 1.3704 | 15.2442 | 16.6146 | 15.7095 | 0.6788 | 0.4608 | 3 | 8.4456 | 16.2967 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6508 | 75926.025 | 44266.8001 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 260.7 | 0:240:120 | 0:00 | 7.8671 | 7 | 1.0842 | 12.7921 | 13.8763 | 13.5274 | 0.5213 | 0.2718 | 3 | 7.8671 | 14.6167 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6511 | 75969.102 | 44266.8006 | Vista Speed | E | 100E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 265.3 | 0:240:120 | 0:00 | 7.2406 | 7 | 0.454 | 11.6014 | 12.0554 | 11.8996 | 0.2236 | 0.05 | 3 | 7.2406 | 12.9327 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6514 | 76143.001 | 44266.8026 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 330 | 0:240:120 | 0:00 | 14.4295 | 7 | 17.9518 | 127.0919 | 145.0437 | 139.1598 | 8.8229 | 77.8442 | 3 | 14.4295 | 115.8085 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6517 | 76581.471 | 44266.8076 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 330.3795 | 0:240:120 | 0:00 | 14.2781 | 7 | 18.0076 | 127.038 | 145.0456 | 139.0412 | 9.0006 | 81.011 | 3 | 14.2781 | 108.3406 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6520 | 77002.149 | 44266.8125 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 333.6993 | 0:240:120 | 0:00 | 13.0717 | 7 | 17.9977 | 109.0432 | 127.0409 | 121.0385 | 8.9958 | 80.9247 | 3 | 13.0717 | 69.1274 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6523 | 77368.72 | 44266.8168 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 336.7166 | 0:240:120 | 0:00 | 12.1312 | 7 | 17.9993 | 91.0444 | 109.0437 | 103.0428 | 8.9983 | 80.9697 | 3 | 12.1312 | 51.8935 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6526 | 77680.869 | 44266.8204 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 340.4412 | 0:240:120 | 0:00 | 11.1324 | 7 | 17.9956 | 73.048 | 91.0436 | 83.1652 | 8.0863 | 65.3884 | 3 | 11.1324 | 39.5878 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6529 | 77921.346 | 44266.8231 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 345.2405 | 0:240:120 | 0:00 | 10.0526 | 7 | 0.0329 | 55.02 | 55.0529 | 55.0459 | 0.01 | 0.0001 | 3 | 10.0526 | 30.2336 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6532 | 78071.779 | 44266.8249 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 350.4578 | 0:240:120 | 0:00 | 9.0811 | 7 | 17.9994 | 19.0552 | 37.0546 | 25.0598 | 8.9954 | 80.9169 | 3 | 9.0811 | 23.983 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6535 | 78167.258 | 44266.826 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 355.0437 | 0:240:120 | 0:00 | 8.3608 | 7 | 0.9152 | 17.147 | 18.0622 | 17.7638 | 0.4456 | 0.1985 | 3 | 8.3608 | 20.2511 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6538 | 78223.711 | 44266.8266 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 360.4095 | 0:240:120 | 0:00 | 7.6417 | 7 | 1.0014 | 16.0648 | 17.0662 | 16.4006 | 0.4987 | 0.2487 | 3 | 7.6417 | 17.0947 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6541 | 78276.071 | 44266.8273 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 366.9556 | 0:240:120 | 0:00 | 6.905 | 7 | 0.9994 | 14.0742 | 15.0736 | 14.4021 | 0.4883 | 0.2385 | 3 | 6.905 | 14.3255 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6544 | 78322.532 | 44266.8278 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 371.7571 | 0:240:120 | 0:00 | 6.4424 | 7 | 0.9945 | 12.087 | 13.0815 | 12.7489 | 0.4962 | 0.2462 | 3 | 6.4424 | 12.7829 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6547 | 78364.714 | 44266.8283 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 376.6213 | 0:240:120 | 0:00 | 6.0279 | 7 | 0.8762 | 11.0867 | 11.9629 | 11.3692 | 0.4209 | 0.1772 | 3 | 6.0279 | 11.5108 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6550 | 78402.36 | 44266.8287 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 381.931 | 0:240:120 | 0:00 | 5.6273 | 7 | 0.9965 | 9.0966 | 10.0931 | 9.7165 | 0.4683 | 0.2193 | 3 | 5.6273 | 10.369 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6553 | 78434.381 | 44266.8291 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 387.7038 | 0:240:120 | 0:00 | 5.243 | 7 | 0.3299 | 8.4388 | 8.7687 | 8.6579 | 0.164 | 0.0269 | 3 | 5.243 | 9.3464 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6556 | 78463.474 | 44266.8294 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 393.9573 | 0:240:120 | 0:00 | 4.8765 | 7 | 0.3311 | 7.7802 | 8.1113 | 7.9995 | 0.1638 | 0.0268 | 3 | 4.8765 | 8.4316 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6559 | 78490.619 | 44266.8297 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 398.7126 | 0:240:120 | 0:00 | 4.6271 | 7 | 0.3332 | 7.4476 | 7.7808 | 7.5595 | 0.1656 | 0.0274 | 3 | 4.6271 | 7.8398 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6562 | 78516.638 | 44266.83 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 403.9299 | 0:240:120 | 0:00 | 4.3784 | 7 | 0.3302 | 6.7907 | 7.1209 | 7.0103 | 0.1641 | 0.0269 | 3 | 4.3784 | 7.2727 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6565 | 78540.836 | 44266.8303 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 411.6783 | 0:240:120 | 0:00 | 4.0498 | 7 | 0.3396 | 6.1239 | 6.4635 | 6.2398 | 0.1672 | 0.028 | 3 | 4.0498 | 6.557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6568 | 78562.461 | 44266.8306 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 420.8347 | 0:240:120 | 0:00 | 3.7137 | 7 | 0.1667 | 5.4739 | 5.6406 | 5.5301 | 0.0826 | 0.0068 | 3 | 3.7137 | 5.8612 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6571 | 78582.302 | 44266.8308 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 429.3366 | 0:240:120 | 0:00 | 3.4427 | 7 | 0.1658 | 4.9856 | 5.1514 | 5.0953 | 0.0814 | 0.0066 | 3 | 3.4427 | 5.3254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6574 | 78600.789 | 44266.831 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 435.8255 | 0:240:120 | 0:00 | 3.2581 | 7 | 0.1635 | 4.6609 | 4.8244 | 4.7694 | 0.0809 | 0.0065 | 3 | 3.2581 | 4.9723 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6577 | 78618.084 | 44266.8312 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 442.4123 | 0:240:120 | 0:00 | 3.0875 | 7 | 0.1629 | 4.3347 | 4.4976 | 4.4425 | 0.0807 | 0.0065 | 3 | 3.0875 | 4.6544 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6580 | 78634.854 | 44266.8314 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 449.9968 | 0:240:120 | 0:00 | 2.9092 | 7 | 0.1938 | 3.9778 | 4.1716 | 4.0748 | 0.0834 | 0.0069 | 3 | 2.9092 | 4.3304 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6583 | 78650.293 | 44266.8316 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 456.7981 | 0:240:120 | 0:00 | 2.7638 | 7 | 0.1575 | 3.7846 | 3.9421 | 3.8666 | 0.0652 | 0.0042 | 3 | 2.7638 | 4.0721 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6586 | 78665.024 | 44266.8318 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 464.6301 | 0:240:120 | 0:00 | 2.6111 | 7 | 0.0981 | 3.591 | 3.6891 | 3.6555 | 0.0481 | 0.0023 | 3 | 2.6111 | 3.8064 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6589 | 78679.076 | 44266.8319 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 474.0164 | 0:240:120 | 0:00 | 2.4461 | 7 | 0.0969 | 3.3014 | 3.3983 | 3.3654 | 0.048 | 0.0023 | 3 | 2.4461 | 3.5256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6592 | 78692.17 | 44266.8321 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 485.045 | 0:240:120 | 0:00 | 2.2736 | 7 | 0.1282 | 3.0137 | 3.1419 | 3.0772 | 0.055 | 0.003 | 3 | 2.2736 | 3.2388 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6595 | 78704.654 | 44266.8322 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 494.8438 | 0:240:120 | 0:00 | 2.1369 | 7 | 0.1273 | 2.8223 | 2.9496 | 2.8855 | 0.0547 | 0.003 | 3 | 2.1369 | 3.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6598 | 78716.231 | 44266.8323 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 504.8395 | 0:240:120 | 0:00 | 2.011 | 7 | 0.1232 | 2.631 | 2.7542 | 2.6921 | 0.0518 | 0.0027 | 3 | 2.011 | 2.8146 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6601 | 78727.305 | 44266.8325 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 515.5535 | 0:240:120 | 0:00 | 1.8892 | 7 | 0.0461 | 2.4779 | 2.524 | 2.5078 | 0.0223 | 0.0005 | 3 | 1.8892 | 2.6229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6604 | 78737.959 | 44266.8326 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 526.4952 | 0:240:120 | 0:00 | 1.777 | 7 | 0.0896 | 2.2997 | 2.3893 | 2.3435 | 0.0383 | 0.0015 | 3 | 1.777 | 2.449 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6607 | 78748.186 | 44266.8327 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 539.2838 | 0:240:120 | 0:00 | 1.6591 | 7 | 0.0891 | 2.1198 | 2.2089 | 2.1639 | 0.0384 | 0.0015 | 3 | 1.6591 | 2.2691 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6610 | 78757.733 | 44266.8328 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 554.5969 | 0:240:120 | 0:00 | 1.5341 | 7 | 0.0666 | 1.9542 | 2.0208 | 1.9886 | 0.0286 | 0.0008 | 3 | 1.5341 | 2.0812 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6613 | 78766.833 | 44266.8329 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 572.6314 | 0:240:120 | 0:00 | 1.4056 | 7 | 0.0377 | 1.7851 | 1.8228 | 1.8095 | 0.0179 | 0.0003 | 3 | 1.4056 | 1.8912 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6616 | 78775.359 | 44266.833 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 595.4047 | 0:240:120 | 0:00 | 1.2667 | 7 | 0.0505 | 1.5872 | 1.6377 | 1.6203 | 0.0246 | 0.0006 | 3 | 1.2667 | 1.6893 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6619 | 78783.273 | 44266.8331 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 615.3807 | 0:240:120 | 0:00 | 1.1623 | 7 | 0.0402 | 1.4562 | 1.4964 | 1.4755 | 0.0168 | 0.0003 | 3 | 1.1623 | 1.5399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6622 | 78790.875 | 44266.8332 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 633.4878 | 0:240:120 | 0:00 | 1.0791 | 7 | 0.0405 | 1.3366 | 1.3771 | 1.3625 | 0.0189 | 0.0004 | 3 | 1.0791 | 1.4223 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6625 | 78798.2 | 44266.8333 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 657.3666 | 0:240:120 | 0:00 | 0.9832 | 7 | 0.0316 | 1.2237 | 1.2553 | 1.2389 | 0.0134 | 0.0002 | 3 | 0.9832 | 1.2882 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6628 | 78805.2 | 44266.8334 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 678.0642 | 0:240:120 | 0:00 | 0.9107 | 7 | 0.0255 | 1.1237 | 1.1492 | 1.1404 | 0.0121 | 0.0001 | 3 | 0.9107 | 1.1877 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6631 | 78811.756 | 44266.8335 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 707.1493 | 0:240:120 | 0:00 | 0.8222 | 7 | 0.0219 | 1.0122 | 1.0341 | 1.0239 | 0.0093 | 0.0001 | 3 | 0.8222 | 1.0665 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6634 | 78817.963 | 44266.8335 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 735.273 | 0:240:120 | 0:00 | 0.749 | 7 | 0.0233 | 0.9169 | 0.9402 | 0.9292 | 0.0095 | 0.0001 | 3 | 0.749 | 0.9671 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6637 | 78824.083 | 44266.8336 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 765.2799 | 0:240:120 | 0:00 | 0.6816 | 7 | 0.0166 | 0.8355 | 0.8521 | 0.8429 | 0.007 | 0 | 3 | 0.6816 | 0.8765 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6640 | 78829.849 | 44266.8337 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 794.1252 | 0:240:120 | 0:00 | 0.6254 | 7 | 0.0168 | 0.7636 | 0.7804 | 0.7715 | 0.0068 | 0 | 3 | 0.6254 | 0.8014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6643 | 78835.4 | 44266.8337 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 832.3403 | 0:240:120 | 0:00 | 0.5614 | 7 | 0.0114 | 0.6847 | 0.6961 | 0.6901 | 0.0047 | 0 | 3 | 0.5614 | 0.7167 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6646 | 78840.465 | 44266.8338 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 872.3935 | 0:240:120 | 0:00 | 0.5047 | 7 | 0.0142 | 0.6133 | 0.6275 | 0.6207 | 0.0057 | 0 | 3 | 0.5047 | 0.642 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6649 | 78845.705 | 44266.8338 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 916.2054 | 0:240:120 | 0:00 | 0.4522 | 7 | 0.0133 | 0.5468 | 0.5601 | 0.5537 | 0.0054 | 0 | 3 | 0.4522 | 0.5735 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6652 | 78850.733 | 44266.8339 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 984.6056 | 0:240:120 | 0:00 | 0.3857 | 7 | 0.0114 | 0.4665 | 0.4779 | 0.4712 | 0.0041 | 0 | 3 | 0.3857 | 0.4872 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6655 | 78855.17 | 44266.834 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1053.888 | 0:240:120 | 0:00 | 0.3326 | 7 | 0.0075 | 0.4008 | 0.4083 | 0.4042 | 0.0031 | 0 | 3 | 0.3326 | 0.4188 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6658 | 78859.608 | 44266.834 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1141.657 | 0:240:120 | 0:00 | 0.28 | 7 | 0.0084 | 0.3351 | 0.3435 | 0.3393 | 0.0033 | 0 | 3 | 0.28 | 0.3514 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6661 | 78863.941 | 44266.8341 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1224.432 | 0:240:120 | 0:00 | 0.2412 | 7 | 0.0116 | 0.2848 | 0.2964 | 0.2918 | 0.004 | 0 | 3 | 0.2412 | 0.3021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6664 | 78868.071 | 44266.8341 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1298.858 | 0:240:120 | 0:00 | 0.2129 | 7 | 0.0085 | 0.2553 | 0.2638 | 0.2582 | 0.003 | 0 | 3 | 0.2129 | 0.2662 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6667 | 78872.244 | 44266.8342 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1393.029 | 0:240:120 | 0:00 | 0.1838 | 7 | 0.0091 | 0.2171 | 0.2262 | 0.2217 | 0.0032 | 0 | 3 | 0.1838 | 0.2294 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6670 | 78876.332 | 44266.8342 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1482.129 | 0:240:120 | 0:00 | 0.1615 | 7 | 0.0064 | 0.1912 | 0.1976 | 0.1941 | 0.002 | 0 | 3 | 0.1615 | 0.2013 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6673 | 78880.034 | 44266.8342 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1608.794 | 0:240:120 | 0:00 | 0.1363 | 7 | 0.005 | 0.1621 | 0.1671 | 0.1644 | 0.0018 | 0 | 3 | 0.1363 | 0.1696 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6676 | 78883.622 | 44266.8343 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1721.995 | 0:240:120 | 0:00 | 0.1184 | 7 | 0.0037 | 0.1409 | 0.1446 | 0.1424 | 0.0016 | 0 | 3 | 0.1184 | 0.1472 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6679 | 78887.53 | 44266.8343 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1865.413 | 0:240:120 | 0:00 | 0.1005 | 7 | 0.0035 | 0.1197 | 0.1232 | 0.1212 | 0.0012 | 0 | 3 | 0.1005 | 0.1248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6682 | 78891.004 | 44266.8344 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1990.692 | 0:240:120 | 0:00 | 0.088 | 7 | 0.0039 | 0.1042 | 0.1081 | 0.1059 | 0.0013 | 0 | 3 | 0.088 | 0.1092 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6685 | 78894.833 | 44266.8344 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2139.313 | 0:240:120 | 0:00 | 0.0759 | 7 | 0.0033 | 0.0899 | 0.0932 | 0.0919 | 0.0012 | 0 | 3 | 0.0759 | 0.0942 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6688 | 78898.648 | 44266.8345 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2315.17 | 0:240:120 | 0:00 | 0.0647 | 7 | 0.0045 | 0.0758 | 0.0803 | 0.0778 | 0.0013 | 0 | 3 | 0.0647 | 0.0801 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6691 | 78902.223 | 44266.8345 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2548.447 | 0:240:120 | 0:00 | 0.0532 | 7 | 0.0037 | 0.0622 | 0.0659 | 0.0641 | 0.0012 | 0 | 3 | 0.0532 | 0.0659 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6694 | 78905.738 | 44266.8345 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2833.413 | 0:240:120 | 0:00 | 0.0429 | 7 | 0.0041 | 0.0495 | 0.0536 | 0.052 | 0.0014 | 0 | 3 | 0.0429 | 0.0531 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6697 | 78909.31 | 44266.8346 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3185.094 | 0:240:120 | 0:00 | 0.0339 | 7 | 0.0029 | 0.0398 | 0.0427 | 0.0414 | 0.0011 | 0 | 3 | 0.0339 | 0.0439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6700 | 78912.836 | 44266.8346 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3700 | 0:240:120 | 0:00 | 0.0251 | 7 | 0.0034 | 0.0297 | 0.0331 | 0.0314 | 0.0012 | 0 | 3 | 0.0251 | 0.0351 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6703 | 78916.132 | 44266.8347 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3987.53 | 0:240:120 | 0:00 | 0.0216 | 7 | 0.003 | 0.0256 | 0.0286 | 0.0276 | 0.0013 | 0 | 3 | 0.0216 | 0.0316 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6706 | 78919.442 | 44266.8347 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4276.66 | 0:240:120 | 0:00 | 0.0187 | 7 | 0.0038 | 0.0222 | 0.026 | 0.0242 | 0.0014 | 0 | 3 | 0.0187 | 0.0287 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6709 | 78923.093 | 44266.8347 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4554.76 | 0:240:120 | 0:00 | 0.0165 | 7 | 0.0028 | 0.0205 | 0.0233 | 0.0224 | 0.001 | 0 | 3 | 0.0165 | 0.0265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6712 | 78926.439 | 44266.8348 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4919.33 | 0:240:120 | 0:00 | 0.0141 | 7 | 0.0027 | 0.0194 | 0.0221 | 0.0209 | 0.0012 | 0 | 3 | 0.0141 | 0.0241 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6715 | 78929.731 | 44266.8348 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5187.09 | 0:240:120 | 0:00 | 0.0127 | 7 | 0.0041 | 0.0171 | 0.0212 | 0.0194 | 0.0015 | 0 | 3 | 0.0127 | 0.0227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6718 | 78933.452 | 44266.8349 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5513.35 | 0:240:120 | 0:00 | 0.0113 | 7 | 0.0012 | 0.0177 | 0.0189 | 0.0183 | 0.0005 | 0 | 3 | 0.0113 | 0.0213 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6721 | 78936.963 | 44266.8349 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5877.74 | 0:240:120 | 0:00 | 0.0099 | 7 | 0.0012 | 0.016 | 0.0172 | 0.0167 | 0.0006 | 0 | 3 | 0.0099 | 0.016 | NP | NP | 0-0-0-1-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6724 | 78940.428 | 44266.8349 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6105.4 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0013 | 0.0152 | 0.0165 | 0.0157 | 0.0005 | 0 | 3 | 0.0092 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6727 | 78943.824 | 44266.835 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6197.67 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.003 | 0.0143 | 0.0173 | 0.0158 | 0.001 | 0 | 3 | 0.0089 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6730 | 78947.287 | 44266.835 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6505.0942 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0042 | 0.0128 | 0.017 | 0.0148 | 0.0015 | 0 | 3 | 0.0081 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6733 | 78950.642 | 44266.8351 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7318.231 | 0:240:120 | 0:00 | 0.0064 | 7 | 0.0058 | 0.0109 | 0.0167 | 0.0138 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6736 | 78954.174 | 44266.8351 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8131.3678 | 0:240:120 | 0:00 | 0.0052 | 7 | 0.0047 | 0.0106 | 0.0153 | 0.013 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6739 | 78957.837 | 44266.8351 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9107.1319 | 0:240:120 | 0:00 | 0.0041 | 7 | 0.0041 | 0.0109 | 0.015 | 0.0127 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6742 | 79088.345 | 44266.8367 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 332 | 0:240:120 | 0:00 | 13.6641 | 7 | 0.3365 | 127.0334 | 127.3699 | 127.1068 | 0.1253 | 0.0157 | 3 | 13.6641 | 84.8939 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6745 | 79455.743 | 44266.8409 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 335.2 | 0:240:120 | 0:00 | 12.5874 | 7 | 0.4215 | 109.0374 | 109.4589 | 109.111 | 0.1384 | 0.0192 | 3 | 12.5874 | 59.3469 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6748 | 79768.379 | 44266.8445 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 338.6 | 0:240:120 | 0:00 | 11.6061 | 7 | 0.0316 | 91.0396 | 91.0712 | 91.0468 | 0.0095 | 0.0001 | 3 | 11.6061 | 44.8612 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6751 | 80027.037 | 44266.8475 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 342.8 | 0:240:120 | 0:00 | 10.5761 | 7 | 17.9998 | 55.0506 | 73.0504 | 67.048 | 8.9975 | 80.9543 | 3 | 10.5761 | 34.3786 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6754 | 80222.486 | 44266.8498 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 347.8 | 0:240:120 | 0:00 | 9.5532 | 7 | 9.1082 | 37.0489 | 46.1571 | 39.8282 | 4.1793 | 17.4662 | 3 | 9.5532 | 26.8178 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6757 | 80334.814 | 44266.8511 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 352.8 | 0:240:120 | 0:00 | 8.6996 | 7 | 0.9976 | 18.0604 | 19.058 | 18.7241 | 0.4966 | 0.2466 | 3 | 8.6996 | 21.9259 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6760 | 80393.231 | 44266.8518 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 357.7 | 0:240:120 | 0:00 | 7.99 | 7 | 0.1107 | 17.0619 | 17.1726 | 17.0833 | 0.038 | 0.0014 | 3 | 7.99 | 18.5609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6763 | 80446.817 | 44266.8524 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 363.7 | 0:240:120 | 0:00 | 7.2544 | 7 | 0.974 | 15.0716 | 16.0456 | 15.389 | 0.4734 | 0.2241 | 3 | 7.2544 | 15.5869 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6766 | 80496.006 | 44266.8529 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 369.4 | 0:240:120 | 0:00 | 6.6622 | 7 | 0.996 | 13.0819 | 14.0779 | 13.4682 | 0.4653 | 0.2165 | 3 | 6.6622 | 13.4988 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6769 | 80539.59 | 44266.8535 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 374.2 | 0:240:120 | 0:00 | 6.228 | 7 | 0.9953 | 11.0907 | 12.086 | 11.7538 | 0.4955 | 0.2456 | 3 | 6.228 | 12.1128 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6772 | 80578.422 | 44266.8539 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 379.3 | 0:240:120 | 0:00 | 5.8196 | 7 | 0.999 | 10.0912 | 11.0902 | 10.4259 | 0.4981 | 0.2481 | 3 | 5.8196 | 10.907 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6775 | 80612.692 | 44266.8543 | Vista Speed | E | 125E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 384.8 | 0:240:120 | 0:00 | 5.4302 | 7 | 0.3303 | 8.7683 | 9.0986 | 8.9873 | 0.1638 | 0.0268 | 3 | 5.4302 | 9.8362 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6778 | 80900.035 | 44266.8576 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 396 | 0:240:120 | 0:00 | 20.339 | 7 | 0.0011 | 199.0435 | 199.0446 | 199.0438 | 0.0004 | 0 | 3 | 20.339 | 9999999 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6781 | 81613.106 | 44266.8659 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 400.3109 | 0:240:120 | 0:00 | 17.9483 | 7 | 0.1751 | 180.8662 | 181.0413 | 181.0107 | 0.0573 | 0.0033 | 3 | 17.9483 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6784 | 82159.365 | 44266.8722 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 402.7199 | 0:240:120 | 0:00 | 16.8333 | 7 | 18.001 | 163.0405 | 181.0415 | 169.6045 | 8.6177 | 74.2647 | 3 | 16.8333 | 1615.3968 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6787 | 82687.591 | 44266.8783 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 405.1432 | 0:240:120 | 0:00 | 15.8376 | 7 | 18.0031 | 145.0424 | 163.0455 | 157.0428 | 8.9989 | 80.9804 | 3 | 15.8376 | 274.4061 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6790 | 83161.852 | 44266.8838 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 409.2154 | 0:240:120 | 0:00 | 14.3952 | 7 | 18.0043 | 127.0391 | 145.0434 | 139.0405 | 9.0005 | 81.0081 | 3 | 14.3952 | 114.0414 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6793 | 83591.406 | 44266.8888 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 411.6783 | 0:240:120 | 0:00 | 13.638 | 7 | 9.899 | 127.0315 | 136.9305 | 130.141 | 4.6633 | 21.7461 | 3 | 13.638 | 84.0833 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6796 | 83994.717 | 44266.8934 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 414.5702 | 0:240:120 | 0:00 | 12.8398 | 7 | 17.997 | 109.0413 | 127.0383 | 116.4357 | 8.172 | 66.7818 | 3 | 12.8398 | 64.163 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6799 | 84361.426 | 44266.8977 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 417.8999 | 0:240:120 | 0:00 | 12.0234 | 7 | 17.9996 | 91.0439 | 109.0435 | 103.0416 | 8.9976 | 80.9567 | 3 | 12.0234 | 50.3306 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6802 | 84673.878 | 44266.9013 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 422.0997 | 0:240:120 | 0:00 | 11.1233 | 7 | 17.9969 | 73.0489 | 91.0458 | 84.4982 | 8.6227 | 74.3502 | 3 | 11.1233 | 39.4943 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6805 | 84914.401 | 44266.9041 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 428.9076 | 0:240:120 | 0:00 | 9.9055 | 7 | 17.9977 | 37.0545 | 55.0522 | 49.0512 | 8.9967 | 80.9402 | 3 | 9.9055 | 29.1776 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6808 | 85064.761 | 44266.9058 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 434.5198 | 0:240:120 | 0:00 | 9.0745 | 7 | 18.0003 | 19.054 | 37.0543 | 25.1399 | 8.9385 | 79.8964 | 3 | 9.0745 | 23.9459 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6811 | 85159.154 | 44266.9069 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 443.7411 | 0:240:120 | 0:00 | 7.9587 | 7 | 1.01 | 16.0823 | 17.0923 | 16.7588 | 0.465 | 0.2162 | 3 | 7.9587 | 18.4245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6814 | 85211.567 | 44266.9075 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 454.9743 | 0:240:120 | 0:00 | 6.9009 | 7 | 0.999 | 14.0741 | 15.0731 | 14.4084 | 0.4982 | 0.2482 | 3 | 6.9009 | 14.3111 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6817 | 85256.89 | 44266.908 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 464.6301 | 0:240:120 | 0:00 | 6.1786 | 7 | 0.9977 | 11.0895 | 12.0872 | 11.7537 | 0.4971 | 0.2471 | 3 | 6.1786 | 11.9621 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6820 | 85293.372 | 44266.9085 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 476.3924 | 0:240:120 | 0:00 | 5.4655 | 7 | 0.3307 | 8.7674 | 9.0981 | 8.9868 | 0.1639 | 0.0269 | 3 | 5.4655 | 9.9303 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6823 | 85322.657 | 44266.9088 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 492.3754 | 0:240:120 | 0:00 | 4.7058 | 7 | 0.3316 | 7.4492 | 7.7808 | 7.6694 | 0.1644 | 0.027 | 3 | 4.7058 | 8.0239 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6826 | 85347.174 | 44266.9091 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 516.5853 | 0:240:120 | 0:00 | 3.8594 | 7 | 0.1641 | 5.6394 | 5.8035 | 5.7477 | 0.0811 | 0.0066 | 3 | 3.8594 | 6.1586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6829 | 85366.46 | 44266.9093 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 549.0782 | 0:240:120 | 0:00 | 3.0754 | 7 | 0.2841 | 4.2142 | 4.4983 | 4.3595 | 0.1157 | 0.0134 | 3 | 3.0754 | 4.6322 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6832 | 85381.936 | 44266.9095 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 593.0276 | 0:240:120 | 0:00 | 2.3757 | 7 | 0.1598 | 3.1417 | 3.3015 | 3.2148 | 0.0696 | 0.0048 | 3 | 2.3757 | 3.4078 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6835 | 85394.296 | 44266.9096 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 640.4948 | 0:240:120 | 0:00 | 1.8775 | 7 | 0.0898 | 2.4333 | 2.5231 | 2.4778 | 0.0386 | 0.0015 | 3 | 1.8775 | 2.6047 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6838 | 85404.362 | 44266.9098 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 701.514 | 0:240:120 | 0:00 | 1.4517 | 7 | 0.0332 | 1.8552 | 1.8884 | 1.8768 | 0.0158 | 0.0003 | 3 | 1.4517 | 1.959 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6841 | 85412.86 | 44266.9099 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 757.6646 | 0:240:120 | 0:00 | 1.1832 | 7 | 0.0391 | 1.4763 | 1.5154 | 1.5009 | 0.0185 | 0.0003 | 3 | 1.1832 | 1.5697 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6844 | 85420.176 | 44266.9099 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 818.3098 | 0:240:120 | 0:00 | 0.9732 | 7 | 0.0323 | 1.2083 | 1.2406 | 1.2235 | 0.0133 | 0.0002 | 3 | 0.9732 | 1.2743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6847 | 85426.93 | 44266.91 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 889.1278 | 0:240:120 | 0:00 | 0.7948 | 7 | 0.0215 | 0.9789 | 1.0004 | 0.989 | 0.009 | 0.0001 | 3 | 0.7948 | 1.0292 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6850 | 85432.975 | 44266.9101 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 975.7836 | 0:240:120 | 0:00 | 0.6384 | 7 | 0.0161 | 0.7803 | 0.7964 | 0.788 | 0.0067 | 0 | 3 | 0.6384 | 0.8188 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6853 | 85438.384 | 44266.9101 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1066.6106 | 0:240:120 | 0:00 | 0.5207 | 7 | 0.0118 | 0.6333 | 0.6451 | 0.6381 | 0.0047 | 0 | 3 | 0.5207 | 0.6631 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6856 | 85443.649 | 44266.9102 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1176.428 | 0:240:120 | 0:00 | 0.4184 | 7 | 0.0125 | 0.5053 | 0.5178 | 0.512 | 0.005 | 0 | 3 | 0.4184 | 0.5295 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6859 | 85448.232 | 44266.9103 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1326.413 | 0:240:120 | 0:00 | 0.3219 | 7 | 0.0125 | 0.3827 | 0.3952 | 0.3887 | 0.0043 | 0 | 3 | 0.3219 | 0.4051 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6862 | 85452.738 | 44266.9103 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1471.789 | 0:240:120 | 0:00 | 0.2576 | 7 | 0.0109 | 0.3068 | 0.3177 | 0.3112 | 0.0039 | 0 | 3 | 0.2576 | 0.3229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6865 | 85457.157 | 44266.9104 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1686.212 | 0:240:120 | 0:00 | 0.1933 | 7 | 0.0073 | 0.2298 | 0.2371 | 0.2337 | 0.0024 | 0 | 3 | 0.1933 | 0.2413 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6868 | 85460.898 | 44266.9104 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1859.825 | 0:240:120 | 0:00 | 0.1575 | 7 | 0.0039 | 0.1881 | 0.192 | 0.1898 | 0.0015 | 0 | 3 | 0.1575 | 0.1963 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6871 | 85464.972 | 44266.9105 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2047.221 | 0:240:120 | 0:00 | 0.1291 | 7 | 0.0043 | 0.1539 | 0.1582 | 0.1555 | 0.0017 | 0 | 3 | 0.1291 | 0.1606 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6874 | 85468.683 | 44266.9105 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2262.524 | 0:240:120 | 0:00 | 0.1051 | 7 | 0.0036 | 0.1249 | 0.1285 | 0.1267 | 0.0013 | 0 | 3 | 0.1051 | 0.1305 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6877 | 85472.388 | 44266.9105 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2545.895 | 0:240:120 | 0:00 | 0.0825 | 7 | 0.003 | 0.0979 | 0.1009 | 0.0992 | 0.0011 | 0 | 3 | 0.0825 | 0.1024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6880 | 85476.043 | 44266.9106 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2905.144 | 0:240:120 | 0:00 | 0.0631 | 7 | 0.0034 | 0.0735 | 0.0769 | 0.0753 | 0.0012 | 0 | 3 | 0.0631 | 0.0782 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6883 | 85479.767 | 44266.9106 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3217.104 | 0:240:120 | 0:00 | 0.0513 | 7 | 0.0025 | 0.0604 | 0.0629 | 0.0617 | 0.001 | 0 | 3 | 0.0513 | 0.0635 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6886 | 85483.318 | 44266.9107 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3584.009 | 0:240:120 | 0:00 | 0.0412 | 7 | 0.0022 | 0.0491 | 0.0513 | 0.0505 | 0.0007 | 0 | 3 | 0.0412 | 0.0512 | P | NP | 0-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6889 | 85486.686 | 44266.9107 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3937.252 | 0:240:120 | 0:00 | 0.0341 | 7 | 0.0029 | 0.0401 | 0.043 | 0.0415 | 0.001 | 0 | 3 | 0.0341 | 0.0441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6892 | 85489.952 | 44266.9107 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4338.301 | 0:240:120 | 0:00 | 0.028 | 7 | 0.0038 | 0.0324 | 0.0362 | 0.0349 | 0.0014 | 0 | 3 | 0.028 | 0.038 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6895 | 85493.53 | 44266.9108 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4684.1 | 0:240:120 | 0:00 | 0.024 | 7 | 0.0029 | 0.0287 | 0.0316 | 0.0303 | 0.0009 | 0 | 3 | 0.024 | 0.034 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6898 | 85496.936 | 44266.9108 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5064.08 | 0:240:120 | 0:00 | 0.0205 | 7 | 0.0023 | 0.0253 | 0.0276 | 0.0265 | 0.0008 | 0 | 3 | 0.0205 | 0.0305 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6901 | 85500.32 | 44266.9109 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5613.49 | 0:240:120 | 0:00 | 0.0167 | 7 | 0.0039 | 0.02 | 0.0239 | 0.0224 | 0.0016 | 0 | 3 | 0.0167 | 0.0267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6904 | 85503.618 | 44266.9109 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6074.94 | 0:240:120 | 0:00 | 0.0143 | 7 | 0.0041 | 0.0185 | 0.0226 | 0.0207 | 0.0013 | 0 | 3 | 0.0143 | 0.0243 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6907 | 85506.831 | 44266.9109 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6574.33 | 0:240:120 | 0:00 | 0.0122 | 7 | 0.0034 | 0.0172 | 0.0206 | 0.0182 | 0.0012 | 0 | 3 | 0.0122 | 0.0222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6910 | 85510.101 | 44266.911 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7079.28 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0013 | 0.0169 | 0.0182 | 0.0173 | 0.0004 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6913 | 85513.374 | 44266.911 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7577.42 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0028 | 0.0146 | 0.0174 | 0.0155 | 0.001 | 0 | 3 | 0.0092 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6916 | 85516.623 | 44266.9111 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7769.24 | 0:240:120 | 0:00 | 0.0087 | 7 | 0.0033 | 0.0135 | 0.0168 | 0.0152 | 0.0012 | 0 | 3 | 0.0087 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6919 | 85520.581 | 44266.9111 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8154.6191 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0032 | 0.0125 | 0.0157 | 0.0145 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6922 | 85524.025 | 44266.9111 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9173.9465 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0046 | 0.0114 | 0.016 | 0.0138 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6925 | 85527.575 | 44266.9112 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10193.2739 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0047 | 0.011 | 0.0157 | 0.0134 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6928 | 85530.911 | 44266.9112 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11416.4668 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0054 | 0.0098 | 0.0152 | 0.0124 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6931 | 85679.249 | 44266.9129 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 410.4 | 0:240:120 | 0:00 | 14.0213 | 7 | 18.0031 | 127.0385 | 145.0416 | 133.9304 | 8.5353 | 72.8513 | 3 | 14.0213 | 97.3796 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6934 | 86099.683 | 44266.9178 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 413.1 | 0:240:120 | 0:00 | 13.2342 | 7 | 18.0007 | 109.0404 | 127.0411 | 121.0398 | 8.9967 | 80.9406 | 3 | 13.2342 | 72.9664 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6937 | 86466.377 | 44266.922 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 416.2 | 0:240:120 | 0:00 | 12.4276 | 7 | 15.6752 | 93.3692 | 109.0444 | 104.5107 | 6.8563 | 47.0089 | 3 | 12.4276 | 56.5687 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6940 | 86778.788 | 44266.9257 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 420 | 0:240:120 | 0:00 | 11.5569 | 7 | 6.7705 | 84.2739 | 91.0444 | 89.3307 | 2.8807 | 8.2987 | 3 | 11.5569 | 44.2716 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6943 | 87037.11 | 44266.9287 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 425.5 | 0:240:120 | 0:00 | 10.4822 | 7 | 17.9981 | 55.052 | 73.0501 | 67.0482 | 8.9965 | 80.937 | 3 | 10.4822 | 33.5866 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6946 | 87223.607 | 44266.9308 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 431.7 | 0:240:120 | 0:00 | 9.4752 | 7 | 7.4728 | 31.4223 | 38.8951 | 35.7165 | 2.5836 | 6.6748 | 3 | 9.4752 | 26.3252 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6949 | 87321.757 | 44266.9319 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 439.1 | 0:240:120 | 0:00 | 8.4866 | 7 | 0.9988 | 18.0575 | 19.0563 | 18.3922 | 0.4975 | 0.2475 | 3 | 8.4866 | 20.8576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6952 | 87379 | 44266.9326 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 449.4 | 0:240:120 | 0:00 | 7.3915 | 7 | 0.9982 | 15.072 | 16.0702 | 15.7367 | 0.4965 | 0.2465 | 3 | 7.3915 | 16.1067 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6955 | 87427.816 | 44266.9332 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 459.8 | 0:240:120 | 0:00 | 6.5219 | 7 | 0.9953 | 12.0862 | 13.0815 | 12.7486 | 0.4965 | 0.2465 | 3 | 6.5219 | 13.0382 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6958 | 87468.482 | 44266.9336 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 470.5 | 0:240:120 | 0:00 | 5.8031 | 7 | 1.0006 | 10.0906 | 11.0912 | 10.4253 | 0.4989 | 0.2489 | 3 | 5.8031 | 10.8602 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6961 | 87502.632 | 44266.934 | Vista Speed | E | 150E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 484.4 | 0:240:120 | 0:00 | 5.0596 | 7 | 0.3312 | 8.1095 | 8.4407 | 8.329 | 0.1643 | 0.027 | 3 | 5.0596 | 8.8818 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6964 | 87723.552 | 44266.9366 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 462 | 0:240:120 | 0:00 | 20.1452 | 7 | 6.6804 | 192.3621 | 199.0425 | 197.4218 | 2.5553 | 6.5295 | 3 | 20.1452 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6967 | 88324.034 | 44266.9435 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 465.0624 | 0:240:120 | 0:00 | 18.648 | 7 | 18.0008 | 181.042 | 199.0428 | 187.1467 | 8.9226 | 79.6131 | 3 | 18.648 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6970 | 88906.373 | 44266.9503 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 469.4525 | 0:240:120 | 0:00 | 16.8394 | 7 | 18.0028 | 163.0409 | 181.0437 | 169.7235 | 8.5437 | 72.9949 | 3 | 16.8394 | 1662.8744 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6973 | 89416.991 | 44266.9562 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 475.9161 | 0:240:120 | 0:00 | 14.714 | 7 | 17.8161 | 127.241 | 145.0571 | 139.3567 | 8.5488 | 73.0823 | 3 | 14.714 | 132.4569 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6976 | 89837.495 | 44266.9611 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 480.6989 | 0:240:120 | 0:00 | 13.4435 | 7 | 17.9958 | 109.0458 | 127.0416 | 121.047 | 8.9873 | 80.7718 | 3 | 13.4435 | 78.4178 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6979 | 90203.899 | 44266.9653 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 485.5301 | 0:240:120 | 0:00 | 12.355 | 7 | 17.9985 | 91.0444 | 109.0429 | 103.0416 | 8.9976 | 80.9576 | 3 | 12.355 | 55.3702 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6982 | 90516.499 | 44266.9689 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 492.3754 | 0:240:120 | 0:00 | 11.0698 | 7 | 17.9972 | 73.0505 | 91.0477 | 82.261 | 7.8166 | 61.0986 | 3 | 11.0698 | 38.9528 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6985 | 90757.247 | 44266.9717 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 498.8181 | 0:240:120 | 0:00 | 10.0704 | 7 | 18.3239 | 37.0535 | 55.3774 | 49.1093 | 8.9947 | 80.9053 | 3 | 10.0704 | 30.3641 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6988 | 90907.769 | 44266.9735 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 506.3564 | 0:240:120 | 0:00 | 9.096 | 7 | 17.9963 | 19.0569 | 37.0532 | 25.5825 | 8.6678 | 75.1307 | 3 | 9.096 | 24.0675 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6991 | 91003.249 | 44266.9746 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 515.0387 | 0:240:120 | 0:00 | 8.1708 | 7 | 0.9974 | 17.0651 | 18.0625 | 17.7288 | 0.4971 | 0.2471 | 3 | 8.1708 | 19.3672 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6994 | 91058.751 | 44266.9752 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 522.8223 | 0:240:120 | 0:00 | 7.4779 | 7 | 0.9951 | 15.0739 | 16.069 | 15.7361 | 0.4963 | 0.2463 | 3 | 7.4779 | 16.4421 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6997 | 91109.174 | 44266.9758 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 530.7236 | 0:240:120 | 0:00 | 6.8769 | 7 | 1.9228 | 13.0824 | 15.0052 | 14.0369 | 0.8112 | 0.658 | 3 | 6.8769 | 14.2277 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7000 | 91155.74 | 44266.9763 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 538.2058 | 0:240:120 | 0:00 | 6.384 | 7 | 0.9947 | 12.0871 | 13.0818 | 12.7478 | 0.4953 | 0.2453 | 3 | 6.384 | 12.5977 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7003 | 91196.215 | 44266.9768 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 547.9815 | 0:240:120 | 0:00 | 5.8293 | 7 | 1.0006 | 10.0913 | 11.0919 | 10.4442 | 0.486 | 0.2362 | 3 | 5.8293 | 10.9345 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7006 | 91230.67 | 44266.9772 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 555.7068 | 0:240:120 | 0:00 | 5.4491 | 7 | 0.3303 | 8.7691 | 9.0994 | 8.9877 | 0.1634 | 0.0267 | 3 | 5.4491 | 9.8864 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7009 | 91260.823 | 44266.9775 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 565.8004 | 0:240:120 | 0:00 | 5.0148 | 7 | 0.3312 | 8.1092 | 8.4404 | 8.3281 | 0.1641 | 0.0269 | 3 | 5.0148 | 8.7703 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7012 | 91288.726 | 44266.9779 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 574.926 | 0:240:120 | 0:00 | 4.6724 | 7 | 0.3318 | 7.4494 | 7.7812 | 7.6677 | 0.1631 | 0.0266 | 3 | 4.6724 | 7.9455 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7015 | 91314.629 | 44266.9782 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 584.199 | 0:240:120 | 0:00 | 4.3647 | 7 | 0.3314 | 6.7908 | 7.1222 | 7.0054 | 0.1609 | 0.0259 | 3 | 4.3647 | 7.2422 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7018 | 91338.248 | 44266.9784 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 596.5971 | 0:240:120 | 0:00 | 4.0054 | 7 | 0.3313 | 5.8018 | 6.1331 | 6.022 | 0.1645 | 0.0271 | 3 | 4.0054 | 6.463 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7021 | 91359.35 | 44266.9787 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 609.8675 | 0:240:120 | 0:00 | 3.6746 | 7 | 0.1636 | 5.3133 | 5.4769 | 5.4215 | 0.081 | 0.0066 | 3 | 3.6746 | 5.7826 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7024 | 91378.688 | 44266.9789 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 622.1875 | 0:240:120 | 0:00 | 3.4078 | 7 | 0.3277 | 4.8233 | 5.151 | 4.9866 | 0.1414 | 0.02 | 3 | 3.4078 | 5.2578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7027 | 91397.082 | 44266.9791 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 636.6635 | 0:240:120 | 0:00 | 3.1345 | 7 | 0.3271 | 4.3344 | 4.6615 | 4.4973 | 0.141 | 0.0199 | 3 | 3.1345 | 4.7413 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7030 | 91413.712 | 44266.9793 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 650.1748 | 0:240:120 | 0:00 | 2.9117 | 7 | 0.1914 | 3.9792 | 4.1706 | 4.0749 | 0.0828 | 0.0069 | 3 | 2.9117 | 4.3349 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7033 | 91428.929 | 44266.9795 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 668.6372 | 0:240:120 | 0:00 | 2.6482 | 7 | 0.1941 | 3.5914 | 3.7855 | 3.6878 | 0.0839 | 0.007 | 3 | 2.6482 | 3.8704 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7036 | 91443.309 | 44266.9797 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 686.2493 | 0:240:120 | 0:00 | 2.4324 | 7 | 0.1956 | 3.2035 | 3.3991 | 3.3011 | 0.0839 | 0.007 | 3 | 2.4324 | 3.5026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7039 | 91456.63 | 44266.9798 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 704.3256 | 0:240:120 | 0:00 | 2.2401 | 7 | 0.1269 | 2.9503 | 3.0772 | 3.0151 | 0.0532 | 0.0028 | 3 | 2.2401 | 3.1838 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7042 | 91469.024 | 44266.9799 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 725.7756 | 0:240:120 | 0:00 | 2.043 | 7 | 0.065 | 2.6957 | 2.7607 | 2.7378 | 0.0308 | 0.001 | 3 | 2.043 | 2.8656 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7045 | 91480.273 | 44266.9801 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 744.8936 | 0:240:120 | 0:00 | 1.8906 | 7 | 0.0505 | 2.4736 | 2.5241 | 2.5066 | 0.0225 | 0.0005 | 3 | 1.8906 | 2.6251 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7048 | 91490.88 | 44266.9802 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 765.2799 | 0:240:120 | 0:00 | 1.7478 | 7 | 0.089 | 2.2542 | 2.3432 | 2.2985 | 0.038 | 0.0014 | 3 | 1.7478 | 2.4041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7051 | 91500.895 | 44266.9803 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 787.798 | 0:240:120 | 0:00 | 1.6096 | 7 | 0.0658 | 2.0534 | 2.1192 | 2.0856 | 0.0283 | 0.0008 | 3 | 1.6096 | 2.1943 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7054 | 91510.331 | 44266.9804 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 814.2288 | 0:240:120 | 0:00 | 1.4691 | 7 | 0.066 | 1.8551 | 1.9211 | 1.8931 | 0.0282 | 0.0008 | 3 | 1.4691 | 1.9847 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7057 | 91519.299 | 44266.9805 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 838.1868 | 0:240:120 | 0:00 | 1.3582 | 7 | 0.0512 | 1.7135 | 1.7647 | 1.7389 | 0.0213 | 0.0005 | 3 | 1.3582 | 1.8219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7060 | 91527.49 | 44266.9806 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 875.8904 | 0:240:120 | 0:00 | 1.2092 | 7 | 0.0448 | 1.5164 | 1.5612 | 1.5373 | 0.0194 | 0.0004 | 3 | 1.2092 | 1.6068 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7063 | 91535.347 | 44266.9807 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 912.5479 | 0:240:120 | 0:00 | 1.0881 | 7 | 0.0405 | 1.3561 | 1.3966 | 1.3754 | 0.017 | 0.0003 | 3 | 1.0881 | 1.4349 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7066 | 91543.081 | 44266.9808 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 950.7399 | 0:240:120 | 0:00 | 0.9814 | 7 | 0.0319 | 1.2238 | 1.2557 | 1.2391 | 0.0133 | 0.0002 | 3 | 0.9814 | 1.2856 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7069 | 91549.897 | 44266.9809 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 984.6056 | 0:240:120 | 0:00 | 0.9001 | 7 | 0.0261 | 1.1102 | 1.1363 | 1.126 | 0.0116 | 0.0001 | 3 | 0.9001 | 1.1732 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7072 | 91556.423 | 44266.981 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1022.7404 | 0:240:120 | 0:00 | 0.8207 | 7 | 0.0216 | 1.0117 | 1.0333 | 1.022 | 0.0091 | 0.0001 | 3 | 0.8207 | 1.0645 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7075 | 91562.656 | 44266.981 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1064.4788 | 0:240:120 | 0:00 | 0.7459 | 7 | 0.0179 | 0.917 | 0.9349 | 0.9251 | 0.0073 | 0.0001 | 3 | 0.7459 | 0.963 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7078 | 91568.689 | 44266.9811 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1106.809 | 0:240:120 | 0:00 | 0.6804 | 7 | 0.0209 | 0.8314 | 0.8523 | 0.8414 | 0.0087 | 0.0001 | 3 | 0.6804 | 0.8749 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7081 | 91574.369 | 44266.9812 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1162.392 | 0:240:120 | 0:00 | 0.6072 | 7 | 0.0206 | 0.7374 | 0.758 | 0.7481 | 0.0086 | 0.0001 | 3 | 0.6072 | 0.7774 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7084 | 91580.015 | 44266.9812 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1213.465 | 0:240:120 | 0:00 | 0.5503 | 7 | 0.0179 | 0.6674 | 0.6853 | 0.6756 | 0.0076 | 0.0001 | 3 | 0.5503 | 0.7021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7087 | 91585.124 | 44266.9813 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1260.468 | 0:240:120 | 0:00 | 0.505 | 7 | 0.0296 | 0.6012 | 0.6308 | 0.6179 | 0.009 | 0.0001 | 3 | 0.505 | 0.6424 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7090 | 91590.097 | 44266.9814 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1342.429 | 0:240:120 | 0:00 | 0.4386 | 7 | 0.0199 | 0.5253 | 0.5452 | 0.5352 | 0.0063 | 0 | 3 | 0.4386 | 0.5558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7093 | 91595.044 | 44266.9814 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1408.44 | 0:240:120 | 0:00 | 0.3945 | 7 | 0.0157 | 0.4713 | 0.487 | 0.4783 | 0.0055 | 0 | 3 | 0.3945 | 0.4986 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7096 | 91599.601 | 44266.9815 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1486.584 | 0:240:120 | 0:00 | 0.3506 | 7 | 0.0148 | 0.4185 | 0.4333 | 0.4254 | 0.0047 | 0 | 3 | 0.3506 | 0.4419 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7099 | 91604.158 | 44266.9815 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1586.42 | 0:240:120 | 0:00 | 0.3046 | 7 | 0.0131 | 0.3612 | 0.3743 | 0.3682 | 0.004 | 0 | 3 | 0.3046 | 0.3829 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7102 | 91608.766 | 44266.9816 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1677.797 | 0:240:120 | 0:00 | 0.2701 | 7 | 0.0094 | 0.3213 | 0.3307 | 0.3262 | 0.0033 | 0 | 3 | 0.2701 | 0.3389 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7105 | 91612.987 | 44266.9816 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1760.297 | 0:240:120 | 0:00 | 0.2439 | 7 | 0.0101 | 0.2899 | 0.3 | 0.2947 | 0.0035 | 0 | 3 | 0.2439 | 0.3055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7108 | 91617.121 | 44266.9817 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1846.856 | 0:240:120 | 0:00 | 0.2203 | 7 | 0.0064 | 0.2633 | 0.2697 | 0.2659 | 0.0023 | 0 | 3 | 0.2203 | 0.2756 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7111 | 91621.344 | 44266.9817 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1949.321 | 0:240:120 | 0:00 | 0.1967 | 7 | 0.0049 | 0.2351 | 0.24 | 0.2367 | 0.0018 | 0 | 3 | 0.1967 | 0.2457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7114 | 91625.147 | 44266.9818 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2065.723 | 0:240:120 | 0:00 | 0.1742 | 7 | 0.0061 | 0.207 | 0.2131 | 0.2095 | 0.0021 | 0 | 3 | 0.1742 | 0.2173 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7117 | 91629.391 | 44266.9818 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2202.255 | 0:240:120 | 0:00 | 0.1525 | 7 | 0.0062 | 0.1797 | 0.1859 | 0.1827 | 0.0021 | 0 | 3 | 0.1525 | 0.1899 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7120 | 91633.155 | 44266.9818 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2357.223 | 0:240:120 | 0:00 | 0.1324 | 7 | 0.0036 | 0.1579 | 0.1615 | 0.1591 | 0.0013 | 0 | 3 | 0.1324 | 0.1648 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7123 | 91636.662 | 44266.9819 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2510.497 | 0:240:120 | 0:00 | 0.1163 | 7 | 0.0027 | 0.1381 | 0.1408 | 0.1394 | 0.001 | 0 | 3 | 0.1163 | 0.1446 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7126 | 91640.286 | 44266.9819 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2689.841 | 0:240:120 | 0:00 | 0.1009 | 7 | 0.0034 | 0.12 | 0.1234 | 0.121 | 0.0012 | 0 | 3 | 0.1009 | 0.1254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7129 | 91643.937 | 44266.982 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2844.776 | 0:240:120 | 0:00 | 0.09 | 7 | 0.004 | 0.1061 | 0.1101 | 0.1078 | 0.0015 | 0 | 3 | 0.09 | 0.1117 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7132 | 91647.551 | 44266.982 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3023.702 | 0:240:120 | 0:00 | 0.0795 | 7 | 0.0033 | 0.094 | 0.0973 | 0.0956 | 0.0012 | 0 | 3 | 0.0795 | 0.0986 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7135 | 91651.052 | 44266.9821 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3194.664 | 0:240:120 | 0:00 | 0.071 | 7 | 0.0035 | 0.0837 | 0.0872 | 0.0854 | 0.0012 | 0 | 3 | 0.071 | 0.0881 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7138 | 91654.652 | 44266.9821 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3395.612 | 0:240:120 | 0:00 | 0.0627 | 7 | 0.0022 | 0.074 | 0.0762 | 0.0751 | 0.0007 | 0 | 3 | 0.0627 | 0.0778 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7141 | 91658.301 | 44266.9821 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3591.192 | 0:240:120 | 0:00 | 0.056 | 7 | 0.0028 | 0.0662 | 0.069 | 0.0675 | 0.0011 | 0 | 3 | 0.056 | 0.0694 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7144 | 91661.875 | 44266.9822 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3794.241 | 0:240:120 | 0:00 | 0.0501 | 7 | 0.0024 | 0.059 | 0.0614 | 0.0602 | 0.0008 | 0 | 3 | 0.0501 | 0.062 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7147 | 91665.534 | 44266.9822 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4012.778 | 0:240:120 | 0:00 | 0.0447 | 7 | 0.003 | 0.0526 | 0.0556 | 0.0541 | 0.0009 | 0 | 3 | 0.0447 | 0.0554 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7150 | 91669.186 | 44266.9823 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4252.402 | 0:240:120 | 0:00 | 0.0398 | 7 | 0.0031 | 0.0469 | 0.05 | 0.0484 | 0.001 | 0 | 3 | 0.0398 | 0.0498 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
7153 | 91672.835 | 44266.9823 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4470.422 | 0:240:120 | 0:00 | 0.036 | 7 | 0.0025 | 0.0426 | 0.0451 | 0.0441 | 0.0009 | 0 | 3 | 0.036 | 0.046 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7156 | 91676.543 | 44266.9824 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4709.034 | 0:240:120 | 0:00 | 0.0324 | 7 | 0.0028 | 0.0383 | 0.0411 | 0.0399 | 0.001 | 0 | 3 | 0.0324 | 0.0424 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7159 | 91679.942 | 44266.9824 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4960.384 | 0:240:120 | 0:00 | 0.0292 | 7 | 0.0024 | 0.0345 | 0.0369 | 0.036 | 0.0008 | 0 | 3 | 0.0292 | 0.0392 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7162 | 91683.586 | 44266.9824 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5239.22 | 0:240:120 | 0:00 | 0.0261 | 7 | 0.0042 | 0.0299 | 0.0341 | 0.0328 | 0.0014 | 0 | 3 | 0.0261 | 0.0361 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7165 | 91686.973 | 44266.9825 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5546.53 | 0:240:120 | 0:00 | 0.0233 | 7 | 0.0036 | 0.0276 | 0.0312 | 0.0294 | 0.0011 | 0 | 3 | 0.0233 | 0.0333 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7168 | 91690.287 | 44266.9825 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5830.91 | 0:240:120 | 0:00 | 0.0211 | 7 | 0.003 | 0.0254 | 0.0284 | 0.027 | 0.0012 | 0 | 3 | 0.0211 | 0.0311 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7171 | 91693.791 | 44266.9826 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6142.14 | 0:240:120 | 0:00 | 0.019 | 7 | 0.0032 | 0.0231 | 0.0263 | 0.025 | 0.0011 | 0 | 3 | 0.019 | 0.029 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7174 | 91697.351 | 44266.9826 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6418.43 | 0:240:120 | 0:00 | 0.0174 | 7 | 0.003 | 0.0216 | 0.0246 | 0.0232 | 0.0011 | 0 | 3 | 0.0174 | 0.0274 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7177 | 91700.935 | 44266.9826 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6788.11 | 0:240:120 | 0:00 | 0.0155 | 7 | 0.0037 | 0.0196 | 0.0233 | 0.0214 | 0.0012 | 0 | 3 | 0.0155 | 0.0255 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7180 | 91704.706 | 44266.9827 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7058.08 | 0:240:120 | 0:00 | 0.0144 | 7 | 0.0028 | 0.0186 | 0.0214 | 0.0204 | 0.0013 | 0 | 3 | 0.0144 | 0.0244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7183 | 91708.383 | 44266.9827 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7397.73 | 0:240:120 | 0:00 | 0.0131 | 7 | 0.0041 | 0.0175 | 0.0216 | 0.0195 | 0.0014 | 0 | 3 | 0.0131 | 0.0231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7186 | 91711.64 | 44266.9828 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7691.94 | 0:240:120 | 0:00 | 0.0121 | 7 | 0.003 | 0.0176 | 0.0206 | 0.0184 | 0.0012 | 0 | 3 | 0.0121 | 0.0221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7189 | 91714.945 | 44266.9828 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8005.85 | 0:240:120 | 0:00 | 0.0111 | 7 | 0.0011 | 0.0175 | 0.0186 | 0.0181 | 0.0006 | 0 | 3 | 0.0111 | 0.0211 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7192 | 91718.267 | 44266.9828 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8299.31 | 0:240:120 | 0:00 | 0.0104 | 7 | 0.0016 | 0.0165 | 0.0181 | 0.0174 | 0.0006 | 0 | 3 | 0.0104 | 0.0204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7195 | 91721.993 | 44266.9829 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8509.41 | 0:240:120 | 0:00 | 0.0099 | 7 | 0.0001 | 0.0169 | 0.017 | 0.017 | 0.0001 | 0 | 3 | 0.0099 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7198 | 91725.977 | 44266.9829 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8724.83 | 0:240:120 | 0:00 | 0.0094 | 7 | 0.0028 | 0.015 | 0.0178 | 0.0161 | 0.0009 | 0 | 3 | 0.0094 | 0.016 | NP | NP | 1-1-0-1-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
7201 | 91729.39 | 44266.983 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9157.6095 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0037 | 0.0135 | 0.0172 | 0.0154 | 0.0012 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
7204 | 91732.916 | 44266.983 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10302.3106 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0052 | 0.0111 | 0.0163 | 0.0137 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7207 | 91736.502 | 44266.983 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11447.0118 | 0:240:120 | 0:00 | 0.0054 | 7 | 0.0043 | 0.0109 | 0.0152 | 0.0131 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7210 | 91866.45 | 44266.9845 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 483.1 | 0:240:120 | 0:00 | 12.8809 | 7 | 18.1478 | 108.8922 | 127.04 | 114.9986 | 8.9579 | 80.2437 | 3 | 12.8809 | 65.004 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7213 | 92230.048 | 44266.9888 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 489 | 0:240:120 | 0:00 | 11.6706 | 7 | 20.7978 | 85.6009 | 106.3987 | 95.2477 | 8.3401 | 69.5575 | 3 | 11.6706 | 45.6508 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7216 | 92518.224 | 44266.9921 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 495.6 | 0:240:120 | 0:00 | 10.5476 | 7 | 17.9988 | 55.0508 | 73.0496 | 67.0478 | 8.9971 | 80.9469 | 3 | 10.5476 | 34.1358 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7219 | 92722.397 | 44266.9945 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 502.6 | 0:240:120 | 0:00 | 9.5586 | 7 | 18.3757 | 36.6761 | 55.0518 | 42.9995 | 9.0393 | 81.7083 | 3 | 9.5586 | 26.8528 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7222 | 92854.626 | 44266.996 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 510.7 | 0:240:120 | 0:00 | 8.6103 | 7 | 0.9958 | 18.0622 | 19.058 | 18.6948 | 0.4759 | 0.2265 | 3 | 8.6103 | 21.4716 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7225 | 92913.019 | 44266.9967 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 518.9 | 0:240:120 | 0:00 | 7.813 | 7 | 0.9959 | 16.0698 | 17.0657 | 16.733 | 0.497 | 0.247 | 3 | 7.813 | 17.802 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7228 | 92965.526 | 44266.9973 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 526.8 | 0:240:120 | 0:00 | 7.1639 | 7 | 0.9968 | 14.0772 | 15.074 | 14.7405 | 0.4971 | 0.2471 | 3 | 7.1639 | 15.2516 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7231 | 93012.975 | 44266.9978 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 534.5 | 0:240:120 | 0:00 | 6.6198 | 7 | 1.0073 | 13.0712 | 14.0785 | 13.4114 | 0.4997 | 0.2497 | 3 | 6.6198 | 13.3584 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7234 | 93056.299 | 44266.9983 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 543.1 | 0:240:120 | 0:00 | 6.0949 | 7 | 0.9962 | 11.0903 | 12.0865 | 11.4845 | 0.4618 | 0.2133 | 3 | 6.0949 | 11.71 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7237 | 93093.799 | 44266.9988 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 551.8 | 0:240:120 | 0:00 | 5.6356 | 7 | 0.9977 | 9.0967 | 10.0944 | 9.7609 | 0.4972 | 0.2472 | 3 | 5.6356 | 10.3919 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7240 | 93126.025 | 44266.9991 | Vista Speed | E | 175E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 560.8 | 0:240:120 | 0:00 | 5.2219 | 7 | 0.3302 | 8.4392 | 8.7694 | 8.6584 | 0.1642 | 0.027 | 3 | 5.2219 | 9.2924 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7243 | 93414.894 | 44267.0025 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 528 | 0:240:120 | 0:00 | 20.5112 | 7 | 0.0158 | 199.031 | 199.0468 | 199.0405 | 0.0053 | 0 | 3 | 20.5112 | 9999999 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7246 | 94150.57 | 44267.011 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 529.65 | 0:240:120 | 0:00 | 19.7535 | 7 | 18.0039 | 181.0397 | 199.0436 | 193.0416 | 8.9998 | 80.9964 | 3 | 19.7535 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7249 | 94750.628 | 44267.0179 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 532.4 | 0:240:120 | 0:00 | 18.6033 | 7 | 18.0096 | 181.0327 | 199.0423 | 187.0683 | 8.9783 | 80.6099 | 3 | 18.6033 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7252 | 95333.087 | 44267.0247 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 536.5943 | 0:240:120 | 0:00 | 17.0769 | 7 | 18.003 | 163.0395 | 181.0425 | 175.0399 | 8.9997 | 80.9942 | 3 | 17.0769 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7255 | 95861.727 | 44267.0308 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 540.9041 | 0:240:120 | 0:00 | 15.7393 | 7 | 18.0017 | 145.0391 | 163.0408 | 157.0393 | 8.9984 | 80.9718 | 3 | 15.7393 | 252.3019 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7258 | 96336.281 | 44267.0363 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 546.887 | 0:240:120 | 0:00 | 14.1825 | 7 | 18.0062 | 127.0378 | 145.044 | 139.0393 | 9.0003 | 81.0051 | 3 | 14.1825 | 104.0288 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7261 | 96756.706 | 44267.0411 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 554.0425 | 0:240:120 | 0:00 | 12.666 | 7 | 18.0022 | 109.0385 | 127.0407 | 115.0404 | 8.999 | 80.9825 | 3 | 12.666 | 60.7875 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7264 | 97105.19 | 44267.0452 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 561.8536 | 0:240:120 | 0:00 | 11.326 | 7 | 17.9957 | 73.0493 | 91.045 | 85.0453 | 8.9957 | 80.9226 | 3 | 11.326 | 41.6376 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7267 | 97345.768 | 44267.048 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 572.0583 | 0:240:120 | 0:00 | 9.9312 | 7 | 17.9983 | 37.0548 | 55.0531 | 49.0509 | 8.9968 | 80.9424 | 3 | 9.9312 | 29.3592 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7270 | 97478.428 | 44267.0495 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 583.6149 | 0:240:120 | 0:00 | 8.6953 | 7 | 0.9957 | 18.0607 | 19.0564 | 18.724 | 0.4968 | 0.2468 | 3 | 8.6953 | 21.904 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7273 | 97536.664 | 44267.0502 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 596.0009 | 0:240:120 | 0:00 | 7.6533 | 7 | 1.0032 | 16.0621 | 17.0653 | 16.3986 | 0.4995 | 0.2495 | 3 | 7.6533 | 17.142 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7276 | 97588.17 | 44267.0508 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 611.0885 | 0:240:120 | 0:00 | 6.6587 | 7 | 0.9965 | 13.0818 | 14.0783 | 13.4195 | 0.4939 | 0.2439 | 3 | 6.6587 | 13.4871 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7279 | 97630.808 | 44267.0513 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 625.306 | 0:240:120 | 0:00 | 5.9166 | 7 | 0.9984 | 10.0926 | 11.091 | 10.7574 | 0.4972 | 0.2472 | 3 | 5.9166 | 11.1853 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7282 | 97665.065 | 44267.0517 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 643.0622 | 0:240:120 | 0:00 | 5.1773 | 7 | 0.3424 | 8.4274 | 8.7698 | 8.5464 | 0.1666 | 0.0277 | 3 | 5.1773 | 9.1783 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7285 | 97693.416 | 44267.052 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 664.6376 | 0:240:120 | 0:00 | 4.4766 | 7 | 0.6584 | 6.7927 | 7.4511 | 7.13 | 0.2741 | 0.0751 | 3 | 4.4766 | 7.4938 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7288 | 97717.695 | 44267.0523 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 681.4621 | 0:240:120 | 0:00 | 4.0379 | 7 | 0.5401 | 5.8025 | 6.3426 | 6.0758 | 0.2176 | 0.0473 | 3 | 4.0379 | 6.5316 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7291 | 97738.853 | 44267.0525 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 695.9249 | 0:240:120 | 0:00 | 3.7174 | 7 | 0.3232 | 5.3175 | 5.6407 | 5.4839 | 0.132 | 0.0174 | 3 | 3.7174 | 5.8688 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7294 | 97758.555 | 44267.0527 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 715.6853 | 0:240:120 | 0:00 | 3.3456 | 7 | 0.1643 | 4.823 | 4.9873 | 4.9284 | 0.0792 | 0.0063 | 3 | 3.3456 | 5.1386 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7297 | 97776.394 | 44267.053 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 739.6972 | 0:240:120 | 0:00 | 2.9731 | 7 | 0.1539 | 4.0749 | 4.2288 | 4.1487 | 0.0582 | 0.0034 | 3 | 2.9731 | 4.4456 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7300 | 97791.722 | 44267.0531 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 764.5143 | 0:240:120 | 0:00 | 2.6571 | 7 | 0.1941 | 3.5914 | 3.7855 | 3.6879 | 0.0837 | 0.007 | 3 | 2.6571 | 3.8859 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7303 | 97805.801 | 44267.0533 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 791.7459 | 0:240:120 | 0:00 | 2.371 | 7 | 0.1599 | 3.141 | 3.3009 | 3.2147 | 0.0697 | 0.0049 | 3 | 2.371 | 3.3999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7306 | 97818.828 | 44267.0534 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 818.3098 | 0:240:120 | 0:00 | 2.1386 | 7 | 0.1284 | 2.8228 | 2.9512 | 2.8859 | 0.0548 | 0.003 | 3 | 2.1386 | 3.0188 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7309 | 97830.442 | 44267.0536 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 849.1549 | 0:240:120 | 0:00 | 1.9131 | 7 | 0.0894 | 2.4781 | 2.5675 | 2.5227 | 0.0382 | 0.0015 | 3 | 1.9131 | 2.6603 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7312 | 97841.132 | 44267.0537 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 875.0148 | 0:240:120 | 0:00 | 1.7529 | 7 | 0.09 | 2.2541 | 2.3441 | 2.2989 | 0.0382 | 0.0015 | 3 | 1.7529 | 2.412 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7315 | 97850.909 | 44267.0538 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 906.1833 | 0:240:120 | 0:00 | 1.5873 | 7 | 0.0655 | 2.0204 | 2.0859 | 2.0535 | 0.028 | 0.0008 | 3 | 1.5873 | 2.1608 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7318 | 97860.413 | 44267.0539 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 942.2226 | 0:240:120 | 0:00 | 1.4258 | 7 | 0.0583 | 1.7965 | 1.8548 | 1.8358 | 0.0267 | 0.0007 | 3 | 1.4258 | 1.9208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7321 | 97869.074 | 44267.054 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 981.6565 | 0:240:120 | 0:00 | 1.2777 | 7 | 0.0512 | 1.6123 | 1.6635 | 1.6377 | 0.0215 | 0.0005 | 3 | 1.2777 | 1.7051 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7324 | 97877.146 | 44267.0541 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1025.8127 | 0:240:120 | 0:00 | 1.1394 | 7 | 0.028 | 1.4276 | 1.4556 | 1.4463 | 0.0129 | 0.0002 | 3 | 1.1394 | 1.5074 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7327 | 97884.547 | 44267.0542 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1070.8852 | 0:240:120 | 0:00 | 1.0215 | 7 | 0.0325 | 1.2715 | 1.304 | 1.2873 | 0.0137 | 0.0002 | 3 | 1.0215 | 1.3415 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7330 | 97891.302 | 44267.0543 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1116.819 | 0:240:120 | 0:00 | 0.9203 | 7 | 0.0267 | 1.1364 | 1.1631 | 1.1514 | 0.0112 | 0.0001 | 3 | 0.9203 | 1.201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7333 | 97897.811 | 44267.0544 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1171.731 | 0:240:120 | 0:00 | 0.8188 | 7 | 0.0209 | 1.0123 | 1.0332 | 1.022 | 0.0089 | 0.0001 | 3 | 0.8188 | 1.0618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7336 | 97904.029 | 44267.0544 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1230.57 | 0:240:120 | 0:00 | 0.7285 | 7 | 0.0345 | 0.8807 | 0.9152 | 0.8988 | 0.0126 | 0.0002 | 3 | 0.7285 | 0.9395 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7339 | 97910.428 | 44267.0545 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1296.262 | 0:240:120 | 0:00 | 0.6449 | 7 | 0.0326 | 0.7787 | 0.8113 | 0.7951 | 0.0095 | 0.0001 | 3 | 0.6449 | 0.8274 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7342 | 97916.35 | 44267.0546 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1353.209 | 0:240:120 | 0:00 | 0.584 | 7 | 0.0242 | 0.7034 | 0.7276 | 0.7167 | 0.0083 | 0.0001 | 3 | 0.584 | 0.7465 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7345 | 97921.434 | 44267.0546 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1419.748 | 0:240:120 | 0:00 | 0.5235 | 7 | 0.0218 | 0.6292 | 0.651 | 0.6407 | 0.0085 | 0.0001 | 3 | 0.5235 | 0.6668 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7348 | 97926.649 | 44267.0547 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1485.099 | 0:240:120 | 0:00 | 0.4731 | 7 | 0.0186 | 0.5678 | 0.5864 | 0.578 | 0.0059 | 0 | 3 | 0.4731 | 0.6008 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7351 | 97931.588 | 44267.0547 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1558.128 | 0:240:120 | 0:00 | 0.4252 | 7 | 0.0179 | 0.5074 | 0.5253 | 0.516 | 0.0058 | 0 | 3 | 0.4252 | 0.5384 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7354 | 97936.324 | 44267.0548 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1633.104 | 0:240:120 | 0:00 | 0.3834 | 7 | 0.0151 | 0.456 | 0.4711 | 0.4649 | 0.0044 | 0 | 3 | 0.3834 | 0.4843 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7357 | 97941.107 | 44267.0549 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1734.084 | 0:240:120 | 0:00 | 0.3364 | 7 | 0.0138 | 0.4006 | 0.4144 | 0.4076 | 0.0048 | 0 | 3 | 0.3364 | 0.4237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7360 | 97945.79 | 44267.0549 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1833.964 | 0:240:120 | 0:00 | 0.2981 | 7 | 0.0112 | 0.3555 | 0.3667 | 0.3613 | 0.0035 | 0 | 3 | 0.2981 | 0.3746 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7363 | 97950.008 | 44267.055 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2000.669 | 0:240:120 | 0:00 | 0.2476 | 7 | 0.0095 | 0.2935 | 0.303 | 0.2978 | 0.0035 | 0 | 3 | 0.2476 | 0.3101 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7366 | 97954.463 | 44267.055 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2195.655 | 0:240:120 | 0:00 | 0.2034 | 7 | 0.0076 | 0.2405 | 0.2481 | 0.2442 | 0.0028 | 0 | 3 | 0.2034 | 0.2542 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7369 | 97958.539 | 44267.0551 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2392.841 | 0:240:120 | 0:00 | 0.1699 | 7 | 0.0043 | 0.2016 | 0.2059 | 0.2035 | 0.0015 | 0 | 3 | 0.1699 | 0.2119 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7372 | 97962.245 | 44267.0551 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2668.413 | 0:240:120 | 0:00 | 0.1355 | 7 | 0.0048 | 0.1607 | 0.1655 | 0.1628 | 0.0016 | 0 | 3 | 0.1355 | 0.1686 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7375 | 97966.097 | 44267.0551 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2910.963 | 0:240:120 | 0:00 | 0.1132 | 7 | 0.0032 | 0.1339 | 0.1371 | 0.1358 | 0.001 | 0 | 3 | 0.1132 | 0.1407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7378 | 97969.656 | 44267.0552 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3169.21 | 0:240:120 | 0:00 | 0.0951 | 7 | 0.0039 | 0.1121 | 0.116 | 0.1137 | 0.0014 | 0 | 3 | 0.0951 | 0.1181 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7381 | 97973.031 | 44267.0552 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3440.041 | 0:240:120 | 0:00 | 0.0804 | 7 | 0.0029 | 0.0952 | 0.0981 | 0.0966 | 0.001 | 0 | 3 | 0.0804 | 0.0998 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7384 | 97976.806 | 44267.0553 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3798.036 | 0:240:120 | 0:00 | 0.0658 | 7 | 0.0034 | 0.0777 | 0.0811 | 0.0793 | 0.0012 | 0 | 3 | 0.0658 | 0.0815 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7387 | 97980.515 | 44267.0553 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4189.086 | 0:240:120 | 0:00 | 0.0539 | 7 | 0.004 | 0.0622 | 0.0662 | 0.0644 | 0.0013 | 0 | 3 | 0.0539 | 0.0667 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7390 | 97984.035 | 44267.0554 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4737.37 | 0:240:120 | 0:00 | 0.042 | 7 | 0.003 | 0.0495 | 0.0525 | 0.0514 | 0.0013 | 0 | 3 | 0.042 | 0.052 | P | NP | 0-1-0-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
7393 | 97987.522 | 44267.0554 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5235.604 | 0:240:120 | 0:00 | 0.0343 | 7 | 0.0029 | 0.0401 | 0.043 | 0.0415 | 0.0009 | 0 | 3 | 0.0343 | 0.0443 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7396 | 97990.69 | 44267.0554 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5825.08 | 0:240:120 | 0:00 | 0.0277 | 7 | 0.0033 | 0.0319 | 0.0352 | 0.034 | 0.0012 | 0 | 3 | 0.0277 | 0.0377 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7399 | 97994.262 | 44267.0555 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6444.15 | 0:240:120 | 0:00 | 0.0226 | 7 | 0.0021 | 0.0271 | 0.0292 | 0.0285 | 0.0008 | 0 | 3 | 0.0226 | 0.0326 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7402 | 97997.486 | 44267.0555 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7086.37 | 0:240:120 | 0:00 | 0.0187 | 7 | 0.0036 | 0.0225 | 0.0261 | 0.0242 | 0.0011 | 0 | 3 | 0.0187 | 0.0287 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7405 | 98000.987 | 44267.0556 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7792.59 | 0:240:120 | 0:00 | 0.0154 | 7 | 0.004 | 0.0189 | 0.0229 | 0.0212 | 0.0012 | 0 | 3 | 0.0154 | 0.0254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7408 | 98004.321 | 44267.0556 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8475.44 | 0:240:120 | 0:00 | 0.013 | 7 | 0.0037 | 0.0177 | 0.0214 | 0.0192 | 0.0012 | 0 | 3 | 0.013 | 0.023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7411 | 98008.258 | 44267.0556 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9135.54 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.0024 | 0.0172 | 0.0196 | 0.0181 | 0.0008 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7414 | 98011.649 | 44267.0557 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9527.41 | 0:240:120 | 0:00 | 0.0103 | 7 | 0.0016 | 0.0164 | 0.018 | 0.0173 | 0.0005 | 0 | 3 | 0.0103 | 0.0203 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7417 | 98015.138 | 44267.0557 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10000 | 0:240:120 | 0:00 | 0.0094 | 7 | 0.0017 | 0.0153 | 0.017 | 0.0163 | 0.0007 | 0 | 3 | 0.0094 | 0.016 | NP | NP | 1-0-0-1-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
7420 | 98018.99 | 44267.0558 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11250 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0034 | 0.0126 | 0.016 | 0.0143 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7423 | 98149.553 | 44267.0573 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 550.5 | 0:240:120 | 0:00 | 13.3764 | 7 | 18.0003 | 109.0417 | 127.042 | 121.0386 | 8.9967 | 80.9399 | 3 | 13.3764 | 76.6031 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7426 | 98516.132 | 44267.0615 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 557.9 | 0:240:120 | 0:00 | 11.9692 | 7 | 18.003 | 91.0418 | 109.0448 | 102.6555 | 8.7287 | 76.1906 | 3 | 11.9692 | 49.5688 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7429 | 98810.726 | 44267.0649 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 567 | 0:240:120 | 0:00 | 10.58 | 7 | 18.0002 | 55.0516 | 73.0518 | 67.0493 | 8.9975 | 80.9543 | 3 | 10.58 | 34.4121 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7432 | 98997.078 | 44267.0671 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 577.8 | 0:240:120 | 0:00 | 9.2792 | 7 | 17.9969 | 19.0573 | 37.0542 | 31.0531 | 8.9968 | 80.9424 | 3 | 9.2792 | 25.1309 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7435 | 99092.38 | 44267.0682 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 589.8 | 0:240:120 | 0:00 | 8.1445 | 7 | 0.9968 | 17.0652 | 18.062 | 17.6025 | 0.437 | 0.1909 | 3 | 8.1445 | 19.2479 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7438 | 99146.805 | 44267.0688 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 603.5 | 0:240:120 | 0:00 | 7.1275 | 7 | 0.9967 | 14.078 | 15.0747 | 14.7417 | 0.4969 | 0.2469 | 3 | 7.1275 | 15.1185 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7441 | 99192.327 | 44267.0693 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 618.2 | 0:240:120 | 0:00 | 6.2677 | 7 | 1.4977 | 11.0915 | 12.5892 | 11.8112 | 0.563 | 0.317 | 3 | 6.2677 | 12.2349 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7444 | 99229.471 | 44267.0698 | Vista Speed | E | 200E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 634.2 | 0:240:120 | 0:00 | 5.5242 | 7 | 0.33 | 8.7687 | 9.0987 | 8.9879 | 0.1639 | 0.0269 | 3 | 5.5242 | 10.0881 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7447 | 99451.64 | 44267.0723 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 641.7774 | 0:240:120 | 0:00 | 18.8855 | 7 | 18.0028 | 181.0399 | 199.0427 | 191.2531 | 8.0364 | 64.5831 | 3 | 18.8855 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7450 | 100016.106 | 44267.0789 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 650.8249 | 0:240:120 | 0:00 | 16.2463 | 7 | 18.0166 | 145.0432 | 163.0598 | 157.0478 | 8.9999 | 80.9975 | 3 | 16.2463 | 424.1758 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7453 | 100472.515 | 44267.0842 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 667.3007 | 0:240:120 | 0:00 | 12.8989 | 7 | 17.9975 | 109.0431 | 127.0406 | 116.955 | 7.9804 | 63.6871 | 3 | 12.8989 | 65.3756 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7456 | 100803.08 | 44267.088 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 685.564 | 0:240:120 | 0:00 | 10.4494 | 7 | 17.9998 | 55.0523 | 73.0521 | 67.0489 | 8.9968 | 80.9418 | 3 | 10.4494 | 33.3148 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7459 | 100971.415 | 44267.0899 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 706.442 | 0:240:120 | 0:00 | 8.5415 | 7 | 0.9987 | 18.0581 | 19.0568 | 18.3927 | 0.4978 | 0.2478 | 3 | 8.5415 | 21.1276 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7462 | 101027.078 | 44267.0906 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 734.5371 | 0:240:120 | 0:00 | 6.8095 | 7 | 0.9964 | 13.0809 | 14.0773 | 13.7443 | 0.4969 | 0.2469 | 3 | 6.8095 | 13.9955 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7465 | 101068.561 | 44267.0911 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 763.7509 | 0:240:120 | 0:00 | 5.5851 | 7 | 1.0502 | 9.0453 | 10.0955 | 9.4176 | 0.5077 | 0.2578 | 3 | 5.5851 | 10.2533 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7468 | 101100.062 | 44267.0914 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 790.1641 | 0:240:120 | 0:00 | 4.7793 | 7 | 0.6615 | 7.449 | 8.1105 | 7.7797 | 0.2858 | 0.0817 | 3 | 4.7793 | 8.1979 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7471 | 101125.967 | 44267.0917 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 815.859 | 0:240:120 | 0:00 | 4.1738 | 7 | 0.6514 | 6.1326 | 6.784 | 6.4385 | 0.2588 | 0.067 | 3 | 4.1738 | 6.8228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7474 | 101147.985 | 44267.092 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 843.2314 | 0:240:120 | 0:00 | 3.6631 | 7 | 0.1651 | 5.3121 | 5.4772 | 5.4216 | 0.0814 | 0.0066 | 3 | 3.6631 | 5.7595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7477 | 101166.986 | 44267.0922 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 869.781 | 0:240:120 | 0:00 | 3.2632 | 7 | 0.1642 | 4.6603 | 4.8245 | 4.7691 | 0.081 | 0.0066 | 3 | 3.2632 | 4.982 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7480 | 101184.328 | 44267.0924 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 893.585 | 0:240:120 | 0:00 | 2.9645 | 7 | 0.0967 | 4.0753 | 4.172 | 4.139 | 0.0474 | 0.0022 | 3 | 2.9645 | 4.4301 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7483 | 101199.589 | 44267.0926 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 920.7979 | 0:240:120 | 0:00 | 2.6764 | 7 | 0.099 | 3.6873 | 3.7863 | 3.7527 | 0.0482 | 0.0023 | 3 | 2.6764 | 3.9193 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7486 | 101213.606 | 44267.0927 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 946.9449 | 0:240:120 | 0:00 | 2.4417 | 7 | 0.0975 | 3.3015 | 3.399 | 3.3358 | 0.0472 | 0.0022 | 3 | 2.4417 | 3.5181 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7489 | 101226.361 | 44267.0929 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 988.5513 | 0:240:120 | 0:00 | 2.1332 | 7 | 0.0831 | 2.8227 | 2.9058 | 2.8688 | 0.0351 | 0.0012 | 3 | 2.1332 | 3.0101 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7492 | 101237.898 | 44267.093 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1026.8401 | 0:240:120 | 0:00 | 1.9028 | 7 | 0.0588 | 2.4781 | 2.5369 | 2.5109 | 0.0247 | 0.0006 | 3 | 1.9028 | 2.6441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7495 | 101247.989 | 44267.0931 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1094.7057 | 0:240:120 | 0:00 | 1.5837 | 7 | 0.0663 | 2.0204 | 2.0867 | 2.0526 | 0.0284 | 0.0008 | 3 | 1.5837 | 2.1553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7498 | 101257.238 | 44267.0932 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1170.554 | 0:240:120 | 0:00 | 1.3196 | 7 | 0.0506 | 1.6633 | 1.7139 | 1.688 | 0.0215 | 0.0005 | 3 | 1.3196 | 1.7657 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7501 | 101265.237 | 44267.0933 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1274.405 | 0:240:120 | 0:00 | 1.0587 | 7 | 0.0421 | 1.3043 | 1.3464 | 1.3259 | 0.016 | 0.0003 | 3 | 1.0587 | 1.3935 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7504 | 101272.454 | 44267.0934 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1365.452 | 0:240:120 | 0:00 | 0.8918 | 7 | 0.0485 | 1.0848 | 1.1333 | 1.1094 | 0.0169 | 0.0003 | 3 | 0.8918 | 1.1617 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7507 | 101279.056 | 44267.0935 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1500.026 | 0:240:120 | 0:00 | 0.7117 | 7 | 0.0329 | 0.8605 | 0.8934 | 0.8782 | 0.0111 | 0.0001 | 3 | 0.7117 | 0.917 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7510 | 101285.023 | 44267.0936 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1652.816 | 0:240:120 | 0:00 | 0.5684 | 7 | 0.0252 | 0.6833 | 0.7085 | 0.696 | 0.0092 | 0.0001 | 3 | 0.5684 | 0.7259 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7513 | 101290.034 | 44267.0936 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1837.638 | 0:240:120 | 0:00 | 0.4477 | 7 | 0.0226 | 0.5321 | 0.5547 | 0.5445 | 0.0077 | 0.0001 | 3 | 0.4477 | 0.5676 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7516 | 101294.715 | 44267.0937 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2080.243 | 0:240:120 | 0:00 | 0.341 | 7 | 0.0129 | 0.4046 | 0.4175 | 0.4107 | 0.0042 | 0 | 3 | 0.341 | 0.4295 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7519 | 101299.198 | 44267.0937 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2331.428 | 0:240:120 | 0:00 | 0.2668 | 7 | 0.009 | 0.3178 | 0.3268 | 0.3215 | 0.0032 | 0 | 3 | 0.2668 | 0.3346 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7522 | 101303.327 | 44267.0938 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2633.95 | 0:240:120 | 0:00 | 0.2061 | 7 | 0.0071 | 0.2437 | 0.2508 | 0.2472 | 0.0026 | 0 | 3 | 0.2061 | 0.2575 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7525 | 101307.143 | 44267.0938 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3057.153 | 0:240:120 | 0:00 | 0.151 | 7 | 0.0034 | 0.1794 | 0.1828 | 0.1806 | 0.0012 | 0 | 3 | 0.151 | 0.188 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7528 | 101310.654 | 44267.0939 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3474.614 | 0:240:120 | 0:00 | 0.1159 | 7 | 0.0038 | 0.1372 | 0.141 | 0.139 | 0.0014 | 0 | 3 | 0.1159 | 0.144 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7531 | 101314.254 | 44267.0939 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4045.008 | 0:240:120 | 0:00 | 0.0849 | 7 | 0.0029 | 0.1001 | 0.103 | 0.1015 | 0.0011 | 0 | 3 | 0.0849 | 0.1053 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7534 | 101317.835 | 44267.0939 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4723.18 | 0:240:120 | 0:00 | 0.0619 | 7 | 0.0017 | 0.0734 | 0.0751 | 0.0744 | 0.0008 | 0 | 3 | 0.0619 | 0.0767 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7537 | 101321.453 | 44267.094 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5570.488 | 0:240:120 | 0:00 | 0.0443 | 7 | 0.0037 | 0.0513 | 0.055 | 0.0536 | 0.0012 | 0 | 3 | 0.0443 | 0.0548 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7540 | 101324.684 | 44267.094 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6343.832 | 0:240:120 | 0:00 | 0.0341 | 7 | 0.0031 | 0.0399 | 0.043 | 0.042 | 0.0014 | 0 | 3 | 0.0341 | 0.0441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7543 | 101328.176 | 44267.0941 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7564.623 | 0:240:120 | 0:00 | 0.0239 | 7 | 0.0035 | 0.0279 | 0.0314 | 0.03 | 0.0012 | 0 | 3 | 0.0239 | 0.0339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7546 | 101331.675 | 44267.0941 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8649.344 | 0:240:120 | 0:00 | 0.0183 | 7 | 0.0031 | 0.0223 | 0.0254 | 0.0241 | 0.0013 | 0 | 3 | 0.0183 | 0.0283 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7549 | 101334.928 | 44267.0941 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10129.812 | 0:240:120 | 0:00 | 0.0133 | 7 | 0.0041 | 0.0177 | 0.0218 | 0.0196 | 0.0015 | 0 | 3 | 0.0133 | 0.0233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7552 | 101338.198 | 44267.0942 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11409.86 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0011 | 0.0168 | 0.0179 | 0.0174 | 0.0003 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7555 | 101432.649 | 44267.0953 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 676.4 | 0:240:120 | 0:00 | 11.5581 | 7 | 17.9983 | 73.0481 | 91.0464 | 85.0445 | 8.9963 | 80.933 | 3 | 11.5581 | 44.2856 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7558 | 101655.082 | 44267.0978 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 696 | 0:240:120 | 0:00 | 9.4069 | 7 | 17.9984 | 19.0562 | 37.0546 | 31.0537 | 8.9972 | 80.9498 | 3 | 9.4069 | 25.9022 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7561 | 101748.577 | 44267.0989 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 720.5 | 0:240:120 | 0:00 | 7.5855 | 7 | 1.2488 | 15.0735 | 16.3223 | 15.7649 | 0.5244 | 0.275 | 3 | 7.5855 | 16.8683 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7564 | 101796.442 | 44267.0995 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 749.1 | 0:240:120 | 0:00 | 6.1446 | 7 | 0.9962 | 11.0901 | 12.0863 | 11.7527 | 0.4969 | 0.2469 | 3 | 6.1446 | 11.859 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7567 | 101832.558 | 44267.0999 | Vista Speed | E | 250E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 777 | 0:240:120 | 0:00 | 5.153 | 7 | 0.6604 | 8.1085 | 8.7689 | 8.4384 | 0.2852 | 0.0814 | 3 | 5.153 | 9.1165 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7570 | 102053.62 | 44267.1025 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 757.6646 | 0:240:120 | 0:00 | 19.116 | 7 | 18.0036 | 181.0385 | 199.0421 | 193.0341 | 8.9954 | 80.9172 | 3 | 19.116 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7573 | 102653.874 | 44267.1094 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 759.9416 | 0:240:120 | 0:00 | 18.4734 | 7 | 18.0035 | 181.0371 | 199.0406 | 187.0396 | 9 | 80.9997 | 3 | 18.4734 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7576 | 103236.194 | 44267.1161 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 764.5143 | 0:240:120 | 0:00 | 17.3002 | 7 | 18.0045 | 163.0384 | 181.0429 | 175.0395 | 8.9997 | 80.9939 | 3 | 17.3002 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7579 | 103764.809 | 44267.1223 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 772.1978 | 0:240:120 | 0:00 | 15.6199 | 7 | 18.0015 | 145.0417 | 163.0432 | 157.0414 | 8.9986 | 80.9751 | 3 | 15.6199 | 229.5154 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7582 | 104222.103 | 44267.1276 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 783.8688 | 0:240:120 | 0:00 | 13.5897 | 7 | 20.4052 | 109.043 | 129.4482 | 121.5491 | 9.113 | 83.0461 | 3 | 13.5897 | 82.6186 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7585 | 104590.805 | 44267.1318 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 795.7147 | 0:240:120 | 0:00 | 11.9848 | 7 | 18.0007 | 91.0437 | 109.0444 | 98.3281 | 8.2431 | 67.949 | 3 | 11.9848 | 49.787 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7588 | 104903.282 | 44267.1354 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 804.5158 | 0:240:120 | 0:00 | 11.0064 | 7 | 18.0048 | 73.0421 | 91.0469 | 79.0466 | 8.9988 | 80.979 | 3 | 11.0064 | 38.3241 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7591 | 105143.696 | 44267.1382 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 816.6752 | 0:240:120 | 0:00 | 9.8778 | 7 | 17.9978 | 37.0535 | 55.0513 | 49.0501 | 8.9967 | 80.9399 | 3 | 9.8778 | 28.9838 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7594 | 105276.091 | 44267.1398 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 830.6771 | 0:240:120 | 0:00 | 8.8196 | 7 | 0.9971 | 18.0609 | 19.058 | 18.7243 | 0.497 | 0.247 | 3 | 8.8196 | 22.5524 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7597 | 105334.684 | 44267.1404 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 844.0751 | 0:240:120 | 0:00 | 7.9872 | 7 | 1.0904 | 16.0682 | 17.1586 | 16.7431 | 0.5059 | 0.2559 | 3 | 7.9872 | 18.5485 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7600 | 105387.365 | 44267.141 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 860.266 | 0:240:120 | 0:00 | 7.1565 | 7 | 0.9965 | 14.0778 | 15.0743 | 14.7412 | 0.4968 | 0.2468 | 3 | 7.1565 | 15.2245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7603 | 105433.701 | 44267.1416 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 875.0148 | 0:240:120 | 0:00 | 6.5269 | 7 | 0.9949 | 12.0867 | 13.0816 | 12.749 | 0.4963 | 0.2463 | 3 | 6.5269 | 13.0547 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7606 | 105474.225 | 44267.142 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 890.9076 | 0:240:120 | 0:00 | 5.9527 | 7 | 0.9959 | 10.0951 | 11.091 | 10.7579 | 0.4968 | 0.2468 | 3 | 5.9527 | 11.2902 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7609 | 105508.879 | 44267.1424 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 907.9972 | 0:240:120 | 0:00 | 5.4294 | 7 | 0.3297 | 8.7685 | 9.0982 | 8.984 | 0.1616 | 0.0261 | 3 | 5.4294 | 9.8342 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7612 | 105538.016 | 44267.1428 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 935.6501 | 0:240:120 | 0:00 | 4.7387 | 7 | 0.3323 | 7.4492 | 7.7815 | 7.6695 | 0.1646 | 0.0271 | 3 | 4.7387 | 8.1015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7615 | 105563.936 | 44267.1431 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 961.2559 | 0:240:120 | 0:00 | 4.2264 | 7 | 0.3347 | 6.459 | 6.7937 | 6.6033 | 0.1541 | 0.0238 | 3 | 4.2264 | 6.9371 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7618 | 105586.436 | 44267.1433 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 999.4864 | 0:240:120 | 0:00 | 3.6221 | 7 | 0.1661 | 5.3113 | 5.4774 | 5.3676 | 0.0818 | 0.0067 | 3 | 3.6221 | 5.6777 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7621 | 105605.345 | 44267.1436 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1035.0868 | 0:240:120 | 0:00 | 3.1824 | 7 | 0.1641 | 4.4971 | 4.6612 | 4.6059 | 0.081 | 0.0066 | 3 | 3.1824 | 4.8303 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7624 | 105621.988 | 44267.1438 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1073.0291 | 0:240:120 | 0:00 | 2.8062 | 7 | 0.0986 | 3.8808 | 3.9794 | 3.9459 | 0.0482 | 0.0023 | 3 | 2.8062 | 4.1469 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7627 | 105636.895 | 44267.1439 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1119.052 | 0:240:120 | 0:00 | 2.4421 | 7 | 0.1269 | 3.2716 | 3.3985 | 3.342 | 0.0501 | 0.0025 | 3 | 2.4421 | 3.5189 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7630 | 105649.681 | 44267.1441 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1170.554 | 0:240:120 | 0:00 | 2.1205 | 7 | 0.0636 | 2.8224 | 2.886 | 2.8643 | 0.0308 | 0.0009 | 3 | 2.1205 | 2.9897 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7633 | 105661.134 | 44267.1442 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1214.686 | 0:240:120 | 0:00 | 1.8975 | 7 | 0.0801 | 2.4437 | 2.5238 | 2.4998 | 0.029 | 0.0008 | 3 | 1.8975 | 2.6359 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7636 | 105671.713 | 44267.1443 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1285.933 | 0:240:120 | 0:00 | 1.6107 | 7 | 0.0813 | 2.0203 | 2.1016 | 2.0701 | 0.0309 | 0.001 | 3 | 1.6107 | 2.196 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7639 | 105680.9 | 44267.1444 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1373.669 | 0:240:120 | 0:00 | 1.3446 | 7 | 0.0537 | 1.6914 | 1.7451 | 1.7164 | 0.0177 | 0.0003 | 3 | 1.3446 | 1.8021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7642 | 105689.15 | 44267.1445 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1482.129 | 0:240:120 | 0:00 | 1.1027 | 7 | 0.0665 | 1.3396 | 1.4061 | 1.3765 | 0.0257 | 0.0007 | 3 | 1.1027 | 1.4555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7645 | 105696.617 | 44267.1446 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1580.095 | 0:240:120 | 0:00 | 0.9391 | 7 | 0.0605 | 1.1384 | 1.1989 | 1.1672 | 0.018 | 0.0003 | 3 | 0.9391 | 1.227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7648 | 105703.321 | 44267.1447 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1676.125 | 0:240:120 | 0:00 | 0.8133 | 7 | 0.0302 | 0.9965 | 1.0267 | 1.0081 | 0.0107 | 0.0001 | 3 | 0.8133 | 1.0544 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7651 | 105709.285 | 44267.1448 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1763.817 | 0:240:120 | 0:00 | 0.7203 | 7 | 0.0322 | 0.8716 | 0.9038 | 0.8874 | 0.0114 | 0.0001 | 3 | 0.7203 | 0.9284 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7654 | 105715.096 | 44267.1448 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1910.722 | 0:240:120 | 0:00 | 0.5979 | 7 | 0.0238 | 0.7176 | 0.7414 | 0.7321 | 0.0081 | 0.0001 | 3 | 0.5979 | 0.7649 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7657 | 105720.389 | 44267.1449 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2061.598 | 0:240:120 | 0:00 | 0.503 | 7 | 0.0198 | 0.6021 | 0.6219 | 0.6125 | 0.0071 | 0.0001 | 3 | 0.503 | 0.6398 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7660 | 105725.412 | 44267.145 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2255.748 | 0:240:120 | 0:00 | 0.4116 | 7 | 0.0135 | 0.4915 | 0.505 | 0.4986 | 0.0044 | 0 | 3 | 0.4116 | 0.5207 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7663 | 105729.99 | 44267.145 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2561.218 | 0:240:120 | 0:00 | 0.3121 | 7 | 0.0115 | 0.3712 | 0.3827 | 0.377 | 0.0034 | 0 | 3 | 0.3121 | 0.3924 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7666 | 105734.308 | 44267.1451 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2963.829 | 0:240:120 | 0:00 | 0.2285 | 7 | 0.0064 | 0.2715 | 0.2779 | 0.2743 | 0.0026 | 0 | 3 | 0.2285 | 0.286 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7669 | 105738.326 | 44267.1451 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3355.11 | 0:240:120 | 0:00 | 0.1761 | 7 | 0.0063 | 0.2079 | 0.2142 | 0.2108 | 0.0023 | 0 | 3 | 0.1761 | 0.2197 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7672 | 105742.096 | 44267.1451 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3809.443 | 0:240:120 | 0:00 | 0.1353 | 7 | 0.005 | 0.1601 | 0.1651 | 0.1623 | 0.0018 | 0 | 3 | 0.1353 | 0.1683 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7675 | 105745.693 | 44267.1452 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4342.646 | 0:240:120 | 0:00 | 0.1033 | 7 | 0.0031 | 0.123 | 0.1261 | 0.1241 | 0.0012 | 0 | 3 | 0.1033 | 0.1283 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7678 | 105749.651 | 44267.1452 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5178.338 | 0:240:120 | 0:00 | 0.0721 | 7 | 0.003 | 0.085 | 0.088 | 0.0866 | 0.0011 | 0 | 3 | 0.0721 | 0.0894 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7681 | 105753.253 | 44267.1453 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5838.558 | 0:240:120 | 0:00 | 0.0565 | 7 | 0.0027 | 0.0668 | 0.0695 | 0.068 | 0.0009 | 0 | 3 | 0.0565 | 0.07 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7684 | 105756.826 | 44267.1453 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6715.94 | 0:240:120 | 0:00 | 0.0425 | 7 | 0.002 | 0.0503 | 0.0523 | 0.0515 | 0.0007 | 0 | 3 | 0.0425 | 0.0527 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7687 | 105760.49 | 44267.1454 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7504.354 | 0:240:120 | 0:00 | 0.034 | 7 | 0.0017 | 0.0406 | 0.0423 | 0.0416 | 0.0007 | 0 | 3 | 0.034 | 0.044 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7690 | 105764.197 | 44267.1454 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8503.539 | 0:240:120 | 0:00 | 0.0264 | 7 | 0.003 | 0.0315 | 0.0345 | 0.0328 | 0.0011 | 0 | 3 | 0.0264 | 0.0364 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7693 | 105767.562 | 44267.1454 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9674.401 | 0:240:120 | 0:00 | 0.0204 | 7 | 0.0031 | 0.0242 | 0.0273 | 0.0263 | 0.0011 | 0 | 3 | 0.0204 | 0.0304 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7696 | 105770.819 | 44267.1455 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10940.622 | 0:240:120 | 0:00 | 0.0159 | 7 | 0.0041 | 0.0197 | 0.0238 | 0.0218 | 0.0013 | 0 | 3 | 0.0159 | 0.0259 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7699 | 105900.352 | 44267.147 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 789.8 | 0:240:120 | 0:00 | 12.7388 | 7 | 19.8948 | 107.1432 | 127.038 | 114.7177 | 9.016 | 81.2877 | 3 | 12.7388 | 62.1687 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7702 | 106248.809 | 44267.151 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 800.1 | 0:240:120 | 0:00 | 11.4778 | 7 | 17.9959 | 73.0507 | 91.0466 | 85.0455 | 8.9959 | 80.9265 | 3 | 11.4778 | 43.345 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7705 | 106507.093 | 44267.154 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 810.6 | 0:240:120 | 0:00 | 10.4133 | 7 | 17.9993 | 55.0507 | 73.05 | 62.6477 | 8.1607 | 66.5965 | 3 | 10.4133 | 33.0197 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7708 | 106693.649 | 44267.1562 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 823.7 | 0:240:120 | 0:00 | 9.3192 | 7 | 17.9998 | 19.0561 | 37.0559 | 31.053 | 8.9966 | 80.939 | 3 | 9.3192 | 25.3695 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7711 | 106789.128 | 44267.1573 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 837.4 | 0:240:120 | 0:00 | 8.3829 | 7 | 0.9965 | 17.0647 | 18.0612 | 17.7283 | 0.4971 | 0.2471 | 3 | 8.3829 | 20.3563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7714 | 106845.028 | 44267.1579 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 852.2 | 0:240:120 | 0:00 | 7.5495 | 7 | 0.9976 | 15.0737 | 16.0713 | 15.7373 | 0.4964 | 0.2464 | 3 | 7.5495 | 16.7248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7717 | 106895.056 | 44267.1585 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 867.6 | 0:240:120 | 0:00 | 6.8303 | 7 | 0.9967 | 13.0818 | 14.0785 | 13.7445 | 0.4967 | 0.2468 | 3 | 6.8303 | 14.0668 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7720 | 106938.572 | 44267.159 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 883 | 0:240:120 | 0:00 | 6.2265 | 7 | 0.9966 | 11.0903 | 12.0869 | 11.7536 | 0.4966 | 0.2466 | 3 | 6.2265 | 12.1081 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7723 | 106976.366 | 44267.1594 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 899.5 | 0:240:120 | 0:00 | 5.6788 | 7 | 0.9979 | 9.0969 | 10.0948 | 9.7611 | 0.4975 | 0.2475 | 3 | 5.6788 | 10.5114 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7726 | 107008.087 | 44267.1598 | Vista Speed | E | 300E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 921.8 | 0:240:120 | 0:00 | 5.0638 | 7 | 0.3306 | 8.1091 | 8.4397 | 8.3288 | 0.1646 | 0.0271 | 3 | 5.0638 | 8.8921 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7729 | 107229.234 | 44267.1624 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 991.5224 | 0:240:120 | 0:00 | 18.9545 | 7 | 18.0033 | 181.0398 | 199.0431 | 188.7366 | 8.2996 | 68.883 | 3 | 18.9545 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7732 | 107829.688 | 44267.1693 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 993.5068 | 0:240:120 | 0:00 | 18.5285 | 7 | 18.0024 | 181.0378 | 199.0402 | 187.0394 | 8.9994 | 80.9892 | 3 | 18.5285 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7735 | 108394.491 | 44267.1758 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1010.5414 | 0:240:120 | 0:00 | 15.5077 | 7 | 17.999 | 145.0432 | 163.0422 | 156.4851 | 8.6528 | 74.8713 | 3 | 15.5077 | 211.3229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7738 | 108850.617 | 44267.1811 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1033.0188 | 0:240:120 | 0:00 | 12.7178 | 7 | 18.0038 | 109.0385 | 127.0423 | 115.041 | 8.999 | 80.9816 | 3 | 12.7178 | 61.7661 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7741 | 109181.162 | 44267.185 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1057.0538 | 0:240:120 | 0:00 | 10.627 | 7 | 17.9981 | 55.0522 | 73.0503 | 67.0489 | 8.9973 | 80.9511 | 3 | 10.627 | 34.8178 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7744 | 109367.545 | 44267.1871 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1079.4872 | 0:240:120 | 0:00 | 9.1861 | 7 | 17.9979 | 19.0572 | 37.0551 | 28.0855 | 7.8619 | 61.8096 | 3 | 9.1861 | 24.584 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7747 | 109461.976 | 44267.1882 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1104.598 | 0:240:120 | 0:00 | 7.9523 | 7 | 0.9975 | 16.0688 | 17.0663 | 16.7326 | 0.4967 | 0.2467 | 3 | 7.9523 | 18.3967 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7750 | 109514.266 | 44267.1888 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1130.294 | 0:240:120 | 0:00 | 6.9718 | 7 | 1.0001 | 14.0737 | 15.0738 | 14.4084 | 0.4985 | 0.2485 | 3 | 6.9718 | 14.5597 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7753 | 109559.826 | 44267.1893 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1161.237 | 0:240:120 | 0:00 | 6.0506 | 7 | 1.9931 | 10.0945 | 12.0876 | 11.09 | 0.8619 | 0.7429 | 3 | 6.0506 | 11.5781 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7756 | 109596.339 | 44267.1898 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1187.065 | 0:240:120 | 0:00 | 5.4363 | 7 | 0.3307 | 8.7679 | 9.0986 | 8.9847 | 0.1618 | 0.0262 | 3 | 5.4363 | 9.8523 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7759 | 109626.142 | 44267.1901 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1218.327 | 0:240:120 | 0:00 | 4.8284 | 7 | 0.7063 | 7.4043 | 8.1106 | 7.8407 | 0.2542 | 0.0646 | 3 | 4.8284 | 8.3155 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7762 | 109652.263 | 44267.1904 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1247.928 | 0:240:120 | 0:00 | 4.3556 | 7 | 0.572 | 6.4496 | 7.0216 | 6.7846 | 0.1546 | 0.0239 | 3 | 4.3556 | 7.2219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7765 | 109675.266 | 44267.1907 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1276.957 | 0:240:120 | 0:00 | 3.9657 | 7 | 0.448 | 5.5778 | 6.0258 | 5.8465 | 0.1532 | 0.0235 | 3 | 3.9657 | 6.3796 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7768 | 109695.729 | 44267.1909 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1313.224 | 0:240:120 | 0:00 | 3.5576 | 7 | 0.2875 | 5.0451 | 5.3326 | 5.2006 | 0.1001 | 0.01 | 3 | 3.5576 | 5.5499 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7771 | 109714.771 | 44267.1911 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1341.087 | 0:240:120 | 0:00 | 3.2909 | 7 | 0.4028 | 4.5562 | 4.959 | 4.7527 | 0.1266 | 0.016 | 3 | 3.2909 | 5.0345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7774 | 109732.229 | 44267.1913 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1373.669 | 0:240:120 | 0:00 | 3.0202 | 7 | 0.2563 | 4.0858 | 4.3421 | 4.2317 | 0.0768 | 0.0059 | 3 | 3.0202 | 4.5311 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7777 | 109748.276 | 44267.1915 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1400.014 | 0:240:120 | 0:00 | 2.828 | 7 | 0.2499 | 3.7887 | 4.0386 | 3.9178 | 0.0871 | 0.0076 | 3 | 2.828 | 4.1855 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7780 | 109763.153 | 44267.1917 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1436.886 | 0:240:120 | 0:00 | 2.5919 | 7 | 0.2055 | 3.4634 | 3.6689 | 3.5781 | 0.0765 | 0.0059 | 3 | 2.5919 | 3.7734 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7783 | 109777.327 | 44267.1919 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1465.915 | 0:240:120 | 0:00 | 2.4285 | 7 | 0.1746 | 3.1832 | 3.3578 | 3.2841 | 0.0616 | 0.0038 | 3 | 2.4285 | 3.4961 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7786 | 109790.17 | 44267.192 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1501.522 | 0:240:120 | 0:00 | 2.2507 | 7 | 0.1134 | 2.9495 | 3.0629 | 3.0163 | 0.043 | 0.0019 | 3 | 2.2507 | 3.2011 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7789 | 109802.505 | 44267.1921 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1534.929 | 0:240:120 | 0:00 | 2.1028 | 7 | 0.1338 | 2.7224 | 2.8562 | 2.8007 | 0.0387 | 0.0015 | 3 | 2.1028 | 2.9613 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7792 | 109813.946 | 44267.1923 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1565.938 | 0:240:120 | 0:00 | 1.9796 | 7 | 0.1305 | 2.5317 | 2.6622 | 2.6066 | 0.0523 | 0.0027 | 3 | 1.9796 | 2.7649 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7795 | 109825.299 | 44267.1924 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1608.794 | 0:240:120 | 0:00 | 1.828 | 7 | 0.0794 | 2.3562 | 2.4356 | 2.3939 | 0.0289 | 0.0008 | 3 | 1.828 | 2.5277 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7798 | 109835.526 | 44267.1925 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1639.649 | 0:240:120 | 0:00 | 1.7303 | 7 | 0.1136 | 2.1834 | 2.297 | 2.2502 | 0.0385 | 0.0015 | 3 | 1.7303 | 2.3774 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7801 | 109845.416 | 44267.1926 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1677.797 | 0:240:120 | 0:00 | 1.621 | 7 | 0.0841 | 2.0508 | 2.1349 | 2.0867 | 0.0299 | 0.0009 | 3 | 1.621 | 2.2115 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7804 | 109854.93 | 44267.1927 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1721.995 | 0:240:120 | 0:00 | 1.5079 | 7 | 0.104 | 1.8808 | 1.9848 | 1.9349 | 0.0343 | 0.0012 | 3 | 1.5079 | 2.0422 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7807 | 109864.1 | 44267.1929 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1777.985 | 0:240:120 | 0:00 | 1.3821 | 7 | 0.0706 | 1.7171 | 1.7877 | 1.7543 | 0.0262 | 0.0007 | 3 | 1.3821 | 1.8568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7810 | 109872.437 | 44267.193 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1845.008 | 0:240:120 | 0:00 | 1.2527 | 7 | 0.0626 | 1.5556 | 1.6182 | 1.5876 | 0.0242 | 0.0006 | 3 | 1.2527 | 1.6691 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7813 | 109880.306 | 44267.193 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1912.636 | 0:240:120 | 0:00 | 1.1408 | 7 | 0.0375 | 1.4166 | 1.4541 | 1.4376 | 0.0128 | 0.0002 | 3 | 1.1408 | 1.5094 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7816 | 109887.86 | 44267.1931 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2008.688 | 0:240:120 | 0:00 | 1.0075 | 7 | 0.0364 | 1.2351 | 1.2715 | 1.2567 | 0.0134 | 0.0002 | 3 | 1.0075 | 1.3219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7819 | 109896.239 | 44267.1932 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2139.313 | 0:240:120 | 0:00 | 0.8625 | 7 | 0.0375 | 1.0465 | 1.084 | 1.0637 | 0.0128 | 0.0002 | 3 | 0.8625 | 1.1215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7822 | 109902.677 | 44267.1933 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2258.003 | 0:240:120 | 0:00 | 0.7575 | 7 | 0.0274 | 0.9192 | 0.9466 | 0.9308 | 0.0092 | 0.0001 | 3 | 0.7575 | 0.9786 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7825 | 109908.458 | 44267.1934 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2402.433 | 0:240:120 | 0:00 | 0.6547 | 7 | 0.0214 | 0.7905 | 0.8119 | 0.8017 | 0.0077 | 0.0001 | 3 | 0.6547 | 0.8405 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7828 | 109914.372 | 44267.1934 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2528.141 | 0:240:120 | 0:00 | 0.582 | 7 | 0.0263 | 0.6963 | 0.7226 | 0.7094 | 0.0103 | 0.0001 | 3 | 0.582 | 0.7439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7831 | 109919.638 | 44267.1935 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2644.499 | 0:240:120 | 0:00 | 0.5253 | 7 | 0.0141 | 0.6309 | 0.645 | 0.6384 | 0.0049 | 0 | 3 | 0.5253 | 0.6691 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7834 | 109924.857 | 44267.1936 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2805.22 | 0:240:120 | 0:00 | 0.4601 | 7 | 0.0146 | 0.5514 | 0.566 | 0.5587 | 0.006 | 0 | 3 | 0.4601 | 0.5838 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7837 | 109929.738 | 44267.1936 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2972.739 | 0:240:120 | 0:00 | 0.4046 | 7 | 0.0125 | 0.4822 | 0.4947 | 0.4894 | 0.0044 | 0 | 3 | 0.4046 | 0.5117 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7840 | 109934.365 | 44267.1937 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3204.267 | 0:240:120 | 0:00 | 0.3434 | 7 | 0.0126 | 0.4067 | 0.4193 | 0.4136 | 0.0041 | 0 | 3 | 0.3434 | 0.4327 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7843 | 109938.775 | 44267.1937 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3562.57 | 0:240:120 | 0:00 | 0.2733 | 7 | 0.0086 | 0.324 | 0.3326 | 0.3279 | 0.003 | 0 | 3 | 0.2733 | 0.3429 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7846 | 109942.866 | 44267.1938 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3847.734 | 0:240:120 | 0:00 | 0.2321 | 7 | 0.0062 | 0.2757 | 0.2819 | 0.2783 | 0.0022 | 0 | 3 | 0.2321 | 0.2904 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7849 | 109946.968 | 44267.1938 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4189.086 | 0:240:120 | 0:00 | 0.194 | 7 | 0.0054 | 0.2301 | 0.2355 | 0.2325 | 0.0023 | 0 | 3 | 0.194 | 0.2423 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7852 | 109950.695 | 44267.1939 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4569.862 | 0:240:120 | 0:00 | 0.1618 | 7 | 0.0052 | 0.1911 | 0.1963 | 0.1933 | 0.0017 | 0 | 3 | 0.1618 | 0.2016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7855 | 109954.541 | 44267.1939 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4965.345 | 0:240:120 | 0:00 | 0.1362 | 7 | 0.0037 | 0.1612 | 0.1649 | 0.1626 | 0.0015 | 0 | 3 | 0.1362 | 0.1695 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7858 | 109958.169 | 44267.1939 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5246.087 | 0:240:120 | 0:00 | 0.1216 | 7 | 0.0045 | 0.1436 | 0.1481 | 0.1451 | 0.0015 | 0 | 3 | 0.1216 | 0.1512 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7861 | 109961.813 | 44267.194 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5576.065 | 0:240:120 | 0:00 | 0.1072 | 7 | 0.0033 | 0.1267 | 0.13 | 0.1276 | 0.0013 | 0 | 3 | 0.1072 | 0.1332 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7864 | 109965.423 | 44267.194 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6022.379 | 0:240:120 | 0:00 | 0.0916 | 7 | 0.0038 | 0.1072 | 0.111 | 0.1092 | 0.0014 | 0 | 3 | 0.0916 | 0.1137 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7867 | 109969.044 | 44267.1941 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6362.895 | 0:240:120 | 0:00 | 0.0818 | 7 | 0.0037 | 0.096 | 0.0997 | 0.0978 | 0.0012 | 0 | 3 | 0.0818 | 0.1015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7870 | 109972.833 | 44267.1941 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6844.761 | 0:240:120 | 0:00 | 0.0705 | 7 | 0.0038 | 0.0826 | 0.0864 | 0.0842 | 0.0014 | 0 | 3 | 0.0705 | 0.0874 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7873 | 109976.503 | 44267.1942 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7297.147 | 0:240:120 | 0:00 | 0.0619 | 7 | 0.003 | 0.0722 | 0.0752 | 0.0739 | 0.001 | 0 | 3 | 0.0619 | 0.0767 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7876 | 109980.075 | 44267.1942 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7904.897 | 0:240:120 | 0:00 | 0.0526 | 7 | 0.0029 | 0.062 | 0.0649 | 0.0633 | 0.0009 | 0 | 3 | 0.0526 | 0.0652 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7879 | 109983.521 | 44267.1942 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8452.675 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0025 | 0.0543 | 0.0568 | 0.0555 | 0.0009 | 0 | 3 | 0.046 | 0.0569 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7882 | 109987.038 | 44267.1943 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9111.003 | 0:240:120 | 0:00 | 0.0395 | 7 | 0.0032 | 0.0461 | 0.0493 | 0.0481 | 0.0013 | 0 | 3 | 0.0395 | 0.0495 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7885 | 109990.362 | 44267.1943 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9840.27 | 0:240:120 | 0:00 | 0.0338 | 7 | 0.004 | 0.0388 | 0.0428 | 0.0411 | 0.0014 | 0 | 3 | 0.0338 | 0.0438 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7888 | 109994.109 | 44267.1944 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10564.323 | 0:240:120 | 0:00 | 0.0293 | 7 | 0.003 | 0.0344 | 0.0374 | 0.0362 | 0.001 | 0 | 3 | 0.0293 | 0.0393 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7891 | 109997.539 | 44267.1944 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11273.79 | 0:240:120 | 0:00 | 0.0257 | 7 | 0.0024 | 0.0299 | 0.0323 | 0.0317 | 0.001 | 0 | 3 | 0.0257 | 0.0357 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7894 | 110092.205 | 44267.1955 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1045 | 0:240:120 | 0:00 | 11.5879 | 7 | 17.9943 | 73.0504 | 91.0447 | 85.0451 | 8.9959 | 80.9258 | 3 | 11.5879 | 44.6417 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7897 | 110332.765 | 44267.1983 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1068.3 | 0:240:120 | 0:00 | 9.856 | 7 | 17.9981 | 37.0535 | 55.0516 | 49.0502 | 8.9971 | 80.9481 | 3 | 9.856 | 28.8324 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7900 | 110465.439 | 44267.1998 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1092 | 0:240:120 | 0:00 | 8.5304 | 7 | 1.6835 | 17.3752 | 19.0587 | 18.2 | 0.691 | 0.4775 | 3 | 8.5304 | 21.0728 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7903 | 110522.721 | 44267.2005 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1117.4 | 0:240:120 | 0:00 | 7.4344 | 7 | 0.9944 | 15.0754 | 16.0698 | 15.7376 | 0.4964 | 0.2464 | 3 | 7.4344 | 16.2725 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7906 | 110571.153 | 44267.201 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1145.8 | 0:240:120 | 0:00 | 6.4807 | 7 | 0.9969 | 12.0864 | 13.0833 | 12.7491 | 0.4964 | 0.2464 | 3 | 6.4807 | 12.9055 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7909 | 110610.575 | 44267.2015 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1174.2 | 0:240:120 | 0:00 | 5.7276 | 7 | 0.9966 | 9.0979 | 10.0945 | 9.7612 | 0.497 | 0.247 | 3 | 5.7276 | 10.6472 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7912 | 110642.574 | 44267.2019 | Vista Speed | E | 400E | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1202.7 | 0:240:120 | 0:00 | 5.1162 | 7 | 0.3324 | 8.109 | 8.4414 | 8.3291 | 0.1646 | 0.0271 | 3 | 5.1162 | 9.0237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0

## Main_Charac-20210309 140936-Com (hidden)
Index | Time Interval | Timestamp | Curve Family | Type | Amp Type | Test Type | Trip Type | Interrupter# | Start Type | PE | DT1 | DT2 | OCC Freq | Source Freq | Current | Phase A:B:C | X/R:Angle | Expected Time | P_Select | Max Delta | Min Time | Max Time | Average | Std Dev | Variance | Count | Min T Spec | Max T Spec | Ave T Result | T Result | Indiv T | TC Result | Indiv TC
1 | 86.224 | 44264.591 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28 | 0:240:120 | 0:00 | 7.9066 | 7 | 15.2597 | 67.8228 | 83.0825 | 74.6728 | 6.418 | 41.1902 | 3 | 7.9066 | Inf | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4 | 318.188 | 44264.5937 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.56 | 0:240:120 | 0:00 | 6.6007 | 7 | 16.8878 | 47.2596 | 64.1474 | 55.4209 | 7.0716 | 50.0074 | 3 | 6.6007 | 44.1934 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7 | 494.103 | 44264.5957 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.1312 | 0:240:120 | 0:00 | 5.6347 | 7 | 18.2125 | 27.2739 | 45.4864 | 36.3227 | 7.5297 | 56.6969 | 3 | 5.6347 | 21.6565 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
10 | 613.548 | 44264.5971 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.7138 | 0:240:120 | 0:00 | 4.8916 | 7 | 16.8449 | 9.5153 | 26.3602 | 15.8799 | 7.8467 | 61.571 | 3 | 4.8916 | 14.1488 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
13 | 677.861 | 44264.5979 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.3081 | 0:240:120 | 0:00 | 4.3028 | 7 | 0.8849 | 8.3858 | 9.2707 | 8.7619 | 0.386 | 0.149 | 3 | 4.3028 | 10.5447 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
16 | 706.558 | 44264.5982 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.9143 | 0:240:120 | 0:00 | 3.825 | 7 | 0.8701 | 7.237 | 8.1071 | 7.6561 | 0.3629 | 0.1317 | 3 | 3.825 | 8.4281 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
19 | 732.049 | 44264.5985 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.5325 | 0:240:120 | 0:00 | 3.4298 | 7 | 0.9761 | 6.1065 | 7.0826 | 6.5707 | 0.4171 | 0.1739 | 3 | 3.4298 | 6.9747 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
22 | 754.5 | 44264.5987 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.1632 | 0:240:120 | 0:00 | 3.0977 | 7 | 0.9223 | 4.9648 | 5.8871 | 5.3406 | 0.4122 | 0.1699 | 3 | 3.0977 | 5.9157 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
25 | 773.46 | 44264.599 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.8065 | 0:240:120 | 0:00 | 2.815 | 7 | 0.3284 | 4.3179 | 4.6463 | 4.468 | 0.1418 | 0.0201 | 3 | 2.815 | 5.1104 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
28 | 789.639 | 44264.5992 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.4626 | 0:240:120 | 0:00 | 2.5716 | 7 | 0.3359 | 3.9361 | 4.272 | 4.0734 | 0.1504 | 0.0226 | 3 | 2.5716 | 4.4777 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
31 | 804.822 | 44264.5993 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.1318 | 0:240:120 | 0:00 | 2.3599 | 7 | 0.3479 | 3.5057 | 3.8536 | 3.6607 | 0.1475 | 0.0218 | 3 | 2.3599 | 3.968 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
34 | 818.592 | 44264.5995 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.8145 | 0:240:120 | 0:00 | 2.1743 | 7 | 0.3395 | 3.1146 | 3.4541 | 3.2524 | 0.153 | 0.0234 | 3 | 2.1743 | 3.5488 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
37 | 831.383 | 44264.5996 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.5108 | 0:240:120 | 0:00 | 2.0104 | 7 | 0.1803 | 2.8227 | 3.003 | 2.9028 | 0.0753 | 0.0057 | 3 | 2.0104 | 3.1982 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
40 | 842.937 | 44264.5998 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.221 | 0:240:120 | 0:00 | 1.8646 | 7 | 0.177 | 2.6156 | 2.7926 | 2.6848 | 0.0811 | 0.0066 | 3 | 1.8646 | 2.9009 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
43 | 853.824 | 44264.5999 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.9454 | 0:240:120 | 0:00 | 1.7343 | 7 | 0.1701 | 2.392 | 2.5621 | 2.4616 | 0.0752 | 0.0057 | 3 | 1.7343 | 2.6458 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
46 | 864.057 | 44264.6 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.6843 | 0:240:120 | 0:00 | 1.6171 | 7 | 0.1797 | 2.1754 | 2.3551 | 2.2505 | 0.0775 | 0.006 | 3 | 1.6171 | 2.4247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
49 | 873.53 | 44264.6001 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.438 | 0:240:120 | 0:00 | 1.5113 | 7 | 0.1101 | 2.0306 | 2.1407 | 2.074 | 0.0503 | 0.0025 | 3 | 1.5113 | 2.2312 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
52 | 882.597 | 44264.6002 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.2068 | 0:240:120 | 0:00 | 1.4154 | 7 | 0.1046 | 1.8961 | 2.0007 | 1.9339 | 0.0499 | 0.0025 | 3 | 1.4154 | 2.0608 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
55 | 891.202 | 44264.6003 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.9909 | 0:240:120 | 0:00 | 1.328 | 7 | 0.1041 | 1.7548 | 1.8589 | 1.7911 | 0.0503 | 0.0025 | 3 | 1.328 | 1.9095 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
58 | 899.453 | 44264.6004 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.7907 | 0:240:120 | 0:00 | 1.2482 | 7 | 0.085 | 1.6277 | 1.7127 | 1.6572 | 0.0411 | 0.0017 | 3 | 1.2482 | 1.7745 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
61 | 907.269 | 44264.6005 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.6065 | 0:240:120 | 0:00 | 1.1751 | 7 | 0.0706 | 1.5308 | 1.6014 | 1.5562 | 0.0331 | 0.0011 | 3 | 1.1751 | 1.6534 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
64 | 914.528 | 44264.6006 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.4387 | 0:240:120 | 0:00 | 1.1079 | 7 | 0.0699 | 1.435 | 1.5049 | 1.461 | 0.0325 | 0.0011 | 3 | 1.1079 | 1.5441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
67 | 921.49 | 44264.6007 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.2874 | 0:240:120 | 0:00 | 1.046 | 7 | 0.0706 | 1.3386 | 1.4092 | 1.3637 | 0.0333 | 0.0011 | 3 | 1.046 | 1.4451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
70 | 928.289 | 44264.6008 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.1532 | 0:240:120 | 0:00 | 0.9888 | 7 | 0.0551 | 1.2651 | 1.3202 | 1.2863 | 0.0254 | 0.0006 | 3 | 0.9888 | 1.3551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
73 | 935.078 | 44264.6008 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.0362 | 0:240:120 | 0:00 | 0.9358 | 7 | 0.0585 | 1.1938 | 1.2523 | 1.2168 | 0.026 | 0.0007 | 3 | 0.9358 | 1.273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
76 | 941.442 | 44264.6009 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.937 | 0:240:120 | 0:00 | 0.8866 | 7 | 0.0586 | 1.1171 | 1.1757 | 1.1377 | 0.0271 | 0.0007 | 3 | 0.8866 | 1.1979 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
79 | 947.613 | 44264.601 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.8557 | 0:240:120 | 0:00 | 0.8409 | 7 | 0.0413 | 1.0621 | 1.1034 | 1.0786 | 0.0185 | 0.0003 | 3 | 0.8409 | 1.1288 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
82 | 953.63 | 44264.601 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.7928 | 0:240:120 | 0:00 | 0.7984 | 7 | 0.0476 | 1.0024 | 1.05 | 1.021 | 0.0218 | 0.0005 | 3 | 0.7984 | 1.0653 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
85 | 959.62 | 44264.6011 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.7487 | 0:240:120 | 0:00 | 0.7587 | 7 | 0.0397 | 0.9489 | 0.9886 | 0.9639 | 0.0181 | 0.0003 | 3 | 0.7587 | 1.0066 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
88 | 965.2 | 44264.6012 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.7237 | 0:240:120 | 0:00 | 0.7216 | 7 | 0.0366 | 0.9017 | 0.9383 | 0.9161 | 0.0164 | 0.0003 | 3 | 0.7216 | 0.9523 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
91 | 970.733 | 44264.6012 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.7181 | 0:240:120 | 0:00 | 0.6869 | 7 | 0.032 | 0.858 | 0.89 | 0.8698 | 0.0148 | 0.0002 | 3 | 0.6869 | 0.902 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
94 | 976.238 | 44264.6013 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.7325 | 0:240:120 | 0:00 | 0.6544 | 7 | 0.0293 | 0.8134 | 0.8427 | 0.8239 | 0.0135 | 0.0002 | 3 | 0.6544 | 0.8552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
97 | 981.559 | 44264.6014 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.7671 | 0:240:120 | 0:00 | 0.6239 | 7 | 0.0296 | 0.7744 | 0.804 | 0.785 | 0.0137 | 0.0002 | 3 | 0.6239 | 0.8117 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
100 | 986.84 | 44264.6014 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.8225 | 0:240:120 | 0:00 | 0.5952 | 7 | 0.0304 | 0.7352 | 0.7656 | 0.7459 | 0.0147 | 0.0002 | 3 | 0.5952 | 0.7711 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
103 | 991.683 | 44264.6015 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.8989 | 0:240:120 | 0:00 | 0.5683 | 7 | 0.0244 | 0.7011 | 0.7255 | 0.7104 | 0.0111 | 0.0001 | 3 | 0.5683 | 0.7332 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
106 | 996.566 | 44264.6015 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.9969 | 0:240:120 | 0:00 | 0.5429 | 7 | 0.025 | 0.6692 | 0.6942 | 0.6782 | 0.0116 | 0.0001 | 3 | 0.5429 | 0.6978 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
109 | 1001.282 | 44264.6016 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.1168 | 0:240:120 | 0:00 | 0.519 | 7 | 0.0237 | 0.6381 | 0.6618 | 0.6474 | 0.01 | 0.0001 | 3 | 0.519 | 0.6646 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
112 | 1005.764 | 44264.6017 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.2592 | 0:240:120 | 0:00 | 0.4964 | 7 | 0.0204 | 0.6102 | 0.6306 | 0.6185 | 0.009 | 0.0001 | 3 | 0.4964 | 0.6334 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
115 | 1010.478 | 44264.6017 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.4244 | 0:240:120 | 0:00 | 0.4751 | 7 | 0.0205 | 0.5813 | 0.6018 | 0.589 | 0.0094 | 0.0001 | 3 | 0.4751 | 0.6042 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
118 | 1015.017 | 44264.6018 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.6129 | 0:240:120 | 0:00 | 0.455 | 7 | 0.0188 | 0.5565 | 0.5753 | 0.5641 | 0.0085 | 0.0001 | 3 | 0.455 | 0.5767 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
121 | 1019.62 | 44264.6018 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.8251 | 0:240:120 | 0:00 | 0.4359 | 7 | 0.0177 | 0.5334 | 0.5511 | 0.5398 | 0.0079 | 0.0001 | 3 | 0.4359 | 0.5508 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
124 | 1024.018 | 44264.6019 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.0616 | 0:240:120 | 0:00 | 0.4179 | 7 | 0.015 | 0.5104 | 0.5254 | 0.5162 | 0.0069 | 0 | 3 | 0.4179 | 0.5265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
127 | 1028.446 | 44264.6019 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.3228 | 0:240:120 | 0:00 | 0.4009 | 7 | 0.0155 | 0.4888 | 0.5043 | 0.4945 | 0.0069 | 0 | 3 | 0.4009 | 0.5035 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
130 | 1032.485 | 44264.602 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.6093 | 0:240:120 | 0:00 | 0.3847 | 7 | 0.0142 | 0.4688 | 0.483 | 0.4744 | 0.0063 | 0 | 3 | 0.3847 | 0.4818 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
133 | 1036.536 | 44264.602 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.9215 | 0:240:120 | 0:00 | 0.3694 | 7 | 0.0138 | 0.4503 | 0.4641 | 0.4553 | 0.0061 | 0 | 3 | 0.3694 | 0.4613 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
136 | 1040.526 | 44264.6021 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.2599 | 0:240:120 | 0:00 | 0.3548 | 7 | 0.0115 | 0.4327 | 0.4442 | 0.4368 | 0.0053 | 0 | 3 | 0.3548 | 0.4419 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
139 | 1044.638 | 44264.6021 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.6251 | 0:240:120 | 0:00 | 0.341 | 7 | 0.0127 | 0.4143 | 0.427 | 0.4194 | 0.0056 | 0 | 3 | 0.341 | 0.4236 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
142 | 1048.716 | 44264.6021 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.0176 | 0:240:120 | 0:00 | 0.3279 | 7 | 0.0115 | 0.398 | 0.4095 | 0.4027 | 0.0052 | 0 | 3 | 0.3279 | 0.4062 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
145 | 1052.87 | 44264.6022 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.438 | 0:240:120 | 0:00 | 0.3154 | 7 | 0.0115 | 0.382 | 0.3935 | 0.3869 | 0.0049 | 0 | 3 | 0.3154 | 0.3898 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
148 | 1056.731 | 44264.6022 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.8867 | 0:240:120 | 0:00 | 0.3036 | 7 | 0.0108 | 0.3678 | 0.3786 | 0.372 | 0.0044 | 0 | 3 | 0.3036 | 0.3742 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
151 | 1060.574 | 44264.6023 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.3645 | 0:240:120 | 0:00 | 0.2923 | 7 | 0.0093 | 0.3548 | 0.3641 | 0.3583 | 0.0041 | 0 | 3 | 0.2923 | 0.3594 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
154 | 1064.408 | 44264.6023 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.8718 | 0:240:120 | 0:00 | 0.2816 | 7 | 0.0101 | 0.3405 | 0.3506 | 0.3448 | 0.0041 | 0 | 3 | 0.2816 | 0.3454 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
157 | 1068.522 | 44264.6024 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.4092 | 0:240:120 | 0:00 | 0.2713 | 7 | 0.01 | 0.328 | 0.338 | 0.3321 | 0.0041 | 0 | 3 | 0.2713 | 0.332 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
160 | 1072.216 | 44264.6024 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.9774 | 0:240:120 | 0:00 | 0.2616 | 7 | 0.0088 | 0.3163 | 0.3251 | 0.3198 | 0.0037 | 0 | 3 | 0.2616 | 0.3194 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
163 | 1076.012 | 44264.6025 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.5769 | 0:240:120 | 0:00 | 0.2523 | 7 | 0.008 | 0.305 | 0.313 | 0.3083 | 0.0034 | 0 | 3 | 0.2523 | 0.3073 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
166 | 1079.871 | 44264.6025 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.2085 | 0:240:120 | 0:00 | 0.2435 | 7 | 0.0094 | 0.2937 | 0.3031 | 0.2975 | 0.0042 | 0 | 3 | 0.2435 | 0.2958 | NP | NP | 0-1-0-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
169 | 1083.433 | 44264.6026 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.8726 | 0:240:120 | 0:00 | 0.235 | 7 | 0.0075 | 0.2836 | 0.2911 | 0.2864 | 0.003 | 0 | 3 | 0.235 | 0.2849 | NP | NP | 0-1-0-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
172 | 1086.873 | 44264.6026 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.5701 | 0:240:120 | 0:00 | 0.227 | 7 | 0.0079 | 0.2734 | 0.2813 | 0.2767 | 0.0034 | 0 | 3 | 0.227 | 0.2745 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
175 | 1090.691 | 44264.6026 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.3015 | 0:240:120 | 0:00 | 0.2193 | 7 | 0.0083 | 0.2639 | 0.2722 | 0.2675 | 0.0034 | 0 | 3 | 0.2193 | 0.2647 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
178 | 1094.242 | 44264.6027 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.0675 | 0:240:120 | 0:00 | 0.212 | 7 | 0.0068 | 0.2555 | 0.2623 | 0.2584 | 0.0029 | 0 | 3 | 0.212 | 0.2552 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
181 | 1097.811 | 44264.6027 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.8689 | 0:240:120 | 0:00 | 0.205 | 7 | 0.0074 | 0.2469 | 0.2543 | 0.2497 | 0.003 | 0 | 3 | 0.205 | 0.2462 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
184 | 1101.433 | 44264.6028 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.7062 | 0:240:120 | 0:00 | 0.1983 | 7 | 0.0067 | 0.2388 | 0.2455 | 0.2419 | 0.0026 | 0 | 3 | 0.1983 | 0.2379 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
187 | 1105.049 | 44264.6028 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.5804 | 0:240:120 | 0:00 | 0.1919 | 7 | 0.0063 | 0.2317 | 0.238 | 0.2347 | 0.0025 | 0 | 3 | 0.1919 | 0.2303 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
190 | 1108.571 | 44264.6028 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.492 | 0:240:120 | 0:00 | 0.1858 | 7 | 0.0069 | 0.2233 | 0.2302 | 0.2263 | 0.0028 | 0 | 3 | 0.1858 | 0.2229 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
193 | 1112.085 | 44264.6029 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.4418 | 0:240:120 | 0:00 | 0.1799 | 7 | 0.0056 | 0.2172 | 0.2228 | 0.2197 | 0.0022 | 0 | 3 | 0.1799 | 0.2159 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
196 | 1115.621 | 44264.6029 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.4306 | 0:240:120 | 0:00 | 0.1744 | 7 | 0.004 | 0.2113 | 0.2153 | 0.213 | 0.0017 | 0 | 3 | 0.1744 | 0.2092 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
199 | 1119.083 | 44264.603 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.4593 | 0:240:120 | 0:00 | 0.169 | 7 | 0.0048 | 0.2042 | 0.209 | 0.2065 | 0.0019 | 0 | 3 | 0.169 | 0.2028 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
202 | 1122.517 | 44264.603 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.5284 | 0:240:120 | 0:00 | 0.1639 | 7 | 0.0049 | 0.1972 | 0.2021 | 0.2 | 0.0018 | 0 | 3 | 0.1639 | 0.1967 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
205 | 1126.013 | 44264.603 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.639 | 0:240:120 | 0:00 | 0.159 | 7 | 0.0045 | 0.1921 | 0.1966 | 0.1942 | 0.0017 | 0 | 3 | 0.159 | 0.1908 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
208 | 1129.364 | 44264.6031 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.7918 | 0:240:120 | 0:00 | 0.1544 | 7 | 0.0057 | 0.1856 | 0.1913 | 0.1884 | 0.0021 | 0 | 3 | 0.1544 | 0.1852 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
211 | 1132.879 | 44264.6031 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.9876 | 0:240:120 | 0:00 | 0.1499 | 7 | 0.0052 | 0.1808 | 0.186 | 0.1832 | 0.0019 | 0 | 3 | 0.1499 | 0.1799 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
214 | 1136.083 | 44264.6032 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.2274 | 0:240:120 | 0:00 | 0.1456 | 7 | 0.0059 | 0.1748 | 0.1807 | 0.1776 | 0.0023 | 0 | 3 | 0.1456 | 0.1747 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
217 | 1139.54 | 44264.6032 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.5119 | 0:240:120 | 0:00 | 0.1415 | 7 | 0.005 | 0.1699 | 0.1749 | 0.1721 | 0.0019 | 0 | 3 | 0.1415 | 0.1698 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
220 | 1143.013 | 44264.6032 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.8422 | 0:240:120 | 0:00 | 0.1376 | 7 | 0.0041 | 0.1658 | 0.1699 | 0.1678 | 0.0016 | 0 | 3 | 0.1376 | 0.1651 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
223 | 1146.587 | 44264.6033 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.219 | 0:240:120 | 0:00 | 0.1338 | 7 | 0.0045 | 0.1611 | 0.1656 | 0.1631 | 0.0016 | 0 | 3 | 0.1338 | 0.1606 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
226 | 1149.845 | 44264.6033 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.6434 | 0:240:120 | 0:00 | 0.1303 | 7 | 0.005 | 0.156 | 0.161 | 0.1586 | 0.0019 | 0 | 3 | 0.1303 | 0.1563 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
229 | 1153.14 | 44264.6034 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.1163 | 0:240:120 | 0:00 | 0.1268 | 7 | 0.0039 | 0.1522 | 0.1561 | 0.1545 | 0.0015 | 0 | 3 | 0.1268 | 0.1522 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
232 | 1156.413 | 44264.6034 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.6386 | 0:240:120 | 0:00 | 0.1235 | 7 | 0.0041 | 0.1492 | 0.1533 | 0.1508 | 0.0014 | 0 | 3 | 0.1235 | 0.1482 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
235 | 1159.536 | 44264.6034 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131.2114 | 0:240:120 | 0:00 | 0.1203 | 7 | 0.0038 | 0.1456 | 0.1494 | 0.1473 | 0.0015 | 0 | 3 | 0.1203 | 0.1444 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
238 | 1162.987 | 44264.6035 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.8356 | 0:240:120 | 0:00 | 0.1173 | 7 | 0.004 | 0.1412 | 0.1452 | 0.1433 | 0.0015 | 0 | 3 | 0.1173 | 0.1408 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
241 | 1166.244 | 44264.6035 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.5123 | 0:240:120 | 0:00 | 0.1144 | 7 | 0.0038 | 0.1376 | 0.1414 | 0.1394 | 0.0014 | 0 | 3 | 0.1144 | 0.1373 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
244 | 1169.471 | 44264.6035 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 139.2425 | 0:240:120 | 0:00 | 0.1116 | 7 | 0.0035 | 0.1345 | 0.138 | 0.1363 | 0.0013 | 0 | 3 | 0.1116 | 0.1339 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
247 | 1172.739 | 44264.6036 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.0274 | 0:240:120 | 0:00 | 0.1089 | 7 | 0.0042 | 0.1311 | 0.1353 | 0.1333 | 0.0015 | 0 | 3 | 0.1089 | 0.1307 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
250 | 1176.005 | 44264.6036 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.8679 | 0:240:120 | 0:00 | 0.1064 | 7 | 0.0038 | 0.128 | 0.1318 | 0.1303 | 0.0014 | 0 | 3 | 0.1064 | 0.1277 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
253 | 1179.222 | 44264.6037 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.7653 | 0:240:120 | 0:00 | 0.1039 | 7 | 0.0039 | 0.125 | 0.1289 | 0.1271 | 0.0014 | 0 | 3 | 0.1039 | 0.1247 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
256 | 1182.414 | 44264.6037 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.7206 | 0:240:120 | 0:00 | 0.1016 | 7 | 0.003 | 0.1226 | 0.1256 | 0.124 | 0.001 | 0 | 3 | 0.1016 | 0.1219 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
259 | 1185.554 | 44264.6037 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.735 | 0:240:120 | 0:00 | 0.0993 | 7 | 0.0031 | 0.1198 | 0.1229 | 0.1218 | 0.0012 | 0 | 3 | 0.0993 | 0.1192 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
262 | 1188.742 | 44264.6038 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.8097 | 0:240:120 | 0:00 | 0.0972 | 7 | 0.0043 | 0.1165 | 0.1208 | 0.1187 | 0.0017 | 0 | 3 | 0.0972 | 0.1166 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
265 | 1191.917 | 44264.6038 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 159.9459 | 0:240:120 | 0:00 | 0.0951 | 7 | 0.003 | 0.1148 | 0.1178 | 0.1163 | 0.0011 | 0 | 3 | 0.0951 | 0.1141 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
268 | 1195.24 | 44264.6038 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 163.1448 | 0:240:120 | 0:00 | 0.0931 | 7 | 0.0034 | 0.1116 | 0.115 | 0.1135 | 0.0013 | 0 | 3 | 0.0931 | 0.1117 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
271 | 1198.314 | 44264.6039 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.4077 | 0:240:120 | 0:00 | 0.0912 | 7 | 0.0034 | 0.1095 | 0.1129 | 0.1116 | 0.0014 | 0 | 3 | 0.0912 | 0.1094 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
274 | 1201.519 | 44264.6039 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.7359 | 0:240:120 | 0:00 | 0.0893 | 7 | 0.0029 | 0.1081 | 0.111 | 0.1093 | 0.001 | 0 | 3 | 0.0893 | 0.1072 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
277 | 1204.717 | 44264.604 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 173.1306 | 0:240:120 | 0:00 | 0.0876 | 7 | 0.0032 | 0.1053 | 0.1085 | 0.107 | 0.0012 | 0 | 3 | 0.0876 | 0.1051 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
280 | 1207.925 | 44264.604 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176.5932 | 0:240:120 | 0:00 | 0.0859 | 7 | 0.003 | 0.1023 | 0.1053 | 0.1041 | 0.0012 | 0 | 3 | 0.0859 | 0.1031 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
283 | 1211.155 | 44264.604 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 180.1251 | 0:240:120 | 0:00 | 0.0843 | 7 | 0.0025 | 0.1012 | 0.1037 | 0.1029 | 0.001 | 0 | 3 | 0.0843 | 0.1011 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
286 | 1214.281 | 44264.6041 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.7276 | 0:240:120 | 0:00 | 0.0827 | 7 | 0.0041 | 0.0989 | 0.103 | 0.1011 | 0.0014 | 0 | 3 | 0.0827 | 0.0993 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
289 | 1217.506 | 44264.6041 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 187.4021 | 0:240:120 | 0:00 | 0.0812 | 7 | 0.0035 | 0.0971 | 0.1006 | 0.0992 | 0.0013 | 0 | 3 | 0.0812 | 0.0975 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
292 | 1220.772 | 44264.6041 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 191.1502 | 0:240:120 | 0:00 | 0.0798 | 7 | 0.0033 | 0.0958 | 0.0991 | 0.0976 | 0.0013 | 0 | 3 | 0.0798 | 0.0958 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
295 | 1223.918 | 44264.6042 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.9732 | 0:240:120 | 0:00 | 0.0784 | 7 | 0.0028 | 0.0936 | 0.0964 | 0.0956 | 0.001 | 0 | 3 | 0.0784 | 0.0941 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
298 | 1227.124 | 44264.6042 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 198.8726 | 0:240:120 | 0:00 | 0.0771 | 7 | 0.0029 | 0.0919 | 0.0948 | 0.0938 | 0.0013 | 0 | 3 | 0.0771 | 0.0925 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
301 | 1230.253 | 44264.6043 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 202.8501 | 0:240:120 | 0:00 | 0.0758 | 7 | 0.0025 | 0.0908 | 0.0933 | 0.0923 | 0.0011 | 0 | 3 | 0.0758 | 0.091 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
304 | 1233.552 | 44264.6043 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 206.9071 | 0:240:120 | 0:00 | 0.0746 | 7 | 0.0031 | 0.0885 | 0.0916 | 0.0905 | 0.001 | 0 | 3 | 0.0746 | 0.0896 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
307 | 1236.65 | 44264.6043 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 211.0452 | 0:240:120 | 0:00 | 0.0735 | 7 | 0.0031 | 0.0877 | 0.0908 | 0.0895 | 0.0011 | 0 | 3 | 0.0735 | 0.0882 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
310 | 1239.904 | 44264.6044 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 215.2661 | 0:240:120 | 0:00 | 0.0723 | 7 | 0.0026 | 0.0867 | 0.0893 | 0.0879 | 0.001 | 0 | 3 | 0.0723 | 0.0868 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
313 | 1243.155 | 44264.6044 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 219.5715 | 0:240:120 | 0:00 | 0.0713 | 7 | 0.0025 | 0.0853 | 0.0878 | 0.087 | 0.0009 | 0 | 3 | 0.0713 | 0.0855 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
316 | 1246.248 | 44264.6044 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.9629 | 0:240:120 | 0:00 | 0.0702 | 7 | 0.0031 | 0.0833 | 0.0864 | 0.0853 | 0.0013 | 0 | 3 | 0.0702 | 0.0843 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
319 | 1249.511 | 44264.6045 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 228.4421 | 0:240:120 | 0:00 | 0.0692 | 7 | 0.0025 | 0.0825 | 0.085 | 0.084 | 0.001 | 0 | 3 | 0.0692 | 0.0831 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
322 | 1252.755 | 44264.6045 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 233.011 | 0:240:120 | 0:00 | 0.0683 | 7 | 0.0034 | 0.0812 | 0.0846 | 0.0832 | 0.0013 | 0 | 3 | 0.0683 | 0.0819 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
325 | 1256.016 | 44264.6045 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.6712 | 0:240:120 | 0:00 | 0.0674 | 7 | 0.0024 | 0.0804 | 0.0828 | 0.0817 | 0.0009 | 0 | 3 | 0.0674 | 0.0809 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
328 | 1259.237 | 44264.6046 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 242.4246 | 0:240:120 | 0:00 | 0.0665 | 7 | 0.003 | 0.079 | 0.082 | 0.0809 | 0.001 | 0 | 3 | 0.0665 | 0.0798 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
331 | 1262.332 | 44264.6046 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 247.2731 | 0:240:120 | 0:00 | 0.0657 | 7 | 0.0027 | 0.0781 | 0.0808 | 0.0793 | 0.001 | 0 | 3 | 0.0657 | 0.0788 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
334 | 1265.596 | 44264.6047 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 252.2186 | 0:240:120 | 0:00 | 0.0648 | 7 | 0.0029 | 0.0771 | 0.08 | 0.0785 | 0.0011 | 0 | 3 | 0.0648 | 0.0778 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
337 | 1268.718 | 44264.6047 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 257.263 | 0:240:120 | 0:00 | 0.0641 | 7 | 0.0025 | 0.0764 | 0.0789 | 0.0777 | 0.001 | 0 | 3 | 0.0641 | 0.0769 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
340 | 1271.98 | 44264.6047 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 262.4082 | 0:240:120 | 0:00 | 0.0633 | 7 | 0.0032 | 0.0748 | 0.078 | 0.0768 | 0.0011 | 0 | 3 | 0.0633 | 0.076 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
343 | 1275.229 | 44264.6048 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 267.6564 | 0:240:120 | 0:00 | 0.0626 | 7 | 0.0027 | 0.0739 | 0.0766 | 0.0754 | 0.001 | 0 | 3 | 0.0626 | 0.0751 | NP | NP | 1-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
346 | 1278.243 | 44264.6048 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 273.0095 | 0:240:120 | 0:00 | 0.0619 | 7 | 0.0029 | 0.073 | 0.0759 | 0.0747 | 0.0011 | 0 | 3 | 0.0619 | 0.0743 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
349 | 1281.476 | 44264.6048 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 278.4697 | 0:240:120 | 0:00 | 0.0613 | 7 | 0.003 | 0.0718 | 0.0748 | 0.0736 | 0.001 | 0 | 3 | 0.0613 | 0.0735 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
352 | 1284.754 | 44264.6049 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 284.0391 | 0:240:120 | 0:00 | 0.0606 | 7 | 0.0026 | 0.0719 | 0.0745 | 0.0735 | 0.0009 | 0 | 3 | 0.0606 | 0.0727 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
355 | 1288.017 | 44264.6049 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 289.7199 | 0:240:120 | 0:00 | 0.06 | 7 | 0.0011 | 0.0715 | 0.0726 | 0.0722 | 0.0005 | 0 | 3 | 0.06 | 0.072 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
358 | 1291.137 | 44264.605 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 295.5143 | 0:240:120 | 0:00 | 0.0594 | 7 | 0.0029 | 0.0694 | 0.0723 | 0.071 | 0.0009 | 0 | 3 | 0.0594 | 0.0713 | P | NP | 1-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
361 | 1295.45 | 44264.605 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 301.4246 | 0:240:120 | 0:00 | 0.0589 | 7 | 0.0029 | 0.0692 | 0.0721 | 0.0708 | 0.001 | 0 | 3 | 0.0589 | 0.0706 | NP | NP | 1-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
364 | 1298.701 | 44264.605 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 307.4531 | 0:240:120 | 0:00 | 0.0583 | 7 | 0.0025 | 0.0687 | 0.0712 | 0.0701 | 0.0009 | 0 | 3 | 0.0583 | 0.07 | NP | NP | 0-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
367 | 1301.898 | 44264.6051 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 313.6021 | 0:240:120 | 0:00 | 0.0578 | 7 | 0.0027 | 0.068 | 0.0707 | 0.0693 | 0.001 | 0 | 3 | 0.0578 | 0.0693 | P | NP | 1-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
370 | 1305.145 | 44264.6051 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 319.8742 | 0:240:120 | 0:00 | 0.0573 | 7 | 0.003 | 0.0674 | 0.0704 | 0.0688 | 0.0012 | 0 | 3 | 0.0573 | 0.0688 | NP | NP | 0-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
373 | 1308.259 | 44264.6052 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 326.2716 | 0:240:120 | 0:00 | 0.0568 | 7 | 0.0025 | 0.0662 | 0.0687 | 0.0677 | 0.0009 | 0 | 3 | 0.0568 | 0.0682 | P | NP | 0-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
376 | 1311.492 | 44264.6052 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 332.7971 | 0:240:120 | 0:00 | 0.0564 | 7 | 0.0032 | 0.0658 | 0.069 | 0.0675 | 0.0011 | 0 | 3 | 0.0564 | 0.0676 | P | NP | 1-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
379 | 1314.751 | 44264.6052 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 339.453 | 0:240:120 | 0:00 | 0.0559 | 7 | 0.0028 | 0.0649 | 0.0677 | 0.0665 | 0.0011 | 0 | 3 | 0.0559 | 0.0671 | P | NP | 1-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
382 | 1318.004 | 44264.6053 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 346.2421 | 0:240:120 | 0:00 | 0.0555 | 7 | 0.0031 | 0.0637 | 0.0668 | 0.0658 | 0.0012 | 0 | 3 | 0.0555 | 0.0666 | P | NP | 0-1-0-0-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
385 | 1321.235 | 44264.6053 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 353.1669 | 0:240:120 | 0:00 | 0.0551 | 7 | 0.0039 | 0.0634 | 0.0673 | 0.0656 | 0.0014 | 0 | 3 | 0.0551 | 0.0661 | P | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
388 | 1324.493 | 44264.6053 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 360.2303 | 0:240:120 | 0:00 | 0.0547 | 7 | 0.0033 | 0.0639 | 0.0672 | 0.0655 | 0.0011 | 0 | 3 | 0.0547 | 0.0656 | P | NP | 0-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
391 | 1327.739 | 44264.6054 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 367.4349 | 0:240:120 | 0:00 | 0.0543 | 7 | 0.004 | 0.0621 | 0.0661 | 0.0643 | 0.0013 | 0 | 3 | 0.0543 | 0.0652 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
394 | 1330.951 | 44264.6054 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 374.7836 | 0:240:120 | 0:00 | 0.0539 | 7 | 0.0028 | 0.0626 | 0.0654 | 0.0639 | 0.001 | 0 | 3 | 0.0539 | 0.0647 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
397 | 1334.192 | 44264.6055 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 382.2792 | 0:240:120 | 0:00 | 0.0536 | 7 | 0.0028 | 0.0617 | 0.0645 | 0.063 | 0.001 | 0 | 3 | 0.0536 | 0.0643 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
400 | 1337.455 | 44264.6055 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 389.9248 | 0:240:120 | 0:00 | 0.0533 | 7 | 0.0041 | 0.0612 | 0.0653 | 0.0633 | 0.0014 | 0 | 3 | 0.0533 | 0.0639 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
403 | 1340.744 | 44264.6055 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 397.7233 | 0:240:120 | 0:00 | 0.0529 | 7 | 0.003 | 0.061 | 0.064 | 0.0624 | 0.0011 | 0 | 3 | 0.0529 | 0.0635 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
406 | 1343.891 | 44264.6056 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 405.6778 | 0:240:120 | 0:00 | 0.0526 | 7 | 0.0023 | 0.0602 | 0.0625 | 0.0616 | 0.001 | 0 | 3 | 0.0526 | 0.0631 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
409 | 1347.111 | 44264.6056 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 413.7913 | 0:240:120 | 0:00 | 0.0523 | 7 | 0.0034 | 0.0598 | 0.0632 | 0.0616 | 0.0012 | 0 | 3 | 0.0523 | 0.0628 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
412 | 1350.367 | 44264.6056 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 422.0672 | 0:240:120 | 0:00 | 0.052 | 7 | 0.0025 | 0.0592 | 0.0617 | 0.0608 | 0.0009 | 0 | 3 | 0.052 | 0.0624 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
415 | 1353.6 | 44264.6057 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 430.5085 | 0:240:120 | 0:00 | 0.0518 | 7 | 0.0027 | 0.0592 | 0.0619 | 0.0606 | 0.0009 | 0 | 3 | 0.0518 | 0.0621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
418 | 1356.731 | 44264.6057 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 439.1187 | 0:240:120 | 0:00 | 0.0515 | 7 | 0.0029 | 0.0588 | 0.0617 | 0.0603 | 0.001 | 0 | 3 | 0.0515 | 0.0618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
421 | 1359.982 | 44264.6058 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 447.901 | 0:240:120 | 0:00 | 0.0513 | 7 | 0.0037 | 0.0574 | 0.0611 | 0.06 | 0.0014 | 0 | 3 | 0.0513 | 0.0615 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
424 | 1363.233 | 44264.6058 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 456.8591 | 0:240:120 | 0:00 | 0.051 | 7 | 0.0031 | 0.0577 | 0.0608 | 0.0593 | 0.0011 | 0 | 3 | 0.051 | 0.0612 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
427 | 1366.463 | 44264.6058 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 465.9962 | 0:240:120 | 0:00 | 0.0508 | 7 | 0.0025 | 0.058 | 0.0605 | 0.0591 | 0.0008 | 0 | 3 | 0.0508 | 0.0609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
430 | 1369.692 | 44264.6059 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 475.3162 | 0:240:120 | 0:00 | 0.0505 | 7 | 0.0033 | 0.0567 | 0.06 | 0.0587 | 0.0012 | 0 | 3 | 0.0505 | 0.0607 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
433 | 1372.772 | 44264.6059 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 484.8225 | 0:240:120 | 0:00 | 0.0503 | 7 | 0.0031 | 0.0563 | 0.0594 | 0.0581 | 0.0011 | 0 | 3 | 0.0503 | 0.0604 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
436 | 1376.05 | 44264.6059 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 494.5189 | 0:240:120 | 0:00 | 0.0501 | 7 | 0.0028 | 0.0561 | 0.0589 | 0.0579 | 0.001 | 0 | 3 | 0.0501 | 0.0601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
439 | 1379.273 | 44264.606 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 504.4093 | 0:240:120 | 0:00 | 0.0499 | 7 | 0.0036 | 0.0564 | 0.06 | 0.0581 | 0.0012 | 0 | 3 | 0.0499 | 0.0599 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
442 | 1382.526 | 44264.606 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 514.4975 | 0:240:120 | 0:00 | 0.0497 | 7 | 0.0028 | 0.0561 | 0.0589 | 0.0576 | 0.0011 | 0 | 3 | 0.0497 | 0.0597 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
445 | 1385.761 | 44264.606 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 524.7875 | 0:240:120 | 0:00 | 0.0495 | 7 | 0.0041 | 0.0545 | 0.0586 | 0.0567 | 0.0015 | 0 | 3 | 0.0495 | 0.0595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
448 | 1389.003 | 44264.6061 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 535.2832 | 0:240:120 | 0:00 | 0.0494 | 7 | 0.0027 | 0.0556 | 0.0583 | 0.0569 | 0.001 | 0 | 3 | 0.0494 | 0.0594 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
451 | 1392.26 | 44264.6061 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 545.9889 | 0:240:120 | 0:00 | 0.0492 | 7 | 0.0028 | 0.0552 | 0.058 | 0.0567 | 0.001 | 0 | 3 | 0.0492 | 0.0592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
454 | 1395.509 | 44264.6062 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 556.9087 | 0:240:120 | 0:00 | 0.049 | 7 | 0.0033 | 0.0544 | 0.0577 | 0.0563 | 0.0012 | 0 | 3 | 0.049 | 0.059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
457 | 1398.756 | 44264.6062 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 568.0468 | 0:240:120 | 0:00 | 0.0489 | 7 | 0.004 | 0.0543 | 0.0583 | 0.0562 | 0.0014 | 0 | 3 | 0.0489 | 0.0589 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
460 | 1401.989 | 44264.6062 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 579.4078 | 0:240:120 | 0:00 | 0.0487 | 7 | 0.0034 | 0.0539 | 0.0573 | 0.0558 | 0.0011 | 0 | 3 | 0.0487 | 0.0587 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
463 | 1405.229 | 44264.6063 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 590.9959 | 0:240:120 | 0:00 | 0.0486 | 7 | 0.0025 | 0.0538 | 0.0563 | 0.0549 | 0.0008 | 0 | 3 | 0.0486 | 0.0586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
466 | 1408.47 | 44264.6063 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 602.8158 | 0:240:120 | 0:00 | 0.0484 | 7 | 0.0031 | 0.0537 | 0.0568 | 0.055 | 0.001 | 0 | 3 | 0.0484 | 0.0584 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
469 | 1411.828 | 44264.6064 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 614.8722 | 0:240:120 | 0:00 | 0.0483 | 7 | 0.0029 | 0.0532 | 0.0561 | 0.0553 | 0.001 | 0 | 3 | 0.0483 | 0.0583 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
472 | 1415.072 | 44264.6064 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 627.1696 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.003 | 0.0531 | 0.0561 | 0.0548 | 0.0012 | 0 | 3 | 0.0482 | 0.0582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
475 | 1418.323 | 44264.6064 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 639.713 | 0:240:120 | 0:00 | 0.0481 | 7 | 0.0025 | 0.0533 | 0.0558 | 0.0547 | 0.0008 | 0 | 3 | 0.0481 | 0.0581 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
478 | 1421.56 | 44264.6065 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 652.5072 | 0:240:120 | 0:00 | 0.0479 | 7 | 0.0033 | 0.0525 | 0.0558 | 0.0543 | 0.0011 | 0 | 3 | 0.0479 | 0.0579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
481 | 1424.82 | 44264.6065 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 665.5574 | 0:240:120 | 0:00 | 0.0478 | 7 | 0.0028 | 0.0523 | 0.0551 | 0.0539 | 0.001 | 0 | 3 | 0.0478 | 0.0578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
484 | 1428.087 | 44264.6065 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 678.8685 | 0:240:120 | 0:00 | 0.0477 | 7 | 0.0029 | 0.0527 | 0.0556 | 0.0541 | 0.0011 | 0 | 3 | 0.0477 | 0.0577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
487 | 1431.326 | 44264.6066 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 692.4459 | 0:240:120 | 0:00 | 0.0476 | 7 | 0.0022 | 0.0519 | 0.0541 | 0.0532 | 0.0008 | 0 | 3 | 0.0476 | 0.0576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
490 | 1434.696 | 44264.6066 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 706.2948 | 0:240:120 | 0:00 | 0.0475 | 7 | 0.0021 | 0.0518 | 0.0539 | 0.0532 | 0.0008 | 0 | 3 | 0.0475 | 0.0575 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
493 | 1437.959 | 44264.6067 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 720.4207 | 0:240:120 | 0:00 | 0.0474 | 7 | 0.0029 | 0.052 | 0.0549 | 0.0533 | 0.001 | 0 | 3 | 0.0474 | 0.0574 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
496 | 1441.211 | 44264.6067 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 734.8291 | 0:240:120 | 0:00 | 0.0473 | 7 | 0.0028 | 0.0515 | 0.0543 | 0.053 | 0.001 | 0 | 3 | 0.0473 | 0.0573 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
499 | 1444.48 | 44264.6067 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 749.5257 | 0:240:120 | 0:00 | 0.0472 | 7 | 0.0032 | 0.0515 | 0.0547 | 0.0531 | 0.0012 | 0 | 3 | 0.0472 | 0.0572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
502 | 1447.735 | 44264.6068 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 764.5162 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.004 | 0.051 | 0.055 | 0.0531 | 0.0014 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
505 | 1450.976 | 44264.6068 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 779.8066 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.004 | 0.0508 | 0.0548 | 0.0528 | 0.0013 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
508 | 1454.232 | 44264.6068 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 795.4027 | 0:240:120 | 0:00 | 0.047 | 7 | 0.0033 | 0.0512 | 0.0545 | 0.053 | 0.0012 | 0 | 3 | 0.047 | 0.057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
511 | 1457.499 | 44264.6069 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 811.3108 | 0:240:120 | 0:00 | 0.0469 | 7 | 0.0028 | 0.0516 | 0.0544 | 0.0527 | 0.0009 | 0 | 3 | 0.0469 | 0.0569 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
514 | 1460.764 | 44264.6069 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 827.537 | 0:240:120 | 0:00 | 0.0468 | 7 | 0.004 | 0.0506 | 0.0546 | 0.0525 | 0.0011 | 0 | 3 | 0.0468 | 0.0568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
517 | 1464.054 | 44264.607 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 844.0877 | 0:240:120 | 0:00 | 0.0468 | 7 | 0.003 | 0.0513 | 0.0543 | 0.0526 | 0.0009 | 0 | 3 | 0.0468 | 0.0568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
520 | 1467.314 | 44264.607 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 860.9695 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0046 | 0.0501 | 0.0547 | 0.0526 | 0.0014 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
523 | 1470.604 | 44264.607 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 878.1888 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.0029 | 0.0511 | 0.054 | 0.0521 | 0.0009 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
526 | 1473.98 | 44264.6071 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 895.7526 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.0042 | 0.0505 | 0.0547 | 0.0522 | 0.0015 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
529 | 1477.248 | 44264.6071 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 913.6677 | 0:240:120 | 0:00 | 0.0465 | 7 | 0.0028 | 0.0502 | 0.053 | 0.0518 | 0.0012 | 0 | 3 | 0.0465 | 0.0565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
532 | 1480.495 | 44264.6071 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 931.941 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.005 | 0.0498 | 0.0548 | 0.0526 | 0.0017 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
535 | 1483.676 | 44264.6072 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 950.5799 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0038 | 0.0498 | 0.0536 | 0.0518 | 0.0014 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
538 | 1486.884 | 44264.6072 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 969.5914 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0029 | 0.0501 | 0.053 | 0.0516 | 0.0009 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
541 | 1490.159 | 44264.6073 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 988.9833 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0029 | 0.0507 | 0.0536 | 0.052 | 0.001 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
544 | 1493.438 | 44264.6073 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1008.7629 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0036 | 0.0503 | 0.0539 | 0.0518 | 0.0011 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
547 | 1496.706 | 44264.6073 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1028.9382 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0038 | 0.0498 | 0.0536 | 0.0516 | 0.0011 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
550 | 1499.958 | 44264.6074 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1049.517 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.004 | 0.0497 | 0.0537 | 0.0516 | 0.0014 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
553 | 1503.252 | 44264.6074 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1070.5073 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0025 | 0.0506 | 0.0531 | 0.0517 | 0.0009 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
556 | 1506.516 | 44264.6074 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1091.9175 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0049 | 0.0499 | 0.0548 | 0.0516 | 0.0014 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
559 | 1509.797 | 44264.6075 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1113.7558 | 0:240:120 | 0:00 | 0.046 | 7 | 0.004 | 0.0497 | 0.0537 | 0.0514 | 0.0013 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
562 | 1513.08 | 44264.6075 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1136.0309 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0029 | 0.0493 | 0.0522 | 0.0511 | 0.001 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
565 | 1516.336 | 44264.6076 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1158.7515 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.002 | 0.0499 | 0.0519 | 0.0511 | 0.0007 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
568 | 1519.6 | 44264.6076 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1181.9266 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0033 | 0.0499 | 0.0532 | 0.0513 | 0.0012 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
571 | 1522.89 | 44264.6076 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1205.5651 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.003 | 0.0494 | 0.0524 | 0.0509 | 0.001 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
574 | 1526.166 | 44264.6077 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1229.6764 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0018 | 0.0501 | 0.0519 | 0.0508 | 0.0007 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
577 | 1529.432 | 44264.6077 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1254.2699 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0029 | 0.0494 | 0.0523 | 0.0507 | 0.0009 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
580 | 1532.733 | 44264.6078 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1279.3553 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0033 | 0.0489 | 0.0522 | 0.0508 | 0.0011 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
583 | 1535.898 | 44264.6078 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1304.9424 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.003 | 0.0493 | 0.0523 | 0.0509 | 0.001 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
586 | 1539.207 | 44264.6078 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1331.0413 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0035 | 0.0495 | 0.053 | 0.0509 | 0.001 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
589 | 1542.538 | 44264.6079 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1357.6621 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0026 | 0.0488 | 0.0514 | 0.0506 | 0.0009 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
592 | 1545.933 | 44264.6079 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1384.8153 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.003 | 0.0485 | 0.0515 | 0.0506 | 0.001 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
595 | 1549.201 | 44264.6079 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1412.5117 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0031 | 0.0486 | 0.0517 | 0.0505 | 0.0011 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
598 | 1552.486 | 44264.608 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1440.7619 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0018 | 0.0494 | 0.0512 | 0.0505 | 0.0006 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
601 | 1555.799 | 44264.608 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1469.5771 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0018 | 0.0492 | 0.051 | 0.0504 | 0.0007 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
604 | 1559.095 | 44264.6081 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1498.9687 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0014 | 0.0497 | 0.0511 | 0.0505 | 0.0006 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
607 | 1562.371 | 44264.6081 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1528.948 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0035 | 0.0485 | 0.052 | 0.0501 | 0.0011 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
610 | 1565.647 | 44264.6081 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1559.527 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0027 | 0.0493 | 0.052 | 0.0503 | 0.001 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
613 | 1569.032 | 44264.6082 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1590.7175 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0028 | 0.0482 | 0.051 | 0.0502 | 0.001 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
616 | 1572.413 | 44264.6082 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1622.5319 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0026 | 0.0494 | 0.052 | 0.0505 | 0.001 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
619 | 1575.689 | 44264.6082 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1654.9825 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0038 | 0.0478 | 0.0516 | 0.05 | 0.0012 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
622 | 1579.005 | 44264.6083 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1688.0822 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0019 | 0.049 | 0.0509 | 0.0503 | 0.0007 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
625 | 1582.283 | 44264.6083 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1721.8438 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0029 | 0.0486 | 0.0515 | 0.0499 | 0.0009 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
628 | 1585.687 | 44264.6084 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1756.2807 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.002 | 0.0489 | 0.0509 | 0.05 | 0.0006 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
631 | 1589.004 | 44264.6084 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1791.4063 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0018 | 0.0484 | 0.0502 | 0.0495 | 0.0007 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
634 | 1592.429 | 44264.6084 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1827.2344 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0016 | 0.0486 | 0.0502 | 0.0496 | 0.0006 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
637 | 1595.731 | 44264.6085 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1863.7791 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0026 | 0.0479 | 0.0505 | 0.0498 | 0.0009 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
640 | 1598.922 | 44264.6085 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1901.0547 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0021 | 0.0489 | 0.051 | 0.0498 | 0.0007 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
643 | 1602.192 | 44264.6086 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1939.0758 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0028 | 0.0481 | 0.0509 | 0.0496 | 0.0009 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
646 | 1605.517 | 44264.6086 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1977.8573 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0017 | 0.0483 | 0.05 | 0.0494 | 0.0007 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
649 | 1608.697 | 44264.6086 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2017.4145 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0019 | 0.0488 | 0.0507 | 0.0496 | 0.0007 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
652 | 1611.981 | 44264.6087 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2057.7628 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0019 | 0.0485 | 0.0504 | 0.0496 | 0.0008 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
655 | 1615.283 | 44264.6087 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2098.918 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0028 | 0.0481 | 0.0509 | 0.0497 | 0.0009 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
658 | 1618.562 | 44264.6087 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2140.8964 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0016 | 0.0485 | 0.0501 | 0.0495 | 0.0006 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
661 | 1621.863 | 44264.6088 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2183.7143 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.002 | 0.0487 | 0.0507 | 0.05 | 0.0007 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
664 | 1625.163 | 44264.6088 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2227.3886 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0023 | 0.0485 | 0.0508 | 0.0499 | 0.0007 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
667 | 1628.35 | 44264.6089 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2271.9364 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0021 | 0.0482 | 0.0503 | 0.0495 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
670 | 1631.659 | 44264.6089 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2317.3751 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0011 | 0.0496 | 0.0507 | 0.05 | 0.0005 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
673 | 1635 | 44264.6089 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2363.7226 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0024 | 0.0485 | 0.0509 | 0.0496 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
676 | 1638.295 | 44264.609 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2410.997 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0025 | 0.0486 | 0.0511 | 0.0496 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
679 | 1641.597 | 44264.609 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2459.217 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.002 | 0.0479 | 0.0499 | 0.0492 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
682 | 1644.926 | 44264.609 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2508.4013 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0015 | 0.0485 | 0.05 | 0.0495 | 0.0006 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
685 | 1648.35 | 44264.6091 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2558.5694 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0023 | 0.0479 | 0.0502 | 0.0493 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
688 | 1651.671 | 44264.6091 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2609.7407 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0024 | 0.0482 | 0.0506 | 0.0494 | 0.0007 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
691 | 1654.98 | 44264.6092 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2661.9356 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0019 | 0.0479 | 0.0498 | 0.0491 | 0.0007 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
694 | 1658.33 | 44264.6092 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2715.1743 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0024 | 0.0479 | 0.0503 | 0.0491 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
697 | 1661.555 | 44264.6092 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2769.4777 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0022 | 0.0477 | 0.0499 | 0.0492 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
700 | 1664.887 | 44264.6093 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2824.8673 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0025 | 0.0479 | 0.0504 | 0.0496 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
703 | 1668.097 | 44264.6093 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2881.3646 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0026 | 0.0475 | 0.0501 | 0.0492 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
706 | 1671.419 | 44264.6094 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2938.9919 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.0481 | 0.0505 | 0.0493 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
709 | 1674.776 | 44264.6094 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2997.7718 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.0481 | 0.0504 | 0.0494 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
712 | 1678.073 | 44264.6094 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3057.7272 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0022 | 0.0479 | 0.0501 | 0.0493 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
715 | 1681.367 | 44264.6095 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3118.8818 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0022 | 0.0477 | 0.0499 | 0.0489 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
718 | 1684.675 | 44264.6095 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3181.2594 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0019 | 0.048 | 0.0499 | 0.0491 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
721 | 1688.025 | 44264.6095 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3244.8846 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0018 | 0.0485 | 0.0503 | 0.0495 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
724 | 1691.344 | 44264.6096 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3309.7823 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0017 | 0.0486 | 0.0503 | 0.0495 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
727 | 1694.655 | 44264.6096 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3375.9779 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0026 | 0.0478 | 0.0504 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
730 | 1697.854 | 44264.6097 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3443.4975 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0014 | 0.048 | 0.0494 | 0.0489 | 0.0006 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
733 | 1701.094 | 44264.6097 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3512.3674 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0027 | 0.0479 | 0.0506 | 0.0491 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
736 | 1704.461 | 44264.6097 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3582.6148 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0014 | 0.0489 | 0.0503 | 0.0497 | 0.0006 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
739 | 1707.783 | 44264.6098 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3654.2671 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0026 | 0.048 | 0.0506 | 0.0491 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
742 | 1711.152 | 44264.6098 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3727.3524 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0019 | 0.0483 | 0.0502 | 0.0492 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
745 | 1714.485 | 44264.6099 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3801.8995 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0017 | 0.0488 | 0.0505 | 0.0496 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
748 | 1717.808 | 44264.6099 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3877.9375 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.0481 | 0.0505 | 0.0495 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
751 | 1721.042 | 44264.6099 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3955.4962 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.0478 | 0.0503 | 0.0493 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
754 | 1724.372 | 44264.61 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4034.6061 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0031 | 0.0475 | 0.0506 | 0.0492 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
757 | 1727.717 | 44264.61 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4115.2982 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0022 | 0.0477 | 0.0499 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
760 | 1731.174 | 44264.61 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4197.6042 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.003 | 0.0478 | 0.0508 | 0.049 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
763 | 1734.626 | 44264.6101 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4281.5563 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.048 | 0.0505 | 0.0492 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
766 | 1737.859 | 44264.6101 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4367.1874 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0028 | 0.0477 | 0.0505 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
769 | 1741.208 | 44264.6102 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4454.5312 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0018 | 0.0486 | 0.0504 | 0.0494 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
772 | 1744.692 | 44264.6102 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4543.6218 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0017 | 0.0484 | 0.0501 | 0.049 | 0.0006 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
775 | 1748.103 | 44264.6102 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4634.4942 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.0478 | 0.0503 | 0.0491 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
778 | 1751.454 | 44264.6103 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4727.1841 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0017 | 0.0489 | 0.0506 | 0.0495 | 0.0006 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
781 | 1754.784 | 44264.6103 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4821.7278 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0019 | 0.0479 | 0.0498 | 0.0489 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
784 | 1758.03 | 44264.6104 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4918.1624 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.0482 | 0.0506 | 0.0494 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
787 | 1761.48 | 44264.6104 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5016.5256 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0021 | 0.0481 | 0.0502 | 0.0491 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
790 | 1764.808 | 44264.6104 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5116.8561 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0026 | 0.0475 | 0.0501 | 0.0491 | 0.0009 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
793 | 1768.159 | 44264.6105 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5219.1932 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0019 | 0.0478 | 0.0497 | 0.0489 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
796 | 1771.422 | 44264.6105 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5323.5771 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0015 | 0.0476 | 0.0491 | 0.0486 | 0.0005 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
799 | 1774.78 | 44264.6106 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5430.0486 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0024 | 0.0479 | 0.0503 | 0.049 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
802 | 1778.03 | 44264.6106 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5538.6496 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0016 | 0.0481 | 0.0497 | 0.0488 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
805 | 1781.371 | 44264.6106 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5649.4226 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0022 | 0.0479 | 0.0501 | 0.0491 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
808 | 1784.712 | 44264.6107 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5762.4111 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0017 | 0.0483 | 0.05 | 0.0491 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
811 | 1787.949 | 44264.6107 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5877.6593 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0017 | 0.0484 | 0.0501 | 0.0491 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
814 | 1791.2 | 44264.6107 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5995.2125 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0017 | 0.0483 | 0.05 | 0.0493 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
817 | 1794.56 | 44264.6108 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6115.1167 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0021 | 0.0478 | 0.0499 | 0.0489 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
820 | 1797.937 | 44264.6108 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6237.4191 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0011 | 0.0488 | 0.0499 | 0.0492 | 0.0005 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
823 | 1801.296 | 44264.6109 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6362.1674 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0014 | 0.0483 | 0.0497 | 0.0489 | 0.0005 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
826 | 1804.551 | 44264.6109 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6489.4108 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0021 | 0.0484 | 0.0505 | 0.0493 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
829 | 1807.929 | 44264.6109 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6619.199 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0018 | 0.0479 | 0.0497 | 0.0487 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
832 | 1811.268 | 44264.611 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6751.583 | 0:240:120 | 0:00 | 0.045 | 7 | 0.002 | 0.0483 | 0.0503 | 0.0491 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
835 | 1814.545 | 44264.611 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6886.6146 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0025 | 0.0475 | 0.05 | 0.0486 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
838 | 1817.882 | 44264.6111 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7024.3469 | 0:240:120 | 0:00 | 0.045 | 7 | 0.002 | 0.0478 | 0.0498 | 0.049 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
841 | 1821.255 | 44264.6111 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7164.8339 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0026 | 0.0477 | 0.0503 | 0.0489 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
844 | 1824.599 | 44264.6111 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7308.1305 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0012 | 0.0479 | 0.0491 | 0.0487 | 0.0005 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
847 | 1827.847 | 44264.6112 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7454.2932 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0023 | 0.0477 | 0.05 | 0.0488 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
850 | 1831.119 | 44264.6112 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7603.379 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0024 | 0.048 | 0.0504 | 0.0491 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
853 | 1834.494 | 44264.6112 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7755.4466 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0017 | 0.0479 | 0.0496 | 0.0486 | 0.0005 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
856 | 1837.862 | 44264.6113 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7910.5555 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0012 | 0.0484 | 0.0496 | 0.0491 | 0.0004 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
859 | 1841.218 | 44264.6113 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8068.7666 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0019 | 0.0479 | 0.0498 | 0.0489 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
862 | 1844.594 | 44264.6114 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8230.142 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0012 | 0.0484 | 0.0496 | 0.0487 | 0.0005 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
865 | 1847.969 | 44264.6114 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8394.7448 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0018 | 0.0477 | 0.0495 | 0.0486 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
868 | 1851.224 | 44264.6114 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8562.6397 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0012 | 0.0479 | 0.0491 | 0.0485 | 0.0005 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
871 | 1854.567 | 44264.6115 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8733.8925 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0012 | 0.0478 | 0.049 | 0.0485 | 0.0005 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
874 | 1857.85 | 44264.6115 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8908.5704 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0026 | 0.0478 | 0.0504 | 0.049 | 0.0009 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
877 | 1861.147 | 44264.6116 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9086.7418 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0012 | 0.0482 | 0.0494 | 0.0487 | 0.0004 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
880 | 1864.508 | 44264.6116 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9268.4766 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0015 | 0.0485 | 0.05 | 0.0491 | 0.0005 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
883 | 1867.883 | 44264.6116 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9453.8461 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0016 | 0.0482 | 0.0498 | 0.0491 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
886 | 1871.152 | 44264.6117 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9642.923 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0024 | 0.0475 | 0.0499 | 0.0486 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
889 | 1874.522 | 44264.6117 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9835.7815 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0011 | 0.0479 | 0.049 | 0.0486 | 0.0004 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
892 | 1877.822 | 44264.6117 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10032.4971 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0023 | 0.0476 | 0.0499 | 0.0488 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
895 | 1881.122 | 44264.6118 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10233.1471 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0027 | 0.0477 | 0.0504 | 0.0484 | 0.0009 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
898 | 1884.427 | 44264.6118 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10437.81 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0016 | 0.0478 | 0.0494 | 0.0488 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
901 | 1887.808 | 44264.6119 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10646.5662 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0018 | 0.0478 | 0.0496 | 0.0487 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
904 | 1891.189 | 44264.6119 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10859.4976 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0019 | 0.0474 | 0.0493 | 0.0485 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
907 | 1894.447 | 44264.6119 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11076.6875 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0026 | 0.0473 | 0.0499 | 0.0485 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
910 | 1897.838 | 44264.612 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11298.2213 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0015 | 0.0476 | 0.0491 | 0.0484 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
913 | 1901.121 | 44264.612 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11524.1857 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0024 | 0.0468 | 0.0492 | 0.0482 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
916 | 1904.445 | 44264.6121 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11754.6694 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0014 | 0.0476 | 0.049 | 0.0481 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
919 | 1907.829 | 44264.6121 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11989.7628 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0018 | 0.0475 | 0.0493 | 0.0485 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
922 | 1964.019 | 44264.6127 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.8 | 0:240:120 | 0:00 | 6.1593 | 7 | 18.8475 | 35.543 | 54.3905 | 44.2731 | 7.7437 | 59.9655 | 3 | 6.1593 | 30.8029 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
925 | 2109.348 | 44264.6144 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.4 | 0:240:120 | 0:00 | 5.2673 | 7 | 18.2704 | 16.6303 | 34.9007 | 24.1565 | 7.7146 | 59.5156 | 3 | 5.2673 | 17.4158 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
928 | 2193.048 | 44264.6154 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30 | 0:240:120 | 0:00 | 4.5905 | 7 | 3.0699 | 8.937 | 12.0069 | 9.9807 | 1.4326 | 2.0523 | 3 | 4.5905 | 12.0642 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
931 | 2228.745 | 44264.6158 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.6 | 0:240:120 | 0:00 | 4.0596 | 7 | 0.8777 | 7.7765 | 8.6542 | 8.1655 | 0.3791 | 0.1437 | 3 | 4.0596 | 9.4117 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
934 | 2256.684 | 44264.6161 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.2 | 0:240:120 | 0:00 | 3.6324 | 7 | 0.9727 | 6.6278 | 7.6005 | 7.0989 | 0.4102 | 0.1683 | 3 | 3.6324 | 7.6909 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
937 | 2281.549 | 44264.6164 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.8 | 0:240:120 | 0:00 | 3.2813 | 7 | 1.0178 | 5.558 | 6.5758 | 6.0202 | 0.4436 | 0.1968 | 3 | 3.2813 | 6.4848 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
940 | 2303.123 | 44264.6167 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.5 | 0:240:120 | 0:00 | 2.9436 | 7 | 0.7031 | 4.4869 | 5.19 | 4.7592 | 0.3227 | 0.1042 | 3 | 2.9436 | 5.4665 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
943 | 2320.784 | 44264.6169 | Vista Coord | Main | 25Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.1 | 0:240:120 | 0:00 | 2.7011 | 7 | 0.3295 | 4.128 | 4.4575 | 4.2866 | 0.1384 | 0.0192 | 3 | 2.7011 | 4.8079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
946 | 2432.467 | 44264.6182 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33 | 0:240:120 | 0:00 | 9.5688 | 7 | 16.2756 | 81.5801 | 97.8557 | 86.2332 | 5.7565 | 33.1368 | 3 | 9.5688 | 9999999 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
949 | 2764.614 | 44264.622 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.66 | 0:240:120 | 0:00 | 7.7705 | 7 | 16.8308 | 63.7699 | 80.6007 | 70.6085 | 7.5948 | 57.6814 | 3 | 7.7705 | 101.5883 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
952 | 2990.761 | 44264.6246 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.3332 | 0:240:120 | 0:00 | 6.502 | 7 | 16.8577 | 45.1222 | 61.9799 | 51.6502 | 7.7281 | 59.723 | 3 | 6.502 | 32.8902 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
955 | 3160.007 | 44264.6266 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.0199 | 0:240:120 | 0:00 | 5.5599 | 7 | 16.0439 | 26.6499 | 42.6938 | 32.8483 | 7.3441 | 53.9353 | 3 | 5.5599 | 19.3218 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
958 | 3270.142 | 44264.6279 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.7203 | 0:240:120 | 0:00 | 4.833 | 7 | 12.6476 | 9.5118 | 22.1594 | 13.7685 | 6.1832 | 38.2325 | 3 | 4.833 | 13.5272 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
961 | 3326.254 | 44264.6285 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.4347 | 0:240:120 | 0:00 | 4.2557 | 7 | 0.8333 | 8.3676 | 9.2009 | 8.7211 | 0.3643 | 0.1327 | 3 | 4.2557 | 10.3153 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
964 | 3355.876 | 44264.6289 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.1634 | 0:240:120 | 0:00 | 3.7863 | 7 | 0.9005 | 7.2025 | 8.103 | 7.6194 | 0.3851 | 0.1483 | 3 | 3.7863 | 8.2753 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
967 | 3382.156 | 44264.6292 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.9066 | 0:240:120 | 0:00 | 3.3975 | 7 | 0.9802 | 6.1104 | 7.0906 | 6.4627 | 0.4701 | 0.221 | 3 | 3.3975 | 6.8658 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
970 | 3405.484 | 44264.6294 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.6648 | 0:240:120 | 0:00 | 3.0704 | 7 | 0.9001 | 5.0033 | 5.9034 | 5.3405 | 0.4127 | 0.1703 | 3 | 3.0704 | 5.8343 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
973 | 3425.331 | 44264.6297 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.4381 | 0:240:120 | 0:00 | 2.7916 | 7 | 0.2993 | 4.3231 | 4.6224 | 4.4478 | 0.1319 | 0.0174 | 3 | 2.7916 | 5.0472 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
976 | 3441.964 | 44264.6298 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.2268 | 0:240:120 | 0:00 | 2.5513 | 7 | 0.3279 | 3.9394 | 4.2673 | 4.0537 | 0.1586 | 0.0252 | 3 | 2.5513 | 4.4273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
979 | 3457.445 | 44264.63 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.0314 | 0:240:120 | 0:00 | 2.3422 | 7 | 0.2757 | 3.5373 | 3.813 | 3.6557 | 0.1188 | 0.0141 | 3 | 2.3422 | 3.9269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
982 | 3471.565 | 44264.6302 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.852 | 0:240:120 | 0:00 | 2.1587 | 7 | 0.3354 | 3.1148 | 3.4502 | 3.2348 | 0.1611 | 0.026 | 3 | 2.1587 | 3.5146 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
985 | 3484.443 | 44264.6303 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.689 | 0:240:120 | 0:00 | 1.9965 | 7 | 0.1639 | 2.8317 | 2.9956 | 2.8943 | 0.0752 | 0.0057 | 3 | 1.9965 | 3.1694 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
988 | 3496.285 | 44264.6305 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.5428 | 0:240:120 | 0:00 | 1.8523 | 7 | 0.1647 | 2.623 | 2.7877 | 2.6823 | 0.0777 | 0.006 | 3 | 1.8523 | 2.8763 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
991 | 3507.424 | 44264.6306 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.4137 | 0:240:120 | 0:00 | 1.7232 | 7 | 0.1632 | 2.3929 | 2.5561 | 2.4525 | 0.0774 | 0.006 | 3 | 1.7232 | 2.6246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
994 | 3517.904 | 44264.6307 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.3019 | 0:240:120 | 0:00 | 1.6071 | 7 | 0.1634 | 2.1698 | 2.3332 | 2.2375 | 0.072 | 0.0052 | 3 | 1.6071 | 2.4062 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
997 | 3527.718 | 44264.6308 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.208 | 0:240:120 | 0:00 | 1.5023 | 7 | 0.1026 | 2.0313 | 2.1339 | 2.0702 | 0.0471 | 0.0022 | 3 | 1.5023 | 2.215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1000 | 3537.101 | 44264.6309 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.1321 | 0:240:120 | 0:00 | 1.4072 | 7 | 0.1063 | 1.8934 | 1.9997 | 1.9332 | 0.0497 | 0.0025 | 3 | 1.4072 | 2.0464 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1003 | 3545.969 | 44264.6311 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.0748 | 0:240:120 | 0:00 | 1.3205 | 7 | 0.1015 | 1.754 | 1.8555 | 1.7898 | 0.0489 | 0.0024 | 3 | 1.3205 | 1.8967 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1006 | 3554.376 | 44264.6311 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.0363 | 0:240:120 | 0:00 | 1.2414 | 7 | 0.0827 | 1.6285 | 1.7112 | 1.6572 | 0.0399 | 0.0016 | 3 | 1.2414 | 1.7631 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1009 | 3562.339 | 44264.6312 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.017 | 0:240:120 | 0:00 | 1.1688 | 7 | 0.0677 | 1.5301 | 1.5978 | 1.5542 | 0.0326 | 0.0011 | 3 | 1.1688 | 1.643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1012 | 3570.506 | 44264.6313 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.0173 | 0:240:120 | 0:00 | 1.1021 | 7 | 0.0662 | 1.4358 | 1.502 | 1.4595 | 0.0318 | 0.001 | 3 | 1.1021 | 1.5348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1015 | 3578.074 | 44264.6314 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.0377 | 0:240:120 | 0:00 | 1.0406 | 7 | 0.0687 | 1.3381 | 1.4068 | 1.3628 | 0.0326 | 0.0011 | 3 | 1.0406 | 1.4367 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1018 | 3585.304 | 44264.6315 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.0784 | 0:240:120 | 0:00 | 0.9838 | 7 | 0.0541 | 1.2652 | 1.3193 | 1.2874 | 0.024 | 0.0006 | 3 | 0.9838 | 1.3474 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1021 | 3592.255 | 44264.6316 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.14 | 0:240:120 | 0:00 | 0.9312 | 7 | 0.0568 | 1.1884 | 1.2452 | 1.2096 | 0.0263 | 0.0007 | 3 | 0.9312 | 1.266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1024 | 3598.86 | 44264.6317 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.2228 | 0:240:120 | 0:00 | 0.8824 | 7 | 0.05 | 1.1176 | 1.1676 | 1.1352 | 0.0242 | 0.0006 | 3 | 0.8824 | 1.1914 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1027 | 3605.18 | 44264.6317 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.3273 | 0:240:120 | 0:00 | 0.837 | 7 | 0.0395 | 1.0629 | 1.1024 | 1.0777 | 0.0179 | 0.0003 | 3 | 0.837 | 1.1229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1030 | 3611.528 | 44264.6318 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.4538 | 0:240:120 | 0:00 | 0.7947 | 7 | 0.0412 | 1.0031 | 1.0443 | 1.0187 | 0.019 | 0.0004 | 3 | 0.7947 | 1.0598 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1033 | 3617.863 | 44264.6319 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.6029 | 0:240:120 | 0:00 | 0.7553 | 7 | 0.0365 | 0.9495 | 0.986 | 0.9629 | 0.0171 | 0.0003 | 3 | 0.7553 | 1.0015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1036 | 3623.99 | 44264.632 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.7749 | 0:240:120 | 0:00 | 0.7184 | 7 | 0.0312 | 0.9016 | 0.9328 | 0.9126 | 0.0148 | 0.0002 | 3 | 0.7184 | 0.9476 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1039 | 3629.603 | 44264.632 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.9704 | 0:240:120 | 0:00 | 0.6839 | 7 | 0.0335 | 0.8555 | 0.889 | 0.8671 | 0.0159 | 0.0003 | 3 | 0.6839 | 0.8976 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1042 | 3635.354 | 44264.6321 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.1898 | 0:240:120 | 0:00 | 0.6516 | 7 | 0.0297 | 0.8094 | 0.8391 | 0.8219 | 0.0126 | 0.0002 | 3 | 0.6516 | 0.8512 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1045 | 3641.02 | 44264.6322 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.4336 | 0:240:120 | 0:00 | 0.6212 | 7 | 0.0237 | 0.7743 | 0.798 | 0.7827 | 0.0112 | 0.0001 | 3 | 0.6212 | 0.8079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1048 | 3646.322 | 44264.6322 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.7023 | 0:240:120 | 0:00 | 0.5927 | 7 | 0.0273 | 0.7345 | 0.7618 | 0.744 | 0.0123 | 0.0002 | 3 | 0.5927 | 0.7676 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1051 | 3651.678 | 44264.6323 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.9964 | 0:240:120 | 0:00 | 0.5659 | 7 | 0.0223 | 0.7004 | 0.7227 | 0.7091 | 0.0101 | 0.0001 | 3 | 0.5659 | 0.7299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1054 | 3657.055 | 44264.6323 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.3163 | 0:240:120 | 0:00 | 0.5407 | 7 | 0.0229 | 0.6678 | 0.6907 | 0.6764 | 0.0106 | 0.0001 | 3 | 0.5407 | 0.6947 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1057 | 3662.203 | 44264.6324 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.6626 | 0:240:120 | 0:00 | 0.5169 | 7 | 0.0201 | 0.6373 | 0.6574 | 0.6451 | 0.0091 | 0.0001 | 3 | 0.5169 | 0.6617 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1060 | 3667.453 | 44264.6325 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.0359 | 0:240:120 | 0:00 | 0.4944 | 7 | 0.018 | 0.6092 | 0.6272 | 0.6159 | 0.0082 | 0.0001 | 3 | 0.4944 | 0.6307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1063 | 3672.334 | 44264.6325 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.4366 | 0:240:120 | 0:00 | 0.4732 | 7 | 0.0206 | 0.5795 | 0.6001 | 0.5873 | 0.0095 | 0.0001 | 3 | 0.4732 | 0.6017 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1066 | 3677.256 | 44264.6326 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.8653 | 0:240:120 | 0:00 | 0.4532 | 7 | 0.0182 | 0.5556 | 0.5738 | 0.5626 | 0.0081 | 0.0001 | 3 | 0.4532 | 0.5743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1069 | 3682.042 | 44264.6326 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.3226 | 0:240:120 | 0:00 | 0.4343 | 7 | 0.0165 | 0.5309 | 0.5474 | 0.5371 | 0.0077 | 0.0001 | 3 | 0.4343 | 0.5486 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1072 | 3687.06 | 44264.6327 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.8091 | 0:240:120 | 0:00 | 0.4164 | 7 | 0.0143 | 0.5094 | 0.5237 | 0.5151 | 0.0063 | 0 | 3 | 0.4164 | 0.5244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1075 | 3691.698 | 44264.6327 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.3252 | 0:240:120 | 0:00 | 0.3994 | 7 | 0.0153 | 0.4871 | 0.5024 | 0.4931 | 0.0069 | 0 | 3 | 0.3994 | 0.5015 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1078 | 3696.197 | 44264.6328 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.8718 | 0:240:120 | 0:00 | 0.3833 | 7 | 0.0131 | 0.467 | 0.4801 | 0.4719 | 0.0057 | 0 | 3 | 0.3833 | 0.4799 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1081 | 3700.916 | 44264.6328 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.4492 | 0:240:120 | 0:00 | 0.368 | 7 | 0.0132 | 0.4486 | 0.4618 | 0.4534 | 0.0061 | 0 | 3 | 0.368 | 0.4595 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1084 | 3705.383 | 44264.6329 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.0582 | 0:240:120 | 0:00 | 0.3536 | 7 | 0.0119 | 0.4312 | 0.4431 | 0.4357 | 0.0051 | 0 | 3 | 0.3536 | 0.4402 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1087 | 3709.761 | 44264.6329 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.6993 | 0:240:120 | 0:00 | 0.3398 | 7 | 0.0125 | 0.4132 | 0.4257 | 0.4179 | 0.0054 | 0 | 3 | 0.3398 | 0.422 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1090 | 3714.125 | 44264.633 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.3733 | 0:240:120 | 0:00 | 0.3268 | 7 | 0.0114 | 0.3967 | 0.4081 | 0.4017 | 0.0046 | 0 | 3 | 0.3268 | 0.4047 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1093 | 3718.347 | 44264.633 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.0808 | 0:240:120 | 0:00 | 0.3143 | 7 | 0.0104 | 0.3817 | 0.3921 | 0.3857 | 0.0045 | 0 | 3 | 0.3143 | 0.3884 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1096 | 3722.614 | 44264.6331 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.8224 | 0:240:120 | 0:00 | 0.3025 | 7 | 0.0092 | 0.3675 | 0.3767 | 0.3711 | 0.0039 | 0 | 3 | 0.3025 | 0.3728 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1099 | 3726.876 | 44264.6331 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.5989 | 0:240:120 | 0:00 | 0.2913 | 7 | 0.0103 | 0.353 | 0.3633 | 0.3568 | 0.0045 | 0 | 3 | 0.2913 | 0.3581 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1102 | 3731.044 | 44264.6332 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.4108 | 0:240:120 | 0:00 | 0.2806 | 7 | 0.008 | 0.3408 | 0.3488 | 0.3437 | 0.0037 | 0 | 3 | 0.2806 | 0.3441 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1105 | 3735.166 | 44264.6332 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.259 | 0:240:120 | 0:00 | 0.2704 | 7 | 0.0096 | 0.3271 | 0.3367 | 0.3309 | 0.0043 | 0 | 3 | 0.2704 | 0.3309 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1108 | 3739.284 | 44264.6333 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.1442 | 0:240:120 | 0:00 | 0.2607 | 7 | 0.0081 | 0.316 | 0.3241 | 0.3193 | 0.0036 | 0 | 3 | 0.2607 | 0.3182 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1111 | 3743.761 | 44264.6333 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.0671 | 0:240:120 | 0:00 | 0.2515 | 7 | 0.0077 | 0.3045 | 0.3122 | 0.3077 | 0.0034 | 0 | 3 | 0.2515 | 0.3063 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1114 | 3747.673 | 44264.6334 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.0285 | 0:240:120 | 0:00 | 0.2427 | 7 | 0.0067 | 0.2941 | 0.3008 | 0.2968 | 0.0029 | 0 | 3 | 0.2427 | 0.2948 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1117 | 3751.821 | 44264.6334 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.029 | 0:240:120 | 0:00 | 0.2343 | 7 | 0.0073 | 0.2833 | 0.2906 | 0.2861 | 0.003 | 0 | 3 | 0.2343 | 0.284 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1120 | 3755.831 | 44264.6335 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.0696 | 0:240:120 | 0:00 | 0.2263 | 7 | 0.0088 | 0.2723 | 0.2811 | 0.276 | 0.0037 | 0 | 3 | 0.2263 | 0.2736 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1123 | 3759.86 | 44264.6335 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.151 | 0:240:120 | 0:00 | 0.2186 | 7 | 0.0064 | 0.2637 | 0.2701 | 0.2668 | 0.0026 | 0 | 3 | 0.2186 | 0.2638 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1126 | 3763.73 | 44264.6336 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 108.274 | 0:240:120 | 0:00 | 0.2113 | 7 | 0.0066 | 0.2556 | 0.2622 | 0.2584 | 0.0026 | 0 | 3 | 0.2113 | 0.2544 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1129 | 3767.977 | 44264.6336 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.4395 | 0:240:120 | 0:00 | 0.2043 | 7 | 0.0062 | 0.2468 | 0.253 | 0.2493 | 0.0026 | 0 | 3 | 0.2043 | 0.2455 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1132 | 3771.874 | 44264.6337 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.6483 | 0:240:120 | 0:00 | 0.1977 | 7 | 0.0054 | 0.2395 | 0.2449 | 0.2417 | 0.0023 | 0 | 3 | 0.1977 | 0.2372 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1135 | 3775.666 | 44264.6337 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.9013 | 0:240:120 | 0:00 | 0.1913 | 7 | 0.0071 | 0.2305 | 0.2376 | 0.2338 | 0.0026 | 0 | 3 | 0.1913 | 0.2296 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1138 | 3779.403 | 44264.6338 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.1993 | 0:240:120 | 0:00 | 0.1852 | 7 | 0.0063 | 0.223 | 0.2293 | 0.2257 | 0.0026 | 0 | 3 | 0.1852 | 0.2223 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1141 | 3783.206 | 44264.6338 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.5433 | 0:240:120 | 0:00 | 0.1794 | 7 | 0.0052 | 0.2172 | 0.2224 | 0.2196 | 0.0021 | 0 | 3 | 0.1794 | 0.2153 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1144 | 3787.106 | 44264.6338 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.9341 | 0:240:120 | 0:00 | 0.1739 | 7 | 0.0052 | 0.2107 | 0.2159 | 0.2129 | 0.002 | 0 | 3 | 0.1739 | 0.2086 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1147 | 3791.01 | 44264.6339 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.3728 | 0:240:120 | 0:00 | 0.1686 | 7 | 0.0052 | 0.2036 | 0.2088 | 0.2059 | 0.002 | 0 | 3 | 0.1686 | 0.2023 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1150 | 3794.558 | 44264.6339 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.8603 | 0:240:120 | 0:00 | 0.1635 | 7 | 0.006 | 0.197 | 0.203 | 0.1999 | 0.002 | 0 | 3 | 0.1635 | 0.1962 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1153 | 3798.63 | 44264.634 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 129.3975 | 0:240:120 | 0:00 | 0.1586 | 7 | 0.0046 | 0.1915 | 0.1961 | 0.1938 | 0.0016 | 0 | 3 | 0.1586 | 0.1903 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1156 | 3802.387 | 44264.634 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131.9854 | 0:240:120 | 0:00 | 0.154 | 7 | 0.0051 | 0.1856 | 0.1907 | 0.188 | 0.0019 | 0 | 3 | 0.154 | 0.1847 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1159 | 3805.927 | 44264.6341 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.6251 | 0:240:120 | 0:00 | 0.1495 | 7 | 0.0052 | 0.1802 | 0.1854 | 0.183 | 0.0018 | 0 | 3 | 0.1495 | 0.1794 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1162 | 3809.727 | 44264.6341 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.3176 | 0:240:120 | 0:00 | 0.1452 | 7 | 0.005 | 0.1752 | 0.1802 | 0.1773 | 0.002 | 0 | 3 | 0.1452 | 0.1743 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1165 | 3813.366 | 44264.6341 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 140.064 | 0:240:120 | 0:00 | 0.1412 | 7 | 0.0052 | 0.1695 | 0.1747 | 0.1722 | 0.0021 | 0 | 3 | 0.1412 | 0.1694 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1168 | 3817.161 | 44264.6342 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.8653 | 0:240:120 | 0:00 | 0.1373 | 7 | 0.0037 | 0.1658 | 0.1695 | 0.1677 | 0.0015 | 0 | 3 | 0.1373 | 0.1647 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1171 | 3820.816 | 44264.6342 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 145.7226 | 0:240:120 | 0:00 | 0.1335 | 7 | 0.0045 | 0.1607 | 0.1652 | 0.1629 | 0.0017 | 0 | 3 | 0.1335 | 0.1602 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1174 | 3824.501 | 44264.6343 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.637 | 0:240:120 | 0:00 | 0.1299 | 7 | 0.0041 | 0.1565 | 0.1606 | 0.1588 | 0.0016 | 0 | 3 | 0.1299 | 0.1559 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1177 | 3827.948 | 44264.6343 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 151.6098 | 0:240:120 | 0:00 | 0.1265 | 7 | 0.005 | 0.1515 | 0.1565 | 0.1543 | 0.0018 | 0 | 3 | 0.1265 | 0.1518 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1180 | 3831.379 | 44264.6344 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 154.642 | 0:240:120 | 0:00 | 0.1232 | 7 | 0.0042 | 0.1481 | 0.1523 | 0.1507 | 0.0014 | 0 | 3 | 0.1232 | 0.1479 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1183 | 3835.272 | 44264.6344 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 157.7348 | 0:240:120 | 0:00 | 0.1201 | 7 | 0.003 | 0.1457 | 0.1487 | 0.1471 | 0.0012 | 0 | 3 | 0.1201 | 0.1441 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1186 | 3839.08 | 44264.6344 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.8895 | 0:240:120 | 0:00 | 0.117 | 7 | 0.0036 | 0.1409 | 0.1445 | 0.1429 | 0.0013 | 0 | 3 | 0.117 | 0.1405 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1189 | 3842.634 | 44264.6345 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.1073 | 0:240:120 | 0:00 | 0.1141 | 7 | 0.0044 | 0.1368 | 0.1412 | 0.1396 | 0.0014 | 0 | 3 | 0.1141 | 0.137 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1192 | 3846.166 | 44264.6345 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 167.3894 | 0:240:120 | 0:00 | 0.1114 | 7 | 0.0033 | 0.1343 | 0.1376 | 0.1364 | 0.0012 | 0 | 3 | 0.1114 | 0.1336 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1195 | 3849.58 | 44264.6346 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.7372 | 0:240:120 | 0:00 | 0.1087 | 7 | 0.0042 | 0.1306 | 0.1348 | 0.1331 | 0.0016 | 0 | 3 | 0.1087 | 0.1305 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1198 | 3853.018 | 44264.6346 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 174.152 | 0:240:120 | 0:00 | 0.1062 | 7 | 0.003 | 0.1275 | 0.1305 | 0.1296 | 0.0011 | 0 | 3 | 0.1062 | 0.1274 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1201 | 3856.443 | 44264.6346 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 177.635 | 0:240:120 | 0:00 | 0.1037 | 7 | 0.0031 | 0.1251 | 0.1282 | 0.1267 | 0.0012 | 0 | 3 | 0.1037 | 0.1245 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1204 | 3860.028 | 44264.6347 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 181.1877 | 0:240:120 | 0:00 | 0.1014 | 7 | 0.0031 | 0.122 | 0.1251 | 0.1237 | 0.0013 | 0 | 3 | 0.1014 | 0.1217 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1207 | 3863.581 | 44264.6347 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 184.8115 | 0:240:120 | 0:00 | 0.0991 | 7 | 0.0038 | 0.1194 | 0.1232 | 0.1215 | 0.0014 | 0 | 3 | 0.0991 | 0.119 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1210 | 3867.273 | 44264.6348 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 188.5077 | 0:240:120 | 0:00 | 0.097 | 7 | 0.0028 | 0.1169 | 0.1197 | 0.1189 | 0.0012 | 0 | 3 | 0.097 | 0.1164 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1213 | 3870.819 | 44264.6348 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 192.2778 | 0:240:120 | 0:00 | 0.0949 | 7 | 0.0018 | 0.1149 | 0.1167 | 0.1159 | 0.0007 | 0 | 3 | 0.0949 | 0.1139 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1216 | 3874.265 | 44264.6349 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 196.1234 | 0:240:120 | 0:00 | 0.0929 | 7 | 0.0042 | 0.111 | 0.1152 | 0.1137 | 0.0015 | 0 | 3 | 0.0929 | 0.1115 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1219 | 3877.796 | 44264.6349 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 200.0459 | 0:240:120 | 0:00 | 0.091 | 7 | 0.0031 | 0.1093 | 0.1124 | 0.1112 | 0.0012 | 0 | 3 | 0.091 | 0.1092 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1222 | 3881.247 | 44264.6349 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 204.0468 | 0:240:120 | 0:00 | 0.0892 | 7 | 0.0036 | 0.1075 | 0.1111 | 0.1091 | 0.0011 | 0 | 3 | 0.0892 | 0.107 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1225 | 3884.677 | 44264.635 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.1277 | 0:240:120 | 0:00 | 0.0874 | 7 | 0.003 | 0.1065 | 0.1095 | 0.1078 | 0.0011 | 0 | 3 | 0.0874 | 0.1049 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1228 | 3888.354 | 44264.635 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 212.2903 | 0:240:120 | 0:00 | 0.0858 | 7 | 0.0035 | 0.1022 | 0.1057 | 0.1043 | 0.0014 | 0 | 3 | 0.0858 | 0.1029 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1231 | 3891.803 | 44264.6351 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 216.5361 | 0:240:120 | 0:00 | 0.0841 | 7 | 0.0036 | 0.1004 | 0.104 | 0.1027 | 0.0014 | 0 | 3 | 0.0841 | 0.101 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1234 | 3895.38 | 44264.6351 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 220.8668 | 0:240:120 | 0:00 | 0.0826 | 7 | 0.0023 | 0.0998 | 0.1021 | 0.1011 | 0.0008 | 0 | 3 | 0.0826 | 0.0991 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1237 | 3898.808 | 44264.6351 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 225.2841 | 0:240:120 | 0:00 | 0.0811 | 7 | 0.0033 | 0.0972 | 0.1005 | 0.0991 | 0.0013 | 0 | 3 | 0.0811 | 0.0973 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1240 | 3902.361 | 44264.6352 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 229.7898 | 0:240:120 | 0:00 | 0.0797 | 7 | 0.0021 | 0.0961 | 0.0982 | 0.0971 | 0.0007 | 0 | 3 | 0.0797 | 0.0956 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1243 | 3905.765 | 44264.6352 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.3856 | 0:240:120 | 0:00 | 0.0783 | 7 | 0.0026 | 0.0933 | 0.0959 | 0.0953 | 0.001 | 0 | 3 | 0.0783 | 0.094 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1246 | 3909.212 | 44264.6353 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 239.0733 | 0:240:120 | 0:00 | 0.077 | 7 | 0.0035 | 0.0919 | 0.0954 | 0.0937 | 0.0013 | 0 | 3 | 0.077 | 0.0924 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1249 | 3912.666 | 44264.6353 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 243.8548 | 0:240:120 | 0:00 | 0.0757 | 7 | 0.0037 | 0.0905 | 0.0942 | 0.0926 | 0.0012 | 0 | 3 | 0.0757 | 0.0909 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1252 | 3916.113 | 44264.6353 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 248.7319 | 0:240:120 | 0:00 | 0.0745 | 7 | 0.0041 | 0.0882 | 0.0923 | 0.0909 | 0.0015 | 0 | 3 | 0.0745 | 0.0894 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1255 | 3919.531 | 44264.6354 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 253.7065 | 0:240:120 | 0:00 | 0.0734 | 7 | 0.0036 | 0.0874 | 0.091 | 0.0893 | 0.0013 | 0 | 3 | 0.0734 | 0.088 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1258 | 3922.972 | 44264.6354 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 258.7807 | 0:240:120 | 0:00 | 0.0722 | 7 | 0.003 | 0.0864 | 0.0894 | 0.0882 | 0.0013 | 0 | 3 | 0.0722 | 0.0867 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1261 | 3926.398 | 44264.6355 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 263.9563 | 0:240:120 | 0:00 | 0.0712 | 7 | 0.0016 | 0.0857 | 0.0873 | 0.0866 | 0.0006 | 0 | 3 | 0.0712 | 0.0854 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1264 | 3929.816 | 44264.6355 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 269.2354 | 0:240:120 | 0:00 | 0.0701 | 7 | 0.0032 | 0.0837 | 0.0869 | 0.0853 | 0.0012 | 0 | 3 | 0.0701 | 0.0842 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1267 | 3933.269 | 44264.6355 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 274.6201 | 0:240:120 | 0:00 | 0.0692 | 7 | 0.0027 | 0.0826 | 0.0853 | 0.0842 | 0.0011 | 0 | 3 | 0.0692 | 0.083 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1270 | 3936.732 | 44264.6356 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 280.1125 | 0:240:120 | 0:00 | 0.0682 | 7 | 0.0037 | 0.0816 | 0.0853 | 0.0834 | 0.0012 | 0 | 3 | 0.0682 | 0.0818 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1273 | 3940.269 | 44264.6356 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 285.7147 | 0:240:120 | 0:00 | 0.0673 | 7 | 0.0031 | 0.0802 | 0.0833 | 0.0818 | 0.0011 | 0 | 3 | 0.0673 | 0.0808 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1276 | 3943.714 | 44264.6357 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 291.429 | 0:240:120 | 0:00 | 0.0664 | 7 | 0.0027 | 0.0796 | 0.0823 | 0.081 | 0.0009 | 0 | 3 | 0.0664 | 0.0797 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1279 | 3947.529 | 44264.6357 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 297.2576 | 0:240:120 | 0:00 | 0.0656 | 7 | 0.0025 | 0.0775 | 0.08 | 0.0793 | 0.0009 | 0 | 3 | 0.0656 | 0.0787 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1282 | 3951.027 | 44264.6357 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 303.2028 | 0:240:120 | 0:00 | 0.0648 | 7 | 0.003 | 0.0768 | 0.0798 | 0.0785 | 0.0009 | 0 | 3 | 0.0648 | 0.0777 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1285 | 3954.539 | 44264.6358 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 309.2668 | 0:240:120 | 0:00 | 0.064 | 7 | 0.0033 | 0.0761 | 0.0794 | 0.0777 | 0.0011 | 0 | 3 | 0.064 | 0.0768 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1288 | 3957.995 | 44264.6358 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 315.4522 | 0:240:120 | 0:00 | 0.0633 | 7 | 0.0027 | 0.0748 | 0.0775 | 0.0763 | 0.001 | 0 | 3 | 0.0633 | 0.0759 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1291 | 3961.557 | 44264.6359 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 321.7612 | 0:240:120 | 0:00 | 0.0625 | 7 | 0.0034 | 0.0745 | 0.0779 | 0.0761 | 0.0013 | 0 | 3 | 0.0625 | 0.075 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1294 | 3965.239 | 44264.6359 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 328.1964 | 0:240:120 | 0:00 | 0.0619 | 7 | 0.0035 | 0.0726 | 0.0761 | 0.0746 | 0.0011 | 0 | 3 | 0.0619 | 0.0742 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1297 | 3968.661 | 44264.6359 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 334.7604 | 0:240:120 | 0:00 | 0.0612 | 7 | 0.0025 | 0.0719 | 0.0744 | 0.0734 | 0.0011 | 0 | 3 | 0.0612 | 0.0734 | P | NP | 1-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1300 | 3972.267 | 44264.636 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 341.4556 | 0:240:120 | 0:00 | 0.0606 | 7 | 0.0029 | 0.072 | 0.0749 | 0.0733 | 0.0009 | 0 | 3 | 0.0606 | 0.0727 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1303 | 3975.804 | 44264.636 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 348.2847 | 0:240:120 | 0:00 | 0.0599 | 7 | 0.0028 | 0.0707 | 0.0735 | 0.0721 | 0.001 | 0 | 3 | 0.0599 | 0.0719 | NP | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1306 | 3979.343 | 44264.6361 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 355.2504 | 0:240:120 | 0:00 | 0.0594 | 7 | 0.0032 | 0.0699 | 0.0731 | 0.0712 | 0.001 | 0 | 3 | 0.0594 | 0.0712 | P | NP | 1-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1309 | 3982.795 | 44264.6361 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 362.3554 | 0:240:120 | 0:00 | 0.0588 | 7 | 0.0025 | 0.0694 | 0.0719 | 0.0706 | 0.0008 | 0 | 3 | 0.0588 | 0.0706 | NP | NP | 0-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1312 | 3986.165 | 44264.6361 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 369.6025 | 0:240:120 | 0:00 | 0.0583 | 7 | 0.0025 | 0.0691 | 0.0716 | 0.0701 | 0.0008 | 0 | 3 | 0.0583 | 0.0699 | NP | NP | 0-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1315 | 3989.599 | 44264.6362 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 376.9945 | 0:240:120 | 0:00 | 0.0577 | 7 | 0.0031 | 0.0671 | 0.0702 | 0.0691 | 0.0012 | 0 | 3 | 0.0577 | 0.0693 | P | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1318 | 3993.156 | 44264.6362 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 384.5344 | 0:240:120 | 0:00 | 0.0572 | 7 | 0.0025 | 0.0671 | 0.0696 | 0.0688 | 0.0008 | 0 | 3 | 0.0572 | 0.0687 | NP | NP | 0-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1321 | 3996.694 | 44264.6363 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 392.2251 | 0:240:120 | 0:00 | 0.0568 | 7 | 0.0024 | 0.0665 | 0.0689 | 0.0678 | 0.0009 | 0 | 3 | 0.0568 | 0.0681 | P | NP | 1-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1324 | 4000.159 | 44264.6363 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 400.0696 | 0:240:120 | 0:00 | 0.0563 | 7 | 0.0029 | 0.066 | 0.0689 | 0.0674 | 0.0011 | 0 | 3 | 0.0563 | 0.0676 | P | NP | 1-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1327 | 4003.578 | 44264.6363 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 408.071 | 0:240:120 | 0:00 | 0.0559 | 7 | 0.0028 | 0.0654 | 0.0682 | 0.0666 | 0.001 | 0 | 3 | 0.0559 | 0.067 | P | NP | 1-1-0-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1330 | 4006.981 | 44264.6364 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 416.2324 | 0:240:120 | 0:00 | 0.0554 | 7 | 0.0029 | 0.0639 | 0.0668 | 0.0657 | 0.001 | 0 | 3 | 0.0554 | 0.0665 | P | NP | 0-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1333 | 4010.436 | 44264.6364 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 424.5571 | 0:240:120 | 0:00 | 0.055 | 7 | 0.0025 | 0.0637 | 0.0662 | 0.0653 | 0.001 | 0 | 3 | 0.055 | 0.066 | P | NP | 0-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1336 | 4013.865 | 44264.6365 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 433.0482 | 0:240:120 | 0:00 | 0.0546 | 7 | 0.0031 | 0.0633 | 0.0664 | 0.065 | 0.0013 | 0 | 3 | 0.0546 | 0.0656 | P | NP | 1-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1339 | 4017.302 | 44264.6365 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 441.7092 | 0:240:120 | 0:00 | 0.0543 | 7 | 0.0039 | 0.0622 | 0.0661 | 0.0642 | 0.0013 | 0 | 3 | 0.0543 | 0.0651 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1342 | 4020.732 | 44264.6365 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 450.5434 | 0:240:120 | 0:00 | 0.0539 | 7 | 0.0042 | 0.0618 | 0.066 | 0.064 | 0.0013 | 0 | 3 | 0.0539 | 0.0647 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1345 | 4024.242 | 44264.6366 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 459.5542 | 0:240:120 | 0:00 | 0.0536 | 7 | 0.003 | 0.0612 | 0.0642 | 0.0632 | 0.0011 | 0 | 3 | 0.0536 | 0.0643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1348 | 4027.68 | 44264.6366 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 468.7453 | 0:240:120 | 0:00 | 0.0532 | 7 | 0.0029 | 0.0613 | 0.0642 | 0.063 | 0.0011 | 0 | 3 | 0.0532 | 0.0639 | P | NP | 0-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1351 | 4031.131 | 44264.6367 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 478.1202 | 0:240:120 | 0:00 | 0.0529 | 7 | 0.0023 | 0.0612 | 0.0635 | 0.0626 | 0.001 | 0 | 3 | 0.0529 | 0.0635 | P | NP | 0-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1354 | 4034.588 | 44264.6367 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 487.6826 | 0:240:120 | 0:00 | 0.0526 | 7 | 0.0033 | 0.0601 | 0.0634 | 0.0618 | 0.0011 | 0 | 3 | 0.0526 | 0.0631 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1357 | 4037.986 | 44264.6367 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 497.4363 | 0:240:120 | 0:00 | 0.0523 | 7 | 0.0025 | 0.0601 | 0.0626 | 0.0615 | 0.0008 | 0 | 3 | 0.0523 | 0.0628 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1360 | 4041.411 | 44264.6368 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 507.385 | 0:240:120 | 0:00 | 0.052 | 7 | 0.0029 | 0.059 | 0.0619 | 0.0608 | 0.0011 | 0 | 3 | 0.052 | 0.0624 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1363 | 4044.867 | 44264.6368 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 517.5327 | 0:240:120 | 0:00 | 0.0517 | 7 | 0.0025 | 0.0589 | 0.0614 | 0.0605 | 0.0009 | 0 | 3 | 0.0517 | 0.0621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1366 | 4048.271 | 44264.6369 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 527.8834 | 0:240:120 | 0:00 | 0.0515 | 7 | 0.0029 | 0.0593 | 0.0622 | 0.0606 | 0.0011 | 0 | 3 | 0.0515 | 0.0618 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1369 | 4052.056 | 44264.6369 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 538.441 | 0:240:120 | 0:00 | 0.0512 | 7 | 0.0029 | 0.0581 | 0.061 | 0.0598 | 0.0012 | 0 | 3 | 0.0512 | 0.0615 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1372 | 4055.52 | 44264.6369 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 549.2099 | 0:240:120 | 0:00 | 0.051 | 7 | 0.0031 | 0.0575 | 0.0606 | 0.0594 | 0.0011 | 0 | 3 | 0.051 | 0.0612 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1375 | 4058.97 | 44264.637 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 560.1941 | 0:240:120 | 0:00 | 0.0508 | 7 | 0.003 | 0.0573 | 0.0603 | 0.0589 | 0.0011 | 0 | 3 | 0.0508 | 0.0609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1378 | 4062.5 | 44264.637 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 571.3979 | 0:240:120 | 0:00 | 0.0505 | 7 | 0.0031 | 0.0571 | 0.0602 | 0.0588 | 0.0012 | 0 | 3 | 0.0505 | 0.0606 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1381 | 4065.921 | 44264.6371 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 582.8259 | 0:240:120 | 0:00 | 0.0503 | 7 | 0.0028 | 0.0565 | 0.0593 | 0.058 | 0.0008 | 0 | 3 | 0.0503 | 0.0604 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1384 | 4069.587 | 44264.6371 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 594.4824 | 0:240:120 | 0:00 | 0.0501 | 7 | 0.0031 | 0.0565 | 0.0596 | 0.058 | 0.0012 | 0 | 3 | 0.0501 | 0.0601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1387 | 4073.002 | 44264.6372 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 606.3721 | 0:240:120 | 0:00 | 0.0499 | 7 | 0.0036 | 0.0554 | 0.059 | 0.0576 | 0.0014 | 0 | 3 | 0.0499 | 0.0599 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1390 | 4076.432 | 44264.6372 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 618.4995 | 0:240:120 | 0:00 | 0.0497 | 7 | 0.0042 | 0.0556 | 0.0598 | 0.0576 | 0.0014 | 0 | 3 | 0.0497 | 0.0597 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1393 | 4080.108 | 44264.6372 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 630.8695 | 0:240:120 | 0:00 | 0.0495 | 7 | 0.003 | 0.0552 | 0.0582 | 0.0567 | 0.001 | 0 | 3 | 0.0495 | 0.0595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1396 | 4083.548 | 44264.6373 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 643.4869 | 0:240:120 | 0:00 | 0.0494 | 7 | 0.0027 | 0.0553 | 0.058 | 0.0566 | 0.0009 | 0 | 3 | 0.0494 | 0.0594 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1399 | 4086.907 | 44264.6373 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 656.3566 | 0:240:120 | 0:00 | 0.0492 | 7 | 0.0036 | 0.0542 | 0.0578 | 0.0563 | 0.0011 | 0 | 3 | 0.0492 | 0.0592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1402 | 4090.319 | 44264.6374 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 669.4838 | 0:240:120 | 0:00 | 0.049 | 7 | 0.0033 | 0.0547 | 0.058 | 0.0566 | 0.0012 | 0 | 3 | 0.049 | 0.059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1405 | 4094.1 | 44264.6374 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 682.8734 | 0:240:120 | 0:00 | 0.0489 | 7 | 0.0033 | 0.0547 | 0.058 | 0.0564 | 0.0012 | 0 | 3 | 0.0489 | 0.0589 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1408 | 4097.546 | 44264.6374 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 696.5309 | 0:240:120 | 0:00 | 0.0487 | 7 | 0.0029 | 0.054 | 0.0569 | 0.0555 | 0.001 | 0 | 3 | 0.0487 | 0.0587 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1411 | 4100.935 | 44264.6375 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 710.4615 | 0:240:120 | 0:00 | 0.0486 | 7 | 0.0029 | 0.0538 | 0.0567 | 0.0553 | 0.001 | 0 | 3 | 0.0486 | 0.0586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1414 | 4104.624 | 44264.6375 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 724.6708 | 0:240:120 | 0:00 | 0.0484 | 7 | 0.0029 | 0.0541 | 0.057 | 0.0556 | 0.0011 | 0 | 3 | 0.0484 | 0.0584 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1417 | 4108.062 | 44264.6376 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 739.1642 | 0:240:120 | 0:00 | 0.0483 | 7 | 0.0031 | 0.0533 | 0.0564 | 0.0549 | 0.001 | 0 | 3 | 0.0483 | 0.0583 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1420 | 4111.752 | 44264.6376 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 753.9475 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0028 | 0.0531 | 0.0559 | 0.0544 | 0.001 | 0 | 3 | 0.0482 | 0.0582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1423 | 4115.182 | 44264.6376 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 769.0264 | 0:240:120 | 0:00 | 0.048 | 7 | 0.0028 | 0.0533 | 0.0561 | 0.0546 | 0.0011 | 0 | 3 | 0.048 | 0.058 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1426 | 4118.602 | 44264.6377 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 784.4069 | 0:240:120 | 0:00 | 0.0479 | 7 | 0.0018 | 0.053 | 0.0548 | 0.0542 | 0.0007 | 0 | 3 | 0.0479 | 0.0579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1429 | 4122.376 | 44264.6377 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 800.0951 | 0:240:120 | 0:00 | 0.0478 | 7 | 0.0036 | 0.0521 | 0.0557 | 0.0538 | 0.0013 | 0 | 3 | 0.0478 | 0.0578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1432 | 4125.765 | 44264.6378 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 816.097 | 0:240:120 | 0:00 | 0.0477 | 7 | 0.0023 | 0.052 | 0.0543 | 0.0534 | 0.0011 | 0 | 3 | 0.0477 | 0.0577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1435 | 4129.122 | 44264.6378 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 832.4189 | 0:240:120 | 0:00 | 0.0476 | 7 | 0.0036 | 0.0516 | 0.0552 | 0.0535 | 0.0011 | 0 | 3 | 0.0476 | 0.0576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1438 | 4132.782 | 44264.6378 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 849.0673 | 0:240:120 | 0:00 | 0.0475 | 7 | 0.003 | 0.0519 | 0.0549 | 0.0533 | 0.0009 | 0 | 3 | 0.0475 | 0.0575 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1441 | 4136.226 | 44264.6379 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 866.0486 | 0:240:120 | 0:00 | 0.0474 | 7 | 0.0032 | 0.0514 | 0.0546 | 0.053 | 0.001 | 0 | 3 | 0.0474 | 0.0574 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1444 | 4139.54 | 44264.6379 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 883.3696 | 0:240:120 | 0:00 | 0.0473 | 7 | 0.0039 | 0.0509 | 0.0548 | 0.0532 | 0.0013 | 0 | 3 | 0.0473 | 0.0573 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1447 | 4142.968 | 44264.638 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 901.037 | 0:240:120 | 0:00 | 0.0472 | 7 | 0.004 | 0.0507 | 0.0547 | 0.0529 | 0.0012 | 0 | 3 | 0.0472 | 0.0572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1450 | 4146.631 | 44264.638 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 919.0577 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0034 | 0.0514 | 0.0548 | 0.053 | 0.001 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1453 | 4150.179 | 44264.638 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 937.4389 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0022 | 0.0513 | 0.0535 | 0.0527 | 0.0009 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1456 | 4153.5 | 44264.6381 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 956.1877 | 0:240:120 | 0:00 | 0.047 | 7 | 0.0032 | 0.0514 | 0.0546 | 0.0529 | 0.0012 | 0 | 3 | 0.047 | 0.057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1459 | 4156.923 | 44264.6381 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 975.3114 | 0:240:120 | 0:00 | 0.0469 | 7 | 0.0029 | 0.0514 | 0.0543 | 0.0526 | 0.0009 | 0 | 3 | 0.0469 | 0.0569 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1462 | 4160.376 | 44264.6382 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 994.8177 | 0:240:120 | 0:00 | 0.0468 | 7 | 0.0026 | 0.0515 | 0.0541 | 0.0527 | 0.0009 | 0 | 3 | 0.0468 | 0.0568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1465 | 4163.791 | 44264.6382 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1014.714 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0035 | 0.0512 | 0.0547 | 0.0526 | 0.0011 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1468 | 4167.126 | 44264.6382 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1035.0083 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0031 | 0.0508 | 0.0539 | 0.0524 | 0.0011 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1471 | 4170.584 | 44264.6383 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1055.7085 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.0024 | 0.0513 | 0.0537 | 0.0525 | 0.0008 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1474 | 4174.013 | 44264.6383 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1076.8226 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.0041 | 0.0497 | 0.0538 | 0.052 | 0.0014 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1477 | 4177.36 | 44264.6384 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1098.3591 | 0:240:120 | 0:00 | 0.0465 | 7 | 0.0028 | 0.0508 | 0.0536 | 0.0521 | 0.001 | 0 | 3 | 0.0465 | 0.0565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1480 | 4180.775 | 44264.6384 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1120.3263 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0039 | 0.0498 | 0.0537 | 0.0519 | 0.0014 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1483 | 4184.326 | 44264.6384 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1142.7328 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0034 | 0.0504 | 0.0538 | 0.052 | 0.0011 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1486 | 4187.77 | 44264.6385 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1165.5874 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.003 | 0.0503 | 0.0533 | 0.0519 | 0.001 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1489 | 4191.203 | 44264.6385 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1188.8992 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0025 | 0.0508 | 0.0533 | 0.0519 | 0.0008 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1492 | 4194.69 | 44264.6386 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1212.6772 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0038 | 0.0499 | 0.0537 | 0.0517 | 0.0014 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1495 | 4198.012 | 44264.6386 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1236.9307 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0034 | 0.0497 | 0.0531 | 0.0516 | 0.0012 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1498 | 4201.456 | 44264.6386 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1261.6693 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0031 | 0.0498 | 0.0529 | 0.0513 | 0.0011 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1501 | 4204.78 | 44264.6387 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1286.9027 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0035 | 0.0502 | 0.0537 | 0.0516 | 0.0011 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1504 | 4208.685 | 44264.6387 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1312.6408 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0037 | 0.0497 | 0.0534 | 0.0517 | 0.0013 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1507 | 4212.135 | 44264.6388 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1338.8936 | 0:240:120 | 0:00 | 0.046 | 7 | 0.004 | 0.0497 | 0.0537 | 0.0513 | 0.0013 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1510 | 4215.573 | 44264.6388 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1365.6715 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0029 | 0.0495 | 0.0524 | 0.0512 | 0.001 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1513 | 4218.894 | 44264.6388 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1392.9849 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0028 | 0.0499 | 0.0527 | 0.0512 | 0.0011 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1516 | 4222.338 | 44264.6389 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1420.8446 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.003 | 0.0493 | 0.0523 | 0.0511 | 0.001 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1519 | 4225.836 | 44264.6389 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1449.2615 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0036 | 0.0491 | 0.0527 | 0.0509 | 0.0013 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1522 | 4229.272 | 44264.639 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1478.2467 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0042 | 0.0495 | 0.0537 | 0.0511 | 0.0014 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1525 | 4232.481 | 44264.639 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1507.8116 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0029 | 0.0494 | 0.0523 | 0.0509 | 0.0011 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1528 | 4235.919 | 44264.639 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1537.9679 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0029 | 0.0488 | 0.0517 | 0.0508 | 0.0012 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1531 | 4239.251 | 44264.6391 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1568.7272 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0021 | 0.0498 | 0.0519 | 0.0508 | 0.0007 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1534 | 4242.502 | 44264.6391 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1600.1018 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0031 | 0.0491 | 0.0522 | 0.0507 | 0.001 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1537 | 4245.925 | 44264.6392 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1632.1038 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0029 | 0.049 | 0.0519 | 0.0503 | 0.0009 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1540 | 4249.373 | 44264.6392 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1664.7459 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0017 | 0.0498 | 0.0515 | 0.0509 | 0.0006 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1543 | 4252.838 | 44264.6392 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1698.0408 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0017 | 0.0497 | 0.0514 | 0.0507 | 0.0006 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1546 | 4256.19 | 44264.6393 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1732.0016 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0017 | 0.0499 | 0.0516 | 0.0507 | 0.0006 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1549 | 4259.621 | 44264.6393 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1766.6416 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0029 | 0.0491 | 0.052 | 0.0507 | 0.001 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1552 | 4263.147 | 44264.6394 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1801.9745 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0015 | 0.0498 | 0.0513 | 0.0506 | 0.0005 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1555 | 4266.471 | 44264.6394 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1838.014 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0022 | 0.0489 | 0.0511 | 0.0499 | 0.0007 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1558 | 4270.037 | 44264.6394 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1874.7742 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0025 | 0.0489 | 0.0514 | 0.0503 | 0.0008 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1561 | 4273.369 | 44264.6395 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1912.2697 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0019 | 0.0493 | 0.0512 | 0.0504 | 0.0008 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1564 | 4276.776 | 44264.6395 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1950.5151 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0019 | 0.0497 | 0.0516 | 0.0506 | 0.0006 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1567 | 4280.22 | 44264.6396 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1989.5254 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0016 | 0.0496 | 0.0512 | 0.0505 | 0.0006 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1570 | 4283.406 | 44264.6396 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2029.3159 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0022 | 0.0489 | 0.0511 | 0.0502 | 0.0006 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1573 | 4286.812 | 44264.6396 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2069.9023 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0028 | 0.0485 | 0.0513 | 0.0505 | 0.0009 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1576 | 4290.263 | 44264.6397 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2111.3003 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0019 | 0.0493 | 0.0512 | 0.0504 | 0.0008 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1579 | 4293.676 | 44264.6397 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2153.5263 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0034 | 0.0482 | 0.0516 | 0.0499 | 0.0012 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1582 | 4297.103 | 44264.6397 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2196.5968 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0026 | 0.0483 | 0.0509 | 0.0496 | 0.001 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1585 | 4300.538 | 44264.6398 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2240.5288 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0024 | 0.0494 | 0.0518 | 0.0504 | 0.0007 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1588 | 4303.875 | 44264.6398 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2285.3393 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0013 | 0.0493 | 0.0506 | 0.0502 | 0.0005 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1591 | 4307.287 | 44264.6399 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2331.0461 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0029 | 0.0487 | 0.0516 | 0.0499 | 0.0009 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1594 | 4310.712 | 44264.6399 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2377.6671 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0026 | 0.048 | 0.0506 | 0.0496 | 0.0008 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1597 | 4314.128 | 44264.6399 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2425.2204 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0017 | 0.0488 | 0.0505 | 0.0496 | 0.0006 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1600 | 4317.774 | 44264.64 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2473.7248 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0025 | 0.0484 | 0.0509 | 0.0495 | 0.0008 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1603 | 4321.329 | 44264.64 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2523.1993 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.003 | 0.0479 | 0.0509 | 0.0495 | 0.0009 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1606 | 4324.656 | 44264.6401 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2573.6633 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0028 | 0.0483 | 0.0511 | 0.0496 | 0.001 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1609 | 4328.063 | 44264.6401 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2625.1366 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0024 | 0.0481 | 0.0505 | 0.0494 | 0.0009 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1612 | 4331.391 | 44264.6401 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2677.6393 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0022 | 0.0483 | 0.0505 | 0.0495 | 0.0008 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1615 | 4334.722 | 44264.6402 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2731.1921 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0028 | 0.0479 | 0.0507 | 0.0494 | 0.001 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1618 | 4338.336 | 44264.6402 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2785.8159 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0024 | 0.048 | 0.0504 | 0.0495 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1621 | 4341.779 | 44264.6403 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2841.5322 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0025 | 0.0481 | 0.0506 | 0.0498 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1624 | 4345.175 | 44264.6403 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2898.3629 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0024 | 0.0482 | 0.0506 | 0.0493 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1627 | 4348.523 | 44264.6403 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2956.3301 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0025 | 0.0481 | 0.0506 | 0.0498 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1630 | 4351.958 | 44264.6404 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3015.4567 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0023 | 0.0483 | 0.0506 | 0.0498 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1633 | 4355.252 | 44264.6404 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3075.7659 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0025 | 0.0479 | 0.0504 | 0.0492 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1636 | 4358.569 | 44264.6405 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3137.2812 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0022 | 0.0482 | 0.0504 | 0.0495 | 0.0007 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1639 | 4362.001 | 44264.6405 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3200.0268 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.003 | 0.0478 | 0.0508 | 0.0496 | 0.001 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1642 | 4365.428 | 44264.6405 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3264.0273 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.002 | 0.0483 | 0.0503 | 0.0494 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1645 | 4368.83 | 44264.6406 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3329.3079 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0028 | 0.0481 | 0.0509 | 0.0495 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1648 | 4372.123 | 44264.6406 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3395.8941 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0023 | 0.0482 | 0.0505 | 0.0494 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1651 | 4375.673 | 44264.6407 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3463.8119 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0021 | 0.0483 | 0.0504 | 0.0496 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1654 | 4379.119 | 44264.6407 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3533.0882 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0029 | 0.0482 | 0.0511 | 0.0497 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1657 | 4382.479 | 44264.6407 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3603.7499 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0017 | 0.0483 | 0.05 | 0.0493 | 0.0006 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1660 | 4385.61 | 44264.6408 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3675.8249 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.002 | 0.0483 | 0.0503 | 0.0494 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1663 | 4389.055 | 44264.6408 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3749.3414 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.0481 | 0.0506 | 0.0494 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1666 | 4392.354 | 44264.6408 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3824.3283 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0032 | 0.0479 | 0.0511 | 0.0493 | 0.0011 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1669 | 4395.806 | 44264.6409 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3900.8148 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0019 | 0.0487 | 0.0506 | 0.0496 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1672 | 4399.367 | 44264.6409 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3978.8311 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.0481 | 0.0504 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1675 | 4403.017 | 44264.641 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4058.4077 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0018 | 0.0481 | 0.0499 | 0.0491 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1678 | 4406.591 | 44264.641 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4139.5759 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0043 | 0.0482 | 0.0525 | 0.0493 | 0.0013 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1681 | 4410.122 | 44264.6411 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4222.3674 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0026 | 0.0481 | 0.0507 | 0.0493 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1684 | 4413.528 | 44264.6411 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4306.8148 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0016 | 0.048 | 0.0496 | 0.049 | 0.0005 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1687 | 4416.781 | 44264.6411 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4392.9511 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.0479 | 0.0502 | 0.0494 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1690 | 4420.102 | 44264.6412 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4480.8101 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0027 | 0.0478 | 0.0505 | 0.0493 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1693 | 4423.34 | 44264.6412 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4570.4263 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.048 | 0.0503 | 0.0495 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1696 | 4426.656 | 44264.6412 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4661.8348 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0026 | 0.048 | 0.0506 | 0.0491 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1699 | 4430.218 | 44264.6413 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4755.0715 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.0479 | 0.0503 | 0.0491 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1702 | 4433.688 | 44264.6413 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4850.1729 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0032 | 0.0477 | 0.0509 | 0.0491 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1705 | 4437.251 | 44264.6414 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4947.1764 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.048 | 0.0503 | 0.0493 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1708 | 4440.561 | 44264.6414 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5046.1199 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0019 | 0.048 | 0.0499 | 0.049 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1711 | 4443.847 | 44264.6414 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5147.0423 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0026 | 0.0482 | 0.0508 | 0.0492 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1714 | 4447.209 | 44264.6415 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5249.9832 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.048 | 0.0504 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1717 | 4450.633 | 44264.6415 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5354.9828 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0017 | 0.0484 | 0.0501 | 0.049 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1720 | 4454.008 | 44264.6416 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5462.0825 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0013 | 0.0486 | 0.0499 | 0.0489 | 0.0005 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1723 | 4457.449 | 44264.6416 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5571.3241 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0012 | 0.0492 | 0.0504 | 0.0497 | 0.0005 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1726 | 4460.66 | 44264.6416 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5682.7506 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0016 | 0.0486 | 0.0502 | 0.0494 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1729 | 4464.126 | 44264.6417 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5796.4056 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0022 | 0.0482 | 0.0504 | 0.0493 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1732 | 4467.655 | 44264.6417 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5912.3337 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.0476 | 0.05 | 0.0487 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1735 | 4470.899 | 44264.6418 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6030.5804 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0017 | 0.048 | 0.0497 | 0.0491 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1738 | 4474.443 | 44264.6418 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6151.192 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0024 | 0.048 | 0.0504 | 0.0493 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1741 | 4478.038 | 44264.6418 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6274.2159 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0019 | 0.0482 | 0.0501 | 0.0491 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1744 | 4481.457 | 44264.6419 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6399.7002 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0026 | 0.0475 | 0.0501 | 0.0491 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1747 | 4484.926 | 44264.6419 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6527.6942 | 0:240:120 | 0:00 | 0.045 | 7 | 0.003 | 0.0475 | 0.0505 | 0.0489 | 0.0009 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1750 | 4488.268 | 44264.642 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6658.2481 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0023 | 0.0479 | 0.0502 | 0.0489 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1753 | 4491.601 | 44264.642 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6791.413 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0025 | 0.0478 | 0.0503 | 0.049 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1756 | 4495.013 | 44264.642 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6927.2413 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0022 | 0.048 | 0.0502 | 0.0493 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1759 | 4498.453 | 44264.6421 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7065.7861 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0025 | 0.0477 | 0.0502 | 0.0491 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1762 | 4501.79 | 44264.6421 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7207.1018 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0018 | 0.0479 | 0.0497 | 0.049 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1765 | 4505.051 | 44264.6422 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7351.2439 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0024 | 0.0477 | 0.0501 | 0.0489 | 0.0009 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1768 | 4508.72 | 44264.6422 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7498.2688 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0023 | 0.0481 | 0.0504 | 0.0492 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1771 | 4512.065 | 44264.6422 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7648.2341 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0023 | 0.0474 | 0.0497 | 0.0485 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1774 | 4515.492 | 44264.6423 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7801.1988 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0022 | 0.0479 | 0.0501 | 0.049 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1777 | 4519.019 | 44264.6423 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7957.2228 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0016 | 0.0475 | 0.0491 | 0.0486 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1780 | 4522.588 | 44264.6424 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8116.3672 | 0:240:120 | 0:00 | 0.045 | 7 | 0.003 | 0.0474 | 0.0504 | 0.049 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1783 | 4525.895 | 44264.6424 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8278.6946 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0019 | 0.0481 | 0.05 | 0.0494 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1786 | 4529.232 | 44264.6424 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8444.2685 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0021 | 0.0483 | 0.0504 | 0.049 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1789 | 4532.603 | 44264.6425 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8613.1539 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0022 | 0.0475 | 0.0497 | 0.0484 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1792 | 4536.163 | 44264.6425 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8785.4169 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0014 | 0.048 | 0.0494 | 0.0488 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1795 | 4539.475 | 44264.6426 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8961.1253 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0014 | 0.0482 | 0.0496 | 0.0488 | 0.0004 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1798 | 4542.692 | 44264.6426 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9140.3478 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0013 | 0.0483 | 0.0496 | 0.0486 | 0.0004 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1801 | 4546.043 | 44264.6426 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9323.1547 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0021 | 0.0478 | 0.0499 | 0.0489 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1804 | 4549.57 | 44264.6427 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9509.6178 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0023 | 0.0476 | 0.0499 | 0.0485 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1807 | 4553.107 | 44264.6427 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9699.8102 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0024 | 0.0473 | 0.0497 | 0.0484 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1810 | 4556.422 | 44264.6427 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9893.8064 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0017 | 0.0484 | 0.0501 | 0.0493 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1813 | 4559.736 | 44264.6428 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10091.6825 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0016 | 0.0478 | 0.0494 | 0.0487 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1816 | 4563.174 | 44264.6428 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10293.5162 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0026 | 0.0475 | 0.0501 | 0.0486 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1819 | 4566.494 | 44264.6429 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10499.3865 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0022 | 0.0472 | 0.0494 | 0.0483 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1822 | 4569.829 | 44264.6429 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10709.3742 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0017 | 0.0476 | 0.0493 | 0.0484 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1825 | 4573.168 | 44264.6429 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10923.5617 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0028 | 0.0472 | 0.05 | 0.0488 | 0.0009 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1828 | 4576.514 | 44264.643 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11142.0329 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0028 | 0.0472 | 0.05 | 0.0489 | 0.001 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1831 | 4579.947 | 44264.643 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11364.8736 | 0:240:120 | 0:00 | 0.045 | 7 | 0.003 | 0.0468 | 0.0498 | 0.0484 | 0.001 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1834 | 4583.388 | 44264.6431 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11592.1711 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0028 | 0.0469 | 0.0497 | 0.0484 | 0.0009 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1837 | 4586.721 | 44264.6431 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11824.0145 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0032 | 0.0467 | 0.0499 | 0.0483 | 0.0011 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1840 | 4636.059 | 44264.6437 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.7 | 0:240:120 | 0:00 | 5.9643 | 7 | 17.0537 | 29.9038 | 46.9575 | 37.9752 | 6.6753 | 44.5598 | 3 | 5.9643 | 23.9453 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1843 | 4760.495 | 44264.6451 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.4 | 0:240:120 | 0:00 | 5.1418 | 7 | 16.5764 | 11.9639 | 28.5403 | 19.4344 | 7.0134 | 49.1884 | 3 | 5.1418 | 15.6891 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1846 | 4829.954 | 44264.6459 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.1 | 0:240:120 | 0:00 | 4.5092 | 7 | 0.999 | 8.73 | 9.729 | 9.1828 | 0.4101 | 0.1682 | 3 | 4.5092 | 11.6131 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1849 | 4860.904 | 44264.6463 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.8 | 0:240:120 | 0:00 | 4.0077 | 7 | 0.9415 | 7.6524 | 8.5939 | 8.0621 | 0.4185 | 0.1751 | 3 | 4.0077 | 9.1851 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1852 | 4889.358 | 44264.6466 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.5 | 0:240:120 | 0:00 | 3.6006 | 7 | 0.9635 | 6.6279 | 7.5914 | 6.9981 | 0.4493 | 0.2019 | 3 | 3.6006 | 7.5744 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1855 | 4914.162 | 44264.6469 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.3 | 0:240:120 | 0:00 | 3.2202 | 7 | 0.8615 | 5.4674 | 6.3289 | 5.8066 | 0.3883 | 0.1508 | 3 | 3.2202 | 6.2911 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1858 | 4934.908 | 44264.6471 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.1 | 0:240:120 | 0:00 | 2.9075 | 7 | 0.663 | 4.4533 | 5.1163 | 4.7105 | 0.3042 | 0.0926 | 3 | 2.9075 | 5.3652 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1861 | 4952.608 | 44264.6473 | Vista Coord | Main | 30Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.8 | 0:240:120 | 0:00 | 2.6764 | 7 | 0.3312 | 4.1147 | 4.4459 | 4.2373 | 0.1563 | 0.0244 | 3 | 2.6764 | 4.7439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1864 | 5065.62 | 44264.6486 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44 | 0:240:120 | 0:00 | 9.5688 | 7 | 16.0263 | 83.4908 | 99.5171 | 89.3375 | 7.6417 | 58.3953 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1867 | 5349.277 | 44264.6519 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.88 | 0:240:120 | 0:00 | 7.7705 | 7 | 15.9959 | 65.5075 | 81.5034 | 71.3522 | 7.6175 | 58.0266 | 3 | 7.7705 | 101.5883 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1870 | 5579.064 | 44264.6546 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.7776 | 0:240:120 | 0:00 | 6.502 | 7 | 16.5467 | 46.9366 | 63.4833 | 52.9174 | 7.9361 | 62.9821 | 3 | 6.502 | 32.8902 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1873 | 5754.396 | 44264.6566 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.6932 | 0:240:120 | 0:00 | 5.5599 | 7 | 17.4001 | 27.8796 | 45.2797 | 33.7849 | 8.6111 | 74.1511 | 3 | 5.5599 | 19.3218 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1876 | 5873.292 | 44264.658 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.627 | 0:240:120 | 0:00 | 4.833 | 7 | 15.7406 | 9.6053 | 25.3459 | 14.8316 | 7.7885 | 60.6605 | 3 | 4.833 | 13.5272 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1879 | 5936.153 | 44264.6587 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.5796 | 0:240:120 | 0:00 | 4.2557 | 7 | 0.7199 | 8.5755 | 9.2954 | 8.8215 | 0.3517 | 0.1237 | 3 | 4.2557 | 10.3153 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1882 | 5966.013 | 44264.6591 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.5511 | 0:240:120 | 0:00 | 3.7863 | 7 | 0.63 | 7.4834 | 8.1134 | 7.7304 | 0.2858 | 0.0817 | 3 | 3.7863 | 8.2753 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1885 | 5992.647 | 44264.6594 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.5422 | 0:240:120 | 0:00 | 3.3975 | 7 | 0.9159 | 6.1839 | 7.0998 | 6.5619 | 0.4073 | 0.1659 | 3 | 3.3975 | 6.8658 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1888 | 6016.012 | 44264.6596 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.553 | 0:240:120 | 0:00 | 3.0704 | 7 | 0.9448 | 5.1033 | 6.0481 | 5.4148 | 0.4625 | 0.2139 | 3 | 3.0704 | 5.8343 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1891 | 6035.92 | 44264.6599 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.5841 | 0:240:120 | 0:00 | 2.7916 | 7 | 0.2664 | 4.4144 | 4.6808 | 4.5123 | 0.1257 | 0.0158 | 3 | 2.7916 | 5.0472 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1894 | 6052.7 | 44264.6601 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.6358 | 0:240:120 | 0:00 | 2.5513 | 7 | 0.3164 | 3.9643 | 4.2807 | 4.0894 | 0.1432 | 0.0205 | 3 | 2.5513 | 4.4273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1897 | 6068.152 | 44264.6602 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.7085 | 0:240:120 | 0:00 | 2.3422 | 7 | 0.26 | 3.6123 | 3.8723 | 3.7007 | 0.1277 | 0.0163 | 3 | 2.3422 | 3.9269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1900 | 6082.434 | 44264.6604 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.8026 | 0:240:120 | 0:00 | 2.1587 | 7 | 0.3201 | 3.1364 | 3.4565 | 3.262 | 0.1463 | 0.0214 | 3 | 2.1587 | 3.5146 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1903 | 6095.563 | 44264.6606 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.9187 | 0:240:120 | 0:00 | 1.9965 | 7 | 0.1632 | 2.8674 | 3.0306 | 2.926 | 0.0744 | 0.0055 | 3 | 1.9965 | 3.1694 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1906 | 6107.469 | 44264.6607 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.0571 | 0:240:120 | 0:00 | 1.8523 | 7 | 0.1647 | 2.6342 | 2.7989 | 2.6905 | 0.0805 | 0.0065 | 3 | 1.8523 | 2.8763 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1909 | 6118.692 | 44264.6608 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.2182 | 0:240:120 | 0:00 | 1.7232 | 7 | 0.1565 | 2.3998 | 2.5563 | 2.4675 | 0.0673 | 0.0045 | 3 | 1.7232 | 2.6246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1912 | 6129.261 | 44264.661 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.4026 | 0:240:120 | 0:00 | 1.6071 | 7 | 0.1404 | 2.2181 | 2.3585 | 2.2664 | 0.068 | 0.0046 | 3 | 1.6071 | 2.4062 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1915 | 6139.235 | 44264.6611 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.6106 | 0:240:120 | 0:00 | 1.5023 | 7 | 0.0956 | 2.0468 | 2.1424 | 2.0791 | 0.0472 | 0.0022 | 3 | 1.5023 | 2.215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1918 | 6148.646 | 44264.6612 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.8428 | 0:240:120 | 0:00 | 1.4072 | 7 | 0.098 | 1.9025 | 2.0005 | 1.9364 | 0.0477 | 0.0023 | 3 | 1.4072 | 2.0464 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1921 | 6157.672 | 44264.6613 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.0997 | 0:240:120 | 0:00 | 1.3205 | 7 | 0.0969 | 1.7584 | 1.8553 | 1.7922 | 0.0471 | 0.0022 | 3 | 1.3205 | 1.8967 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1924 | 6166.139 | 44264.6614 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.3817 | 0:240:120 | 0:00 | 1.2414 | 7 | 0.083 | 1.6289 | 1.7119 | 1.6601 | 0.0384 | 0.0015 | 3 | 1.2414 | 1.7631 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1927 | 6174.123 | 44264.6615 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.6893 | 0:240:120 | 0:00 | 1.1688 | 7 | 0.0653 | 1.5336 | 1.5989 | 1.5567 | 0.0312 | 0.001 | 3 | 1.1688 | 1.643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1930 | 6182.103 | 44264.6616 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.0231 | 0:240:120 | 0:00 | 1.1021 | 7 | 0.0629 | 1.4388 | 1.5017 | 1.4604 | 0.0306 | 0.0009 | 3 | 1.1021 | 1.5348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1933 | 6189.633 | 44264.6617 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.3836 | 0:240:120 | 0:00 | 1.0406 | 7 | 0.067 | 1.3401 | 1.4071 | 1.3641 | 0.0318 | 0.001 | 3 | 1.0406 | 1.4367 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1936 | 6197.083 | 44264.6617 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.7712 | 0:240:120 | 0:00 | 0.9838 | 7 | 0.0479 | 1.2722 | 1.3201 | 1.2891 | 0.0231 | 0.0005 | 3 | 0.9838 | 1.3474 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1939 | 6204.274 | 44264.6618 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.1867 | 0:240:120 | 0:00 | 0.9312 | 7 | 0.0513 | 1.197 | 1.2483 | 1.2162 | 0.0237 | 0.0006 | 3 | 0.9312 | 1.266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1942 | 6211.017 | 44264.6619 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.6304 | 0:240:120 | 0:00 | 0.8824 | 7 | 0.0474 | 1.1183 | 1.1657 | 1.1345 | 0.0231 | 0.0005 | 3 | 0.8824 | 1.1914 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1945 | 6217.549 | 44264.662 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.103 | 0:240:120 | 0:00 | 0.837 | 7 | 0.0356 | 1.0667 | 1.1023 | 1.0798 | 0.0166 | 0.0003 | 3 | 0.837 | 1.1229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1948 | 6224.207 | 44264.6621 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.6051 | 0:240:120 | 0:00 | 0.7947 | 7 | 0.038 | 1.0058 | 1.0438 | 1.0185 | 0.0186 | 0.0003 | 3 | 0.7947 | 1.0598 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1951 | 6230.443 | 44264.6621 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.1372 | 0:240:120 | 0:00 | 0.7553 | 7 | 0.0366 | 0.9504 | 0.987 | 0.9636 | 0.0169 | 0.0003 | 3 | 0.7553 | 1.0015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1954 | 6236.354 | 44264.6622 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.6999 | 0:240:120 | 0:00 | 0.7184 | 7 | 0.0299 | 0.9028 | 0.9327 | 0.9128 | 0.0143 | 0.0002 | 3 | 0.7184 | 0.9476 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1957 | 6242.048 | 44264.6623 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.2939 | 0:240:120 | 0:00 | 0.6839 | 7 | 0.0319 | 0.8581 | 0.89 | 0.8706 | 0.0141 | 0.0002 | 3 | 0.6839 | 0.8976 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1960 | 6247.695 | 44264.6623 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.9198 | 0:240:120 | 0:00 | 0.6516 | 7 | 0.0253 | 0.8141 | 0.8394 | 0.8232 | 0.0121 | 0.0001 | 3 | 0.6516 | 0.8512 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1963 | 6253.208 | 44264.6624 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.5782 | 0:240:120 | 0:00 | 0.6212 | 7 | 0.023 | 0.7749 | 0.7979 | 0.7832 | 0.0106 | 0.0001 | 3 | 0.6212 | 0.8079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1966 | 6258.81 | 44264.6625 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.2697 | 0:240:120 | 0:00 | 0.5927 | 7 | 0.0257 | 0.7354 | 0.7611 | 0.7446 | 0.0117 | 0.0001 | 3 | 0.5927 | 0.7676 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1969 | 6264.018 | 44264.6625 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.9951 | 0:240:120 | 0:00 | 0.5659 | 7 | 0.0221 | 0.7009 | 0.723 | 0.709 | 0.0103 | 0.0001 | 3 | 0.5659 | 0.7299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1972 | 6269.339 | 44264.6626 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.755 | 0:240:120 | 0:00 | 0.5407 | 7 | 0.0209 | 0.6689 | 0.6898 | 0.6765 | 0.0094 | 0.0001 | 3 | 0.5407 | 0.6947 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1975 | 6274.666 | 44264.6626 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.5501 | 0:240:120 | 0:00 | 0.5169 | 7 | 0.0183 | 0.6382 | 0.6565 | 0.6451 | 0.008 | 0.0001 | 3 | 0.5169 | 0.6617 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1978 | 6279.79 | 44264.6627 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.3811 | 0:240:120 | 0:00 | 0.4944 | 7 | 0.0165 | 0.6108 | 0.6273 | 0.617 | 0.0075 | 0.0001 | 3 | 0.4944 | 0.6307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1981 | 6284.852 | 44264.6628 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.2488 | 0:240:120 | 0:00 | 0.4732 | 7 | 0.0192 | 0.5812 | 0.6004 | 0.5882 | 0.0089 | 0.0001 | 3 | 0.4732 | 0.6017 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1984 | 6289.592 | 44264.6628 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.1537 | 0:240:120 | 0:00 | 0.4532 | 7 | 0.0165 | 0.5567 | 0.5732 | 0.5629 | 0.0077 | 0.0001 | 3 | 0.4532 | 0.5743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1987 | 6294.268 | 44264.6629 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.0968 | 0:240:120 | 0:00 | 0.4343 | 7 | 0.0163 | 0.5326 | 0.5489 | 0.5384 | 0.0072 | 0.0001 | 3 | 0.4343 | 0.5486 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1990 | 6298.943 | 44264.6629 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.0788 | 0:240:120 | 0:00 | 0.4164 | 7 | 0.0136 | 0.5103 | 0.5239 | 0.5156 | 0.006 | 0 | 3 | 0.4164 | 0.5244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1993 | 6303.404 | 44264.663 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.1003 | 0:240:120 | 0:00 | 0.3994 | 7 | 0.0125 | 0.4894 | 0.5019 | 0.4938 | 0.0058 | 0 | 3 | 0.3994 | 0.5015 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1996 | 6308.167 | 44264.663 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.1623 | 0:240:120 | 0:00 | 0.3833 | 7 | 0.0108 | 0.4691 | 0.4799 | 0.4728 | 0.005 | 0 | 3 | 0.3833 | 0.4799 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1999 | 6312.737 | 44264.6631 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.2656 | 0:240:120 | 0:00 | 0.368 | 7 | 0.0119 | 0.45 | 0.4619 | 0.4545 | 0.0054 | 0 | 3 | 0.368 | 0.4595 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2002 | 6317.233 | 44264.6631 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.4109 | 0:240:120 | 0:00 | 0.3536 | 7 | 0.0113 | 0.4317 | 0.443 | 0.4362 | 0.0046 | 0 | 3 | 0.3536 | 0.4402 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2005 | 6321.475 | 44264.6632 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.5991 | 0:240:120 | 0:00 | 0.3398 | 7 | 0.0126 | 0.4138 | 0.4264 | 0.4192 | 0.0053 | 0 | 3 | 0.3398 | 0.422 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2008 | 6325.956 | 44264.6632 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.8311 | 0:240:120 | 0:00 | 0.3268 | 7 | 0.0092 | 0.3989 | 0.4081 | 0.4021 | 0.0042 | 0 | 3 | 0.3268 | 0.4047 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2011 | 6330.175 | 44264.6633 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.1077 | 0:240:120 | 0:00 | 0.3143 | 7 | 0.009 | 0.3826 | 0.3916 | 0.3857 | 0.0044 | 0 | 3 | 0.3143 | 0.3884 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2014 | 6334.308 | 44264.6633 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.4299 | 0:240:120 | 0:00 | 0.3025 | 7 | 0.0088 | 0.3681 | 0.3769 | 0.3718 | 0.0037 | 0 | 3 | 0.3025 | 0.3728 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2017 | 6338.947 | 44264.6634 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.7985 | 0:240:120 | 0:00 | 0.2913 | 7 | 0.009 | 0.3538 | 0.3628 | 0.3575 | 0.0038 | 0 | 3 | 0.2913 | 0.3581 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2020 | 6343.512 | 44264.6634 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.2144 | 0:240:120 | 0:00 | 0.2806 | 7 | 0.0075 | 0.3406 | 0.3481 | 0.3439 | 0.0032 | 0 | 3 | 0.2806 | 0.3441 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2023 | 6347.705 | 44264.6635 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.6787 | 0:240:120 | 0:00 | 0.2704 | 7 | 0.0093 | 0.3288 | 0.3381 | 0.3319 | 0.0038 | 0 | 3 | 0.2704 | 0.3309 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2026 | 6351.714 | 44264.6635 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.1923 | 0:240:120 | 0:00 | 0.2607 | 7 | 0.0079 | 0.3165 | 0.3244 | 0.3194 | 0.0034 | 0 | 3 | 0.2607 | 0.3182 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2029 | 6355.878 | 44264.6636 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.7561 | 0:240:120 | 0:00 | 0.2515 | 7 | 0.0068 | 0.3057 | 0.3125 | 0.3083 | 0.0029 | 0 | 3 | 0.2515 | 0.3063 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2032 | 6359.998 | 44264.6636 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.3713 | 0:240:120 | 0:00 | 0.2427 | 7 | 0.0077 | 0.2938 | 0.3015 | 0.297 | 0.0034 | 0 | 3 | 0.2427 | 0.2948 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2035 | 6364.041 | 44264.6637 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.0387 | 0:240:120 | 0:00 | 0.2343 | 7 | 0.0068 | 0.2838 | 0.2906 | 0.2863 | 0.0029 | 0 | 3 | 0.2343 | 0.284 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2038 | 6368.337 | 44264.6637 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.7595 | 0:240:120 | 0:00 | 0.2263 | 7 | 0.0066 | 0.2737 | 0.2803 | 0.2762 | 0.003 | 0 | 3 | 0.2263 | 0.2736 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2041 | 6372.261 | 44264.6638 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.5347 | 0:240:120 | 0:00 | 0.2186 | 7 | 0.0067 | 0.2639 | 0.2706 | 0.2671 | 0.0026 | 0 | 3 | 0.2186 | 0.2638 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2044 | 6376.213 | 44264.6638 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.3654 | 0:240:120 | 0:00 | 0.2113 | 7 | 0.0066 | 0.2558 | 0.2624 | 0.2586 | 0.0026 | 0 | 3 | 0.2113 | 0.2544 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2047 | 6380.233 | 44264.6639 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.2527 | 0:240:120 | 0:00 | 0.2043 | 7 | 0.0056 | 0.2472 | 0.2528 | 0.2496 | 0.0024 | 0 | 3 | 0.2043 | 0.2455 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2050 | 6384.259 | 44264.6639 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.1977 | 0:240:120 | 0:00 | 0.1977 | 7 | 0.0057 | 0.2391 | 0.2448 | 0.2419 | 0.0022 | 0 | 3 | 0.1977 | 0.2372 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2053 | 6388.249 | 44264.6639 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.2017 | 0:240:120 | 0:00 | 0.1913 | 7 | 0.0057 | 0.2314 | 0.2371 | 0.2341 | 0.0022 | 0 | 3 | 0.1913 | 0.2296 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2056 | 6392.143 | 44264.664 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.2657 | 0:240:120 | 0:00 | 0.1852 | 7 | 0.004 | 0.2252 | 0.2292 | 0.2265 | 0.0017 | 0 | 3 | 0.1852 | 0.2223 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2059 | 6396.173 | 44264.664 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 159.391 | 0:240:120 | 0:00 | 0.1794 | 7 | 0.0048 | 0.2171 | 0.2219 | 0.2195 | 0.0016 | 0 | 3 | 0.1794 | 0.2153 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2062 | 6400.096 | 44264.6641 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 162.5788 | 0:240:120 | 0:00 | 0.1739 | 7 | 0.0057 | 0.2105 | 0.2162 | 0.2132 | 0.0022 | 0 | 3 | 0.1739 | 0.2086 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2065 | 6403.927 | 44264.6641 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.8304 | 0:240:120 | 0:00 | 0.1686 | 7 | 0.0052 | 0.2042 | 0.2094 | 0.2064 | 0.0018 | 0 | 3 | 0.1686 | 0.2023 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2068 | 6407.919 | 44264.6642 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.147 | 0:240:120 | 0:00 | 0.1635 | 7 | 0.0045 | 0.1976 | 0.2021 | 0.1999 | 0.0017 | 0 | 3 | 0.1635 | 0.1962 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2071 | 6411.507 | 44264.6642 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 172.53 | 0:240:120 | 0:00 | 0.1586 | 7 | 0.0041 | 0.1916 | 0.1957 | 0.1936 | 0.0016 | 0 | 3 | 0.1586 | 0.1903 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2074 | 6415.031 | 44264.6643 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175.9806 | 0:240:120 | 0:00 | 0.154 | 7 | 0.0052 | 0.1854 | 0.1906 | 0.1878 | 0.0019 | 0 | 3 | 0.154 | 0.1847 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2077 | 6418.618 | 44264.6643 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 179.5002 | 0:240:120 | 0:00 | 0.1495 | 7 | 0.0041 | 0.1805 | 0.1846 | 0.1825 | 0.0017 | 0 | 3 | 0.1495 | 0.1794 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2080 | 6422.322 | 44264.6643 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.0902 | 0:240:120 | 0:00 | 0.1452 | 7 | 0.0041 | 0.1755 | 0.1796 | 0.1775 | 0.0015 | 0 | 3 | 0.1452 | 0.1743 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2083 | 6425.932 | 44264.6644 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 186.752 | 0:240:120 | 0:00 | 0.1412 | 7 | 0.0049 | 0.1698 | 0.1747 | 0.1723 | 0.0019 | 0 | 3 | 0.1412 | 0.1694 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2086 | 6429.583 | 44264.6644 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 190.487 | 0:240:120 | 0:00 | 0.1373 | 7 | 0.0052 | 0.1653 | 0.1705 | 0.1677 | 0.0018 | 0 | 3 | 0.1373 | 0.1647 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2089 | 6433.125 | 44264.6645 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.2968 | 0:240:120 | 0:00 | 0.1335 | 7 | 0.0036 | 0.1612 | 0.1648 | 0.1633 | 0.0013 | 0 | 3 | 0.1335 | 0.1602 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2092 | 6437.223 | 44264.6645 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 198.1827 | 0:240:120 | 0:00 | 0.1299 | 7 | 0.0038 | 0.1568 | 0.1606 | 0.1588 | 0.0013 | 0 | 3 | 0.1299 | 0.1559 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2095 | 6441.106 | 44264.6646 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 202.1463 | 0:240:120 | 0:00 | 0.1265 | 7 | 0.0033 | 0.1528 | 0.1561 | 0.1545 | 0.0012 | 0 | 3 | 0.1265 | 0.1518 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2098 | 6444.662 | 44264.6646 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 206.1893 | 0:240:120 | 0:00 | 0.1232 | 7 | 0.0025 | 0.149 | 0.1515 | 0.1506 | 0.001 | 0 | 3 | 0.1232 | 0.1479 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2101 | 6448.119 | 44264.6646 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 210.3131 | 0:240:120 | 0:00 | 0.1201 | 7 | 0.0034 | 0.1451 | 0.1485 | 0.1471 | 0.0013 | 0 | 3 | 0.1201 | 0.1441 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2104 | 6451.667 | 44264.6647 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 214.5193 | 0:240:120 | 0:00 | 0.117 | 7 | 0.0037 | 0.1409 | 0.1446 | 0.143 | 0.0014 | 0 | 3 | 0.117 | 0.1405 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2107 | 6455.275 | 44264.6647 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 218.8097 | 0:240:120 | 0:00 | 0.1141 | 7 | 0.0032 | 0.1376 | 0.1408 | 0.1393 | 0.0013 | 0 | 3 | 0.1141 | 0.137 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2110 | 6458.925 | 44264.6648 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.1859 | 0:240:120 | 0:00 | 0.1114 | 7 | 0.0026 | 0.1348 | 0.1374 | 0.1362 | 0.0009 | 0 | 3 | 0.1114 | 0.1336 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2113 | 6462.37 | 44264.6648 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 227.6496 | 0:240:120 | 0:00 | 0.1087 | 7 | 0.0025 | 0.1318 | 0.1343 | 0.1333 | 0.0008 | 0 | 3 | 0.1087 | 0.1305 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2116 | 6465.848 | 44264.6648 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 232.2026 | 0:240:120 | 0:00 | 0.1062 | 7 | 0.0017 | 0.129 | 0.1307 | 0.1301 | 0.0007 | 0 | 3 | 0.1062 | 0.1274 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2119 | 6469.532 | 44264.6649 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 236.8467 | 0:240:120 | 0:00 | 0.1037 | 7 | 0.0032 | 0.1249 | 0.1281 | 0.1269 | 0.0011 | 0 | 3 | 0.1037 | 0.1245 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2122 | 6472.989 | 44264.6649 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 241.5836 | 0:240:120 | 0:00 | 0.1014 | 7 | 0.0035 | 0.1213 | 0.1248 | 0.1237 | 0.0013 | 0 | 3 | 0.1014 | 0.1217 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2125 | 6476.407 | 44264.665 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.4153 | 0:240:120 | 0:00 | 0.0991 | 7 | 0.0032 | 0.1198 | 0.123 | 0.1216 | 0.0011 | 0 | 3 | 0.0991 | 0.119 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2128 | 6479.87 | 44264.665 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 251.3436 | 0:240:120 | 0:00 | 0.097 | 7 | 0.0025 | 0.1166 | 0.1191 | 0.1182 | 0.0011 | 0 | 3 | 0.097 | 0.1164 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2131 | 6483.35 | 44264.665 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.3704 | 0:240:120 | 0:00 | 0.0949 | 7 | 0.0021 | 0.1149 | 0.117 | 0.1159 | 0.0007 | 0 | 3 | 0.0949 | 0.1139 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2134 | 6486.686 | 44264.6651 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 261.4979 | 0:240:120 | 0:00 | 0.0929 | 7 | 0.0023 | 0.112 | 0.1143 | 0.1135 | 0.001 | 0 | 3 | 0.0929 | 0.1115 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2137 | 6490.366 | 44264.6651 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 266.7278 | 0:240:120 | 0:00 | 0.091 | 7 | 0.0033 | 0.1096 | 0.1129 | 0.1112 | 0.0012 | 0 | 3 | 0.091 | 0.1092 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2140 | 6493.84 | 44264.6652 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 272.0624 | 0:240:120 | 0:00 | 0.0892 | 7 | 0.0013 | 0.1082 | 0.1095 | 0.109 | 0.0006 | 0 | 3 | 0.0892 | 0.107 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2143 | 6497.435 | 44264.6652 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 277.5036 | 0:240:120 | 0:00 | 0.0874 | 7 | 0.0031 | 0.105 | 0.1081 | 0.1068 | 0.001 | 0 | 3 | 0.0874 | 0.1049 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2146 | 6500.899 | 44264.6653 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 283.0537 | 0:240:120 | 0:00 | 0.0858 | 7 | 0.0037 | 0.1019 | 0.1056 | 0.1044 | 0.0013 | 0 | 3 | 0.0858 | 0.1029 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2149 | 6504.253 | 44264.6653 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 288.7148 | 0:240:120 | 0:00 | 0.0841 | 7 | 0.0033 | 0.1013 | 0.1046 | 0.103 | 0.0013 | 0 | 3 | 0.0841 | 0.101 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2152 | 6507.702 | 44264.6653 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.4891 | 0:240:120 | 0:00 | 0.0826 | 7 | 0.004 | 0.0988 | 0.1028 | 0.101 | 0.0014 | 0 | 3 | 0.0826 | 0.0991 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2155 | 6511.289 | 44264.6654 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 300.3788 | 0:240:120 | 0:00 | 0.0811 | 7 | 0.0024 | 0.0976 | 0.1 | 0.0992 | 0.0009 | 0 | 3 | 0.0811 | 0.0973 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2158 | 6514.865 | 44264.6654 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 306.3864 | 0:240:120 | 0:00 | 0.0797 | 7 | 0.0029 | 0.0956 | 0.0985 | 0.0973 | 0.0012 | 0 | 3 | 0.0797 | 0.0956 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2161 | 6518.528 | 44264.6655 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 312.5141 | 0:240:120 | 0:00 | 0.0783 | 7 | 0.0028 | 0.0946 | 0.0974 | 0.0958 | 0.0009 | 0 | 3 | 0.0783 | 0.094 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2164 | 6521.99 | 44264.6655 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 318.7644 | 0:240:120 | 0:00 | 0.077 | 7 | 0.0041 | 0.0917 | 0.0958 | 0.0939 | 0.0014 | 0 | 3 | 0.077 | 0.0924 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2167 | 6525.467 | 44264.6655 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 325.1397 | 0:240:120 | 0:00 | 0.0757 | 7 | 0.0038 | 0.0905 | 0.0943 | 0.0925 | 0.0014 | 0 | 3 | 0.0757 | 0.0909 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2170 | 6528.914 | 44264.6656 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 331.6425 | 0:240:120 | 0:00 | 0.0745 | 7 | 0.0029 | 0.09 | 0.0929 | 0.0912 | 0.0011 | 0 | 3 | 0.0745 | 0.0894 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2173 | 6532.366 | 44264.6656 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 338.2754 | 0:240:120 | 0:00 | 0.0734 | 7 | 0.0033 | 0.0876 | 0.0909 | 0.0892 | 0.0013 | 0 | 3 | 0.0734 | 0.088 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2176 | 6535.818 | 44264.6657 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 345.0409 | 0:240:120 | 0:00 | 0.0722 | 7 | 0.0026 | 0.0866 | 0.0892 | 0.0879 | 0.0009 | 0 | 3 | 0.0722 | 0.0867 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2179 | 6539.487 | 44264.6657 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 351.9417 | 0:240:120 | 0:00 | 0.0712 | 7 | 0.0025 | 0.0851 | 0.0876 | 0.0868 | 0.0009 | 0 | 3 | 0.0712 | 0.0854 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2182 | 6542.969 | 44264.6657 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 358.9805 | 0:240:120 | 0:00 | 0.0701 | 7 | 0.0039 | 0.0832 | 0.0871 | 0.0852 | 0.0012 | 0 | 3 | 0.0701 | 0.0842 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2185 | 6546.426 | 44264.6658 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 366.1601 | 0:240:120 | 0:00 | 0.0692 | 7 | 0.0023 | 0.0829 | 0.0852 | 0.084 | 0.0007 | 0 | 3 | 0.0692 | 0.083 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2188 | 6550.015 | 44264.6658 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 373.4833 | 0:240:120 | 0:00 | 0.0682 | 7 | 0.0034 | 0.0809 | 0.0843 | 0.0827 | 0.0013 | 0 | 3 | 0.0682 | 0.0818 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2191 | 6553.469 | 44264.6659 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 380.953 | 0:240:120 | 0:00 | 0.0673 | 7 | 0.0032 | 0.08 | 0.0832 | 0.082 | 0.001 | 0 | 3 | 0.0673 | 0.0808 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2194 | 6556.918 | 44264.6659 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 388.5721 | 0:240:120 | 0:00 | 0.0664 | 7 | 0.0025 | 0.0791 | 0.0816 | 0.0807 | 0.0011 | 0 | 3 | 0.0664 | 0.0797 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2197 | 6560.37 | 44264.6659 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 396.3435 | 0:240:120 | 0:00 | 0.0656 | 7 | 0.0029 | 0.0776 | 0.0805 | 0.0795 | 0.001 | 0 | 3 | 0.0656 | 0.0787 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2200 | 6563.831 | 44264.666 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 404.2704 | 0:240:120 | 0:00 | 0.0648 | 7 | 0.0027 | 0.0768 | 0.0795 | 0.0784 | 0.001 | 0 | 3 | 0.0648 | 0.0777 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2203 | 6567.298 | 44264.666 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 412.3558 | 0:240:120 | 0:00 | 0.064 | 7 | 0.0018 | 0.0762 | 0.078 | 0.0773 | 0.0007 | 0 | 3 | 0.064 | 0.0768 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2206 | 6570.759 | 44264.6661 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 420.6029 | 0:240:120 | 0:00 | 0.0633 | 7 | 0.0031 | 0.0742 | 0.0773 | 0.0763 | 0.0011 | 0 | 3 | 0.0633 | 0.0759 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2209 | 6574.16 | 44264.6661 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 429.015 | 0:240:120 | 0:00 | 0.0625 | 7 | 0.0036 | 0.0735 | 0.0771 | 0.0757 | 0.0012 | 0 | 3 | 0.0625 | 0.075 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2212 | 6577.659 | 44264.6661 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 437.5953 | 0:240:120 | 0:00 | 0.0619 | 7 | 0.0033 | 0.0726 | 0.0759 | 0.0745 | 0.0012 | 0 | 3 | 0.0619 | 0.0742 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2215 | 6581.302 | 44264.6662 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 446.3472 | 0:240:120 | 0:00 | 0.0612 | 7 | 0.0028 | 0.0719 | 0.0747 | 0.0738 | 0.0012 | 0 | 3 | 0.0612 | 0.0734 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2218 | 6585.018 | 44264.6662 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 455.2741 | 0:240:120 | 0:00 | 0.0606 | 7 | 0.0024 | 0.072 | 0.0744 | 0.0734 | 0.0009 | 0 | 3 | 0.0606 | 0.0727 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2221 | 6588.5 | 44264.6663 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 464.3796 | 0:240:120 | 0:00 | 0.0599 | 7 | 0.0033 | 0.0702 | 0.0735 | 0.0719 | 0.0011 | 0 | 3 | 0.0599 | 0.0719 | NP | NP | 0-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2224 | 6591.953 | 44264.6663 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 473.6672 | 0:240:120 | 0:00 | 0.0594 | 7 | 0.0029 | 0.0694 | 0.0723 | 0.0713 | 0.001 | 0 | 3 | 0.0594 | 0.0712 | NP | NP | 1-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2227 | 6595.506 | 44264.6663 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 483.1405 | 0:240:120 | 0:00 | 0.0588 | 7 | 0.0015 | 0.0697 | 0.0712 | 0.0707 | 0.0006 | 0 | 3 | 0.0588 | 0.0706 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2230 | 6598.905 | 44264.6664 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 492.8033 | 0:240:120 | 0:00 | 0.0583 | 7 | 0.0038 | 0.0677 | 0.0715 | 0.0698 | 0.0012 | 0 | 3 | 0.0583 | 0.0699 | P | NP | 0-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2233 | 6602.432 | 44264.6664 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 502.6594 | 0:240:120 | 0:00 | 0.0577 | 7 | 0.0042 | 0.0668 | 0.071 | 0.0692 | 0.0014 | 0 | 3 | 0.0577 | 0.0693 | P | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2236 | 6605.956 | 44264.6665 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 512.7126 | 0:240:120 | 0:00 | 0.0572 | 7 | 0.0016 | 0.0674 | 0.069 | 0.0685 | 0.0007 | 0 | 3 | 0.0572 | 0.0687 | P | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2239 | 6609.671 | 44264.6665 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 522.9668 | 0:240:120 | 0:00 | 0.0568 | 7 | 0.0032 | 0.0661 | 0.0693 | 0.0678 | 0.0012 | 0 | 3 | 0.0568 | 0.0681 | P | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2242 | 6613.077 | 44264.6666 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 533.4262 | 0:240:120 | 0:00 | 0.0563 | 7 | 0.0026 | 0.0656 | 0.0682 | 0.0671 | 0.0009 | 0 | 3 | 0.0563 | 0.0676 | P | NP | 0-1-1-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2245 | 6616.513 | 44264.6666 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 544.0947 | 0:240:120 | 0:00 | 0.0559 | 7 | 0.0042 | 0.0642 | 0.0684 | 0.0665 | 0.0014 | 0 | 3 | 0.0559 | 0.067 | P | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2248 | 6619.913 | 44264.6666 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 554.9766 | 0:240:120 | 0:00 | 0.0554 | 7 | 0.0022 | 0.0643 | 0.0665 | 0.0658 | 0.0009 | 0 | 3 | 0.0554 | 0.0665 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2251 | 6623.324 | 44264.6667 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 566.0761 | 0:240:120 | 0:00 | 0.055 | 7 | 0.0037 | 0.0636 | 0.0673 | 0.0658 | 0.0012 | 0 | 3 | 0.055 | 0.066 | P | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2254 | 6627.015 | 44264.6667 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 577.3976 | 0:240:120 | 0:00 | 0.0546 | 7 | 0.0015 | 0.0642 | 0.0657 | 0.0649 | 0.0006 | 0 | 3 | 0.0546 | 0.0656 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2257 | 6630.593 | 44264.6668 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 588.9456 | 0:240:120 | 0:00 | 0.0543 | 7 | 0.003 | 0.0625 | 0.0655 | 0.0641 | 0.001 | 0 | 3 | 0.0543 | 0.0651 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2260 | 6634.059 | 44264.6668 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 600.7245 | 0:240:120 | 0:00 | 0.0539 | 7 | 0.0043 | 0.0621 | 0.0664 | 0.0646 | 0.0014 | 0 | 3 | 0.0539 | 0.0647 | P | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2263 | 6637.52 | 44264.6668 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 612.739 | 0:240:120 | 0:00 | 0.0536 | 7 | 0.003 | 0.0617 | 0.0647 | 0.0633 | 0.0011 | 0 | 3 | 0.0536 | 0.0643 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2266 | 6641.047 | 44264.6669 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 624.9938 | 0:240:120 | 0:00 | 0.0532 | 7 | 0.0023 | 0.0618 | 0.0641 | 0.063 | 0.0009 | 0 | 3 | 0.0532 | 0.0639 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2269 | 6644.427 | 44264.6669 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 637.4937 | 0:240:120 | 0:00 | 0.0529 | 7 | 0.0022 | 0.0611 | 0.0633 | 0.0625 | 0.0008 | 0 | 3 | 0.0529 | 0.0635 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2272 | 6647.873 | 44264.667 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 650.2435 | 0:240:120 | 0:00 | 0.0526 | 7 | 0.0032 | 0.0601 | 0.0633 | 0.0619 | 0.0012 | 0 | 3 | 0.0526 | 0.0631 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2275 | 6651.48 | 44264.667 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 663.2484 | 0:240:120 | 0:00 | 0.0523 | 7 | 0.0033 | 0.0599 | 0.0632 | 0.0616 | 0.0011 | 0 | 3 | 0.0523 | 0.0628 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2278 | 6654.917 | 44264.667 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 676.5134 | 0:240:120 | 0:00 | 0.052 | 7 | 0.0027 | 0.0593 | 0.062 | 0.0607 | 0.0008 | 0 | 3 | 0.052 | 0.0624 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2281 | 6658.576 | 44264.6671 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 690.0436 | 0:240:120 | 0:00 | 0.0517 | 7 | 0.0029 | 0.0587 | 0.0616 | 0.0603 | 0.0009 | 0 | 3 | 0.0517 | 0.0621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2284 | 6661.991 | 44264.6671 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 703.8445 | 0:240:120 | 0:00 | 0.0515 | 7 | 0.0026 | 0.0591 | 0.0617 | 0.0605 | 0.0009 | 0 | 3 | 0.0515 | 0.0618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2287 | 6665.422 | 44264.6672 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 717.9214 | 0:240:120 | 0:00 | 0.0512 | 7 | 0.0028 | 0.0582 | 0.061 | 0.06 | 0.0012 | 0 | 3 | 0.0512 | 0.0615 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2290 | 6668.871 | 44264.6672 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 732.2798 | 0:240:120 | 0:00 | 0.051 | 7 | 0.0028 | 0.0573 | 0.0601 | 0.0591 | 0.0011 | 0 | 3 | 0.051 | 0.0612 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2293 | 6672.424 | 44264.6672 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 746.9254 | 0:240:120 | 0:00 | 0.0508 | 7 | 0.0029 | 0.0575 | 0.0604 | 0.0592 | 0.0012 | 0 | 3 | 0.0508 | 0.0609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2296 | 6675.804 | 44264.6673 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 761.8639 | 0:240:120 | 0:00 | 0.0505 | 7 | 0.0033 | 0.0576 | 0.0609 | 0.0593 | 0.0011 | 0 | 3 | 0.0505 | 0.0606 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2299 | 6679.326 | 44264.6673 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 777.1012 | 0:240:120 | 0:00 | 0.0503 | 7 | 0.0038 | 0.0561 | 0.0599 | 0.0581 | 0.0012 | 0 | 3 | 0.0503 | 0.0604 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2302 | 6682.966 | 44264.6674 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 792.6432 | 0:240:120 | 0:00 | 0.0501 | 7 | 0.0031 | 0.0564 | 0.0595 | 0.058 | 0.0012 | 0 | 3 | 0.0501 | 0.0601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2305 | 6686.38 | 44264.6674 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 808.4961 | 0:240:120 | 0:00 | 0.0499 | 7 | 0.0033 | 0.0561 | 0.0594 | 0.058 | 0.0012 | 0 | 3 | 0.0499 | 0.0599 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2308 | 6689.934 | 44264.6674 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 824.666 | 0:240:120 | 0:00 | 0.0497 | 7 | 0.0032 | 0.0561 | 0.0593 | 0.0575 | 0.0011 | 0 | 3 | 0.0497 | 0.0597 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2311 | 6693.356 | 44264.6675 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 841.1593 | 0:240:120 | 0:00 | 0.0495 | 7 | 0.0029 | 0.0551 | 0.058 | 0.0566 | 0.001 | 0 | 3 | 0.0495 | 0.0595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2314 | 6696.778 | 44264.6675 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 857.9825 | 0:240:120 | 0:00 | 0.0494 | 7 | 0.0026 | 0.0551 | 0.0577 | 0.0564 | 0.0009 | 0 | 3 | 0.0494 | 0.0594 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2317 | 6700.229 | 44264.6676 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 875.1422 | 0:240:120 | 0:00 | 0.0492 | 7 | 0.0043 | 0.0544 | 0.0587 | 0.0568 | 0.0015 | 0 | 3 | 0.0492 | 0.0592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2320 | 6703.826 | 44264.6676 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 892.645 | 0:240:120 | 0:00 | 0.049 | 7 | 0.0031 | 0.055 | 0.0581 | 0.0566 | 0.0011 | 0 | 3 | 0.049 | 0.059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2323 | 6708.438 | 44264.6677 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 910.4979 | 0:240:120 | 0:00 | 0.0489 | 7 | 0.0037 | 0.0543 | 0.058 | 0.0564 | 0.0014 | 0 | 3 | 0.0489 | 0.0589 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2326 | 6712.076 | 44264.6677 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 928.7079 | 0:240:120 | 0:00 | 0.0487 | 7 | 0.0041 | 0.0536 | 0.0577 | 0.0557 | 0.0014 | 0 | 3 | 0.0487 | 0.0587 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2329 | 6715.555 | 44264.6677 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 947.282 | 0:240:120 | 0:00 | 0.0486 | 7 | 0.0032 | 0.0534 | 0.0566 | 0.0551 | 0.0012 | 0 | 3 | 0.0486 | 0.0586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2332 | 6719.016 | 44264.6678 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 966.2277 | 0:240:120 | 0:00 | 0.0484 | 7 | 0.0031 | 0.0534 | 0.0565 | 0.055 | 0.0011 | 0 | 3 | 0.0484 | 0.0584 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2335 | 6722.434 | 44264.6678 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 985.5522 | 0:240:120 | 0:00 | 0.0483 | 7 | 0.0036 | 0.0532 | 0.0568 | 0.055 | 0.0012 | 0 | 3 | 0.0483 | 0.0583 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2338 | 6725.757 | 44264.6679 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1005.2633 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0029 | 0.0534 | 0.0563 | 0.0546 | 0.001 | 0 | 3 | 0.0482 | 0.0582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2341 | 6729.17 | 44264.6679 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1025.3685 | 0:240:120 | 0:00 | 0.048 | 7 | 0.003 | 0.053 | 0.056 | 0.0548 | 0.0013 | 0 | 3 | 0.048 | 0.058 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2344 | 6732.267 | 44264.6679 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1045.8759 | 0:240:120 | 0:00 | 0.0479 | 7 | 0.0017 | 0.0532 | 0.0549 | 0.0543 | 0.0006 | 0 | 3 | 0.0479 | 0.0579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2347 | 6735.715 | 44264.668 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1066.7934 | 0:240:120 | 0:00 | 0.0478 | 7 | 0.0029 | 0.0527 | 0.0556 | 0.054 | 0.0011 | 0 | 3 | 0.0478 | 0.0578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2350 | 6739.113 | 44264.668 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1088.1293 | 0:240:120 | 0:00 | 0.0477 | 7 | 0.0032 | 0.0519 | 0.0551 | 0.0536 | 0.0011 | 0 | 3 | 0.0477 | 0.0577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2353 | 6742.551 | 44264.668 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1109.8919 | 0:240:120 | 0:00 | 0.0476 | 7 | 0.0038 | 0.0512 | 0.055 | 0.0534 | 0.0013 | 0 | 3 | 0.0476 | 0.0576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2356 | 6745.981 | 44264.6681 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1132.0897 | 0:240:120 | 0:00 | 0.0475 | 7 | 0.0037 | 0.052 | 0.0557 | 0.0533 | 0.0011 | 0 | 3 | 0.0475 | 0.0575 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2359 | 6749.482 | 44264.6681 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1154.7315 | 0:240:120 | 0:00 | 0.0474 | 7 | 0.0028 | 0.0516 | 0.0544 | 0.0533 | 0.001 | 0 | 3 | 0.0474 | 0.0574 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2362 | 6753.132 | 44264.6682 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1177.8261 | 0:240:120 | 0:00 | 0.0473 | 7 | 0.0026 | 0.0522 | 0.0548 | 0.0533 | 0.0009 | 0 | 3 | 0.0473 | 0.0573 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2365 | 6756.457 | 44264.6682 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1201.3827 | 0:240:120 | 0:00 | 0.0472 | 7 | 0.0033 | 0.0517 | 0.055 | 0.0531 | 0.0011 | 0 | 3 | 0.0472 | 0.0572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2368 | 6759.894 | 44264.6683 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1225.4103 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0029 | 0.0515 | 0.0544 | 0.0529 | 0.0009 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2371 | 6763.321 | 44264.6683 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1249.9185 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0029 | 0.0511 | 0.054 | 0.0527 | 0.0009 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2374 | 6766.74 | 44264.6683 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1274.9169 | 0:240:120 | 0:00 | 0.047 | 7 | 0.0025 | 0.0517 | 0.0542 | 0.0529 | 0.0008 | 0 | 3 | 0.047 | 0.057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2377 | 6770.053 | 44264.6684 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1300.4152 | 0:240:120 | 0:00 | 0.0469 | 7 | 0.0029 | 0.0512 | 0.0541 | 0.0526 | 0.0009 | 0 | 3 | 0.0469 | 0.0569 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2380 | 6773.624 | 44264.6684 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1326.4235 | 0:240:120 | 0:00 | 0.0468 | 7 | 0.0033 | 0.0512 | 0.0545 | 0.0525 | 0.0012 | 0 | 3 | 0.0468 | 0.0568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2383 | 6776.85 | 44264.6684 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1352.952 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0036 | 0.0507 | 0.0543 | 0.0525 | 0.0013 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2386 | 6780.309 | 44264.6685 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1380.011 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0032 | 0.051 | 0.0542 | 0.0524 | 0.0011 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2389 | 6783.998 | 44264.6685 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1407.6113 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.0042 | 0.0506 | 0.0548 | 0.0523 | 0.0014 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2392 | 6787.58 | 44264.6686 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1435.7635 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.0029 | 0.0501 | 0.053 | 0.0521 | 0.001 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2395 | 6790.922 | 44264.6686 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1464.4788 | 0:240:120 | 0:00 | 0.0465 | 7 | 0.003 | 0.0511 | 0.0541 | 0.0522 | 0.0009 | 0 | 3 | 0.0465 | 0.0565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2398 | 6794.27 | 44264.6686 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1493.7683 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0033 | 0.0507 | 0.054 | 0.0522 | 0.0012 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2401 | 6797.371 | 44264.6687 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1523.6437 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.004 | 0.0495 | 0.0535 | 0.0519 | 0.0014 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2404 | 6800.959 | 44264.6687 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1554.1166 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0028 | 0.0506 | 0.0534 | 0.052 | 0.0009 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2407 | 6804.293 | 44264.6688 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1585.1989 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0023 | 0.0506 | 0.0529 | 0.0516 | 0.0009 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2410 | 6807.852 | 44264.6688 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1616.9029 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0013 | 0.0509 | 0.0522 | 0.0516 | 0.0006 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2413 | 6811.046 | 44264.6688 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1649.2409 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0025 | 0.0499 | 0.0524 | 0.0514 | 0.0008 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2416 | 6814.366 | 44264.6689 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1682.2258 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.004 | 0.0496 | 0.0536 | 0.0519 | 0.0013 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2419 | 6817.652 | 44264.6689 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1715.8703 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0029 | 0.0503 | 0.0532 | 0.0517 | 0.0008 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2422 | 6821.191 | 44264.669 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1750.1877 | 0:240:120 | 0:00 | 0.046 | 7 | 0.004 | 0.0495 | 0.0535 | 0.0515 | 0.0014 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2425 | 6824.703 | 44264.669 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1785.1914 | 0:240:120 | 0:00 | 0.046 | 7 | 0.003 | 0.0498 | 0.0528 | 0.0513 | 0.0011 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2428 | 6828.064 | 44264.669 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1820.8953 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0028 | 0.0495 | 0.0523 | 0.0513 | 0.001 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2431 | 6831.475 | 44264.6691 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1857.3132 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0022 | 0.0501 | 0.0523 | 0.0514 | 0.0008 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2434 | 6834.91 | 44264.6691 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1894.4594 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0029 | 0.0497 | 0.0526 | 0.0512 | 0.0009 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2437 | 6838.162 | 44264.6692 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1932.3486 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0023 | 0.0501 | 0.0524 | 0.0512 | 0.0008 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2440 | 6841.464 | 44264.6692 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1970.9956 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0017 | 0.0506 | 0.0523 | 0.0512 | 0.0007 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2443 | 6844.672 | 44264.6692 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2010.4155 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.003 | 0.0505 | 0.0535 | 0.0515 | 0.0012 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2446 | 6848.012 | 44264.6693 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2050.6238 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0034 | 0.0493 | 0.0527 | 0.0509 | 0.0013 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2449 | 6851.317 | 44264.6693 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2091.6363 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0025 | 0.0498 | 0.0523 | 0.051 | 0.0009 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2452 | 6854.762 | 44264.6693 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2133.469 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.003 | 0.0499 | 0.0529 | 0.0509 | 0.0009 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2455 | 6858.208 | 44264.6694 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2176.1384 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0025 | 0.0497 | 0.0522 | 0.0509 | 0.0008 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2458 | 6861.431 | 44264.6694 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2219.6612 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0026 | 0.0496 | 0.0522 | 0.0509 | 0.001 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2461 | 6865.014 | 44264.6695 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2264.0544 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0028 | 0.049 | 0.0518 | 0.0506 | 0.001 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2464 | 6868.687 | 44264.6695 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2309.3355 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0028 | 0.0496 | 0.0524 | 0.0507 | 0.0009 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2467 | 6872.118 | 44264.6695 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2355.5222 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0029 | 0.0489 | 0.0518 | 0.0503 | 0.0009 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2470 | 6875.567 | 44264.6696 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2402.6326 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0025 | 0.0492 | 0.0517 | 0.0506 | 0.0008 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2473 | 6878.795 | 44264.6696 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2450.6853 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0034 | 0.0486 | 0.052 | 0.0503 | 0.001 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2476 | 6882.358 | 44264.6697 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2499.699 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.003 | 0.0485 | 0.0515 | 0.0502 | 0.001 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2479 | 6885.694 | 44264.6697 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2549.693 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0023 | 0.0489 | 0.0512 | 0.0504 | 0.0007 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2482 | 6889.134 | 44264.6697 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2600.6868 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0026 | 0.0493 | 0.0519 | 0.0504 | 0.001 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2485 | 6892.569 | 44264.6698 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2652.7006 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0021 | 0.0493 | 0.0514 | 0.0505 | 0.0008 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2488 | 6895.998 | 44264.6698 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2705.7546 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0035 | 0.0483 | 0.0518 | 0.0504 | 0.0012 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2491 | 6899.332 | 44264.6699 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2759.8697 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0036 | 0.0481 | 0.0517 | 0.0502 | 0.0011 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2494 | 6902.678 | 44264.6699 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2815.0671 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0034 | 0.0479 | 0.0513 | 0.05 | 0.0011 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2497 | 6906.371 | 44264.6699 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2871.3684 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0032 | 0.0488 | 0.052 | 0.0502 | 0.0011 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2500 | 6909.801 | 44264.67 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2928.7958 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.003 | 0.0491 | 0.0521 | 0.0503 | 0.001 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2503 | 6913.121 | 44264.67 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2987.3717 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0036 | 0.048 | 0.0516 | 0.0501 | 0.0012 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2506 | 6916.44 | 44264.6701 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3047.1191 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0035 | 0.0484 | 0.0519 | 0.05 | 0.0012 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2509 | 6919.955 | 44264.6701 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3108.0615 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0029 | 0.0487 | 0.0516 | 0.0502 | 0.001 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2512 | 6923.334 | 44264.6701 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3170.2227 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0022 | 0.049 | 0.0512 | 0.0501 | 0.0007 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2515 | 6926.919 | 44264.6702 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3233.6272 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0036 | 0.0481 | 0.0517 | 0.0499 | 0.0012 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2518 | 6930.433 | 44264.6702 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3298.2997 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0031 | 0.0478 | 0.0509 | 0.0498 | 0.0011 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2521 | 6933.757 | 44264.6703 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3364.2657 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0041 | 0.0484 | 0.0525 | 0.0501 | 0.0013 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2524 | 6937.097 | 44264.6703 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3431.5511 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.004 | 0.0478 | 0.0518 | 0.0497 | 0.0014 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2527 | 6940.489 | 44264.6703 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3500.1821 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0029 | 0.0483 | 0.0512 | 0.0501 | 0.001 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2530 | 6944.182 | 44264.6704 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3570.1857 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0033 | 0.0477 | 0.051 | 0.0497 | 0.0011 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2533 | 6947.608 | 44264.6704 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3641.5894 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0031 | 0.0483 | 0.0514 | 0.0499 | 0.0011 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2536 | 6951.05 | 44264.6705 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3714.4212 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0027 | 0.0482 | 0.0509 | 0.0496 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2539 | 6954.391 | 44264.6705 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3788.7096 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0025 | 0.049 | 0.0515 | 0.0501 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2542 | 6957.775 | 44264.6705 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3864.4838 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0021 | 0.0488 | 0.0509 | 0.0497 | 0.0007 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2545 | 6961.404 | 44264.6706 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3941.7735 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0038 | 0.0481 | 0.0519 | 0.05 | 0.0012 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2548 | 6964.723 | 44264.6706 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4020.609 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0022 | 0.048 | 0.0502 | 0.0494 | 0.0008 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2551 | 6968.361 | 44264.6707 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4101.0212 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0036 | 0.0483 | 0.0519 | 0.05 | 0.0012 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2554 | 6971.827 | 44264.6707 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4183.0416 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0024 | 0.049 | 0.0514 | 0.0499 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2557 | 6975.373 | 44264.6707 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4266.7024 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0043 | 0.0481 | 0.0524 | 0.0497 | 0.0015 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2560 | 6979.04 | 44264.6708 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4352.0365 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.003 | 0.0479 | 0.0509 | 0.0493 | 0.0011 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2563 | 6982.579 | 44264.6708 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4439.0772 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0042 | 0.0478 | 0.052 | 0.0496 | 0.0013 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2566 | 6986.028 | 44264.6709 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4527.8587 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0045 | 0.048 | 0.0525 | 0.0499 | 0.0013 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2569 | 6989.374 | 44264.6709 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4618.4159 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0019 | 0.0485 | 0.0504 | 0.0496 | 0.0007 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2572 | 6992.848 | 44264.6709 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4710.7842 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0032 | 0.0479 | 0.0511 | 0.0493 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2575 | 6996.017 | 44264.671 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4804.9999 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0027 | 0.0489 | 0.0516 | 0.0501 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2578 | 6999.438 | 44264.671 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4901.0999 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0044 | 0.0481 | 0.0525 | 0.0498 | 0.0013 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2581 | 7002.761 | 44264.6711 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4999.1219 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0035 | 0.048 | 0.0515 | 0.0497 | 0.0011 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2584 | 7006.315 | 44264.6711 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5099.1043 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0021 | 0.0486 | 0.0507 | 0.0495 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2587 | 7009.546 | 44264.6711 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5201.0864 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0041 | 0.0484 | 0.0525 | 0.0498 | 0.0013 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2590 | 7012.964 | 44264.6712 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5305.1082 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0007 | 0.0491 | 0.0498 | 0.0495 | 0.0003 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2593 | 7016.209 | 44264.6712 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5411.2103 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.0481 | 0.0504 | 0.0492 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2596 | 7019.651 | 44264.6713 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5519.4345 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.002 | 0.0484 | 0.0504 | 0.0496 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2599 | 7022.978 | 44264.6713 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5629.8232 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0018 | 0.0486 | 0.0504 | 0.0494 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2602 | 7026.327 | 44264.6713 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5742.4197 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0017 | 0.0486 | 0.0503 | 0.0496 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2605 | 7029.866 | 44264.6714 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5857.2681 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.0479 | 0.0504 | 0.0492 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2608 | 7033.309 | 44264.6714 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5974.4134 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0016 | 0.0483 | 0.0499 | 0.0493 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2611 | 7036.757 | 44264.6715 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6093.9017 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.003 | 0.0478 | 0.0508 | 0.0493 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2614 | 7040.075 | 44264.6715 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6215.7797 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.002 | 0.0483 | 0.0503 | 0.0496 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2617 | 7043.439 | 44264.6715 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6340.0953 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.003 | 0.0476 | 0.0506 | 0.0493 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2620 | 7046.985 | 44264.6716 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6466.8972 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.0478 | 0.0501 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2623 | 7050.283 | 44264.6716 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6596.2352 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.0476 | 0.0501 | 0.049 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2626 | 7053.586 | 44264.6716 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6728.1599 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0026 | 0.0476 | 0.0502 | 0.0492 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2629 | 7057.268 | 44264.6717 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6862.7231 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0027 | 0.0478 | 0.0505 | 0.0494 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2632 | 7060.621 | 44264.6717 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6999.9776 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0026 | 0.0477 | 0.0503 | 0.049 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2635 | 7064.408 | 44264.6718 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7139.9771 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0028 | 0.0475 | 0.0503 | 0.0492 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2638 | 7067.943 | 44264.6718 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7282.7766 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0021 | 0.0484 | 0.0505 | 0.0496 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2641 | 7071.297 | 44264.6719 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7428.4322 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.0477 | 0.0502 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2644 | 7074.645 | 44264.6719 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7577.0008 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0019 | 0.0475 | 0.0494 | 0.0486 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2647 | 7078.11 | 44264.6719 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7728.5408 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0027 | 0.0475 | 0.0502 | 0.0491 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2650 | 7081.446 | 44264.672 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7883.1117 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.0475 | 0.0499 | 0.0489 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2653 | 7084.881 | 44264.672 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8040.7739 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0026 | 0.0478 | 0.0504 | 0.0491 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2656 | 7088.4 | 44264.6721 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8201.5894 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0023 | 0.0481 | 0.0504 | 0.0491 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2659 | 7092.023 | 44264.6721 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8365.6212 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0028 | 0.0473 | 0.0501 | 0.049 | 0.001 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2662 | 7095.471 | 44264.6721 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8532.9336 | 0:240:120 | 0:00 | 0.045 | 7 | 0.002 | 0.0475 | 0.0495 | 0.0487 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2665 | 7098.89 | 44264.6722 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8703.5923 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0024 | 0.0476 | 0.05 | 0.0486 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2668 | 7102.449 | 44264.6722 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8877.6641 | 0:240:120 | 0:00 | 0.045 | 7 | 0.002 | 0.0475 | 0.0495 | 0.0483 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2671 | 7105.688 | 44264.6723 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9055.2174 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0018 | 0.0478 | 0.0496 | 0.0487 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2674 | 7109.128 | 44264.6723 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9236.3217 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0018 | 0.0475 | 0.0493 | 0.0485 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2677 | 7112.537 | 44264.6723 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9421.0482 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0025 | 0.0474 | 0.0499 | 0.0486 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2680 | 7115.677 | 44264.6724 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9609.4691 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0017 | 0.0483 | 0.05 | 0.049 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2683 | 7118.94 | 44264.6724 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9801.6585 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0018 | 0.0484 | 0.0502 | 0.0492 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2686 | 7122.194 | 44264.6724 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9997.6917 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0022 | 0.048 | 0.0502 | 0.0491 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2689 | 7125.52 | 44264.6725 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10197.6455 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0016 | 0.048 | 0.0496 | 0.0489 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2692 | 7128.763 | 44264.6725 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10401.5984 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0029 | 0.0472 | 0.0501 | 0.049 | 0.001 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2695 | 7131.911 | 44264.6726 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10609.6304 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0018 | 0.0479 | 0.0497 | 0.0486 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2698 | 7135.569 | 44264.6726 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10821.823 | 0:240:120 | 0:00 | 0.045 | 7 | 0.003 | 0.0473 | 0.0503 | 0.0484 | 0.001 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2701 | 7138.91 | 44264.6726 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11038.2595 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0032 | 0.0469 | 0.0501 | 0.0484 | 0.0011 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2704 | 7142.222 | 44264.6727 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11259.0246 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0032 | 0.047 | 0.0502 | 0.0491 | 0.0013 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2707 | 7145.918 | 44264.6727 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11484.2051 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0024 | 0.0478 | 0.0502 | 0.0488 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2710 | 7149.137 | 44264.6728 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11713.8892 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0016 | 0.0478 | 0.0494 | 0.0486 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2713 | 7152.279 | 44264.6728 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11948.167 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0034 | 0.0467 | 0.0501 | 0.0482 | 0.0012 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2716 | 7203.762 | 44264.6734 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.2 | 0:240:120 | 0:00 | 6.0326 | 7 | 15.9691 | 36.2245 | 52.1936 | 41.0992 | 6.9007 | 47.6197 | 3 | 6.0326 | 24.8711 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2719 | 7339.303 | 44264.675 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.2 | 0:240:120 | 0:00 | 5.1418 | 7 | 12.4414 | 17.9965 | 30.4379 | 22.2611 | 5.8981 | 34.7877 | 3 | 5.1418 | 15.6891 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2722 | 7413.569 | 44264.6758 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.1 | 0:240:120 | 0:00 | 4.5292 | 7 | 1.922 | 9.0755 | 10.9975 | 9.6814 | 0.8961 | 0.803 | 3 | 4.5292 | 11.7228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2725 | 7447.096 | 44264.6762 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.1 | 0:240:120 | 0:00 | 3.9917 | 7 | 0.8085 | 7.7894 | 8.5979 | 8.1723 | 0.3294 | 0.1085 | 3 | 3.9917 | 9.1164 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2728 | 7475.174 | 44264.6765 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50 | 0:240:120 | 0:00 | 3.6006 | 7 | 0.8023 | 6.7966 | 7.5989 | 7.1112 | 0.3687 | 0.1359 | 3 | 3.6006 | 7.5744 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2731 | 7499.995 | 44264.6768 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51 | 0:240:120 | 0:00 | 3.2418 | 7 | 0.9835 | 5.6114 | 6.5949 | 5.9479 | 0.4839 | 0.2341 | 3 | 3.2418 | 6.359 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2734 | 7521.448 | 44264.6771 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.1 | 0:240:120 | 0:00 | 2.9165 | 7 | 0.5889 | 4.5805 | 5.1694 | 4.7808 | 0.281 | 0.0789 | 3 | 2.9165 | 5.3902 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2737 | 7539.232 | 44264.6773 | Vista Coord | Main | 40Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.1 | 0:240:120 | 0:00 | 2.6688 | 7 | 0.2904 | 4.1543 | 4.4447 | 4.2709 | 0.1315 | 0.0173 | 3 | 2.6688 | 4.7242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2740 | 7652.194 | 44264.6786 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55 | 0:240:120 | 0:00 | 9.5688 | 7 | 13.0532 | 86.5188 | 99.572 | 91.456 | 6.1025 | 37.2406 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2743 | 7936.035 | 44264.6819 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.1 | 0:240:120 | 0:00 | 7.7705 | 7 | 14.1541 | 67.4226 | 81.5767 | 73.9183 | 5.8529 | 34.2565 | 3 | 7.7705 | 101.5883 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2746 | 8165.716 | 44264.6845 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.222 | 0:240:120 | 0:00 | 6.502 | 7 | 14.1104 | 49.4665 | 63.5769 | 55.9095 | 5.8659 | 34.4094 | 3 | 6.502 | 32.8902 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2749 | 8341.5 | 44264.6866 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.3664 | 0:240:120 | 0:00 | 5.5599 | 7 | 17.3222 | 28.2011 | 45.5233 | 35.3553 | 7.7139 | 59.505 | 3 | 5.5599 | 19.3218 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2752 | 8462.198 | 44264.688 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.5338 | 0:240:120 | 0:00 | 4.833 | 7 | 17.0412 | 9.5998 | 26.641 | 15.5805 | 8.2466 | 68.0071 | 3 | 4.833 | 13.5272 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2755 | 8527.82 | 44264.6887 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.7244 | 0:240:120 | 0:00 | 4.2557 | 7 | 0.7614 | 8.5933 | 9.3547 | 8.8445 | 0.374 | 0.1399 | 3 | 4.2557 | 10.3153 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2758 | 8557.481 | 44264.6891 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.9389 | 0:240:120 | 0:00 | 3.7863 | 7 | 0.5441 | 7.5897 | 8.1338 | 7.7719 | 0.2674 | 0.0715 | 3 | 3.7863 | 8.2753 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2761 | 8584.105 | 44264.6894 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.1777 | 0:240:120 | 0:00 | 3.3975 | 7 | 0.7688 | 6.3304 | 7.0992 | 6.648 | 0.3427 | 0.1174 | 3 | 3.3975 | 6.8658 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2764 | 8607.731 | 44264.6896 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.4413 | 0:240:120 | 0:00 | 3.0704 | 7 | 0.9806 | 5.1074 | 6.088 | 5.4454 | 0.4773 | 0.2278 | 3 | 3.0704 | 5.8343 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2767 | 8627.533 | 44264.6899 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.7301 | 0:240:120 | 0:00 | 2.7916 | 7 | 0.2381 | 4.4414 | 4.6795 | 4.5149 | 0.1093 | 0.0119 | 3 | 2.7916 | 5.0472 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2770 | 8644.184 | 44264.6901 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.0447 | 0:240:120 | 0:00 | 2.5513 | 7 | 0.3191 | 3.9611 | 4.2802 | 4.1008 | 0.1379 | 0.019 | 3 | 2.5513 | 4.4273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2773 | 8659.695 | 44264.6902 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.3856 | 0:240:120 | 0:00 | 2.3422 | 7 | 0.268 | 3.6168 | 3.8848 | 3.7033 | 0.1268 | 0.0161 | 3 | 2.3422 | 3.9269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2776 | 8673.948 | 44264.6904 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.7533 | 0:240:120 | 0:00 | 2.1587 | 7 | 0.3224 | 3.134 | 3.4564 | 3.2833 | 0.1344 | 0.0181 | 3 | 2.1587 | 3.5146 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2779 | 8686.931 | 44264.6906 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.1484 | 0:240:120 | 0:00 | 1.9965 | 7 | 0.1513 | 2.8775 | 3.0288 | 2.9267 | 0.0716 | 0.0051 | 3 | 1.9965 | 3.1694 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2782 | 8699.167 | 44264.6907 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.5713 | 0:240:120 | 0:00 | 1.8523 | 7 | 0.164 | 2.6343 | 2.7983 | 2.6916 | 0.08 | 0.0064 | 3 | 1.8523 | 2.8763 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2785 | 8710.339 | 44264.6908 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.0228 | 0:240:120 | 0:00 | 1.7232 | 7 | 0.1192 | 2.4375 | 2.5567 | 2.4846 | 0.053 | 0.0028 | 3 | 1.7232 | 2.6246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2788 | 8721.072 | 44264.6909 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.5032 | 0:240:120 | 0:00 | 1.6071 | 7 | 0.1363 | 2.2243 | 2.3606 | 2.2684 | 0.0646 | 0.0042 | 3 | 1.6071 | 2.4062 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2791 | 8731.136 | 44264.6911 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.0133 | 0:240:120 | 0:00 | 1.5023 | 7 | 0.0956 | 2.0469 | 2.1425 | 2.0793 | 0.0471 | 0.0022 | 3 | 1.5023 | 2.215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2794 | 8740.564 | 44264.6912 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.5535 | 0:240:120 | 0:00 | 1.4072 | 7 | 0.0967 | 1.9035 | 2.0002 | 1.9367 | 0.0474 | 0.0023 | 3 | 1.4072 | 2.0464 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2797 | 8749.55 | 44264.6913 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.1246 | 0:240:120 | 0:00 | 1.3205 | 7 | 0.097 | 1.7587 | 1.8557 | 1.7927 | 0.0471 | 0.0022 | 3 | 1.3205 | 1.8967 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2800 | 8758.106 | 44264.6914 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.7271 | 0:240:120 | 0:00 | 1.2414 | 7 | 0.0788 | 1.631 | 1.7098 | 1.6596 | 0.0377 | 0.0014 | 3 | 1.2414 | 1.7631 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2803 | 8766.051 | 44264.6915 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.3616 | 0:240:120 | 0:00 | 1.1688 | 7 | 0.0642 | 1.5342 | 1.5984 | 1.5567 | 0.0309 | 0.001 | 3 | 1.1688 | 1.643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2806 | 8773.98 | 44264.6916 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.0289 | 0:240:120 | 0:00 | 1.1021 | 7 | 0.0636 | 1.4383 | 1.5019 | 1.4607 | 0.0306 | 0.0009 | 3 | 1.1021 | 1.5348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2809 | 8781.895 | 44264.6917 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.7295 | 0:240:120 | 0:00 | 1.0406 | 7 | 0.0641 | 1.3421 | 1.4062 | 1.3635 | 0.0318 | 0.001 | 3 | 1.0406 | 1.4367 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2812 | 8789.056 | 44264.6917 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.464 | 0:240:120 | 0:00 | 0.9838 | 7 | 0.0479 | 1.2729 | 1.3208 | 1.29 | 0.0231 | 0.0005 | 3 | 0.9838 | 1.3474 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2815 | 8796.203 | 44264.6918 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.2333 | 0:240:120 | 0:00 | 0.9312 | 7 | 0.0467 | 1.202 | 1.2487 | 1.2191 | 0.0221 | 0.0005 | 3 | 0.9312 | 1.266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2818 | 8802.877 | 44264.6919 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.038 | 0:240:120 | 0:00 | 0.8824 | 7 | 0.0473 | 1.1178 | 1.1651 | 1.1363 | 0.0214 | 0.0005 | 3 | 0.8824 | 1.1914 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2821 | 8809.08 | 44264.692 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.8788 | 0:240:120 | 0:00 | 0.837 | 7 | 0.0362 | 1.0662 | 1.1024 | 1.0796 | 0.0168 | 0.0003 | 3 | 0.837 | 1.1229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2824 | 8815.534 | 44264.692 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.7563 | 0:240:120 | 0:00 | 0.7947 | 7 | 0.0389 | 1.0069 | 1.0458 | 1.0217 | 0.0177 | 0.0003 | 3 | 0.7947 | 1.0598 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2827 | 8821.848 | 44264.6921 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.6715 | 0:240:120 | 0:00 | 0.7553 | 7 | 0.0352 | 0.9502 | 0.9854 | 0.9633 | 0.0164 | 0.0003 | 3 | 0.7553 | 1.0015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2830 | 8827.809 | 44264.6922 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.6249 | 0:240:120 | 0:00 | 0.7184 | 7 | 0.0289 | 0.9039 | 0.9328 | 0.9146 | 0.0133 | 0.0002 | 3 | 0.7184 | 0.9476 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2833 | 8833.642 | 44264.6923 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.6174 | 0:240:120 | 0:00 | 0.6839 | 7 | 0.0289 | 0.8608 | 0.8897 | 0.8711 | 0.0136 | 0.0002 | 3 | 0.6839 | 0.8976 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2836 | 8839.487 | 44264.6923 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.6497 | 0:240:120 | 0:00 | 0.6516 | 7 | 0.0247 | 0.8146 | 0.8393 | 0.8235 | 0.0115 | 0.0001 | 3 | 0.6516 | 0.8512 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2839 | 8845.167 | 44264.6924 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.7227 | 0:240:120 | 0:00 | 0.6212 | 7 | 0.0226 | 0.7753 | 0.7979 | 0.7835 | 0.0104 | 0.0001 | 3 | 0.6212 | 0.8079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2842 | 8850.67 | 44264.6924 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.8372 | 0:240:120 | 0:00 | 0.5927 | 7 | 0.0247 | 0.7361 | 0.7608 | 0.7448 | 0.0116 | 0.0001 | 3 | 0.5927 | 0.7676 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2845 | 8855.945 | 44264.6925 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.9939 | 0:240:120 | 0:00 | 0.5659 | 7 | 0.0198 | 0.7026 | 0.7224 | 0.7096 | 0.0089 | 0.0001 | 3 | 0.5659 | 0.7299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2848 | 8861.159 | 44264.6926 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.1938 | 0:240:120 | 0:00 | 0.5407 | 7 | 0.0204 | 0.6696 | 0.69 | 0.6773 | 0.0094 | 0.0001 | 3 | 0.5407 | 0.6947 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2851 | 8866.715 | 44264.6926 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.4377 | 0:240:120 | 0:00 | 0.5169 | 7 | 0.0174 | 0.6387 | 0.6561 | 0.6454 | 0.0079 | 0.0001 | 3 | 0.5169 | 0.6617 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2854 | 8871.513 | 44264.6927 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.7264 | 0:240:120 | 0:00 | 0.4944 | 7 | 0.0165 | 0.6109 | 0.6274 | 0.6174 | 0.0074 | 0.0001 | 3 | 0.4944 | 0.6307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2857 | 8876.327 | 44264.6927 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.061 | 0:240:120 | 0:00 | 0.4732 | 7 | 0.0168 | 0.5829 | 0.5997 | 0.5896 | 0.0075 | 0.0001 | 3 | 0.4732 | 0.6017 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2860 | 8881.219 | 44264.6928 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.4422 | 0:240:120 | 0:00 | 0.4532 | 7 | 0.0162 | 0.5569 | 0.5731 | 0.5631 | 0.0072 | 0.0001 | 3 | 0.4532 | 0.5743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2863 | 8886.123 | 44264.6929 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.871 | 0:240:120 | 0:00 | 0.4343 | 7 | 0.0138 | 0.5332 | 0.547 | 0.5386 | 0.0062 | 0 | 3 | 0.4343 | 0.5486 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2866 | 8890.917 | 44264.6929 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.3484 | 0:240:120 | 0:00 | 0.4164 | 7 | 0.0147 | 0.5098 | 0.5245 | 0.516 | 0.006 | 0 | 3 | 0.4164 | 0.5244 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2869 | 8895.484 | 44264.693 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.8754 | 0:240:120 | 0:00 | 0.3994 | 7 | 0.0131 | 0.4893 | 0.5024 | 0.4941 | 0.0058 | 0 | 3 | 0.3994 | 0.5015 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2872 | 8900.143 | 44264.693 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131.4529 | 0:240:120 | 0:00 | 0.3833 | 7 | 0.0093 | 0.4701 | 0.4794 | 0.474 | 0.004 | 0 | 3 | 0.3833 | 0.4799 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2875 | 8904.542 | 44264.6931 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.082 | 0:240:120 | 0:00 | 0.368 | 7 | 0.0117 | 0.4506 | 0.4623 | 0.4552 | 0.005 | 0 | 3 | 0.368 | 0.4595 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2878 | 8908.815 | 44264.6931 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.7636 | 0:240:120 | 0:00 | 0.3536 | 7 | 0.0109 | 0.432 | 0.4429 | 0.4364 | 0.0046 | 0 | 3 | 0.3536 | 0.4402 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2881 | 8913.33 | 44264.6932 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 139.4989 | 0:240:120 | 0:00 | 0.3398 | 7 | 0.0103 | 0.4151 | 0.4254 | 0.4195 | 0.0044 | 0 | 3 | 0.3398 | 0.422 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2884 | 8917.681 | 44264.6932 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.2889 | 0:240:120 | 0:00 | 0.3268 | 7 | 0.0092 | 0.3986 | 0.4078 | 0.4026 | 0.0038 | 0 | 3 | 0.3268 | 0.4047 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2887 | 8922.052 | 44264.6933 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 145.1346 | 0:240:120 | 0:00 | 0.3143 | 7 | 0.009 | 0.3831 | 0.3921 | 0.3866 | 0.0037 | 0 | 3 | 0.3143 | 0.3884 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2890 | 8926.391 | 44264.6933 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.0373 | 0:240:120 | 0:00 | 0.3025 | 7 | 0.0088 | 0.3683 | 0.3771 | 0.3717 | 0.0036 | 0 | 3 | 0.3025 | 0.3728 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2893 | 8930.684 | 44264.6934 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.9981 | 0:240:120 | 0:00 | 0.2913 | 7 | 0.0092 | 0.3547 | 0.3639 | 0.3586 | 0.0035 | 0 | 3 | 0.2913 | 0.3581 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2896 | 8934.978 | 44264.6934 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 154.018 | 0:240:120 | 0:00 | 0.2806 | 7 | 0.0073 | 0.3417 | 0.349 | 0.3444 | 0.0033 | 0 | 3 | 0.2806 | 0.3441 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2899 | 8939.236 | 44264.6935 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 157.0984 | 0:240:120 | 0:00 | 0.2704 | 7 | 0.0069 | 0.3293 | 0.3362 | 0.3319 | 0.0028 | 0 | 3 | 0.2704 | 0.3309 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2902 | 8943.481 | 44264.6935 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.2404 | 0:240:120 | 0:00 | 0.2607 | 7 | 0.0088 | 0.3162 | 0.325 | 0.3202 | 0.0033 | 0 | 3 | 0.2607 | 0.3182 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2905 | 8947.856 | 44264.6936 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 163.4452 | 0:240:120 | 0:00 | 0.2515 | 7 | 0.0068 | 0.3058 | 0.3126 | 0.3088 | 0.0028 | 0 | 3 | 0.2515 | 0.3063 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2908 | 8951.78 | 44264.6936 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.7141 | 0:240:120 | 0:00 | 0.2427 | 7 | 0.0066 | 0.295 | 0.3016 | 0.2976 | 0.0029 | 0 | 3 | 0.2427 | 0.2948 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2911 | 8955.863 | 44264.6937 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.0484 | 0:240:120 | 0:00 | 0.2343 | 7 | 0.0056 | 0.2843 | 0.2899 | 0.287 | 0.0022 | 0 | 3 | 0.2343 | 0.284 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2914 | 8959.982 | 44264.6937 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 173.4493 | 0:240:120 | 0:00 | 0.2263 | 7 | 0.0063 | 0.2737 | 0.28 | 0.2764 | 0.0024 | 0 | 3 | 0.2263 | 0.2736 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2917 | 8964.001 | 44264.6938 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176.9183 | 0:240:120 | 0:00 | 0.2186 | 7 | 0.0062 | 0.2642 | 0.2704 | 0.2672 | 0.0024 | 0 | 3 | 0.2186 | 0.2638 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2920 | 8968.254 | 44264.6938 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 180.4567 | 0:240:120 | 0:00 | 0.2113 | 7 | 0.0063 | 0.2554 | 0.2617 | 0.259 | 0.0023 | 0 | 3 | 0.2113 | 0.2544 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2923 | 8972.312 | 44264.6939 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 184.0658 | 0:240:120 | 0:00 | 0.2043 | 7 | 0.0062 | 0.2475 | 0.2537 | 0.2501 | 0.0024 | 0 | 3 | 0.2043 | 0.2455 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2926 | 8976.361 | 44264.6939 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 187.7471 | 0:240:120 | 0:00 | 0.1977 | 7 | 0.0041 | 0.2397 | 0.2438 | 0.2418 | 0.0015 | 0 | 3 | 0.1977 | 0.2372 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2929 | 8980.166 | 44264.6939 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 191.5021 | 0:240:120 | 0:00 | 0.1913 | 7 | 0.0048 | 0.2322 | 0.237 | 0.2342 | 0.0017 | 0 | 3 | 0.1913 | 0.2296 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2932 | 8984.079 | 44264.694 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 195.3321 | 0:240:120 | 0:00 | 0.1852 | 7 | 0.005 | 0.2245 | 0.2295 | 0.2266 | 0.0019 | 0 | 3 | 0.1852 | 0.2223 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2935 | 8987.75 | 44264.694 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 199.2388 | 0:240:120 | 0:00 | 0.1794 | 7 | 0.0047 | 0.2175 | 0.2222 | 0.2196 | 0.0017 | 0 | 3 | 0.1794 | 0.2153 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2938 | 8991.324 | 44264.6941 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 203.2235 | 0:240:120 | 0:00 | 0.1739 | 7 | 0.0041 | 0.2114 | 0.2155 | 0.2133 | 0.0017 | 0 | 3 | 0.1739 | 0.2086 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2941 | 8995.137 | 44264.6941 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 207.288 | 0:240:120 | 0:00 | 0.1686 | 7 | 0.0041 | 0.2043 | 0.2084 | 0.2062 | 0.0013 | 0 | 3 | 0.1686 | 0.2023 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2944 | 8999.027 | 44264.6942 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 211.4338 | 0:240:120 | 0:00 | 0.1635 | 7 | 0.0054 | 0.1977 | 0.2031 | 0.2002 | 0.0022 | 0 | 3 | 0.1635 | 0.1962 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2947 | 9002.579 | 44264.6942 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 215.6625 | 0:240:120 | 0:00 | 0.1586 | 7 | 0.0037 | 0.1919 | 0.1956 | 0.1941 | 0.0013 | 0 | 3 | 0.1586 | 0.1903 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2950 | 9006.227 | 44264.6942 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 219.9757 | 0:240:120 | 0:00 | 0.154 | 7 | 0.0033 | 0.1869 | 0.1902 | 0.1885 | 0.0013 | 0 | 3 | 0.154 | 0.1847 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2953 | 9009.981 | 44264.6943 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 224.3752 | 0:240:120 | 0:00 | 0.1495 | 7 | 0.0024 | 0.1823 | 0.1847 | 0.1832 | 0.0009 | 0 | 3 | 0.1495 | 0.1794 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2956 | 9013.593 | 44264.6943 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 228.8627 | 0:240:120 | 0:00 | 0.1452 | 7 | 0.0036 | 0.1752 | 0.1788 | 0.1772 | 0.0014 | 0 | 3 | 0.1452 | 0.1743 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2959 | 9017.358 | 44264.6944 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 233.44 | 0:240:120 | 0:00 | 0.1412 | 7 | 0.0025 | 0.171 | 0.1735 | 0.1723 | 0.0009 | 0 | 3 | 0.1412 | 0.1694 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2962 | 9021.181 | 44264.6944 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 238.1088 | 0:240:120 | 0:00 | 0.1373 | 7 | 0.0038 | 0.1657 | 0.1695 | 0.1679 | 0.0013 | 0 | 3 | 0.1373 | 0.1647 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2965 | 9024.96 | 44264.6945 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 242.8709 | 0:240:120 | 0:00 | 0.1335 | 7 | 0.003 | 0.1613 | 0.1643 | 0.1634 | 0.0011 | 0 | 3 | 0.1335 | 0.1602 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2968 | 9028.476 | 44264.6945 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 247.7284 | 0:240:120 | 0:00 | 0.1299 | 7 | 0.0026 | 0.1571 | 0.1597 | 0.1586 | 0.0011 | 0 | 3 | 0.1299 | 0.1559 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2971 | 9032.402 | 44264.6946 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 252.6829 | 0:240:120 | 0:00 | 0.1265 | 7 | 0.0034 | 0.153 | 0.1564 | 0.1546 | 0.0013 | 0 | 3 | 0.1265 | 0.1518 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2974 | 9035.929 | 44264.6946 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 257.7366 | 0:240:120 | 0:00 | 0.1232 | 7 | 0.0029 | 0.1498 | 0.1527 | 0.1514 | 0.001 | 0 | 3 | 0.1232 | 0.1479 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2977 | 9039.385 | 44264.6946 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 262.8913 | 0:240:120 | 0:00 | 0.1201 | 7 | 0.004 | 0.1446 | 0.1486 | 0.147 | 0.0013 | 0 | 3 | 0.1201 | 0.1441 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2980 | 9042.809 | 44264.6947 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 268.1492 | 0:240:120 | 0:00 | 0.117 | 7 | 0.0032 | 0.1412 | 0.1444 | 0.143 | 0.0011 | 0 | 3 | 0.117 | 0.1405 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2983 | 9046.31 | 44264.6947 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 273.5121 | 0:240:120 | 0:00 | 0.1141 | 7 | 0.0028 | 0.1385 | 0.1413 | 0.1398 | 0.001 | 0 | 3 | 0.1141 | 0.137 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2986 | 9049.76 | 44264.6948 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 278.9824 | 0:240:120 | 0:00 | 0.1114 | 7 | 0.0022 | 0.1352 | 0.1374 | 0.1363 | 0.0008 | 0 | 3 | 0.1114 | 0.1336 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2989 | 9053.214 | 44264.6948 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 284.562 | 0:240:120 | 0:00 | 0.1087 | 7 | 0.0029 | 0.1318 | 0.1347 | 0.1335 | 0.0009 | 0 | 3 | 0.1087 | 0.1305 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2992 | 9056.8 | 44264.6948 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 290.2533 | 0:240:120 | 0:00 | 0.1062 | 7 | 0.0018 | 0.129 | 0.1308 | 0.1301 | 0.0007 | 0 | 3 | 0.1062 | 0.1274 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2995 | 9060.227 | 44264.6949 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 296.0583 | 0:240:120 | 0:00 | 0.1037 | 7 | 0.0026 | 0.125 | 0.1276 | 0.1268 | 0.0009 | 0 | 3 | 0.1037 | 0.1245 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2998 | 9063.654 | 44264.6949 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 301.9795 | 0:240:120 | 0:00 | 0.1014 | 7 | 0.0031 | 0.1223 | 0.1254 | 0.1238 | 0.0009 | 0 | 3 | 0.1014 | 0.1217 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3001 | 9067.102 | 44264.695 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 308.0191 | 0:240:120 | 0:00 | 0.0991 | 7 | 0.0041 | 0.119 | 0.1231 | 0.1217 | 0.0016 | 0 | 3 | 0.0991 | 0.119 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3004 | 9070.655 | 44264.695 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 314.1795 | 0:240:120 | 0:00 | 0.097 | 7 | 0.0028 | 0.1176 | 0.1204 | 0.1188 | 0.0009 | 0 | 3 | 0.097 | 0.1164 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3007 | 9074.185 | 44264.695 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 320.4631 | 0:240:120 | 0:00 | 0.0949 | 7 | 0.0033 | 0.114 | 0.1173 | 0.116 | 0.0011 | 0 | 3 | 0.0949 | 0.1139 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3010 | 9077.772 | 44264.6951 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 326.8723 | 0:240:120 | 0:00 | 0.0929 | 7 | 0.0025 | 0.1115 | 0.114 | 0.1134 | 0.0009 | 0 | 3 | 0.0929 | 0.1115 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3013 | 9081.228 | 44264.6951 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 333.4098 | 0:240:120 | 0:00 | 0.091 | 7 | 0.0022 | 0.11 | 0.1122 | 0.1113 | 0.0009 | 0 | 3 | 0.091 | 0.1092 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3016 | 9084.673 | 44264.6952 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 340.078 | 0:240:120 | 0:00 | 0.0892 | 7 | 0.0027 | 0.1076 | 0.1103 | 0.1089 | 0.0008 | 0 | 3 | 0.0892 | 0.107 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3019 | 9088.276 | 44264.6952 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 346.8795 | 0:240:120 | 0:00 | 0.0874 | 7 | 0.0031 | 0.1055 | 0.1086 | 0.1075 | 0.0013 | 0 | 3 | 0.0874 | 0.1049 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3022 | 9091.764 | 44264.6952 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 353.8171 | 0:240:120 | 0:00 | 0.0858 | 7 | 0.0032 | 0.1027 | 0.1059 | 0.1045 | 0.001 | 0 | 3 | 0.0858 | 0.1029 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3025 | 9095.212 | 44264.6953 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 360.8935 | 0:240:120 | 0:00 | 0.0841 | 7 | 0.0035 | 0.1009 | 0.1044 | 0.1029 | 0.0013 | 0 | 3 | 0.0841 | 0.101 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3028 | 9098.534 | 44264.6953 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 368.1113 | 0:240:120 | 0:00 | 0.0826 | 7 | 0.0029 | 0.0993 | 0.1022 | 0.1009 | 0.0012 | 0 | 3 | 0.0826 | 0.0991 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3031 | 9101.968 | 44264.6954 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 375.4736 | 0:240:120 | 0:00 | 0.0811 | 7 | 0.0031 | 0.0981 | 0.1012 | 0.0994 | 0.0011 | 0 | 3 | 0.0811 | 0.0973 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3034 | 9105.445 | 44264.6954 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 382.983 | 0:240:120 | 0:00 | 0.0797 | 7 | 0.0027 | 0.0955 | 0.0982 | 0.0973 | 0.0009 | 0 | 3 | 0.0797 | 0.0956 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3037 | 9108.858 | 44264.6954 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 390.6427 | 0:240:120 | 0:00 | 0.0783 | 7 | 0.0029 | 0.0937 | 0.0966 | 0.0955 | 0.0012 | 0 | 3 | 0.0783 | 0.094 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3040 | 9112.327 | 44264.6955 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 398.4555 | 0:240:120 | 0:00 | 0.077 | 7 | 0.0029 | 0.0925 | 0.0954 | 0.0941 | 0.001 | 0 | 3 | 0.077 | 0.0924 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3043 | 9116.062 | 44264.6955 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 406.4246 | 0:240:120 | 0:00 | 0.0757 | 7 | 0.0028 | 0.0913 | 0.0941 | 0.0927 | 0.001 | 0 | 3 | 0.0757 | 0.0909 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3046 | 9119.715 | 44264.6956 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 414.5531 | 0:240:120 | 0:00 | 0.0745 | 7 | 0.003 | 0.0894 | 0.0924 | 0.091 | 0.001 | 0 | 3 | 0.0745 | 0.0894 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3049 | 9123.302 | 44264.6956 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 422.8442 | 0:240:120 | 0:00 | 0.0734 | 7 | 0.0029 | 0.0879 | 0.0908 | 0.0895 | 0.0009 | 0 | 3 | 0.0734 | 0.088 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3052 | 9126.741 | 44264.6956 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 431.3011 | 0:240:120 | 0:00 | 0.0722 | 7 | 0.0033 | 0.0865 | 0.0898 | 0.0885 | 0.0011 | 0 | 3 | 0.0722 | 0.0867 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3055 | 9130.19 | 44264.6957 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 439.9271 | 0:240:120 | 0:00 | 0.0712 | 7 | 0.0025 | 0.0853 | 0.0878 | 0.0867 | 0.0008 | 0 | 3 | 0.0712 | 0.0854 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3058 | 9133.53 | 44264.6957 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 448.7257 | 0:240:120 | 0:00 | 0.0701 | 7 | 0.0025 | 0.0834 | 0.0859 | 0.0851 | 0.0009 | 0 | 3 | 0.0701 | 0.0842 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3061 | 9137.121 | 44264.6958 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 457.7002 | 0:240:120 | 0:00 | 0.0692 | 7 | 0.0036 | 0.082 | 0.0856 | 0.084 | 0.0011 | 0 | 3 | 0.0692 | 0.083 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3064 | 9140.536 | 44264.6958 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 466.8542 | 0:240:120 | 0:00 | 0.0682 | 7 | 0.0017 | 0.0815 | 0.0832 | 0.0826 | 0.0006 | 0 | 3 | 0.0682 | 0.0818 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3067 | 9144.01 | 44264.6958 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 476.1913 | 0:240:120 | 0:00 | 0.0673 | 7 | 0.0027 | 0.0807 | 0.0834 | 0.082 | 0.0009 | 0 | 3 | 0.0673 | 0.0808 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3070 | 9147.467 | 44264.6959 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 485.7151 | 0:240:120 | 0:00 | 0.0664 | 7 | 0.0032 | 0.0789 | 0.0821 | 0.0809 | 0.0011 | 0 | 3 | 0.0664 | 0.0797 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3073 | 9150.915 | 44264.6959 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 495.4294 | 0:240:120 | 0:00 | 0.0656 | 7 | 0.003 | 0.078 | 0.081 | 0.0795 | 0.001 | 0 | 3 | 0.0656 | 0.0787 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3076 | 9154.366 | 44264.696 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 505.338 | 0:240:120 | 0:00 | 0.0648 | 7 | 0.0025 | 0.077 | 0.0795 | 0.0784 | 0.0008 | 0 | 3 | 0.0648 | 0.0777 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3079 | 9158.423 | 44264.696 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 515.4447 | 0:240:120 | 0:00 | 0.064 | 7 | 0.003 | 0.0758 | 0.0788 | 0.0769 | 0.0009 | 0 | 3 | 0.064 | 0.0768 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3082 | 9162.043 | 44264.6961 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 525.7536 | 0:240:120 | 0:00 | 0.0633 | 7 | 0.0028 | 0.075 | 0.0778 | 0.0765 | 0.0009 | 0 | 3 | 0.0633 | 0.0759 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3085 | 9165.469 | 44264.6961 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 536.2687 | 0:240:120 | 0:00 | 0.0625 | 7 | 0.0022 | 0.0742 | 0.0764 | 0.0754 | 0.0008 | 0 | 3 | 0.0625 | 0.075 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3088 | 9168.917 | 44264.6961 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 546.9941 | 0:240:120 | 0:00 | 0.0619 | 7 | 0.003 | 0.0729 | 0.0759 | 0.0746 | 0.0011 | 0 | 3 | 0.0619 | 0.0742 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3091 | 9172.327 | 44264.6962 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 557.9339 | 0:240:120 | 0:00 | 0.0612 | 7 | 0.003 | 0.0719 | 0.0749 | 0.0737 | 0.0012 | 0 | 3 | 0.0612 | 0.0734 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3094 | 9175.741 | 44264.6962 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 569.0926 | 0:240:120 | 0:00 | 0.0606 | 7 | 0.0029 | 0.0711 | 0.074 | 0.0728 | 0.001 | 0 | 3 | 0.0606 | 0.0727 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3097 | 9179.163 | 44264.6963 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 580.4745 | 0:240:120 | 0:00 | 0.0599 | 7 | 0.0029 | 0.0706 | 0.0735 | 0.0722 | 0.0011 | 0 | 3 | 0.0599 | 0.0719 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3100 | 9182.602 | 44264.6963 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 592.084 | 0:240:120 | 0:00 | 0.0594 | 7 | 0.003 | 0.0697 | 0.0727 | 0.0712 | 0.0012 | 0 | 3 | 0.0594 | 0.0712 | P | NP | 1-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3103 | 9186.26 | 44264.6963 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 603.9256 | 0:240:120 | 0:00 | 0.0588 | 7 | 0.002 | 0.0697 | 0.0717 | 0.0707 | 0.0007 | 0 | 3 | 0.0588 | 0.0706 | NP | NP | 0-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3106 | 9189.659 | 44264.6964 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 616.0042 | 0:240:120 | 0:00 | 0.0583 | 7 | 0.0029 | 0.0686 | 0.0715 | 0.07 | 0.0011 | 0 | 3 | 0.0583 | 0.0699 | NP | NP | 1-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3109 | 9193.079 | 44264.6964 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 628.3242 | 0:240:120 | 0:00 | 0.0577 | 7 | 0.003 | 0.067 | 0.07 | 0.0689 | 0.0012 | 0 | 3 | 0.0577 | 0.0693 | P | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3112 | 9196.538 | 44264.6965 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 640.8907 | 0:240:120 | 0:00 | 0.0572 | 7 | 0.002 | 0.0673 | 0.0693 | 0.0684 | 0.0007 | 0 | 3 | 0.0572 | 0.0687 | P | NP | 1-1-1-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3115 | 9200.227 | 44264.6965 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 653.7085 | 0:240:120 | 0:00 | 0.0568 | 7 | 0.0031 | 0.066 | 0.0691 | 0.0677 | 0.0011 | 0 | 3 | 0.0568 | 0.0681 | P | NP | 1-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3118 | 9203.639 | 44264.6965 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 666.7827 | 0:240:120 | 0:00 | 0.0563 | 7 | 0.0015 | 0.0661 | 0.0676 | 0.0671 | 0.0006 | 0 | 3 | 0.0563 | 0.0676 | P | NP | 0-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3121 | 9207.072 | 44264.6966 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 680.1184 | 0:240:120 | 0:00 | 0.0559 | 7 | 0.0022 | 0.0652 | 0.0674 | 0.0665 | 0.0009 | 0 | 3 | 0.0559 | 0.067 | P | NP | 0-1-0-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3124 | 9210.495 | 44264.6966 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 693.7207 | 0:240:120 | 0:00 | 0.0554 | 7 | 0.0028 | 0.064 | 0.0668 | 0.0657 | 0.0011 | 0 | 3 | 0.0554 | 0.0665 | P | NP | 1-1-1-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3127 | 9214.069 | 44264.6967 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 707.5951 | 0:240:120 | 0:00 | 0.055 | 7 | 0.004 | 0.0634 | 0.0674 | 0.0657 | 0.0015 | 0 | 3 | 0.055 | 0.066 | P | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3130 | 9217.663 | 44264.6967 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 721.7471 | 0:240:120 | 0:00 | 0.0546 | 7 | 0.0029 | 0.0634 | 0.0663 | 0.0651 | 0.001 | 0 | 3 | 0.0546 | 0.0656 | P | NP | 0-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3133 | 9221.104 | 44264.6967 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 736.182 | 0:240:120 | 0:00 | 0.0543 | 7 | 0.0025 | 0.0628 | 0.0653 | 0.064 | 0.001 | 0 | 3 | 0.0543 | 0.0651 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3136 | 9224.532 | 44264.6968 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 750.9056 | 0:240:120 | 0:00 | 0.0539 | 7 | 0.0027 | 0.0624 | 0.0651 | 0.0641 | 0.0009 | 0 | 3 | 0.0539 | 0.0647 | P | NP | 1-1-1-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3139 | 9227.981 | 44264.6968 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 765.9237 | 0:240:120 | 0:00 | 0.0536 | 7 | 0.003 | 0.0614 | 0.0644 | 0.0632 | 0.0011 | 0 | 3 | 0.0536 | 0.0643 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3142 | 9231.393 | 44264.6969 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 781.2422 | 0:240:120 | 0:00 | 0.0532 | 7 | 0.0024 | 0.0618 | 0.0642 | 0.063 | 0.0009 | 0 | 3 | 0.0532 | 0.0639 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3145 | 9234.722 | 44264.6969 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 796.8671 | 0:240:120 | 0:00 | 0.0529 | 7 | 0.0034 | 0.0604 | 0.0638 | 0.0622 | 0.0011 | 0 | 3 | 0.0529 | 0.0635 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3148 | 9238.413 | 44264.6969 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 812.8044 | 0:240:120 | 0:00 | 0.0526 | 7 | 0.0025 | 0.0608 | 0.0633 | 0.062 | 0.001 | 0 | 3 | 0.0526 | 0.0631 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3151 | 9241.821 | 44264.697 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 829.0605 | 0:240:120 | 0:00 | 0.0523 | 7 | 0.0027 | 0.0599 | 0.0626 | 0.0614 | 0.001 | 0 | 3 | 0.0523 | 0.0628 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3154 | 9245.215 | 44264.697 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 845.6417 | 0:240:120 | 0:00 | 0.052 | 7 | 0.0028 | 0.0593 | 0.0621 | 0.0611 | 0.001 | 0 | 3 | 0.052 | 0.0624 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3157 | 9248.657 | 44264.6971 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 862.5545 | 0:240:120 | 0:00 | 0.0517 | 7 | 0.0033 | 0.0587 | 0.062 | 0.0604 | 0.0012 | 0 | 3 | 0.0517 | 0.0621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3160 | 9252.077 | 44264.6971 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 879.8056 | 0:240:120 | 0:00 | 0.0515 | 7 | 0.0029 | 0.0588 | 0.0617 | 0.0603 | 0.0009 | 0 | 3 | 0.0515 | 0.0618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3163 | 9255.501 | 44264.6971 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 897.4017 | 0:240:120 | 0:00 | 0.0512 | 7 | 0.0037 | 0.0574 | 0.0611 | 0.0595 | 0.0011 | 0 | 3 | 0.0512 | 0.0615 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3166 | 9258.925 | 44264.6972 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 915.3498 | 0:240:120 | 0:00 | 0.051 | 7 | 0.0032 | 0.058 | 0.0612 | 0.0596 | 0.001 | 0 | 3 | 0.051 | 0.0612 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3169 | 9262.358 | 44264.6972 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 933.6568 | 0:240:120 | 0:00 | 0.0508 | 7 | 0.0025 | 0.0577 | 0.0602 | 0.059 | 0.0009 | 0 | 3 | 0.0508 | 0.0609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3172 | 9266.008 | 44264.6973 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 952.3299 | 0:240:120 | 0:00 | 0.0505 | 7 | 0.0026 | 0.0578 | 0.0604 | 0.0591 | 0.0009 | 0 | 3 | 0.0505 | 0.0606 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3175 | 9269.459 | 44264.6973 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 971.3765 | 0:240:120 | 0:00 | 0.0503 | 7 | 0.0028 | 0.0569 | 0.0597 | 0.0582 | 0.001 | 0 | 3 | 0.0503 | 0.0604 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3178 | 9272.857 | 44264.6973 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 990.804 | 0:240:120 | 0:00 | 0.0501 | 7 | 0.004 | 0.0559 | 0.0599 | 0.0579 | 0.0013 | 0 | 3 | 0.0501 | 0.0601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3181 | 9276.505 | 44264.6974 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1010.6201 | 0:240:120 | 0:00 | 0.0499 | 7 | 0.003 | 0.0564 | 0.0594 | 0.0579 | 0.0011 | 0 | 3 | 0.0499 | 0.0599 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3184 | 9279.939 | 44264.6974 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1030.8325 | 0:240:120 | 0:00 | 0.0497 | 7 | 0.0042 | 0.0555 | 0.0597 | 0.0578 | 0.0012 | 0 | 3 | 0.0497 | 0.0597 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3187 | 9283.593 | 44264.6975 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1051.4492 | 0:240:120 | 0:00 | 0.0495 | 7 | 0.0032 | 0.0551 | 0.0583 | 0.0568 | 0.001 | 0 | 3 | 0.0495 | 0.0595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3190 | 9286.914 | 44264.6975 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1072.4782 | 0:240:120 | 0:00 | 0.0494 | 7 | 0.0029 | 0.0554 | 0.0583 | 0.0568 | 0.0011 | 0 | 3 | 0.0494 | 0.0594 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3193 | 9290.288 | 44264.6975 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1093.9277 | 0:240:120 | 0:00 | 0.0492 | 7 | 0.0029 | 0.055 | 0.0579 | 0.0564 | 0.0011 | 0 | 3 | 0.0492 | 0.0592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3196 | 9293.924 | 44264.6976 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1115.8063 | 0:240:120 | 0:00 | 0.049 | 7 | 0.0036 | 0.0553 | 0.0589 | 0.057 | 0.001 | 0 | 3 | 0.049 | 0.059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3199 | 9297.367 | 44264.6976 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1138.1224 | 0:240:120 | 0:00 | 0.0489 | 7 | 0.0025 | 0.0553 | 0.0578 | 0.0565 | 0.001 | 0 | 3 | 0.0489 | 0.0589 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3202 | 9300.791 | 44264.6977 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1160.8848 | 0:240:120 | 0:00 | 0.0487 | 7 | 0.0032 | 0.0536 | 0.0568 | 0.0556 | 0.0011 | 0 | 3 | 0.0487 | 0.0587 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3205 | 9304.231 | 44264.6977 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1184.1025 | 0:240:120 | 0:00 | 0.0486 | 7 | 0.0027 | 0.054 | 0.0567 | 0.0553 | 0.0009 | 0 | 3 | 0.0486 | 0.0586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3208 | 9307.643 | 44264.6977 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1207.7846 | 0:240:120 | 0:00 | 0.0484 | 7 | 0.002 | 0.0541 | 0.0561 | 0.0553 | 0.0008 | 0 | 3 | 0.0484 | 0.0584 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3211 | 9310.955 | 44264.6978 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1231.9403 | 0:240:120 | 0:00 | 0.0483 | 7 | 0.0032 | 0.0532 | 0.0564 | 0.0551 | 0.0011 | 0 | 3 | 0.0483 | 0.0583 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3214 | 9314.642 | 44264.6978 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1256.5791 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0027 | 0.0533 | 0.056 | 0.0549 | 0.001 | 0 | 3 | 0.0482 | 0.0582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3217 | 9317.76 | 44264.6979 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1281.7107 | 0:240:120 | 0:00 | 0.048 | 7 | 0.0037 | 0.0529 | 0.0566 | 0.0549 | 0.0012 | 0 | 3 | 0.048 | 0.058 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3220 | 9321.178 | 44264.6979 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1307.3449 | 0:240:120 | 0:00 | 0.0479 | 7 | 0.0029 | 0.0526 | 0.0555 | 0.0544 | 0.0009 | 0 | 3 | 0.0479 | 0.0579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3223 | 9324.945 | 44264.6979 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1333.4918 | 0:240:120 | 0:00 | 0.0478 | 7 | 0.0044 | 0.0513 | 0.0557 | 0.0536 | 0.0015 | 0 | 3 | 0.0478 | 0.0578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3226 | 9328.624 | 44264.698 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1360.1616 | 0:240:120 | 0:00 | 0.0477 | 7 | 0.0034 | 0.052 | 0.0554 | 0.0536 | 0.0012 | 0 | 3 | 0.0477 | 0.0577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3229 | 9332.285 | 44264.698 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1387.3648 | 0:240:120 | 0:00 | 0.0476 | 7 | 0.0031 | 0.052 | 0.0551 | 0.0537 | 0.001 | 0 | 3 | 0.0476 | 0.0576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3232 | 9335.719 | 44264.6981 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1415.1121 | 0:240:120 | 0:00 | 0.0475 | 7 | 0.0035 | 0.0517 | 0.0552 | 0.0532 | 0.0012 | 0 | 3 | 0.0475 | 0.0575 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3235 | 9339.231 | 44264.6981 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1443.4144 | 0:240:120 | 0:00 | 0.0474 | 7 | 0.0029 | 0.0513 | 0.0542 | 0.0531 | 0.001 | 0 | 3 | 0.0474 | 0.0574 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3238 | 9342.676 | 44264.6981 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1472.2827 | 0:240:120 | 0:00 | 0.0473 | 7 | 0.0017 | 0.0519 | 0.0536 | 0.053 | 0.0006 | 0 | 3 | 0.0473 | 0.0573 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3241 | 9346.11 | 44264.6982 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1501.7283 | 0:240:120 | 0:00 | 0.0472 | 7 | 0.0034 | 0.0513 | 0.0547 | 0.0528 | 0.0011 | 0 | 3 | 0.0472 | 0.0572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3244 | 9349.566 | 44264.6982 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1531.7629 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.003 | 0.0518 | 0.0548 | 0.0532 | 0.0011 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3247 | 9353.134 | 44264.6983 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1562.3982 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0028 | 0.0517 | 0.0545 | 0.053 | 0.001 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3250 | 9356.564 | 44264.6983 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1593.6461 | 0:240:120 | 0:00 | 0.047 | 7 | 0.0036 | 0.0505 | 0.0541 | 0.0524 | 0.0013 | 0 | 3 | 0.047 | 0.057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3253 | 9360.128 | 44264.6983 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1625.519 | 0:240:120 | 0:00 | 0.0469 | 7 | 0.0034 | 0.051 | 0.0544 | 0.0528 | 0.0012 | 0 | 3 | 0.0469 | 0.0569 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3256 | 9363.566 | 44264.6984 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1658.0294 | 0:240:120 | 0:00 | 0.0468 | 7 | 0.0028 | 0.0516 | 0.0544 | 0.0529 | 0.0011 | 0 | 3 | 0.0468 | 0.0568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3259 | 9367.013 | 44264.6984 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1691.19 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0025 | 0.051 | 0.0535 | 0.0525 | 0.0008 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3262 | 9370.332 | 44264.6985 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1725.0138 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0028 | 0.0514 | 0.0542 | 0.0526 | 0.0009 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3265 | 9373.771 | 44264.6985 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1759.5141 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.004 | 0.0505 | 0.0545 | 0.0528 | 0.0012 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3268 | 9377.097 | 44264.6985 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1794.7044 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.0027 | 0.051 | 0.0537 | 0.0524 | 0.001 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3271 | 9380.751 | 44264.6986 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1830.5985 | 0:240:120 | 0:00 | 0.0465 | 7 | 0.0032 | 0.0512 | 0.0544 | 0.0523 | 0.0011 | 0 | 3 | 0.0465 | 0.0565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3274 | 9384.176 | 44264.6986 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1867.2104 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0021 | 0.0511 | 0.0532 | 0.0521 | 0.0007 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3277 | 9387.854 | 44264.6987 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1904.5546 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0033 | 0.0503 | 0.0536 | 0.0521 | 0.0011 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3280 | 9391.321 | 44264.6987 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1942.6457 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.003 | 0.0506 | 0.0536 | 0.0521 | 0.0011 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3283 | 9394.765 | 44264.6987 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1981.4986 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0026 | 0.0507 | 0.0533 | 0.052 | 0.0008 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3286 | 9398.194 | 44264.6988 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2021.1286 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0022 | 0.0508 | 0.053 | 0.0519 | 0.0007 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3289 | 9401.855 | 44264.6988 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2061.5512 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0014 | 0.0507 | 0.0521 | 0.0516 | 0.0006 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3292 | 9405.275 | 44264.6989 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2102.7822 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0033 | 0.0501 | 0.0534 | 0.0517 | 0.0011 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3295 | 9408.639 | 44264.6989 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2144.8379 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0031 | 0.0505 | 0.0536 | 0.0518 | 0.0012 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3298 | 9412.005 | 44264.6989 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2187.7346 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0028 | 0.05 | 0.0528 | 0.0516 | 0.0008 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3301 | 9415.269 | 44264.699 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2231.4893 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0027 | 0.0503 | 0.053 | 0.0517 | 0.001 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3304 | 9418.588 | 44264.699 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2276.1191 | 0:240:120 | 0:00 | 0.046 | 7 | 0.003 | 0.0499 | 0.0529 | 0.0514 | 0.0011 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3307 | 9421.895 | 44264.6991 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2321.6415 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0024 | 0.0505 | 0.0529 | 0.0516 | 0.0009 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3310 | 9425.231 | 44264.6991 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2368.0743 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0038 | 0.0498 | 0.0536 | 0.0514 | 0.0013 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3313 | 9428.668 | 44264.6991 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2415.4358 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0015 | 0.0507 | 0.0522 | 0.0514 | 0.0006 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3316 | 9432.204 | 44264.6992 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2463.7445 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0038 | 0.0491 | 0.0529 | 0.0511 | 0.0012 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3319 | 9435.532 | 44264.6992 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2513.0194 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0041 | 0.0495 | 0.0536 | 0.0514 | 0.0013 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3322 | 9438.982 | 44264.6993 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2563.2798 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0034 | 0.05 | 0.0534 | 0.0513 | 0.0011 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3325 | 9442.285 | 44264.6993 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2614.5454 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0027 | 0.0502 | 0.0529 | 0.0513 | 0.0008 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3328 | 9445.62 | 44264.6993 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2666.8363 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0038 | 0.049 | 0.0528 | 0.051 | 0.0012 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3331 | 9449.081 | 44264.6994 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2720.173 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0033 | 0.0495 | 0.0528 | 0.0511 | 0.0012 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3334 | 9452.519 | 44264.6994 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2774.5765 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0031 | 0.0492 | 0.0523 | 0.0508 | 0.0012 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3337 | 9455.957 | 44264.6995 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2830.068 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0029 | 0.049 | 0.0519 | 0.0505 | 0.001 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3340 | 9459.38 | 44264.6995 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2886.6694 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0033 | 0.0492 | 0.0525 | 0.0507 | 0.001 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3343 | 9462.937 | 44264.6995 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2944.4027 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0042 | 0.0485 | 0.0527 | 0.0505 | 0.0014 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3346 | 9466.398 | 44264.6996 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3003.2908 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.005 | 0.0486 | 0.0536 | 0.0508 | 0.0017 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3349 | 9469.738 | 44264.6996 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3063.3566 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0027 | 0.0491 | 0.0518 | 0.0505 | 0.001 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3352 | 9473.072 | 44264.6997 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3124.6237 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0026 | 0.0486 | 0.0512 | 0.0502 | 0.0008 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3355 | 9476.412 | 44264.6997 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3187.1162 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0034 | 0.0489 | 0.0523 | 0.0506 | 0.0011 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3358 | 9479.819 | 44264.6997 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3250.8585 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0017 | 0.0496 | 0.0513 | 0.0504 | 0.0006 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3361 | 9483.148 | 44264.6998 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3315.8757 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0025 | 0.0489 | 0.0514 | 0.0501 | 0.001 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3364 | 9486.471 | 44264.6998 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3382.1932 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0041 | 0.0481 | 0.0522 | 0.0501 | 0.0015 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3367 | 9490.137 | 44264.6999 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3449.8371 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.003 | 0.0488 | 0.0518 | 0.0503 | 0.001 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3370 | 9493.44 | 44264.6999 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3518.8338 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0029 | 0.0485 | 0.0514 | 0.0501 | 0.001 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3373 | 9496.905 | 44264.6999 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3589.2105 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0041 | 0.0482 | 0.0523 | 0.05 | 0.0014 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3376 | 9500.483 | 44264.7 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3660.9947 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.004 | 0.0485 | 0.0525 | 0.05 | 0.0013 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3379 | 9503.891 | 44264.7 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3734.2146 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0041 | 0.0484 | 0.0525 | 0.0503 | 0.0015 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3382 | 9507.217 | 44264.7 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3808.8989 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0037 | 0.0485 | 0.0522 | 0.0501 | 0.0012 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3385 | 9510.753 | 44264.7001 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3885.0769 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0032 | 0.0484 | 0.0516 | 0.0501 | 0.0011 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3388 | 9514.047 | 44264.7001 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3962.7784 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0038 | 0.0482 | 0.052 | 0.0499 | 0.0013 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3391 | 9517.494 | 44264.7002 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4042.034 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0032 | 0.0491 | 0.0523 | 0.0503 | 0.0012 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3394 | 9520.937 | 44264.7002 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4122.8747 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0042 | 0.0484 | 0.0526 | 0.0502 | 0.0016 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3397 | 9524.378 | 44264.7002 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4205.3322 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0042 | 0.0481 | 0.0523 | 0.0498 | 0.0014 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3400 | 9527.842 | 44264.7003 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4289.4388 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0024 | 0.049 | 0.0514 | 0.05 | 0.0009 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3403 | 9531.162 | 44264.7003 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4375.2276 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0041 | 0.0484 | 0.0525 | 0.05 | 0.0013 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3406 | 9534.827 | 44264.7004 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4462.7321 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0042 | 0.048 | 0.0522 | 0.0502 | 0.0014 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3409 | 9538.266 | 44264.7004 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4551.9868 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0036 | 0.0483 | 0.0519 | 0.05 | 0.0013 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3412 | 9541.932 | 44264.7005 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4643.0265 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0027 | 0.0482 | 0.0509 | 0.0496 | 0.001 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3415 | 9545.718 | 44264.7005 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4735.887 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0023 | 0.0488 | 0.0511 | 0.05 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3418 | 9549.059 | 44264.7005 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4830.6048 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0045 | 0.048 | 0.0525 | 0.05 | 0.0018 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3421 | 9552.477 | 44264.7006 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4927.2169 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0038 | 0.0477 | 0.0515 | 0.0497 | 0.0011 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3424 | 9555.811 | 44264.7006 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5025.7612 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0034 | 0.0483 | 0.0517 | 0.0498 | 0.0012 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3427 | 9559.193 | 44264.7006 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5126.2764 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0035 | 0.0478 | 0.0513 | 0.0495 | 0.0012 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3430 | 9562.63 | 44264.7007 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5228.802 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0047 | 0.0477 | 0.0524 | 0.0498 | 0.0015 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3433 | 9565.967 | 44264.7007 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5333.378 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0031 | 0.0486 | 0.0517 | 0.05 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3436 | 9569.512 | 44264.7008 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5440.0456 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.003 | 0.0481 | 0.0511 | 0.0498 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3439 | 9572.828 | 44264.7008 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5548.8465 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0034 | 0.0482 | 0.0516 | 0.0497 | 0.0011 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3442 | 9576.27 | 44264.7008 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5659.8234 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0029 | 0.0487 | 0.0516 | 0.0499 | 0.0011 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3445 | 9579.582 | 44264.7009 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5773.0199 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0046 | 0.0479 | 0.0525 | 0.0497 | 0.0015 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3448 | 9583.216 | 44264.7009 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5888.4803 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0032 | 0.0482 | 0.0514 | 0.0498 | 0.0012 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3451 | 9586.788 | 44264.701 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6006.2499 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0026 | 0.0483 | 0.0509 | 0.0494 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3454 | 9590.179 | 44264.701 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6126.3749 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0029 | 0.0476 | 0.0505 | 0.0491 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3457 | 9593.611 | 44264.701 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6248.9024 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0041 | 0.0484 | 0.0525 | 0.0498 | 0.0013 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3460 | 9596.91 | 44264.7011 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6373.8804 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.003 | 0.0478 | 0.0508 | 0.0492 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3463 | 9600.344 | 44264.7011 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6501.358 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0029 | 0.0477 | 0.0506 | 0.0494 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3466 | 9603.685 | 44264.7012 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6631.3852 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0035 | 0.0475 | 0.051 | 0.0493 | 0.0012 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3469 | 9607.008 | 44264.7012 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6764.0129 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0031 | 0.0476 | 0.0507 | 0.0492 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3472 | 9610.447 | 44264.7012 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6899.2932 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0014 | 0.0491 | 0.0505 | 0.0498 | 0.0006 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3475 | 9613.892 | 44264.7013 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7037.279 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.0486 | 0.051 | 0.0496 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3478 | 9617.225 | 44264.7013 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7178.0246 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0021 | 0.0487 | 0.0508 | 0.0496 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3481 | 9620.764 | 44264.7014 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7321.5851 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.003 | 0.0478 | 0.0508 | 0.0493 | 0.0012 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3484 | 9624.438 | 44264.7014 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7468.0168 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0022 | 0.048 | 0.0502 | 0.0495 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3487 | 9627.779 | 44264.7014 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7617.3771 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.0478 | 0.0502 | 0.0491 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3490 | 9631.448 | 44264.7015 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7769.7247 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.003 | 0.0484 | 0.0514 | 0.0498 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3493 | 9634.895 | 44264.7015 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7925.1192 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.0486 | 0.0509 | 0.0494 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3496 | 9638.283 | 44264.7016 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8083.6216 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0037 | 0.0472 | 0.0509 | 0.0491 | 0.0011 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3499 | 9641.529 | 44264.7016 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8245.294 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.003 | 0.0474 | 0.0504 | 0.0487 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3502 | 9645.083 | 44264.7016 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8410.1999 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0035 | 0.0477 | 0.0512 | 0.0493 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3505 | 9648.435 | 44264.7017 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8578.4039 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0022 | 0.0481 | 0.0503 | 0.0494 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3508 | 9651.874 | 44264.7017 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8749.9719 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0017 | 0.0479 | 0.0496 | 0.0488 | 0.0006 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3511 | 9655.179 | 44264.7018 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8924.9714 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0016 | 0.0478 | 0.0494 | 0.0486 | 0.0006 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3514 | 9658.411 | 44264.7018 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9103.4708 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0037 | 0.0475 | 0.0512 | 0.0489 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3517 | 9661.656 | 44264.7018 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9285.5402 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0029 | 0.0475 | 0.0504 | 0.0489 | 0.0012 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3520 | 9665.282 | 44264.7019 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9471.251 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0017 | 0.048 | 0.0497 | 0.0489 | 0.0006 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3523 | 9668.952 | 44264.7019 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9660.6761 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.0475 | 0.05 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3526 | 9672.21 | 44264.702 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9853.8896 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.0477 | 0.0501 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3529 | 9675.526 | 44264.702 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10050.9674 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0021 | 0.0479 | 0.05 | 0.0491 | 0.0007 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3532 | 9678.943 | 44264.702 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10251.9867 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0029 | 0.0474 | 0.0503 | 0.0487 | 0.0009 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3535 | 9682.272 | 44264.7021 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10457.0264 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0025 | 0.0472 | 0.0497 | 0.0488 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3538 | 9685.673 | 44264.7021 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10666.167 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0023 | 0.0478 | 0.0501 | 0.0493 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3541 | 9689.012 | 44264.7022 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10879.4903 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0023 | 0.0475 | 0.0498 | 0.0483 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3544 | 9692.456 | 44264.7022 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11097.0801 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0019 | 0.0479 | 0.0498 | 0.0488 | 0.0006 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3547 | 9696.028 | 44264.7022 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11319.0217 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0029 | 0.0469 | 0.0498 | 0.0485 | 0.001 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3550 | 9699.619 | 44264.7023 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11545.4022 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0022 | 0.0477 | 0.0499 | 0.0488 | 0.0009 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3553 | 9703.274 | 44264.7023 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11776.3102 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0022 | 0.0478 | 0.05 | 0.0488 | 0.0008 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3556 | 9754.795 | 44264.7029 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.8 | 0:240:120 | 0:00 | 5.9914 | 7 | 16.1589 | 36.5804 | 52.7393 | 41.5071 | 7.1397 | 50.976 | 3 | 5.9914 | 24.3074 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3559 | 9891.963 | 44264.7045 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59 | 0:240:120 | 0:00 | 5.1418 | 7 | 12.4304 | 18.5856 | 31.016 | 22.5803 | 5.9666 | 35.5998 | 3 | 5.1418 | 15.6891 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3562 | 9969.811 | 44264.7054 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.1 | 0:240:120 | 0:00 | 4.5414 | 7 | 4.2464 | 9.0916 | 13.338 | 10.4515 | 2.0385 | 4.1553 | 3 | 4.5414 | 11.7896 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3565 | 10007.881 | 44264.7058 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.3 | 0:240:120 | 0:00 | 4.0205 | 7 | 0.56 | 8.0887 | 8.6487 | 8.2758 | 0.275 | 0.0756 | 3 | 4.0205 | 9.2408 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3568 | 10036.261 | 44264.7062 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.6 | 0:240:120 | 0:00 | 3.5692 | 7 | 0.9712 | 6.6257 | 7.5969 | 7.0553 | 0.4169 | 0.1738 | 3 | 3.5692 | 7.4612 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3571 | 10061.077 | 44264.7065 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.8 | 0:240:120 | 0:00 | 3.2288 | 7 | 0.99 | 5.6064 | 6.5964 | 5.9787 | 0.4648 | 0.216 | 3 | 3.2288 | 6.3181 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3574 | 10082.548 | 44264.7067 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.1 | 0:240:120 | 0:00 | 2.9219 | 7 | 0.6223 | 4.6052 | 5.2275 | 4.8105 | 0.3058 | 0.0935 | 3 | 2.9219 | 5.4053 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3577 | 10100.6 | 44264.7069 | Vista Coord | Main | 50Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.4 | 0:240:120 | 0:00 | 2.6642 | 7 | 0.3182 | 4.1269 | 4.4451 | 4.2762 | 0.1325 | 0.0176 | 3 | 2.6642 | 4.7124 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3580 | 10213.319 | 44264.7082 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.5 | 0:240:120 | 0:00 | 9.5688 | 7 | 11.8968 | 87.6798 | 99.5766 | 92.8987 | 5.095 | 25.9586 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3583 | 10497.683 | 44264.7115 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.93 | 0:240:120 | 0:00 | 7.7705 | 7 | 10.6946 | 70.884 | 81.5786 | 75.1343 | 4.8546 | 23.5667 | 3 | 7.7705 | 101.5883 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3586 | 10727.425 | 44264.7142 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.3886 | 0:240:120 | 0:00 | 6.502 | 7 | 10.335 | 53.2463 | 63.5813 | 56.9783 | 4.9599 | 24.6007 | 3 | 6.502 | 32.8902 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3589 | 10903.157 | 44264.7162 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.8764 | 0:240:120 | 0:00 | 5.5599 | 7 | 13.4965 | 32.0777 | 45.5742 | 37.3366 | 6.2032 | 38.4793 | 3 | 5.5599 | 19.3218 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3592 | 11024.713 | 44264.7176 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.3939 | 0:240:120 | 0:00 | 4.833 | 7 | 17.7366 | 9.6696 | 27.4062 | 15.9088 | 8.6009 | 73.9758 | 3 | 4.833 | 13.5272 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3595 | 11092.093 | 44264.7184 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.9418 | 0:240:120 | 0:00 | 4.2557 | 7 | 0.8143 | 8.5937 | 9.408 | 8.855 | 0.39 | 0.1521 | 3 | 4.2557 | 10.3153 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3598 | 11122.254 | 44264.7187 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.5206 | 0:240:120 | 0:00 | 3.7863 | 7 | 0.5142 | 7.5932 | 8.1074 | 7.764 | 0.253 | 0.064 | 3 | 3.7863 | 8.2753 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3601 | 11148.701 | 44264.719 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.131 | 0:240:120 | 0:00 | 3.3975 | 7 | 0.6772 | 6.4231 | 7.1003 | 6.7202 | 0.2906 | 0.0844 | 3 | 3.3975 | 6.8658 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3604 | 11171.978 | 44264.7193 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.7736 | 0:240:120 | 0:00 | 3.0704 | 7 | 0.9838 | 5.1088 | 6.0926 | 5.4578 | 0.4758 | 0.2264 | 3 | 3.0704 | 5.8343 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3607 | 11192.024 | 44264.7195 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.4491 | 0:240:120 | 0:00 | 2.7916 | 7 | 0.2478 | 4.4415 | 4.6893 | 4.5204 | 0.1158 | 0.0134 | 3 | 2.7916 | 5.0472 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3610 | 11208.658 | 44264.7197 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.1581 | 0:240:120 | 0:00 | 2.5513 | 7 | 0.2984 | 3.9817 | 4.2801 | 4.125 | 0.1215 | 0.0148 | 3 | 2.5513 | 4.4273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3613 | 11224.28 | 44264.7199 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.9013 | 0:240:120 | 0:00 | 2.3422 | 7 | 0.2798 | 3.6182 | 3.898 | 3.7077 | 0.1317 | 0.0173 | 3 | 2.3422 | 3.9269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3616 | 11238.632 | 44264.7201 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.6793 | 0:240:120 | 0:00 | 2.1587 | 7 | 0.2834 | 3.1729 | 3.4563 | 3.297 | 0.1235 | 0.0153 | 3 | 2.1587 | 3.5146 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3619 | 11251.667 | 44264.7202 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.4929 | 0:240:120 | 0:00 | 1.9965 | 7 | 0.1457 | 2.8781 | 3.0238 | 2.9271 | 0.0714 | 0.0051 | 3 | 1.9965 | 3.1694 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3622 | 11263.637 | 44264.7204 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.3427 | 0:240:120 | 0:00 | 1.8523 | 7 | 0.1638 | 2.6344 | 2.7982 | 2.6975 | 0.0762 | 0.0058 | 3 | 1.8523 | 2.8763 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3625 | 11274.954 | 44264.7205 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.2296 | 0:240:120 | 0:00 | 1.7232 | 7 | 0.1094 | 2.4448 | 2.5542 | 2.4897 | 0.0488 | 0.0024 | 3 | 1.7232 | 2.6246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3628 | 11285.804 | 44264.7206 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.1542 | 0:240:120 | 0:00 | 1.6071 | 7 | 0.1378 | 2.2247 | 2.3625 | 2.27 | 0.0665 | 0.0044 | 3 | 1.6071 | 2.4062 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3631 | 11295.839 | 44264.7207 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.1173 | 0:240:120 | 0:00 | 1.5023 | 7 | 0.0978 | 2.0475 | 2.1453 | 2.0804 | 0.048 | 0.0023 | 3 | 1.5023 | 2.215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3634 | 11305.134 | 44264.7209 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.1196 | 0:240:120 | 0:00 | 1.4072 | 7 | 0.0974 | 1.9034 | 2.0008 | 1.9396 | 0.0459 | 0.0021 | 3 | 1.4072 | 2.0464 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3637 | 11314.442 | 44264.721 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.162 | 0:240:120 | 0:00 | 1.3205 | 7 | 0.0969 | 1.7598 | 1.8567 | 1.7996 | 0.0429 | 0.0018 | 3 | 1.3205 | 1.8967 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3640 | 11323.016 | 44264.7211 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.2452 | 0:240:120 | 0:00 | 1.2414 | 7 | 0.079 | 1.6314 | 1.7104 | 1.6659 | 0.0343 | 0.0012 | 3 | 1.2414 | 1.7631 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3643 | 11331.078 | 44264.7212 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 108.3701 | 0:240:120 | 0:00 | 1.1688 | 7 | 0.0628 | 1.5354 | 1.5982 | 1.5643 | 0.027 | 0.0007 | 3 | 1.1688 | 1.643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3646 | 11338.913 | 44264.7212 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.5375 | 0:240:120 | 0:00 | 1.1021 | 7 | 0.0629 | 1.4388 | 1.5017 | 1.4658 | 0.0279 | 0.0008 | 3 | 1.1021 | 1.5348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3649 | 11346.355 | 44264.7213 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.7483 | 0:240:120 | 0:00 | 1.0406 | 7 | 0.0654 | 1.3418 | 1.4072 | 1.3669 | 0.0299 | 0.0009 | 3 | 1.0406 | 1.4367 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3652 | 11353.741 | 44264.7214 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 115.0033 | 0:240:120 | 0:00 | 0.9838 | 7 | 0.0458 | 1.2745 | 1.3203 | 1.2906 | 0.022 | 0.0005 | 3 | 0.9838 | 1.3474 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3655 | 11360.736 | 44264.7215 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.3033 | 0:240:120 | 0:00 | 0.9312 | 7 | 0.0438 | 1.2055 | 1.2493 | 1.2208 | 0.021 | 0.0004 | 3 | 0.9312 | 1.266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3658 | 11367.408 | 44264.7216 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.6494 | 0:240:120 | 0:00 | 0.8824 | 7 | 0.0451 | 1.1196 | 1.1647 | 1.1409 | 0.019 | 0.0004 | 3 | 0.8824 | 1.1914 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3661 | 11373.847 | 44264.7217 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 122.0424 | 0:240:120 | 0:00 | 0.837 | 7 | 0.0354 | 1.0675 | 1.1029 | 1.0799 | 0.0167 | 0.0003 | 3 | 0.837 | 1.1229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3664 | 11380.065 | 44264.7217 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.4832 | 0:240:120 | 0:00 | 0.7947 | 7 | 0.0298 | 1.0142 | 1.044 | 1.0253 | 0.0139 | 0.0002 | 3 | 0.7947 | 1.0598 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3667 | 11386.064 | 44264.7218 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.9729 | 0:240:120 | 0:00 | 0.7553 | 7 | 0.0346 | 0.9517 | 0.9863 | 0.9641 | 0.0165 | 0.0003 | 3 | 0.7553 | 1.0015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3670 | 11392.025 | 44264.7219 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 129.5124 | 0:240:120 | 0:00 | 0.7184 | 7 | 0.0252 | 0.9067 | 0.9319 | 0.9176 | 0.0104 | 0.0001 | 3 | 0.7184 | 0.9476 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3673 | 11398.127 | 44264.7219 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 132.1026 | 0:240:120 | 0:00 | 0.6839 | 7 | 0.0268 | 0.8629 | 0.8897 | 0.8727 | 0.0126 | 0.0002 | 3 | 0.6839 | 0.8976 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3676 | 11403.715 | 44264.722 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.7447 | 0:240:120 | 0:00 | 0.6516 | 7 | 0.0233 | 0.8153 | 0.8386 | 0.8241 | 0.0107 | 0.0001 | 3 | 0.6516 | 0.8512 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3679 | 11409.183 | 44264.7221 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.4395 | 0:240:120 | 0:00 | 0.6212 | 7 | 0.0204 | 0.7771 | 0.7975 | 0.7852 | 0.0092 | 0.0001 | 3 | 0.6212 | 0.8079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3682 | 11414.686 | 44264.7221 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 140.1883 | 0:240:120 | 0:00 | 0.5927 | 7 | 0.0215 | 0.7372 | 0.7587 | 0.7466 | 0.0092 | 0.0001 | 3 | 0.5927 | 0.7676 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3685 | 11419.983 | 44264.7222 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.9921 | 0:240:120 | 0:00 | 0.5659 | 7 | 0.0187 | 0.703 | 0.7217 | 0.711 | 0.0079 | 0.0001 | 3 | 0.5659 | 0.7299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3688 | 11425.531 | 44264.7223 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 145.8519 | 0:240:120 | 0:00 | 0.5407 | 7 | 0.0188 | 0.671 | 0.6898 | 0.6789 | 0.0081 | 0.0001 | 3 | 0.5407 | 0.6947 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3691 | 11430.667 | 44264.7223 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.769 | 0:240:120 | 0:00 | 0.5169 | 7 | 0.015 | 0.6405 | 0.6555 | 0.6462 | 0.0066 | 0 | 3 | 0.5169 | 0.6617 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3694 | 11435.523 | 44264.7224 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 151.7444 | 0:240:120 | 0:00 | 0.4944 | 7 | 0.0153 | 0.6123 | 0.6276 | 0.6182 | 0.0068 | 0 | 3 | 0.4944 | 0.6307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3697 | 11440.725 | 44264.7224 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 154.7793 | 0:240:120 | 0:00 | 0.4732 | 7 | 0.0148 | 0.5849 | 0.5997 | 0.591 | 0.0064 | 0 | 3 | 0.4732 | 0.6017 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3700 | 11445.645 | 44264.7225 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 157.8748 | 0:240:120 | 0:00 | 0.4532 | 7 | 0.0153 | 0.5587 | 0.574 | 0.5648 | 0.0065 | 0 | 3 | 0.4532 | 0.5743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3703 | 11450.585 | 44264.7225 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 161.0323 | 0:240:120 | 0:00 | 0.4343 | 7 | 0.013 | 0.5344 | 0.5474 | 0.5396 | 0.0056 | 0 | 3 | 0.4343 | 0.5486 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3706 | 11455.56 | 44264.7226 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.253 | 0:240:120 | 0:00 | 0.4164 | 7 | 0.0115 | 0.513 | 0.5245 | 0.5168 | 0.0049 | 0 | 3 | 0.4164 | 0.5244 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3709 | 11460.286 | 44264.7227 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 167.538 | 0:240:120 | 0:00 | 0.3994 | 7 | 0.012 | 0.49 | 0.502 | 0.4951 | 0.005 | 0 | 3 | 0.3994 | 0.5015 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3712 | 11464.862 | 44264.7227 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.8888 | 0:240:120 | 0:00 | 0.3833 | 7 | 0.0093 | 0.4697 | 0.479 | 0.4739 | 0.0037 | 0 | 3 | 0.3833 | 0.4799 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3715 | 11469.347 | 44264.7228 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 174.3066 | 0:240:120 | 0:00 | 0.368 | 7 | 0.0096 | 0.4511 | 0.4607 | 0.4548 | 0.0039 | 0 | 3 | 0.368 | 0.4595 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3718 | 11473.837 | 44264.7228 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 177.7927 | 0:240:120 | 0:00 | 0.3536 | 7 | 0.0076 | 0.4344 | 0.442 | 0.4369 | 0.0033 | 0 | 3 | 0.3536 | 0.4402 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3721 | 11478.236 | 44264.7229 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 181.3486 | 0:240:120 | 0:00 | 0.3398 | 7 | 0.0065 | 0.4171 | 0.4236 | 0.4193 | 0.0031 | 0 | 3 | 0.3398 | 0.422 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3724 | 11483.19 | 44264.7229 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 184.9755 | 0:240:120 | 0:00 | 0.3268 | 7 | 0.0052 | 0.4008 | 0.406 | 0.4026 | 0.0022 | 0 | 3 | 0.3268 | 0.4047 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3727 | 11487.589 | 44264.723 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 188.675 | 0:240:120 | 0:00 | 0.3143 | 7 | 0.0089 | 0.383 | 0.3919 | 0.3871 | 0.0036 | 0 | 3 | 0.3143 | 0.3884 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3730 | 11491.975 | 44264.723 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 192.4485 | 0:240:120 | 0:00 | 0.3025 | 7 | 0.0075 | 0.3691 | 0.3766 | 0.3724 | 0.003 | 0 | 3 | 0.3025 | 0.3728 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3733 | 11496.135 | 44264.7231 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 196.2975 | 0:240:120 | 0:00 | 0.2913 | 7 | 0.0062 | 0.3554 | 0.3616 | 0.3582 | 0.0022 | 0 | 3 | 0.2913 | 0.3581 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3736 | 11500.215 | 44264.7231 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 200.2235 | 0:240:120 | 0:00 | 0.2806 | 7 | 0.0063 | 0.3426 | 0.3489 | 0.3451 | 0.0027 | 0 | 3 | 0.2806 | 0.3441 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3739 | 11504.423 | 44264.7232 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 204.2279 | 0:240:120 | 0:00 | 0.2704 | 7 | 0.0066 | 0.3294 | 0.336 | 0.3324 | 0.0027 | 0 | 3 | 0.2704 | 0.3309 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3742 | 11508.451 | 44264.7232 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.3125 | 0:240:120 | 0:00 | 0.2607 | 7 | 0.0043 | 0.318 | 0.3223 | 0.3197 | 0.0018 | 0 | 3 | 0.2607 | 0.3182 | NP | NP | 0-0-0-0-0-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3745 | 11512.325 | 44264.7233 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 212.4787 | 0:240:120 | 0:00 | 0.2515 | 7 | 0.005 | 0.3057 | 0.3107 | 0.3081 | 0.0018 | 0 | 3 | 0.2515 | 0.3063 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3748 | 11516.087 | 44264.7233 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 216.7283 | 0:240:120 | 0:00 | 0.2427 | 7 | 0.0046 | 0.296 | 0.3006 | 0.2978 | 0.0019 | 0 | 3 | 0.2427 | 0.2948 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3751 | 11520.179 | 44264.7233 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 221.0629 | 0:240:120 | 0:00 | 0.2343 | 7 | 0.0047 | 0.2846 | 0.2893 | 0.2869 | 0.0018 | 0 | 3 | 0.2343 | 0.284 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3754 | 11524.274 | 44264.7234 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 225.4841 | 0:240:120 | 0:00 | 0.2263 | 7 | 0.006 | 0.2738 | 0.2798 | 0.2767 | 0.0021 | 0 | 3 | 0.2263 | 0.2736 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3757 | 11528.312 | 44264.7234 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 229.9938 | 0:240:120 | 0:00 | 0.2186 | 7 | 0.0046 | 0.2656 | 0.2702 | 0.2676 | 0.002 | 0 | 3 | 0.2186 | 0.2638 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3760 | 11532.528 | 44264.7235 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.5937 | 0:240:120 | 0:00 | 0.2113 | 7 | 0.0043 | 0.2565 | 0.2608 | 0.2584 | 0.0017 | 0 | 3 | 0.2113 | 0.2544 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3763 | 11536.857 | 44264.7235 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 239.2856 | 0:240:120 | 0:00 | 0.2043 | 7 | 0.0052 | 0.2479 | 0.2531 | 0.2499 | 0.0021 | 0 | 3 | 0.2043 | 0.2455 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3766 | 11540.626 | 44264.7236 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 244.0713 | 0:240:120 | 0:00 | 0.1977 | 7 | 0.0038 | 0.2402 | 0.244 | 0.2419 | 0.0015 | 0 | 3 | 0.1977 | 0.2372 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3769 | 11544.804 | 44264.7236 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 248.9527 | 0:240:120 | 0:00 | 0.1913 | 7 | 0.0038 | 0.2319 | 0.2357 | 0.234 | 0.0014 | 0 | 3 | 0.1913 | 0.2296 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3772 | 11548.564 | 44264.7237 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 253.9318 | 0:240:120 | 0:00 | 0.1852 | 7 | 0.0036 | 0.225 | 0.2286 | 0.2269 | 0.0013 | 0 | 3 | 0.1852 | 0.2223 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3775 | 11552.261 | 44264.7237 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 259.0104 | 0:240:120 | 0:00 | 0.1794 | 7 | 0.0041 | 0.218 | 0.2221 | 0.2198 | 0.0015 | 0 | 3 | 0.1794 | 0.2153 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3778 | 11556.074 | 44264.7238 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 264.1906 | 0:240:120 | 0:00 | 0.1739 | 7 | 0.0028 | 0.2119 | 0.2147 | 0.2134 | 0.0011 | 0 | 3 | 0.1739 | 0.2086 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3781 | 11559.932 | 44264.7238 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 269.4744 | 0:240:120 | 0:00 | 0.1686 | 7 | 0.0033 | 0.2046 | 0.2079 | 0.2065 | 0.0011 | 0 | 3 | 0.1686 | 0.2023 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3784 | 11563.489 | 44264.7238 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 274.8639 | 0:240:120 | 0:00 | 0.1635 | 7 | 0.0032 | 0.1985 | 0.2017 | 0.2 | 0.0011 | 0 | 3 | 0.1635 | 0.1962 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3787 | 11567.153 | 44264.7239 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 280.3612 | 0:240:120 | 0:00 | 0.1586 | 7 | 0.0032 | 0.1929 | 0.1961 | 0.1941 | 0.0012 | 0 | 3 | 0.1586 | 0.1903 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3790 | 11570.549 | 44264.7239 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 285.9684 | 0:240:120 | 0:00 | 0.154 | 7 | 0.004 | 0.1865 | 0.1905 | 0.1881 | 0.0014 | 0 | 3 | 0.154 | 0.1847 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3793 | 11574.274 | 44264.724 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 291.6878 | 0:240:120 | 0:00 | 0.1495 | 7 | 0.0029 | 0.1817 | 0.1846 | 0.1833 | 0.0011 | 0 | 3 | 0.1495 | 0.1794 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3796 | 11578.027 | 44264.724 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 297.5215 | 0:240:120 | 0:00 | 0.1452 | 7 | 0.0039 | 0.1753 | 0.1792 | 0.1776 | 0.0014 | 0 | 3 | 0.1452 | 0.1743 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3799 | 11581.61 | 44264.7241 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 303.472 | 0:240:120 | 0:00 | 0.1412 | 7 | 0.0022 | 0.1716 | 0.1738 | 0.1726 | 0.0007 | 0 | 3 | 0.1412 | 0.1694 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3802 | 11585.191 | 44264.7241 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 309.5414 | 0:240:120 | 0:00 | 0.1373 | 7 | 0.003 | 0.1663 | 0.1693 | 0.1677 | 0.0011 | 0 | 3 | 0.1373 | 0.1647 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3805 | 11588.808 | 44264.7241 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 315.7322 | 0:240:120 | 0:00 | 0.1335 | 7 | 0.0028 | 0.1618 | 0.1646 | 0.1633 | 0.0011 | 0 | 3 | 0.1335 | 0.1602 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3808 | 11592.604 | 44264.7242 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 322.0469 | 0:240:120 | 0:00 | 0.1299 | 7 | 0.0039 | 0.1569 | 0.1608 | 0.1589 | 0.0016 | 0 | 3 | 0.1299 | 0.1559 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3811 | 11596.176 | 44264.7242 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 328.4878 | 0:240:120 | 0:00 | 0.1265 | 7 | 0.0036 | 0.1533 | 0.1569 | 0.1549 | 0.0012 | 0 | 3 | 0.1265 | 0.1518 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3814 | 11599.743 | 44264.7243 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 335.0576 | 0:240:120 | 0:00 | 0.1232 | 7 | 0.0032 | 0.1491 | 0.1523 | 0.1509 | 0.0011 | 0 | 3 | 0.1232 | 0.1479 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3817 | 11603.302 | 44264.7243 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 341.7587 | 0:240:120 | 0:00 | 0.1201 | 7 | 0.0028 | 0.1458 | 0.1486 | 0.1474 | 0.0009 | 0 | 3 | 0.1201 | 0.1441 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3820 | 11606.837 | 44264.7243 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 348.5939 | 0:240:120 | 0:00 | 0.117 | 7 | 0.003 | 0.1421 | 0.1451 | 0.1433 | 0.0009 | 0 | 3 | 0.117 | 0.1405 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3823 | 11610.249 | 44264.7244 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 355.5658 | 0:240:120 | 0:00 | 0.1141 | 7 | 0.0025 | 0.138 | 0.1405 | 0.1394 | 0.0009 | 0 | 3 | 0.1141 | 0.137 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3826 | 11613.695 | 44264.7244 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 362.6771 | 0:240:120 | 0:00 | 0.1114 | 7 | 0.0016 | 0.1352 | 0.1368 | 0.1362 | 0.0006 | 0 | 3 | 0.1114 | 0.1336 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3829 | 11617.215 | 44264.7245 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 369.9306 | 0:240:120 | 0:00 | 0.1087 | 7 | 0.0017 | 0.1322 | 0.1339 | 0.1333 | 0.0007 | 0 | 3 | 0.1087 | 0.1305 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3832 | 11620.565 | 44264.7245 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 377.3292 | 0:240:120 | 0:00 | 0.1062 | 7 | 0.0026 | 0.1286 | 0.1312 | 0.1301 | 0.0009 | 0 | 3 | 0.1062 | 0.1274 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3835 | 11623.999 | 44264.7245 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 384.8758 | 0:240:120 | 0:00 | 0.1037 | 7 | 0.0024 | 0.1253 | 0.1277 | 0.127 | 0.0009 | 0 | 3 | 0.1037 | 0.1245 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3838 | 11627.549 | 44264.7246 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 392.5733 | 0:240:120 | 0:00 | 0.1014 | 7 | 0.0018 | 0.123 | 0.1248 | 0.1238 | 0.0006 | 0 | 3 | 0.1014 | 0.1217 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3841 | 11631.193 | 44264.7246 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 400.4248 | 0:240:120 | 0:00 | 0.0991 | 7 | 0.0021 | 0.1208 | 0.1229 | 0.122 | 0.0007 | 0 | 3 | 0.0991 | 0.119 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3844 | 11634.621 | 44264.7247 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 408.4333 | 0:240:120 | 0:00 | 0.097 | 7 | 0.0025 | 0.1173 | 0.1198 | 0.1186 | 0.0008 | 0 | 3 | 0.097 | 0.1164 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3847 | 11638.043 | 44264.7247 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 416.602 | 0:240:120 | 0:00 | 0.0949 | 7 | 0.0024 | 0.1146 | 0.117 | 0.1159 | 0.0009 | 0 | 3 | 0.0949 | 0.1139 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3850 | 11641.497 | 44264.7248 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 424.934 | 0:240:120 | 0:00 | 0.0929 | 7 | 0.0017 | 0.113 | 0.1147 | 0.1138 | 0.0007 | 0 | 3 | 0.0929 | 0.1115 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3853 | 11645.058 | 44264.7248 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 433.4327 | 0:240:120 | 0:00 | 0.091 | 7 | 0.0035 | 0.1095 | 0.113 | 0.1114 | 0.0012 | 0 | 3 | 0.091 | 0.1092 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3856 | 11648.717 | 44264.7248 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 442.1014 | 0:240:120 | 0:00 | 0.0892 | 7 | 0.0026 | 0.1076 | 0.1102 | 0.1089 | 0.0009 | 0 | 3 | 0.0892 | 0.107 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3859 | 11652.161 | 44264.7249 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 450.9434 | 0:240:120 | 0:00 | 0.0874 | 7 | 0.0035 | 0.1052 | 0.1087 | 0.107 | 0.0012 | 0 | 3 | 0.0874 | 0.1049 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3862 | 11655.811 | 44264.7249 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 459.9622 | 0:240:120 | 0:00 | 0.0858 | 7 | 0.0021 | 0.1032 | 0.1053 | 0.1044 | 0.0007 | 0 | 3 | 0.0858 | 0.1029 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3865 | 11659.464 | 44264.725 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 469.1615 | 0:240:120 | 0:00 | 0.0841 | 7 | 0.0033 | 0.1012 | 0.1045 | 0.1031 | 0.0012 | 0 | 3 | 0.0841 | 0.101 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3868 | 11662.91 | 44264.725 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 478.5447 | 0:240:120 | 0:00 | 0.0826 | 7 | 0.0018 | 0.0999 | 0.1017 | 0.1011 | 0.0006 | 0 | 3 | 0.0826 | 0.0991 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3871 | 11666.478 | 44264.725 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 488.1156 | 0:240:120 | 0:00 | 0.0811 | 7 | 0.0026 | 0.0978 | 0.1004 | 0.0993 | 0.0009 | 0 | 3 | 0.0811 | 0.0973 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3874 | 11669.873 | 44264.7251 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 497.8779 | 0:240:120 | 0:00 | 0.0797 | 7 | 0.0029 | 0.0961 | 0.099 | 0.0976 | 0.0011 | 0 | 3 | 0.0797 | 0.0956 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3877 | 11673.427 | 44264.7251 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 507.8355 | 0:240:120 | 0:00 | 0.0783 | 7 | 0.0024 | 0.0938 | 0.0962 | 0.0952 | 0.0009 | 0 | 3 | 0.0783 | 0.094 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3880 | 11676.965 | 44264.7252 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 517.9922 | 0:240:120 | 0:00 | 0.077 | 7 | 0.0027 | 0.0918 | 0.0945 | 0.0936 | 0.0012 | 0 | 3 | 0.077 | 0.0924 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3883 | 11680.4 | 44264.7252 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 528.352 | 0:240:120 | 0:00 | 0.0757 | 7 | 0.0033 | 0.0904 | 0.0937 | 0.0922 | 0.0012 | 0 | 3 | 0.0757 | 0.0909 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3886 | 11683.843 | 44264.7252 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 538.9191 | 0:240:120 | 0:00 | 0.0745 | 7 | 0.0015 | 0.0901 | 0.0916 | 0.0911 | 0.0006 | 0 | 3 | 0.0745 | 0.0894 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3889 | 11687.16 | 44264.7253 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 549.6975 | 0:240:120 | 0:00 | 0.0734 | 7 | 0.0011 | 0.0886 | 0.0897 | 0.0893 | 0.0005 | 0 | 3 | 0.0734 | 0.088 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3892 | 11690.573 | 44264.7253 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 560.6914 | 0:240:120 | 0:00 | 0.0722 | 7 | 0.0023 | 0.087 | 0.0893 | 0.0882 | 0.0009 | 0 | 3 | 0.0722 | 0.0867 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3895 | 11693.979 | 44264.7254 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 571.9052 | 0:240:120 | 0:00 | 0.0712 | 7 | 0.0027 | 0.0853 | 0.088 | 0.0868 | 0.001 | 0 | 3 | 0.0712 | 0.0854 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3898 | 11697.686 | 44264.7254 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 583.3433 | 0:240:120 | 0:00 | 0.0701 | 7 | 0.0034 | 0.0836 | 0.087 | 0.0857 | 0.0014 | 0 | 3 | 0.0701 | 0.0842 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3901 | 11701.007 | 44264.7254 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 595.0102 | 0:240:120 | 0:00 | 0.0692 | 7 | 0.0032 | 0.0818 | 0.085 | 0.0838 | 0.0013 | 0 | 3 | 0.0692 | 0.083 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3904 | 11704.55 | 44264.7255 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 606.9104 | 0:240:120 | 0:00 | 0.0682 | 7 | 0.002 | 0.0813 | 0.0833 | 0.0826 | 0.0007 | 0 | 3 | 0.0682 | 0.0818 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3907 | 11707.956 | 44264.7255 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 619.0486 | 0:240:120 | 0:00 | 0.0673 | 7 | 0.0025 | 0.081 | 0.0835 | 0.0821 | 0.0008 | 0 | 3 | 0.0673 | 0.0808 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3910 | 11711.513 | 44264.7256 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 631.4296 | 0:240:120 | 0:00 | 0.0664 | 7 | 0.002 | 0.0798 | 0.0818 | 0.081 | 0.0006 | 0 | 3 | 0.0664 | 0.0797 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3913 | 11715.09 | 44264.7256 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 644.0582 | 0:240:120 | 0:00 | 0.0656 | 7 | 0.0027 | 0.0778 | 0.0805 | 0.0794 | 0.001 | 0 | 3 | 0.0656 | 0.0787 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3916 | 11718.508 | 44264.7256 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 656.9394 | 0:240:120 | 0:00 | 0.0648 | 7 | 0.0029 | 0.0766 | 0.0795 | 0.0783 | 0.0013 | 0 | 3 | 0.0648 | 0.0777 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3919 | 11721.835 | 44264.7257 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 670.0781 | 0:240:120 | 0:00 | 0.064 | 7 | 0.0021 | 0.0764 | 0.0785 | 0.0774 | 0.0007 | 0 | 3 | 0.064 | 0.0768 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3922 | 11725.477 | 44264.7257 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 683.4797 | 0:240:120 | 0:00 | 0.0633 | 7 | 0.0027 | 0.0749 | 0.0776 | 0.0763 | 0.001 | 0 | 3 | 0.0633 | 0.0759 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3925 | 11728.913 | 44264.7258 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 697.1493 | 0:240:120 | 0:00 | 0.0625 | 7 | 0.003 | 0.0737 | 0.0767 | 0.0755 | 0.0011 | 0 | 3 | 0.0625 | 0.075 | NP | NP | 0-1-0-0-0-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3928 | 11732.199 | 44264.7258 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 711.0923 | 0:240:120 | 0:00 | 0.0619 | 7 | 0.0023 | 0.0733 | 0.0756 | 0.0747 | 0.001 | 0 | 3 | 0.0619 | 0.0742 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3931 | 11735.64 | 44264.7258 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 725.3141 | 0:240:120 | 0:00 | 0.0612 | 7 | 0.0027 | 0.0721 | 0.0748 | 0.0739 | 0.0013 | 0 | 3 | 0.0612 | 0.0734 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3934 | 11739.037 | 44264.7259 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 739.8204 | 0:240:120 | 0:00 | 0.0606 | 7 | 0.0024 | 0.0718 | 0.0742 | 0.0732 | 0.001 | 0 | 3 | 0.0606 | 0.0727 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3937 | 11742.498 | 44264.7259 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 754.6168 | 0:240:120 | 0:00 | 0.0599 | 7 | 0.0032 | 0.0707 | 0.0739 | 0.0722 | 0.001 | 0 | 3 | 0.0599 | 0.0719 | NP | NP | 1-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3940 | 11745.787 | 44264.726 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 769.7092 | 0:240:120 | 0:00 | 0.0594 | 7 | 0.0029 | 0.0698 | 0.0727 | 0.0711 | 0.0011 | 0 | 3 | 0.0594 | 0.0712 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3943 | 11749.25 | 44264.726 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 785.1033 | 0:240:120 | 0:00 | 0.0588 | 7 | 0.0017 | 0.0699 | 0.0716 | 0.0709 | 0.0007 | 0 | 3 | 0.0588 | 0.0706 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3946 | 11752.617 | 44264.726 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 800.8054 | 0:240:120 | 0:00 | 0.0583 | 7 | 0.003 | 0.0684 | 0.0714 | 0.07 | 0.0011 | 0 | 3 | 0.0583 | 0.0699 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3949 | 11756.187 | 44264.7261 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 816.8215 | 0:240:120 | 0:00 | 0.0577 | 7 | 0.0026 | 0.0674 | 0.07 | 0.0691 | 0.001 | 0 | 3 | 0.0577 | 0.0693 | P | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3952 | 11759.493 | 44264.7261 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 833.1579 | 0:240:120 | 0:00 | 0.0572 | 7 | 0.0027 | 0.067 | 0.0697 | 0.0685 | 0.001 | 0 | 3 | 0.0572 | 0.0687 | P | NP | 0-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3955 | 11763.175 | 44264.7262 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 849.8211 | 0:240:120 | 0:00 | 0.0568 | 7 | 0.0035 | 0.066 | 0.0695 | 0.0679 | 0.0014 | 0 | 3 | 0.0568 | 0.0681 | P | NP | 0-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3958 | 11766.887 | 44264.7262 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 866.8175 | 0:240:120 | 0:00 | 0.0563 | 7 | 0.003 | 0.0657 | 0.0687 | 0.0674 | 0.0011 | 0 | 3 | 0.0563 | 0.0676 | P | NP | 1-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3961 | 11770.8 | 44264.7262 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 884.1539 | 0:240:120 | 0:00 | 0.0559 | 7 | 0.0031 | 0.0648 | 0.0679 | 0.0666 | 0.001 | 0 | 3 | 0.0559 | 0.067 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3964 | 11774.313 | 44264.7263 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 901.837 | 0:240:120 | 0:00 | 0.0554 | 7 | 0.0028 | 0.0641 | 0.0669 | 0.0659 | 0.0013 | 0 | 3 | 0.0554 | 0.0665 | P | NP | 0-1-0-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3967 | 11777.616 | 44264.7263 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 919.8737 | 0:240:120 | 0:00 | 0.055 | 7 | 0.0034 | 0.0633 | 0.0667 | 0.0653 | 0.0011 | 0 | 3 | 0.055 | 0.066 | P | NP | 1-1-0-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3970 | 11781.057 | 44264.7264 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 938.2712 | 0:240:120 | 0:00 | 0.0546 | 7 | 0.0027 | 0.0636 | 0.0663 | 0.0648 | 0.001 | 0 | 3 | 0.0546 | 0.0656 | P | NP | 0-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3973 | 11784.707 | 44264.7264 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 957.0366 | 0:240:120 | 0:00 | 0.0543 | 7 | 0.0026 | 0.0626 | 0.0652 | 0.064 | 0.0009 | 0 | 3 | 0.0543 | 0.0651 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3976 | 11788.447 | 44264.7265 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 976.1773 | 0:240:120 | 0:00 | 0.0539 | 7 | 0.0028 | 0.0626 | 0.0654 | 0.0641 | 0.001 | 0 | 3 | 0.0539 | 0.0647 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3979 | 11791.945 | 44264.7265 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 995.7009 | 0:240:120 | 0:00 | 0.0536 | 7 | 0.0029 | 0.0616 | 0.0645 | 0.0631 | 0.0009 | 0 | 3 | 0.0536 | 0.0643 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3982 | 11795.469 | 44264.7265 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1015.6149 | 0:240:120 | 0:00 | 0.0532 | 7 | 0.0027 | 0.0612 | 0.0639 | 0.0629 | 0.001 | 0 | 3 | 0.0532 | 0.0639 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3985 | 11798.871 | 44264.7266 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1035.9272 | 0:240:120 | 0:00 | 0.0529 | 7 | 0.0028 | 0.0612 | 0.064 | 0.0625 | 0.0008 | 0 | 3 | 0.0529 | 0.0635 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3988 | 11802.346 | 44264.7266 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1056.6457 | 0:240:120 | 0:00 | 0.0526 | 7 | 0.0025 | 0.0601 | 0.0626 | 0.0615 | 0.0009 | 0 | 3 | 0.0526 | 0.0631 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3991 | 11805.745 | 44264.7267 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1077.7786 | 0:240:120 | 0:00 | 0.0523 | 7 | 0.0027 | 0.0599 | 0.0626 | 0.0613 | 0.0009 | 0 | 3 | 0.0523 | 0.0628 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3994 | 11809.156 | 44264.7267 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1099.3342 | 0:240:120 | 0:00 | 0.052 | 7 | 0.0035 | 0.0588 | 0.0623 | 0.0606 | 0.0012 | 0 | 3 | 0.052 | 0.0624 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3997 | 11812.712 | 44264.7267 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1121.3209 | 0:240:120 | 0:00 | 0.0517 | 7 | 0.0028 | 0.0589 | 0.0617 | 0.0605 | 0.0009 | 0 | 3 | 0.0517 | 0.0621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4000 | 11816.264 | 44264.7268 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1143.7473 | 0:240:120 | 0:00 | 0.0515 | 7 | 0.0032 | 0.0588 | 0.062 | 0.0605 | 0.001 | 0 | 3 | 0.0515 | 0.0618 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4003 | 11819.661 | 44264.7268 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1166.6223 | 0:240:120 | 0:00 | 0.0512 | 7 | 0.0032 | 0.0579 | 0.0611 | 0.0596 | 0.0013 | 0 | 3 | 0.0512 | 0.0615 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4006 | 11823.294 | 44264.7269 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1189.9547 | 0:240:120 | 0:00 | 0.051 | 7 | 0.0034 | 0.0575 | 0.0609 | 0.0592 | 0.0012 | 0 | 3 | 0.051 | 0.0612 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4009 | 11826.602 | 44264.7269 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1213.7538 | 0:240:120 | 0:00 | 0.0508 | 7 | 0.0028 | 0.0576 | 0.0604 | 0.0591 | 0.001 | 0 | 3 | 0.0508 | 0.0609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4012 | 11829.887 | 44264.7269 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1238.0289 | 0:240:120 | 0:00 | 0.0505 | 7 | 0.0025 | 0.0574 | 0.0599 | 0.0587 | 0.0011 | 0 | 3 | 0.0505 | 0.0606 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4015 | 11833.297 | 44264.727 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1262.7895 | 0:240:120 | 0:00 | 0.0503 | 7 | 0.0035 | 0.0566 | 0.0601 | 0.0583 | 0.0011 | 0 | 3 | 0.0503 | 0.0604 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4018 | 11836.721 | 44264.727 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1288.0452 | 0:240:120 | 0:00 | 0.0501 | 7 | 0.0039 | 0.0558 | 0.0597 | 0.058 | 0.0015 | 0 | 3 | 0.0501 | 0.0601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4021 | 11840.125 | 44264.727 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1313.8062 | 0:240:120 | 0:00 | 0.0499 | 7 | 0.0042 | 0.0559 | 0.0601 | 0.0578 | 0.0017 | 0 | 3 | 0.0499 | 0.0599 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4024 | 11843.41 | 44264.7271 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1340.0823 | 0:240:120 | 0:00 | 0.0497 | 7 | 0.0034 | 0.0559 | 0.0593 | 0.0576 | 0.0013 | 0 | 3 | 0.0497 | 0.0597 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4027 | 11847.038 | 44264.7271 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1366.8839 | 0:240:120 | 0:00 | 0.0495 | 7 | 0.0035 | 0.0547 | 0.0582 | 0.0567 | 0.0012 | 0 | 3 | 0.0495 | 0.0595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4030 | 11850.34 | 44264.7272 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1394.2216 | 0:240:120 | 0:00 | 0.0494 | 7 | 0.0033 | 0.0546 | 0.0579 | 0.0565 | 0.0013 | 0 | 3 | 0.0494 | 0.0594 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4033 | 11853.89 | 44264.7272 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1422.106 | 0:240:120 | 0:00 | 0.0492 | 7 | 0.0031 | 0.0547 | 0.0578 | 0.0564 | 0.0012 | 0 | 3 | 0.0492 | 0.0592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4036 | 11857.382 | 44264.7272 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1450.5482 | 0:240:120 | 0:00 | 0.049 | 7 | 0.0028 | 0.0549 | 0.0577 | 0.0564 | 0.0011 | 0 | 3 | 0.049 | 0.059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4039 | 11860.803 | 44264.7273 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1479.5591 | 0:240:120 | 0:00 | 0.0489 | 7 | 0.0031 | 0.0545 | 0.0576 | 0.0561 | 0.001 | 0 | 3 | 0.0489 | 0.0589 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4042 | 11864.291 | 44264.7273 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1509.1503 | 0:240:120 | 0:00 | 0.0487 | 7 | 0.0029 | 0.0538 | 0.0567 | 0.0556 | 0.0011 | 0 | 3 | 0.0487 | 0.0587 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4045 | 11867.709 | 44264.7274 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1539.3333 | 0:240:120 | 0:00 | 0.0486 | 7 | 0.0029 | 0.0538 | 0.0567 | 0.0553 | 0.001 | 0 | 3 | 0.0486 | 0.0586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4048 | 11871.118 | 44264.7274 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1570.12 | 0:240:120 | 0:00 | 0.0484 | 7 | 0.0025 | 0.0536 | 0.0561 | 0.0549 | 0.001 | 0 | 3 | 0.0484 | 0.0584 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4051 | 11874.427 | 44264.7274 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1601.5224 | 0:240:120 | 0:00 | 0.0483 | 7 | 0.0027 | 0.0536 | 0.0563 | 0.0551 | 0.001 | 0 | 3 | 0.0483 | 0.0583 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4054 | 11878.046 | 44264.7275 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1633.5528 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0026 | 0.0532 | 0.0558 | 0.0549 | 0.0009 | 0 | 3 | 0.0482 | 0.0582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4057 | 11881.441 | 44264.7275 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1666.2239 | 0:240:120 | 0:00 | 0.048 | 7 | 0.0035 | 0.0529 | 0.0564 | 0.0548 | 0.001 | 0 | 3 | 0.048 | 0.058 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4060 | 11884.655 | 44264.7276 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1699.5483 | 0:240:120 | 0:00 | 0.0479 | 7 | 0.0027 | 0.0528 | 0.0555 | 0.0544 | 0.0011 | 0 | 3 | 0.0479 | 0.0579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4063 | 11887.942 | 44264.7276 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1733.5393 | 0:240:120 | 0:00 | 0.0478 | 7 | 0.0021 | 0.053 | 0.0551 | 0.0542 | 0.0008 | 0 | 3 | 0.0478 | 0.0578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4066 | 11891.48 | 44264.7276 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1768.2101 | 0:240:120 | 0:00 | 0.0477 | 7 | 0.0029 | 0.0524 | 0.0553 | 0.0539 | 0.0011 | 0 | 3 | 0.0477 | 0.0577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4069 | 11894.783 | 44264.7277 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1803.5743 | 0:240:120 | 0:00 | 0.0476 | 7 | 0.0027 | 0.0522 | 0.0549 | 0.0537 | 0.001 | 0 | 3 | 0.0476 | 0.0576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4072 | 11898.393 | 44264.7277 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1839.6458 | 0:240:120 | 0:00 | 0.0475 | 7 | 0.0021 | 0.0524 | 0.0545 | 0.0537 | 0.0008 | 0 | 3 | 0.0475 | 0.0575 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4075 | 11901.784 | 44264.7278 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1876.4387 | 0:240:120 | 0:00 | 0.0474 | 7 | 0.0015 | 0.0524 | 0.0539 | 0.0533 | 0.0006 | 0 | 3 | 0.0474 | 0.0574 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4078 | 11904.973 | 44264.7278 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1913.9675 | 0:240:120 | 0:00 | 0.0473 | 7 | 0.0028 | 0.0522 | 0.055 | 0.0535 | 0.0007 | 0 | 3 | 0.0473 | 0.0573 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4081 | 11908.106 | 44264.7278 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1952.2468 | 0:240:120 | 0:00 | 0.0472 | 7 | 0.0027 | 0.0513 | 0.054 | 0.0532 | 0.001 | 0 | 3 | 0.0472 | 0.0572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4084 | 11911.631 | 44264.7279 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1991.2918 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0027 | 0.0521 | 0.0548 | 0.0533 | 0.0008 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4087 | 11915.001 | 44264.7279 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2031.1176 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0028 | 0.052 | 0.0548 | 0.0532 | 0.0009 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4090 | 11918.424 | 44264.728 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2071.74 | 0:240:120 | 0:00 | 0.047 | 7 | 0.0032 | 0.0516 | 0.0548 | 0.0532 | 0.001 | 0 | 3 | 0.047 | 0.057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4093 | 11921.947 | 44264.728 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2113.1748 | 0:240:120 | 0:00 | 0.0469 | 7 | 0.0017 | 0.0522 | 0.0539 | 0.0529 | 0.0007 | 0 | 3 | 0.0469 | 0.0569 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4096 | 11925.367 | 44264.728 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2155.4382 | 0:240:120 | 0:00 | 0.0468 | 7 | 0.004 | 0.0507 | 0.0547 | 0.0525 | 0.0013 | 0 | 3 | 0.0468 | 0.0568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4099 | 11928.743 | 44264.7281 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2198.547 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0028 | 0.0511 | 0.0539 | 0.0524 | 0.001 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4102 | 11932.05 | 44264.7281 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2242.518 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0014 | 0.0519 | 0.0533 | 0.0527 | 0.0006 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4105 | 11935.725 | 44264.7282 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2287.3683 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.0025 | 0.0516 | 0.0541 | 0.0524 | 0.0009 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4108 | 11938.804 | 44264.7282 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2333.1157 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.0026 | 0.0505 | 0.0531 | 0.0522 | 0.0007 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4111 | 11942.308 | 44264.7282 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2379.778 | 0:240:120 | 0:00 | 0.0465 | 7 | 0.0033 | 0.0508 | 0.0541 | 0.0524 | 0.0012 | 0 | 3 | 0.0465 | 0.0565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4114 | 11945.688 | 44264.7283 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2427.3736 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0032 | 0.0515 | 0.0547 | 0.0527 | 0.0011 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4117 | 11949.087 | 44264.7283 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2475.921 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0032 | 0.0497 | 0.0529 | 0.0517 | 0.0012 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4120 | 11952.266 | 44264.7283 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2525.4394 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0026 | 0.0502 | 0.0528 | 0.0517 | 0.0009 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4123 | 11956.137 | 44264.7284 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2575.9482 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0028 | 0.0509 | 0.0537 | 0.0521 | 0.001 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4126 | 11959.533 | 44264.7284 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2627.4672 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0032 | 0.0498 | 0.053 | 0.0516 | 0.0011 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4129 | 11962.887 | 44264.7285 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2680.0165 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0015 | 0.0508 | 0.0523 | 0.0515 | 0.0006 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4132 | 11966.517 | 44264.7285 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2733.6169 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0037 | 0.05 | 0.0537 | 0.0517 | 0.0014 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4135 | 11969.932 | 44264.7286 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2788.2892 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0038 | 0.0497 | 0.0535 | 0.0516 | 0.0014 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4138 | 11973.351 | 44264.7286 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2844.055 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0032 | 0.0493 | 0.0525 | 0.0514 | 0.0012 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4141 | 11976.64 | 44264.7286 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2900.9361 | 0:240:120 | 0:00 | 0.046 | 7 | 0.004 | 0.0494 | 0.0534 | 0.0515 | 0.0013 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4144 | 11979.834 | 44264.7287 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2958.9548 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0042 | 0.0493 | 0.0535 | 0.0513 | 0.0014 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4147 | 11983.214 | 44264.7287 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3018.1339 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.004 | 0.0492 | 0.0532 | 0.0513 | 0.0014 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4150 | 11986.7 | 44264.7287 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3078.4966 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0041 | 0.0496 | 0.0537 | 0.0515 | 0.0015 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4153 | 11990.334 | 44264.7288 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3140.0665 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0045 | 0.0489 | 0.0534 | 0.0512 | 0.0017 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4156 | 11993.739 | 44264.7288 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3202.8679 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0035 | 0.0494 | 0.0529 | 0.0512 | 0.0012 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4159 | 11997.258 | 44264.7289 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3266.9252 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0036 | 0.0497 | 0.0533 | 0.0512 | 0.0012 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4162 | 12000.886 | 44264.7289 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3332.2637 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0026 | 0.0504 | 0.053 | 0.0513 | 0.001 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4165 | 12004.067 | 44264.7289 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3398.909 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0032 | 0.0494 | 0.0526 | 0.0509 | 0.0011 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4168 | 12007.353 | 44264.729 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3466.8872 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0025 | 0.0499 | 0.0524 | 0.0511 | 0.0009 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4171 | 12010.66 | 44264.729 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3536.2249 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0034 | 0.0494 | 0.0528 | 0.0513 | 0.0012 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4174 | 12014.151 | 44264.7291 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3606.9494 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.003 | 0.05 | 0.053 | 0.0511 | 0.0012 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4177 | 12017.439 | 44264.7291 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3679.0884 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0041 | 0.0495 | 0.0536 | 0.051 | 0.0012 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4180 | 12020.865 | 44264.7291 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3752.6702 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0039 | 0.0487 | 0.0526 | 0.0505 | 0.0013 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4183 | 12024.256 | 44264.7292 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3827.7236 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0015 | 0.0501 | 0.0516 | 0.0509 | 0.0006 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4186 | 12027.524 | 44264.7292 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3904.278 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0044 | 0.0486 | 0.053 | 0.0506 | 0.0014 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4189 | 12031.026 | 44264.7293 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3982.3636 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0029 | 0.0495 | 0.0524 | 0.051 | 0.0011 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4192 | 12034.292 | 44264.7293 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4062.0109 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.003 | 0.049 | 0.052 | 0.0506 | 0.0012 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4195 | 12037.777 | 44264.7293 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4143.2511 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0029 | 0.0495 | 0.0524 | 0.0508 | 0.0009 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4198 | 12041.4 | 44264.7294 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4226.1161 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.003 | 0.0492 | 0.0522 | 0.0504 | 0.001 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4201 | 12044.876 | 44264.7294 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4310.6384 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0028 | 0.049 | 0.0518 | 0.0502 | 0.0011 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4204 | 12048.079 | 44264.7295 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4396.8512 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0041 | 0.0484 | 0.0525 | 0.0504 | 0.0013 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4207 | 12051.491 | 44264.7295 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4484.7882 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0042 | 0.0492 | 0.0534 | 0.0506 | 0.0015 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4210 | 12054.887 | 44264.7295 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4574.484 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0045 | 0.0481 | 0.0526 | 0.0501 | 0.0016 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4213 | 12058.442 | 44264.7296 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4665.9737 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0028 | 0.0487 | 0.0515 | 0.0502 | 0.001 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4216 | 12061.966 | 44264.7296 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4759.2931 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0039 | 0.0485 | 0.0524 | 0.0503 | 0.0014 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4219 | 12065.199 | 44264.7297 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4854.479 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.003 | 0.0481 | 0.0511 | 0.0495 | 0.0011 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4222 | 12068.514 | 44264.7297 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4951.5686 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0042 | 0.0479 | 0.0521 | 0.0499 | 0.0015 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4225 | 12071.816 | 44264.7297 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5050.6 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0041 | 0.0483 | 0.0524 | 0.0502 | 0.0014 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4228 | 12075.217 | 44264.7298 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5151.612 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0033 | 0.0481 | 0.0514 | 0.0499 | 0.001 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4231 | 12078.594 | 44264.7298 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5254.6442 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.003 | 0.0479 | 0.0509 | 0.0497 | 0.0012 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4234 | 12081.975 | 44264.7298 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5359.7371 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0046 | 0.0479 | 0.0525 | 0.0495 | 0.0015 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4237 | 12085.361 | 44264.7299 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5466.9318 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0043 | 0.0482 | 0.0525 | 0.0499 | 0.0015 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4240 | 12088.782 | 44264.7299 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5576.2705 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0027 | 0.0491 | 0.0518 | 0.0501 | 0.001 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4243 | 12092.178 | 44264.73 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5687.7959 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0042 | 0.0483 | 0.0525 | 0.0502 | 0.0015 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4246 | 12095.361 | 44264.73 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5801.5518 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0039 | 0.0481 | 0.052 | 0.0498 | 0.0014 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4249 | 12098.646 | 44264.73 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5917.5828 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0041 | 0.0478 | 0.0519 | 0.0497 | 0.0013 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4252 | 12102.028 | 44264.7301 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6035.9345 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0037 | 0.0479 | 0.0516 | 0.0496 | 0.0014 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4255 | 12105.742 | 44264.7301 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6156.6532 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0036 | 0.0475 | 0.0511 | 0.0492 | 0.0013 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4258 | 12109.245 | 44264.7302 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6279.7862 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0033 | 0.0479 | 0.0512 | 0.0493 | 0.0011 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4261 | 12112.523 | 44264.7302 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6405.382 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0046 | 0.0479 | 0.0525 | 0.0499 | 0.0015 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4264 | 12116.155 | 44264.7302 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6533.4896 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0038 | 0.0478 | 0.0516 | 0.0494 | 0.0013 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4267 | 12119.999 | 44264.7303 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6664.1594 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0039 | 0.0475 | 0.0514 | 0.0494 | 0.0014 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4270 | 12123.416 | 44264.7303 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6797.4426 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0037 | 0.0485 | 0.0522 | 0.05 | 0.0014 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4273 | 12126.699 | 44264.7304 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6933.3914 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.003 | 0.0487 | 0.0517 | 0.0498 | 0.001 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4276 | 12129.888 | 44264.7304 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7072.0593 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.004 | 0.0481 | 0.0521 | 0.0499 | 0.0013 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4279 | 12133.065 | 44264.7304 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7213.5004 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0038 | 0.0477 | 0.0515 | 0.0496 | 0.0013 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4282 | 12136.211 | 44264.7305 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7357.7704 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0044 | 0.0475 | 0.0519 | 0.0496 | 0.0015 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4285 | 12139.592 | 44264.7305 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7504.9259 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0031 | 0.0479 | 0.051 | 0.0493 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4288 | 12142.906 | 44264.7306 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7655.0244 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.0481 | 0.0506 | 0.0496 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4291 | 12146.308 | 44264.7306 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7808.1249 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0031 | 0.0474 | 0.0505 | 0.049 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4294 | 12149.706 | 44264.7306 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7964.2874 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.0478 | 0.0503 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4297 | 12153.101 | 44264.7307 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8123.5731 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0035 | 0.0472 | 0.0507 | 0.0492 | 0.0011 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4300 | 12156.275 | 44264.7307 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8286.0446 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.0481 | 0.0505 | 0.0493 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4303 | 12159.688 | 44264.7307 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8451.7655 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.002 | 0.0476 | 0.0496 | 0.0488 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4306 | 12163.186 | 44264.7308 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8620.8008 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.0474 | 0.0497 | 0.0486 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4309 | 12166.483 | 44264.7308 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8793.2168 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.048 | 0.0503 | 0.0493 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4312 | 12170.01 | 44264.7309 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8969.0811 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0028 | 0.0477 | 0.0505 | 0.0492 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4315 | 12173.286 | 44264.7309 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9148.4627 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0028 | 0.0474 | 0.0502 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4318 | 12176.719 | 44264.7309 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9331.432 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0021 | 0.0482 | 0.0503 | 0.0493 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4321 | 12180.007 | 44264.731 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9518.0606 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.002 | 0.048 | 0.05 | 0.0491 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4324 | 12183.479 | 44264.731 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9708.4218 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.0472 | 0.0497 | 0.0489 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4327 | 12186.756 | 44264.7311 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9902.5903 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0022 | 0.0475 | 0.0497 | 0.0488 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4330 | 12190.029 | 44264.7311 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10100.6421 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0031 | 0.0472 | 0.0503 | 0.0486 | 0.0011 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4333 | 12193.404 | 44264.7311 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10302.6549 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0029 | 0.0473 | 0.0502 | 0.0492 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4336 | 12196.887 | 44264.7312 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10508.708 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.048 | 0.0503 | 0.0491 | 0.0007 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4339 | 12200.169 | 44264.7312 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10718.8822 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0024 | 0.0471 | 0.0495 | 0.0484 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4342 | 12203.57 | 44264.7313 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10933.2598 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0026 | 0.0476 | 0.0502 | 0.0488 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4345 | 12206.934 | 44264.7313 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11151.925 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0018 | 0.0476 | 0.0494 | 0.0486 | 0.0006 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4348 | 12209.958 | 44264.7313 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11374.9635 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0034 | 0.0468 | 0.0502 | 0.0485 | 0.0012 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4351 | 12213.679 | 44264.7314 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11602.4628 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0031 | 0.0469 | 0.05 | 0.0484 | 0.0011 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4354 | 12216.948 | 44264.7314 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11834.512 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.0476 | 0.0499 | 0.0487 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4357 | 12269.684 | 44264.732 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.1 | 0:240:120 | 0:00 | 6.0167 | 7 | 17.2539 | 36.5927 | 53.8466 | 42.0083 | 7.597 | 57.7147 | 3 | 6.0167 | 24.6513 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4360 | 12414.408 | 44264.7337 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.6 | 0:240:120 | 0:00 | 5.1894 | 7 | 16.9722 | 18.6801 | 35.6523 | 24.2631 | 8.1515 | 66.4478 | 3 | 5.1894 | 16.0572 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4363 | 12499.042 | 44264.7347 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.2 | 0:240:120 | 0:00 | 4.5153 | 7 | 1.6489 | 9.0892 | 10.7381 | 9.6276 | 0.8053 | 0.6485 | 3 | 4.5153 | 11.6467 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4366 | 12531.945 | 44264.7351 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.7 | 0:240:120 | 0:00 | 4.0176 | 7 | 0.5222 | 8.0919 | 8.6141 | 8.2657 | 0.2571 | 0.0661 | 3 | 4.0176 | 9.2279 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4369 | 12559.98 | 44264.7354 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.3 | 0:240:120 | 0:00 | 3.5884 | 7 | 0.5496 | 7.0485 | 7.5981 | 7.2481 | 0.2619 | 0.0686 | 3 | 3.5884 | 7.5305 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4372 | 12584.881 | 44264.7357 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83 | 0:240:120 | 0:00 | 3.2169 | 7 | 0.9802 | 5.6046 | 6.5848 | 5.94 | 0.481 | 0.2314 | 3 | 3.2169 | 6.2807 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4375 | 12606.288 | 44264.7359 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.6 | 0:240:120 | 0:00 | 2.9268 | 7 | 0.6452 | 4.6064 | 5.2516 | 4.8173 | 0.3141 | 0.0987 | 3 | 2.9268 | 5.4193 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4378 | 12624.237 | 44264.7361 | Vista Coord | Main | 65Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.3 | 0:240:120 | 0:00 | 2.667 | 7 | 0.2186 | 4.2279 | 4.4465 | 4.3178 | 0.0966 | 0.0093 | 3 | 2.667 | 4.7196 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4381 | 12737.181 | 44264.7374 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.187 | 90.3917 | 99.5787 | 93.5382 | 4.5294 | 20.5154 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4384 | 13020.925 | 44264.7407 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.76 | 0:240:120 | 0:00 | 7.7705 | 7 | 9.055 | 72.525 | 81.58 | 75.5605 | 4.5131 | 20.3683 | 3 | 7.7705 | 101.5883 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4387 | 13251.125 | 44264.7434 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.5552 | 0:240:120 | 0:00 | 6.502 | 7 | 9.81 | 53.7727 | 63.5827 | 57.3623 | 4.6703 | 21.812 | 3 | 6.502 | 32.8902 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4390 | 13427.055 | 44264.7454 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.3863 | 0:240:120 | 0:00 | 5.5599 | 7 | 12.6481 | 32.9339 | 45.582 | 38.3774 | 5.51 | 30.3598 | 3 | 5.5599 | 19.3218 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4393 | 13548.686 | 44264.7468 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.254 | 0:240:120 | 0:00 | 4.833 | 7 | 17.4925 | 9.9419 | 27.4344 | 17.0549 | 7.9448 | 63.1192 | 3 | 4.833 | 13.5272 | NP | NP | 0-1-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
4396 | 13616.013 | 44264.7476 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.1591 | 0:240:120 | 0:00 | 4.2557 | 7 | 0.8079 | 8.5938 | 9.4017 | 8.8658 | 0.3954 | 0.1563 | 3 | 4.2557 | 10.3153 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4399 | 13645.867 | 44264.7479 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.1023 | 0:240:120 | 0:00 | 3.7863 | 7 | 0.5099 | 7.5941 | 8.104 | 7.7647 | 0.2525 | 0.0638 | 3 | 3.7863 | 8.2753 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4402 | 13672.319 | 44264.7483 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.0843 | 0:240:120 | 0:00 | 3.3975 | 7 | 0.5092 | 6.5907 | 7.0999 | 6.7636 | 0.2516 | 0.0633 | 3 | 3.3975 | 6.8658 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4405 | 13695.555 | 44264.7485 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.106 | 0:240:120 | 0:00 | 3.0704 | 7 | 0.985 | 5.1179 | 6.1029 | 5.5295 | 0.4434 | 0.1966 | 3 | 3.0704 | 5.8343 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4408 | 13715.249 | 44264.7488 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.1681 | 0:240:120 | 0:00 | 2.7916 | 7 | 0.198 | 4.4418 | 4.6398 | 4.5073 | 0.0959 | 0.0092 | 3 | 2.7916 | 5.0472 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4411 | 13732.201 | 44264.7489 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.2715 | 0:240:120 | 0:00 | 2.5513 | 7 | 0.2162 | 4.0638 | 4.28 | 4.1524 | 0.0971 | 0.0094 | 3 | 2.5513 | 4.4273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4414 | 13747.671 | 44264.7491 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.4169 | 0:240:120 | 0:00 | 2.3422 | 7 | 0.2761 | 3.6184 | 3.8945 | 3.7077 | 0.1311 | 0.0172 | 3 | 2.3422 | 3.9269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4417 | 13762.171 | 44264.7493 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.6053 | 0:240:120 | 0:00 | 2.1587 | 7 | 0.2359 | 3.2203 | 3.4562 | 3.332 | 0.0951 | 0.009 | 3 | 2.1587 | 3.5146 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4420 | 13775.229 | 44264.7494 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.8374 | 0:240:120 | 0:00 | 1.9965 | 7 | 0.1627 | 2.8785 | 3.0412 | 2.9298 | 0.0746 | 0.0056 | 3 | 1.9965 | 3.1694 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4423 | 13787.229 | 44264.7496 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.1141 | 0:240:120 | 0:00 | 1.8523 | 7 | 0.1636 | 2.6354 | 2.799 | 2.7085 | 0.0728 | 0.0053 | 3 | 1.8523 | 2.8763 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4426 | 13798.229 | 44264.7497 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.4364 | 0:240:120 | 0:00 | 1.7232 | 7 | 0.085 | 2.4697 | 2.5547 | 2.498 | 0.0413 | 0.0017 | 3 | 1.7232 | 2.6246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4429 | 13808.831 | 44264.7498 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.8051 | 0:240:120 | 0:00 | 1.6071 | 7 | 0.1266 | 2.2253 | 2.3519 | 2.268 | 0.0627 | 0.0039 | 3 | 1.6071 | 2.4062 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4432 | 13818.835 | 44264.75 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.2212 | 0:240:120 | 0:00 | 1.5023 | 7 | 0.0967 | 2.0476 | 2.1443 | 2.0815 | 0.0469 | 0.0022 | 3 | 1.5023 | 2.215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4435 | 13828.022 | 44264.7501 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.6857 | 0:240:120 | 0:00 | 1.4072 | 7 | 0.0972 | 1.9035 | 2.0007 | 1.9433 | 0.0446 | 0.002 | 3 | 1.4072 | 2.0464 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4438 | 13836.902 | 44264.7502 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.1994 | 0:240:120 | 0:00 | 1.3205 | 7 | 0.0828 | 1.7726 | 1.8554 | 1.8126 | 0.0337 | 0.0011 | 3 | 1.3205 | 1.8967 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4441 | 13845.447 | 44264.7503 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.7634 | 0:240:120 | 0:00 | 1.2414 | 7 | 0.061 | 1.649 | 1.71 | 1.6726 | 0.028 | 0.0008 | 3 | 1.2414 | 1.7631 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4444 | 13853.598 | 44264.7504 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.3786 | 0:240:120 | 0:00 | 1.1688 | 7 | 0.043 | 1.555 | 1.598 | 1.572 | 0.0192 | 0.0004 | 3 | 1.1688 | 1.643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4447 | 13861.351 | 44264.7504 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.0462 | 0:240:120 | 0:00 | 1.1021 | 7 | 0.0543 | 1.4476 | 1.5019 | 1.4724 | 0.0233 | 0.0005 | 3 | 1.1021 | 1.5348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4450 | 13868.86 | 44264.7505 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.7671 | 0:240:120 | 0:00 | 1.0406 | 7 | 0.0639 | 1.3422 | 1.4061 | 1.3709 | 0.0279 | 0.0008 | 3 | 1.0406 | 1.4367 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4453 | 13876.259 | 44264.7506 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.5425 | 0:240:120 | 0:00 | 0.9838 | 7 | 0.0459 | 1.2747 | 1.3206 | 1.2909 | 0.0219 | 0.0005 | 3 | 0.9838 | 1.3474 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4456 | 13883.218 | 44264.7507 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.3733 | 0:240:120 | 0:00 | 0.9312 | 7 | 0.045 | 1.2062 | 1.2512 | 1.2216 | 0.0213 | 0.0005 | 3 | 0.9312 | 1.266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4459 | 13889.935 | 44264.7508 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.2608 | 0:240:120 | 0:00 | 0.8824 | 7 | 0.0282 | 1.1363 | 1.1645 | 1.1472 | 0.0123 | 0.0002 | 3 | 0.8824 | 1.1914 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4462 | 13896.383 | 44264.7508 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.206 | 0:240:120 | 0:00 | 0.837 | 7 | 0.0326 | 1.0696 | 1.1022 | 1.0824 | 0.015 | 0.0002 | 3 | 0.837 | 1.1229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4465 | 13902.579 | 44264.7509 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.2101 | 0:240:120 | 0:00 | 0.7947 | 7 | 0.0283 | 1.0169 | 1.0452 | 1.0273 | 0.0128 | 0.0002 | 3 | 0.7947 | 1.0598 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4468 | 13908.889 | 44264.751 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.2743 | 0:240:120 | 0:00 | 0.7553 | 7 | 0.0326 | 0.9531 | 0.9857 | 0.9662 | 0.0146 | 0.0002 | 3 | 0.7553 | 1.0015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4471 | 13914.785 | 44264.7511 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 159.3998 | 0:240:120 | 0:00 | 0.7184 | 7 | 0.0188 | 0.9125 | 0.9313 | 0.9194 | 0.0084 | 0.0001 | 3 | 0.7184 | 0.9476 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4474 | 13920.599 | 44264.7511 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 162.5878 | 0:240:120 | 0:00 | 0.6839 | 7 | 0.0277 | 0.8627 | 0.8904 | 0.8728 | 0.0128 | 0.0002 | 3 | 0.6839 | 0.8976 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4477 | 13926.915 | 44264.7512 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.8396 | 0:240:120 | 0:00 | 0.6516 | 7 | 0.0222 | 0.818 | 0.8402 | 0.8252 | 0.0101 | 0.0001 | 3 | 0.6516 | 0.8512 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4480 | 13932.412 | 44264.7513 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.1564 | 0:240:120 | 0:00 | 0.6212 | 7 | 0.0184 | 0.7782 | 0.7966 | 0.7868 | 0.0074 | 0.0001 | 3 | 0.6212 | 0.8079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4483 | 13937.726 | 44264.7513 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 172.5395 | 0:240:120 | 0:00 | 0.5927 | 7 | 0.0158 | 0.7409 | 0.7567 | 0.7477 | 0.0066 | 0 | 3 | 0.5927 | 0.7676 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4486 | 13943.085 | 44264.7514 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175.9903 | 0:240:120 | 0:00 | 0.5659 | 7 | 0.012 | 0.708 | 0.72 | 0.7123 | 0.0054 | 0 | 3 | 0.5659 | 0.7299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4489 | 13948.24 | 44264.7514 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 179.5101 | 0:240:120 | 0:00 | 0.5407 | 7 | 0.0123 | 0.6753 | 0.6876 | 0.6796 | 0.0054 | 0 | 3 | 0.5407 | 0.6947 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4492 | 13953.391 | 44264.7515 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.1003 | 0:240:120 | 0:00 | 0.5169 | 7 | 0.013 | 0.641 | 0.654 | 0.6467 | 0.0055 | 0 | 3 | 0.5169 | 0.6617 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4495 | 13958.468 | 44264.7516 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 186.7623 | 0:240:120 | 0:00 | 0.4944 | 7 | 0.0142 | 0.6135 | 0.6277 | 0.6191 | 0.0061 | 0 | 3 | 0.4944 | 0.6307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4498 | 13963.911 | 44264.7516 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 190.4975 | 0:240:120 | 0:00 | 0.4732 | 7 | 0.0146 | 0.5851 | 0.5997 | 0.5911 | 0.0063 | 0 | 3 | 0.4732 | 0.6017 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4501 | 13968.786 | 44264.7517 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.3075 | 0:240:120 | 0:00 | 0.4532 | 7 | 0.0073 | 0.5626 | 0.5699 | 0.5653 | 0.0031 | 0 | 3 | 0.4532 | 0.5743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4504 | 13973.879 | 44264.7517 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 198.1936 | 0:240:120 | 0:00 | 0.4343 | 7 | 0.0109 | 0.536 | 0.5469 | 0.5399 | 0.0051 | 0 | 3 | 0.4343 | 0.5486 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4507 | 13978.643 | 44264.7518 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 202.1575 | 0:240:120 | 0:00 | 0.4164 | 7 | 0.0067 | 0.5144 | 0.5211 | 0.5169 | 0.003 | 0 | 3 | 0.4164 | 0.5244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4510 | 13983.341 | 44264.7519 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 206.2007 | 0:240:120 | 0:00 | 0.3994 | 7 | 0.0104 | 0.4915 | 0.5019 | 0.4957 | 0.0045 | 0 | 3 | 0.3994 | 0.5015 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4513 | 13988.145 | 44264.7519 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 210.3247 | 0:240:120 | 0:00 | 0.3833 | 7 | 0.0066 | 0.4721 | 0.4787 | 0.4745 | 0.0029 | 0 | 3 | 0.3833 | 0.4799 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4516 | 13992.804 | 44264.752 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 214.5312 | 0:240:120 | 0:00 | 0.368 | 7 | 0.0073 | 0.4528 | 0.4601 | 0.4555 | 0.0032 | 0 | 3 | 0.368 | 0.4595 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4519 | 13997.49 | 44264.752 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 218.8218 | 0:240:120 | 0:00 | 0.3536 | 7 | 0.0064 | 0.4341 | 0.4405 | 0.4366 | 0.0028 | 0 | 3 | 0.3536 | 0.4402 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4522 | 14001.797 | 44264.7521 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.1982 | 0:240:120 | 0:00 | 0.3398 | 7 | 0.0063 | 0.4167 | 0.423 | 0.4192 | 0.0026 | 0 | 3 | 0.3398 | 0.422 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4525 | 14006.196 | 44264.7521 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 227.6622 | 0:240:120 | 0:00 | 0.3268 | 7 | 0.0051 | 0.4009 | 0.406 | 0.4029 | 0.0022 | 0 | 3 | 0.3268 | 0.4047 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4528 | 14010.478 | 44264.7522 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 232.2154 | 0:240:120 | 0:00 | 0.3143 | 7 | 0.0075 | 0.3843 | 0.3918 | 0.3875 | 0.0028 | 0 | 3 | 0.3143 | 0.3884 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4531 | 14014.643 | 44264.7522 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 236.8597 | 0:240:120 | 0:00 | 0.3025 | 7 | 0.0075 | 0.3686 | 0.3761 | 0.3724 | 0.0028 | 0 | 3 | 0.3025 | 0.3728 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4534 | 14018.647 | 44264.7523 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 241.5969 | 0:240:120 | 0:00 | 0.2913 | 7 | 0.0043 | 0.3569 | 0.3612 | 0.3584 | 0.0019 | 0 | 3 | 0.2913 | 0.3581 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4537 | 14022.976 | 44264.7523 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.4289 | 0:240:120 | 0:00 | 0.2806 | 7 | 0.0051 | 0.3426 | 0.3477 | 0.3452 | 0.0021 | 0 | 3 | 0.2806 | 0.3441 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4540 | 14027.404 | 44264.7524 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 251.3575 | 0:240:120 | 0:00 | 0.2704 | 7 | 0.0046 | 0.3309 | 0.3355 | 0.3327 | 0.0018 | 0 | 3 | 0.2704 | 0.3309 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4543 | 14031.383 | 44264.7524 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.3846 | 0:240:120 | 0:00 | 0.2607 | 7 | 0.0052 | 0.3178 | 0.323 | 0.3202 | 0.002 | 0 | 3 | 0.2607 | 0.3182 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4546 | 14035.489 | 44264.7525 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 261.5123 | 0:240:120 | 0:00 | 0.2515 | 7 | 0.0051 | 0.3058 | 0.3109 | 0.3082 | 0.0018 | 0 | 3 | 0.2515 | 0.3063 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4549 | 14039.563 | 44264.7525 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 266.7425 | 0:240:120 | 0:00 | 0.2427 | 7 | 0.0038 | 0.2957 | 0.2995 | 0.2975 | 0.0014 | 0 | 3 | 0.2427 | 0.2948 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4552 | 14043.666 | 44264.7526 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 272.0774 | 0:240:120 | 0:00 | 0.2343 | 7 | 0.0053 | 0.2849 | 0.2902 | 0.2872 | 0.0019 | 0 | 3 | 0.2343 | 0.284 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4555 | 14047.603 | 44264.7526 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 277.5189 | 0:240:120 | 0:00 | 0.2263 | 7 | 0.0038 | 0.2759 | 0.2797 | 0.2774 | 0.0014 | 0 | 3 | 0.2263 | 0.2736 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4558 | 14051.424 | 44264.7526 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 283.0693 | 0:240:120 | 0:00 | 0.2186 | 7 | 0.0052 | 0.2652 | 0.2704 | 0.2675 | 0.0018 | 0 | 3 | 0.2186 | 0.2638 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4561 | 14055.411 | 44264.7527 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 288.7307 | 0:240:120 | 0:00 | 0.2113 | 7 | 0.0029 | 0.2568 | 0.2597 | 0.2584 | 0.0011 | 0 | 3 | 0.2113 | 0.2544 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4564 | 14059.265 | 44264.7527 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.5053 | 0:240:120 | 0:00 | 0.2043 | 7 | 0.0041 | 0.2479 | 0.252 | 0.2498 | 0.0014 | 0 | 3 | 0.2043 | 0.2455 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4567 | 14063.142 | 44264.7528 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 300.3954 | 0:240:120 | 0:00 | 0.1977 | 7 | 0.0041 | 0.2399 | 0.244 | 0.2422 | 0.0015 | 0 | 3 | 0.1977 | 0.2372 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4570 | 14067.232 | 44264.7528 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 306.4033 | 0:240:120 | 0:00 | 0.1913 | 7 | 0.003 | 0.2328 | 0.2358 | 0.2344 | 0.0011 | 0 | 3 | 0.1913 | 0.2296 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4573 | 14071.467 | 44264.7529 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 312.5314 | 0:240:120 | 0:00 | 0.1852 | 7 | 0.0038 | 0.2255 | 0.2293 | 0.2273 | 0.0012 | 0 | 3 | 0.1852 | 0.2223 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4576 | 14075.192 | 44264.7529 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 318.782 | 0:240:120 | 0:00 | 0.1794 | 7 | 0.0034 | 0.2188 | 0.2222 | 0.2204 | 0.0012 | 0 | 3 | 0.1794 | 0.2153 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4579 | 14079.41 | 44264.753 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 325.1577 | 0:240:120 | 0:00 | 0.1739 | 7 | 0.0047 | 0.2113 | 0.216 | 0.2135 | 0.0015 | 0 | 3 | 0.1739 | 0.2086 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4582 | 14083.047 | 44264.753 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 331.6608 | 0:240:120 | 0:00 | 0.1686 | 7 | 0.0041 | 0.2044 | 0.2085 | 0.2064 | 0.0014 | 0 | 3 | 0.1686 | 0.2023 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4585 | 14086.666 | 44264.7531 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 338.294 | 0:240:120 | 0:00 | 0.1635 | 7 | 0.0024 | 0.1996 | 0.202 | 0.2007 | 0.0009 | 0 | 3 | 0.1635 | 0.1962 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4588 | 14090.275 | 44264.7531 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 345.0599 | 0:240:120 | 0:00 | 0.1586 | 7 | 0.0024 | 0.193 | 0.1954 | 0.1944 | 0.0007 | 0 | 3 | 0.1586 | 0.1903 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4591 | 14093.751 | 44264.7531 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 351.9611 | 0:240:120 | 0:00 | 0.154 | 7 | 0.0014 | 0.1883 | 0.1897 | 0.1889 | 0.0005 | 0 | 3 | 0.154 | 0.1847 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4594 | 14097.147 | 44264.7532 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 359.0003 | 0:240:120 | 0:00 | 0.1495 | 7 | 0.0015 | 0.1826 | 0.1841 | 0.1833 | 0.0005 | 0 | 3 | 0.1495 | 0.1794 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4597 | 14100.871 | 44264.7532 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 366.1804 | 0:240:120 | 0:00 | 0.1452 | 7 | 0.0035 | 0.1761 | 0.1796 | 0.1778 | 0.0013 | 0 | 3 | 0.1452 | 0.1743 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4600 | 14104.62 | 44264.7533 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 373.504 | 0:240:120 | 0:00 | 0.1412 | 7 | 0.0028 | 0.1712 | 0.174 | 0.1726 | 0.0009 | 0 | 3 | 0.1412 | 0.1694 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4603 | 14108.136 | 44264.7533 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 380.974 | 0:240:120 | 0:00 | 0.1373 | 7 | 0.0033 | 0.1665 | 0.1698 | 0.1677 | 0.0011 | 0 | 3 | 0.1373 | 0.1647 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4606 | 14111.789 | 44264.7533 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 388.5935 | 0:240:120 | 0:00 | 0.1335 | 7 | 0.0021 | 0.1625 | 0.1646 | 0.1636 | 0.0006 | 0 | 3 | 0.1335 | 0.1602 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4609 | 14115.423 | 44264.7534 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 396.3654 | 0:240:120 | 0:00 | 0.1299 | 7 | 0.0027 | 0.1571 | 0.1598 | 0.1587 | 0.001 | 0 | 3 | 0.1299 | 0.1559 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4612 | 14119.038 | 44264.7534 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 404.2927 | 0:240:120 | 0:00 | 0.1265 | 7 | 0.0025 | 0.1536 | 0.1561 | 0.1548 | 0.0009 | 0 | 3 | 0.1265 | 0.1518 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4615 | 14122.739 | 44264.7535 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 412.3786 | 0:240:120 | 0:00 | 0.1232 | 7 | 0.0029 | 0.1499 | 0.1528 | 0.1509 | 0.0011 | 0 | 3 | 0.1232 | 0.1479 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4618 | 14126.258 | 44264.7535 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 420.6261 | 0:240:120 | 0:00 | 0.1201 | 7 | 0.0025 | 0.146 | 0.1485 | 0.1473 | 0.0009 | 0 | 3 | 0.1201 | 0.1441 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4621 | 14129.65 | 44264.7535 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 429.0386 | 0:240:120 | 0:00 | 0.117 | 7 | 0.0028 | 0.1418 | 0.1446 | 0.1433 | 0.0009 | 0 | 3 | 0.117 | 0.1405 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4624 | 14133.299 | 44264.7536 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 437.6194 | 0:240:120 | 0:00 | 0.1141 | 7 | 0.0035 | 0.1378 | 0.1413 | 0.1398 | 0.0012 | 0 | 3 | 0.1141 | 0.137 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4627 | 14136.745 | 44264.7536 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 446.3718 | 0:240:120 | 0:00 | 0.1114 | 7 | 0.0027 | 0.1346 | 0.1373 | 0.1364 | 0.001 | 0 | 3 | 0.1114 | 0.1336 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4630 | 14140.393 | 44264.7537 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 455.2992 | 0:240:120 | 0:00 | 0.1087 | 7 | 0.0029 | 0.1315 | 0.1344 | 0.1333 | 0.001 | 0 | 3 | 0.1087 | 0.1305 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4633 | 14143.838 | 44264.7537 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 464.4052 | 0:240:120 | 0:00 | 0.1062 | 7 | 0.0021 | 0.1289 | 0.131 | 0.1299 | 0.0007 | 0 | 3 | 0.1062 | 0.1274 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4636 | 14147.231 | 44264.7538 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 473.6933 | 0:240:120 | 0:00 | 0.1037 | 7 | 0.0036 | 0.1251 | 0.1287 | 0.127 | 0.0012 | 0 | 3 | 0.1037 | 0.1245 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4639 | 14150.874 | 44264.7538 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 483.1672 | 0:240:120 | 0:00 | 0.1014 | 7 | 0.0015 | 0.1231 | 0.1246 | 0.124 | 0.0007 | 0 | 3 | 0.1014 | 0.1217 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4642 | 14154.309 | 44264.7538 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 492.8305 | 0:240:120 | 0:00 | 0.0991 | 7 | 0.0027 | 0.12 | 0.1227 | 0.1216 | 0.0011 | 0 | 3 | 0.0991 | 0.119 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4645 | 14157.821 | 44264.7539 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 502.6872 | 0:240:120 | 0:00 | 0.097 | 7 | 0.003 | 0.1171 | 0.1201 | 0.1186 | 0.001 | 0 | 3 | 0.097 | 0.1164 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4648 | 14161.314 | 44264.7539 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 512.7409 | 0:240:120 | 0:00 | 0.0949 | 7 | 0.0015 | 0.1152 | 0.1167 | 0.1158 | 0.0005 | 0 | 3 | 0.0949 | 0.1139 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4651 | 14164.693 | 44264.754 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 522.9957 | 0:240:120 | 0:00 | 0.0929 | 7 | 0.0031 | 0.1123 | 0.1154 | 0.1139 | 0.0011 | 0 | 3 | 0.0929 | 0.1115 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4654 | 14168.069 | 44264.754 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 533.4556 | 0:240:120 | 0:00 | 0.091 | 7 | 0.0031 | 0.1091 | 0.1122 | 0.1112 | 0.0011 | 0 | 3 | 0.091 | 0.1092 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4657 | 14171.453 | 44264.754 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 544.1247 | 0:240:120 | 0:00 | 0.0892 | 7 | 0.0035 | 0.1071 | 0.1106 | 0.1089 | 0.0012 | 0 | 3 | 0.0892 | 0.107 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4660 | 14175.184 | 44264.7541 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 555.0072 | 0:240:120 | 0:00 | 0.0874 | 7 | 0.0036 | 0.1053 | 0.1089 | 0.1071 | 0.0011 | 0 | 3 | 0.0874 | 0.1049 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4663 | 14178.577 | 44264.7541 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 566.1074 | 0:240:120 | 0:00 | 0.0858 | 7 | 0.0022 | 0.1032 | 0.1054 | 0.1044 | 0.0008 | 0 | 3 | 0.0858 | 0.1029 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4666 | 14181.983 | 44264.7542 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 577.4295 | 0:240:120 | 0:00 | 0.0841 | 7 | 0.0024 | 0.1015 | 0.1039 | 0.1029 | 0.0009 | 0 | 3 | 0.0841 | 0.101 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4669 | 14185.37 | 44264.7542 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 588.9781 | 0:240:120 | 0:00 | 0.0826 | 7 | 0.0027 | 0.0999 | 0.1026 | 0.1014 | 0.0008 | 0 | 3 | 0.0826 | 0.0991 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4672 | 14188.902 | 44264.7542 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 600.7577 | 0:240:120 | 0:00 | 0.0811 | 7 | 0.0017 | 0.0984 | 0.1001 | 0.0994 | 0.0007 | 0 | 3 | 0.0811 | 0.0973 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4675 | 14192.291 | 44264.7543 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 612.7728 | 0:240:120 | 0:00 | 0.0797 | 7 | 0.0032 | 0.0962 | 0.0994 | 0.0977 | 0.0012 | 0 | 3 | 0.0797 | 0.0956 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4678 | 14195.577 | 44264.7543 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 625.0283 | 0:240:120 | 0:00 | 0.0783 | 7 | 0.0017 | 0.0947 | 0.0964 | 0.0957 | 0.0006 | 0 | 3 | 0.0783 | 0.094 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4681 | 14199.008 | 44264.7544 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 637.5289 | 0:240:120 | 0:00 | 0.077 | 7 | 0.0036 | 0.0919 | 0.0955 | 0.0938 | 0.0012 | 0 | 3 | 0.077 | 0.0924 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4684 | 14202.398 | 44264.7544 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 650.2794 | 0:240:120 | 0:00 | 0.0757 | 7 | 0.0024 | 0.0911 | 0.0935 | 0.0924 | 0.0009 | 0 | 3 | 0.0757 | 0.0909 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4687 | 14205.793 | 44264.7544 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 663.285 | 0:240:120 | 0:00 | 0.0745 | 7 | 0.0027 | 0.089 | 0.0917 | 0.0909 | 0.0009 | 0 | 3 | 0.0745 | 0.0894 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4690 | 14209.188 | 44264.7545 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 676.5507 | 0:240:120 | 0:00 | 0.0734 | 7 | 0.0019 | 0.0882 | 0.0901 | 0.0892 | 0.0007 | 0 | 3 | 0.0734 | 0.088 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4693 | 14212.712 | 44264.7545 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 690.0817 | 0:240:120 | 0:00 | 0.0722 | 7 | 0.0029 | 0.0869 | 0.0898 | 0.0882 | 0.0009 | 0 | 3 | 0.0722 | 0.0867 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4696 | 14216.088 | 44264.7545 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 703.8834 | 0:240:120 | 0:00 | 0.0712 | 7 | 0.0023 | 0.0858 | 0.0881 | 0.0869 | 0.0008 | 0 | 3 | 0.0712 | 0.0854 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4699 | 14219.426 | 44264.7546 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 717.961 | 0:240:120 | 0:00 | 0.0701 | 7 | 0.0028 | 0.0837 | 0.0865 | 0.0853 | 0.0012 | 0 | 3 | 0.0701 | 0.0842 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4702 | 14222.819 | 44264.7546 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 732.3203 | 0:240:120 | 0:00 | 0.0692 | 7 | 0.002 | 0.0826 | 0.0846 | 0.0839 | 0.0007 | 0 | 3 | 0.0692 | 0.083 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4705 | 14226.199 | 44264.7547 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 746.9667 | 0:240:120 | 0:00 | 0.0682 | 7 | 0.003 | 0.0813 | 0.0843 | 0.0828 | 0.0011 | 0 | 3 | 0.0682 | 0.0818 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4708 | 14229.588 | 44264.7547 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 761.906 | 0:240:120 | 0:00 | 0.0673 | 7 | 0.0036 | 0.0799 | 0.0835 | 0.082 | 0.0011 | 0 | 3 | 0.0673 | 0.0808 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4711 | 14232.871 | 44264.7547 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 777.1441 | 0:240:120 | 0:00 | 0.0664 | 7 | 0.0028 | 0.0792 | 0.082 | 0.0808 | 0.0011 | 0 | 3 | 0.0664 | 0.0797 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4714 | 14236.263 | 44264.7548 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 792.687 | 0:240:120 | 0:00 | 0.0656 | 7 | 0.0021 | 0.0782 | 0.0803 | 0.0793 | 0.0008 | 0 | 3 | 0.0656 | 0.0787 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4717 | 14239.625 | 44264.7548 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 808.5407 | 0:240:120 | 0:00 | 0.0648 | 7 | 0.0029 | 0.0767 | 0.0796 | 0.0785 | 0.0011 | 0 | 3 | 0.0648 | 0.0777 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4720 | 14243.049 | 44264.7549 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 824.7116 | 0:240:120 | 0:00 | 0.064 | 7 | 0.0023 | 0.0763 | 0.0786 | 0.0778 | 0.0009 | 0 | 3 | 0.064 | 0.0768 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4723 | 14246.437 | 44264.7549 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 841.2058 | 0:240:120 | 0:00 | 0.0633 | 7 | 0.0031 | 0.0748 | 0.0779 | 0.0766 | 0.0012 | 0 | 3 | 0.0633 | 0.0759 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4726 | 14250.03 | 44264.7549 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 858.0299 | 0:240:120 | 0:00 | 0.0625 | 7 | 0.003 | 0.0736 | 0.0766 | 0.0756 | 0.0012 | 0 | 3 | 0.0625 | 0.075 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4729 | 14253.528 | 44264.755 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 875.1905 | 0:240:120 | 0:00 | 0.0619 | 7 | 0.0028 | 0.0731 | 0.0759 | 0.0748 | 0.0011 | 0 | 3 | 0.0619 | 0.0742 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4732 | 14256.913 | 44264.755 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 892.6943 | 0:240:120 | 0:00 | 0.0612 | 7 | 0.0021 | 0.0725 | 0.0746 | 0.0738 | 0.0008 | 0 | 3 | 0.0612 | 0.0734 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4735 | 14260.258 | 44264.7551 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 910.5482 | 0:240:120 | 0:00 | 0.0606 | 7 | 0.0027 | 0.072 | 0.0747 | 0.0731 | 0.0009 | 0 | 3 | 0.0606 | 0.0727 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4738 | 14263.63 | 44264.7551 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 928.7592 | 0:240:120 | 0:00 | 0.0599 | 7 | 0.0032 | 0.0708 | 0.074 | 0.0723 | 0.0012 | 0 | 3 | 0.0599 | 0.0719 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4741 | 14267.016 | 44264.7551 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 947.3343 | 0:240:120 | 0:00 | 0.0594 | 7 | 0.0034 | 0.0698 | 0.0732 | 0.0714 | 0.0012 | 0 | 3 | 0.0594 | 0.0712 | NP | NP | 0-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4744 | 14270.552 | 44264.7552 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 966.281 | 0:240:120 | 0:00 | 0.0588 | 7 | 0.003 | 0.069 | 0.072 | 0.0705 | 0.0011 | 0 | 3 | 0.0588 | 0.0706 | P | NP | 0-1-0-0-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4747 | 14274.077 | 44264.7552 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 985.6067 | 0:240:120 | 0:00 | 0.0583 | 7 | 0.0032 | 0.068 | 0.0712 | 0.07 | 0.0013 | 0 | 3 | 0.0583 | 0.0699 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4750 | 14277.931 | 44264.7553 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1005.3188 | 0:240:120 | 0:00 | 0.0577 | 7 | 0.0027 | 0.0679 | 0.0706 | 0.0693 | 0.0011 | 0 | 3 | 0.0577 | 0.0693 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4753 | 14281.45 | 44264.7553 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1025.4252 | 0:240:120 | 0:00 | 0.0572 | 7 | 0.0027 | 0.067 | 0.0697 | 0.0686 | 0.0009 | 0 | 3 | 0.0572 | 0.0687 | P | NP | 0-1-1-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4756 | 14284.845 | 44264.7553 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1045.9337 | 0:240:120 | 0:00 | 0.0568 | 7 | 0.0029 | 0.0663 | 0.0692 | 0.0675 | 0.001 | 0 | 3 | 0.0568 | 0.0681 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4759 | 14288.552 | 44264.7554 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1066.8523 | 0:240:120 | 0:00 | 0.0563 | 7 | 0.0029 | 0.0662 | 0.0691 | 0.0675 | 0.001 | 0 | 3 | 0.0563 | 0.0676 | P | NP | 0-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4762 | 14291.781 | 44264.7554 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1088.1894 | 0:240:120 | 0:00 | 0.0559 | 7 | 0.0037 | 0.0647 | 0.0684 | 0.0665 | 0.0013 | 0 | 3 | 0.0559 | 0.067 | P | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4765 | 14295.138 | 44264.7555 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1109.9532 | 0:240:120 | 0:00 | 0.0554 | 7 | 0.003 | 0.064 | 0.067 | 0.0658 | 0.0012 | 0 | 3 | 0.0554 | 0.0665 | P | NP | 1-1-1-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4768 | 14298.764 | 44264.7555 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1132.1522 | 0:240:120 | 0:00 | 0.055 | 7 | 0.004 | 0.0632 | 0.0672 | 0.0654 | 0.0014 | 0 | 3 | 0.055 | 0.066 | P | NP | 1-1-1-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4771 | 14302.701 | 44264.7556 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1154.7953 | 0:240:120 | 0:00 | 0.0546 | 7 | 0.0033 | 0.0631 | 0.0664 | 0.065 | 0.0014 | 0 | 3 | 0.0546 | 0.0656 | P | NP | 0-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4774 | 14306.056 | 44264.7556 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1177.8912 | 0:240:120 | 0:00 | 0.0543 | 7 | 0.0035 | 0.0624 | 0.0659 | 0.0644 | 0.0012 | 0 | 3 | 0.0543 | 0.0651 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4777 | 14309.39 | 44264.7556 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1201.449 | 0:240:120 | 0:00 | 0.0539 | 7 | 0.0042 | 0.062 | 0.0662 | 0.0644 | 0.0015 | 0 | 3 | 0.0539 | 0.0647 | P | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4780 | 14313.04 | 44264.7557 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1225.478 | 0:240:120 | 0:00 | 0.0536 | 7 | 0.0034 | 0.0615 | 0.0649 | 0.0634 | 0.0012 | 0 | 3 | 0.0536 | 0.0643 | P | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4783 | 14316.38 | 44264.7557 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1249.9876 | 0:240:120 | 0:00 | 0.0532 | 7 | 0.0032 | 0.061 | 0.0642 | 0.0628 | 0.0012 | 0 | 3 | 0.0532 | 0.0639 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4786 | 14319.785 | 44264.7557 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1274.9873 | 0:240:120 | 0:00 | 0.0529 | 7 | 0.0024 | 0.0611 | 0.0635 | 0.0622 | 0.0008 | 0 | 3 | 0.0529 | 0.0635 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4789 | 14323.16 | 44264.7558 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1300.487 | 0:240:120 | 0:00 | 0.0526 | 7 | 0.0024 | 0.0608 | 0.0632 | 0.0621 | 0.0009 | 0 | 3 | 0.0526 | 0.0631 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4792 | 14326.642 | 44264.7558 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1326.4968 | 0:240:120 | 0:00 | 0.0523 | 7 | 0.0022 | 0.0601 | 0.0623 | 0.0616 | 0.0008 | 0 | 3 | 0.0523 | 0.0628 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4795 | 14330.021 | 44264.7559 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1353.0267 | 0:240:120 | 0:00 | 0.052 | 7 | 0.003 | 0.0588 | 0.0618 | 0.0606 | 0.0011 | 0 | 3 | 0.052 | 0.0624 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4798 | 14333.439 | 44264.7559 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1380.0873 | 0:240:120 | 0:00 | 0.0517 | 7 | 0.0028 | 0.0592 | 0.062 | 0.0606 | 0.0009 | 0 | 3 | 0.0517 | 0.0621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4801 | 14336.797 | 44264.7559 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1407.689 | 0:240:120 | 0:00 | 0.0515 | 7 | 0.0029 | 0.0588 | 0.0617 | 0.0603 | 0.0009 | 0 | 3 | 0.0515 | 0.0618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4804 | 14340.186 | 44264.756 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1435.8428 | 0:240:120 | 0:00 | 0.0512 | 7 | 0.0035 | 0.0576 | 0.0611 | 0.0594 | 0.0012 | 0 | 3 | 0.0512 | 0.0615 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4807 | 14343.791 | 44264.756 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1464.5596 | 0:240:120 | 0:00 | 0.051 | 7 | 0.0021 | 0.0579 | 0.06 | 0.0592 | 0.0008 | 0 | 3 | 0.051 | 0.0612 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4810 | 14347.175 | 44264.7561 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1493.8508 | 0:240:120 | 0:00 | 0.0508 | 7 | 0.0029 | 0.0573 | 0.0602 | 0.0588 | 0.0012 | 0 | 3 | 0.0508 | 0.0609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4813 | 14350.527 | 44264.7561 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1523.7279 | 0:240:120 | 0:00 | 0.0505 | 7 | 0.0021 | 0.0574 | 0.0595 | 0.0586 | 0.0008 | 0 | 3 | 0.0505 | 0.0606 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4816 | 14354.051 | 44264.7561 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1554.2024 | 0:240:120 | 0:00 | 0.0503 | 7 | 0.0021 | 0.0569 | 0.059 | 0.058 | 0.0007 | 0 | 3 | 0.0503 | 0.0604 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4819 | 14357.557 | 44264.7562 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1585.2865 | 0:240:120 | 0:00 | 0.0501 | 7 | 0.0034 | 0.0563 | 0.0597 | 0.0583 | 0.0013 | 0 | 3 | 0.0501 | 0.0601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4822 | 14360.926 | 44264.7562 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1616.9922 | 0:240:120 | 0:00 | 0.0499 | 7 | 0.0039 | 0.0559 | 0.0598 | 0.058 | 0.0012 | 0 | 3 | 0.0499 | 0.0599 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4825 | 14364.436 | 44264.7563 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1649.332 | 0:240:120 | 0:00 | 0.0497 | 7 | 0.0014 | 0.0566 | 0.058 | 0.0575 | 0.0006 | 0 | 3 | 0.0497 | 0.0597 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4828 | 14367.824 | 44264.7563 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1682.3187 | 0:240:120 | 0:00 | 0.0495 | 7 | 0.0021 | 0.0556 | 0.0577 | 0.0569 | 0.0008 | 0 | 3 | 0.0495 | 0.0595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4831 | 14371.223 | 44264.7563 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1715.965 | 0:240:120 | 0:00 | 0.0494 | 7 | 0.0034 | 0.0547 | 0.0581 | 0.0567 | 0.0011 | 0 | 3 | 0.0494 | 0.0594 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4834 | 14374.465 | 44264.7564 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1750.2843 | 0:240:120 | 0:00 | 0.0492 | 7 | 0.0029 | 0.0547 | 0.0576 | 0.0569 | 0.001 | 0 | 3 | 0.0492 | 0.0592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4837 | 14378.112 | 44264.7564 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1785.29 | 0:240:120 | 0:00 | 0.049 | 7 | 0.0022 | 0.0555 | 0.0577 | 0.0566 | 0.0008 | 0 | 3 | 0.049 | 0.059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4840 | 14381.399 | 44264.7565 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1820.9958 | 0:240:120 | 0:00 | 0.0489 | 7 | 0.0029 | 0.0548 | 0.0577 | 0.0565 | 0.001 | 0 | 3 | 0.0489 | 0.0589 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4843 | 14384.906 | 44264.7565 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1857.4157 | 0:240:120 | 0:00 | 0.0487 | 7 | 0.0028 | 0.0544 | 0.0572 | 0.056 | 0.0009 | 0 | 3 | 0.0487 | 0.0587 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4846 | 14388.172 | 44264.7565 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1894.5641 | 0:240:120 | 0:00 | 0.0486 | 7 | 0.0022 | 0.0542 | 0.0564 | 0.0554 | 0.0007 | 0 | 3 | 0.0486 | 0.0586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4849 | 14391.444 | 44264.7566 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1932.4553 | 0:240:120 | 0:00 | 0.0484 | 7 | 0.0024 | 0.0543 | 0.0567 | 0.0555 | 0.0009 | 0 | 3 | 0.0484 | 0.0584 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4852 | 14394.967 | 44264.7566 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1971.1045 | 0:240:120 | 0:00 | 0.0483 | 7 | 0.0025 | 0.0537 | 0.0562 | 0.0552 | 0.0009 | 0 | 3 | 0.0483 | 0.0583 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4855 | 14398.362 | 44264.7567 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2010.5265 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0025 | 0.0537 | 0.0562 | 0.0554 | 0.0009 | 0 | 3 | 0.0482 | 0.0582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4858 | 14401.711 | 44264.7567 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2050.7371 | 0:240:120 | 0:00 | 0.048 | 7 | 0.0021 | 0.0541 | 0.0562 | 0.0551 | 0.0007 | 0 | 3 | 0.048 | 0.058 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4861 | 14405.188 | 44264.7567 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2091.7518 | 0:240:120 | 0:00 | 0.0479 | 7 | 0.0028 | 0.0527 | 0.0555 | 0.0543 | 0.0012 | 0 | 3 | 0.0479 | 0.0579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4864 | 14408.813 | 44264.7568 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2133.5868 | 0:240:120 | 0:00 | 0.0478 | 7 | 0.0016 | 0.053 | 0.0546 | 0.0538 | 0.0006 | 0 | 3 | 0.0478 | 0.0578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4867 | 14412.209 | 44264.7568 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2176.2586 | 0:240:120 | 0:00 | 0.0477 | 7 | 0.0023 | 0.0528 | 0.0551 | 0.0539 | 0.0008 | 0 | 3 | 0.0477 | 0.0577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4870 | 14415.472 | 44264.7569 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2219.7838 | 0:240:120 | 0:00 | 0.0476 | 7 | 0.0028 | 0.0525 | 0.0553 | 0.0538 | 0.0007 | 0 | 3 | 0.0476 | 0.0576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4873 | 14418.987 | 44264.7569 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2264.1794 | 0:240:120 | 0:00 | 0.0475 | 7 | 0.0021 | 0.0522 | 0.0543 | 0.0534 | 0.0007 | 0 | 3 | 0.0475 | 0.0575 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4876 | 14422.34 | 44264.7569 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2309.463 | 0:240:120 | 0:00 | 0.0474 | 7 | 0.0034 | 0.0522 | 0.0556 | 0.0539 | 0.0011 | 0 | 3 | 0.0474 | 0.0574 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4879 | 14425.719 | 44264.757 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2355.6523 | 0:240:120 | 0:00 | 0.0473 | 7 | 0.0023 | 0.0524 | 0.0547 | 0.0535 | 0.0008 | 0 | 3 | 0.0473 | 0.0573 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4882 | 14429.097 | 44264.757 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2402.7653 | 0:240:120 | 0:00 | 0.0472 | 7 | 0.0034 | 0.0511 | 0.0545 | 0.053 | 0.0012 | 0 | 3 | 0.0472 | 0.0572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4885 | 14432.475 | 44264.7571 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2450.8206 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0027 | 0.0514 | 0.0541 | 0.0529 | 0.0008 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4888 | 14435.757 | 44264.7571 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2499.837 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0038 | 0.0509 | 0.0547 | 0.0529 | 0.0013 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4891 | 14439.093 | 44264.7571 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2549.8338 | 0:240:120 | 0:00 | 0.047 | 7 | 0.0032 | 0.051 | 0.0542 | 0.0527 | 0.0012 | 0 | 3 | 0.047 | 0.057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4894 | 14442.486 | 44264.7572 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2600.8305 | 0:240:120 | 0:00 | 0.0469 | 7 | 0.004 | 0.0506 | 0.0546 | 0.0527 | 0.0013 | 0 | 3 | 0.0469 | 0.0569 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4897 | 14446.064 | 44264.7572 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2652.8471 | 0:240:120 | 0:00 | 0.0468 | 7 | 0.0021 | 0.0512 | 0.0533 | 0.0527 | 0.0009 | 0 | 3 | 0.0468 | 0.0568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4900 | 14449.55 | 44264.7573 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2705.904 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0028 | 0.0511 | 0.0539 | 0.0525 | 0.001 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4903 | 14452.968 | 44264.7573 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2760.0221 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0032 | 0.0512 | 0.0544 | 0.0526 | 0.0012 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4906 | 14456.33 | 44264.7573 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2815.2225 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.0031 | 0.0509 | 0.054 | 0.0524 | 0.001 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4909 | 14459.629 | 44264.7574 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2871.527 | 0:240:120 | 0:00 | 0.0466 | 7 | 0.0045 | 0.05 | 0.0545 | 0.0524 | 0.0015 | 0 | 3 | 0.0466 | 0.0566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4912 | 14462.978 | 44264.7574 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2928.9575 | 0:240:120 | 0:00 | 0.0465 | 7 | 0.0045 | 0.0501 | 0.0546 | 0.0524 | 0.0015 | 0 | 3 | 0.0465 | 0.0565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4915 | 14466.36 | 44264.7574 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2987.5367 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.003 | 0.0508 | 0.0538 | 0.052 | 0.001 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4918 | 14469.975 | 44264.7575 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3047.2874 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0037 | 0.0508 | 0.0545 | 0.052 | 0.0011 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4921 | 14473.345 | 44264.7575 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3108.2332 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0026 | 0.0506 | 0.0532 | 0.052 | 0.001 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4924 | 14476.831 | 44264.7576 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3170.3978 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0038 | 0.0507 | 0.0545 | 0.0521 | 0.0012 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4927 | 14480.302 | 44264.7576 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3233.8058 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0048 | 0.0497 | 0.0545 | 0.0518 | 0.0017 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4930 | 14483.842 | 44264.7576 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3298.4819 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0046 | 0.05 | 0.0546 | 0.0518 | 0.0015 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4933 | 14487.112 | 44264.7577 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3364.4515 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0025 | 0.0505 | 0.053 | 0.0515 | 0.0008 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4936 | 14490.468 | 44264.7577 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3431.7406 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0044 | 0.0492 | 0.0536 | 0.0516 | 0.0015 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4939 | 14493.878 | 44264.7578 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3500.3754 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0034 | 0.0495 | 0.0529 | 0.0514 | 0.0011 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4942 | 14497.151 | 44264.7578 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3570.3829 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0038 | 0.0499 | 0.0537 | 0.0514 | 0.0013 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4945 | 14500.685 | 44264.7578 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3641.7905 | 0:240:120 | 0:00 | 0.046 | 7 | 0.0048 | 0.049 | 0.0538 | 0.0515 | 0.0015 | 0 | 3 | 0.046 | 0.056 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4948 | 14503.924 | 44264.7579 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3714.6264 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0038 | 0.0499 | 0.0537 | 0.0513 | 0.0012 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4951 | 14507.658 | 44264.7579 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3788.9189 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0023 | 0.0499 | 0.0522 | 0.0512 | 0.0007 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4954 | 14511.293 | 44264.758 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3864.6973 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0042 | 0.0495 | 0.0537 | 0.0513 | 0.0014 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4957 | 14514.897 | 44264.758 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3941.9912 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0026 | 0.0504 | 0.053 | 0.0513 | 0.0009 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4960 | 14518.206 | 44264.758 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4020.831 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0045 | 0.0489 | 0.0534 | 0.051 | 0.0018 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4963 | 14521.604 | 44264.7581 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4101.2476 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0041 | 0.0488 | 0.0529 | 0.0509 | 0.0014 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4966 | 14525.008 | 44264.7581 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4183.2726 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0041 | 0.0494 | 0.0535 | 0.051 | 0.0013 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4969 | 14528.277 | 44264.7582 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4266.938 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.003 | 0.0501 | 0.0531 | 0.0512 | 0.0011 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4972 | 14531.656 | 44264.7582 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4352.2768 | 0:240:120 | 0:00 | 0.0457 | 7 | 0.0042 | 0.0489 | 0.0531 | 0.051 | 0.0014 | 0 | 3 | 0.0457 | 0.0557 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4975 | 14534.955 | 44264.7582 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4439.3223 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0034 | 0.0492 | 0.0526 | 0.051 | 0.0011 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4978 | 14538.213 | 44264.7583 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4528.1088 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0028 | 0.0497 | 0.0525 | 0.0508 | 0.0012 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4981 | 14541.368 | 44264.7583 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4618.671 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0042 | 0.0493 | 0.0535 | 0.0507 | 0.0012 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4984 | 14544.952 | 44264.7584 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4711.0444 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0043 | 0.0492 | 0.0535 | 0.0511 | 0.0018 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4987 | 14548.326 | 44264.7584 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4805.2653 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0039 | 0.049 | 0.0529 | 0.0508 | 0.0013 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4990 | 14551.795 | 44264.7584 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4901.3706 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0031 | 0.0489 | 0.052 | 0.0506 | 0.0011 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4993 | 14555.187 | 44264.7585 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4999.398 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.003 | 0.0498 | 0.0528 | 0.051 | 0.001 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4996 | 14558.568 | 44264.7585 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5099.386 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0041 | 0.0493 | 0.0534 | 0.0509 | 0.0012 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4999 | 14561.813 | 44264.7586 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5201.3737 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.002 | 0.0493 | 0.0513 | 0.0505 | 0.0007 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5002 | 14565.119 | 44264.7586 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5305.4011 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0039 | 0.049 | 0.0529 | 0.0506 | 0.0012 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5005 | 14568.652 | 44264.7586 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5411.5092 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0032 | 0.0486 | 0.0518 | 0.0504 | 0.0012 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5008 | 14572.038 | 44264.7587 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5519.7394 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0045 | 0.0489 | 0.0534 | 0.0504 | 0.0016 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5011 | 14575.29 | 44264.7587 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5630.1341 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0034 | 0.0492 | 0.0526 | 0.0505 | 0.0012 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5014 | 14578.573 | 44264.7587 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5742.7368 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0043 | 0.0488 | 0.0531 | 0.0507 | 0.0014 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5017 | 14581.965 | 44264.7588 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5857.5916 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0046 | 0.0478 | 0.0524 | 0.0502 | 0.0016 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5020 | 14585.254 | 44264.7588 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5974.7434 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0044 | 0.0476 | 0.052 | 0.0501 | 0.0014 | 0 | 3 | 0.0454 | 0.0554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5023 | 14588.893 | 44264.7589 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6094.2383 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0029 | 0.0482 | 0.0511 | 0.0499 | 0.0012 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5026 | 14592.246 | 44264.7589 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6216.123 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0026 | 0.0492 | 0.0518 | 0.0501 | 0.0011 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5029 | 14595.534 | 44264.7589 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6340.4455 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0051 | 0.0475 | 0.0526 | 0.0504 | 0.0015 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5032 | 14599.25 | 44264.759 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6467.2544 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0042 | 0.0475 | 0.0517 | 0.0498 | 0.0013 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5035 | 14602.625 | 44264.759 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6596.5995 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0052 | 0.0474 | 0.0526 | 0.0498 | 0.0017 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5038 | 14605.896 | 44264.7591 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6728.5315 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0035 | 0.0486 | 0.0521 | 0.05 | 0.0014 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5041 | 14609.243 | 44264.7591 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6863.1021 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0043 | 0.0482 | 0.0525 | 0.0498 | 0.0014 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5044 | 14612.407 | 44264.7591 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7000.3641 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0052 | 0.0474 | 0.0526 | 0.0497 | 0.0016 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5047 | 14615.687 | 44264.7592 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7140.3714 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0042 | 0.0477 | 0.0519 | 0.0496 | 0.0014 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5050 | 14619.085 | 44264.7592 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7283.1789 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0028 | 0.048 | 0.0508 | 0.0494 | 0.0011 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5053 | 14622.459 | 44264.7593 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7428.8424 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0051 | 0.0474 | 0.0525 | 0.0496 | 0.0017 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5056 | 14625.847 | 44264.7593 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7577.4193 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0033 | 0.0483 | 0.0516 | 0.0498 | 0.0014 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5059 | 14629.24 | 44264.7593 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7728.9677 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0041 | 0.048 | 0.0521 | 0.0497 | 0.0014 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5062 | 14632.628 | 44264.7594 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7883.547 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0033 | 0.0479 | 0.0512 | 0.0495 | 0.0013 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5065 | 14636.487 | 44264.7594 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8041.218 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.004 | 0.0476 | 0.0516 | 0.0493 | 0.0012 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5068 | 14639.883 | 44264.7595 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8202.0423 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0043 | 0.0476 | 0.0519 | 0.0495 | 0.0014 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5071 | 14643.236 | 44264.7595 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8366.0832 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.004 | 0.0472 | 0.0512 | 0.0493 | 0.0013 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5074 | 14646.64 | 44264.7595 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8533.4048 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0052 | 0.0473 | 0.0525 | 0.0495 | 0.0015 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5077 | 14650.161 | 44264.7596 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8704.0729 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0038 | 0.0477 | 0.0515 | 0.049 | 0.0012 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5080 | 14653.466 | 44264.7596 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8878.1544 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0036 | 0.0483 | 0.0519 | 0.0496 | 0.0011 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5083 | 14656.757 | 44264.7596 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9055.7175 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0031 | 0.0476 | 0.0507 | 0.0491 | 0.001 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5086 | 14660.832 | 44264.7597 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9236.8318 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0026 | 0.0478 | 0.0504 | 0.0492 | 0.001 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5089 | 14664.028 | 44264.7597 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9421.5685 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.0481 | 0.0504 | 0.0491 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5092 | 14667.397 | 44264.7598 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9609.9998 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.003 | 0.0476 | 0.0506 | 0.0493 | 0.0012 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5095 | 14670.682 | 44264.7598 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9802.1998 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0034 | 0.0474 | 0.0508 | 0.0489 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5098 | 14673.949 | 44264.7598 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9998.2438 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0028 | 0.0475 | 0.0503 | 0.0494 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5101 | 14677.437 | 44264.7599 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10198.2087 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0026 | 0.048 | 0.0506 | 0.0492 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5104 | 14680.708 | 44264.7599 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10402.1729 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0027 | 0.0478 | 0.0505 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5107 | 14684.097 | 44264.76 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10610.2163 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0028 | 0.0474 | 0.0502 | 0.049 | 0.0011 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5110 | 14687.476 | 44264.76 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10822.4207 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0027 | 0.0476 | 0.0503 | 0.0492 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5113 | 14690.752 | 44264.76 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11038.8691 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0025 | 0.048 | 0.0505 | 0.0491 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5116 | 14694.148 | 44264.7601 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11259.6465 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0029 | 0.0471 | 0.05 | 0.0488 | 0.0009 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5119 | 14697.441 | 44264.7601 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11484.8394 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0031 | 0.0471 | 0.0502 | 0.0491 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5122 | 14700.83 | 44264.7602 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11714.5362 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0033 | 0.0471 | 0.0504 | 0.0491 | 0.001 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5125 | 14704.11 | 44264.7602 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11948.8269 | 0:240:120 | 0:00 | 0.0451 | 7 | 0.0023 | 0.0479 | 0.0502 | 0.049 | 0.0008 | 0 | 3 | 0.0451 | 0.0551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5128 | 14754.339 | 44264.7608 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.5 | 0:240:120 | 0:00 | 5.9812 | 7 | 16.3773 | 36.5844 | 52.9617 | 41.1222 | 6.7186 | 45.1399 | 3 | 5.9812 | 24.1703 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5131 | 14894.406 | 44264.7624 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.3 | 0:240:120 | 0:00 | 5.1804 | 7 | 17.0582 | 18.5894 | 35.6476 | 24.4069 | 7.9446 | 63.1168 | 3 | 5.1804 | 15.9869 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5134 | 14979.293 | 44264.7634 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.2 | 0:240:120 | 0:00 | 4.5292 | 7 | 3.0325 | 9.0917 | 12.1242 | 9.9476 | 1.2963 | 1.6805 | 3 | 4.5292 | 11.7228 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5137 | 15014.312 | 44264.7638 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.1 | 0:240:120 | 0:00 | 4.0157 | 7 | 0.5133 | 8.0919 | 8.6052 | 8.2635 | 0.2542 | 0.0646 | 3 | 4.0157 | 9.2198 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5140 | 15041.85 | 44264.7641 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.1 | 0:240:120 | 0:00 | 3.5809 | 7 | 0.5063 | 7.0909 | 7.5972 | 7.2618 | 0.2512 | 0.0631 | 3 | 3.5809 | 7.5033 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5143 | 15066.304 | 44264.7644 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.1 | 0:240:120 | 0:00 | 3.2256 | 7 | 0.9711 | 5.6311 | 6.6022 | 6.0532 | 0.4277 | 0.1829 | 3 | 3.2256 | 6.3079 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5146 | 15087.409 | 44264.7646 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.1 | 0:240:120 | 0:00 | 2.93 | 7 | 0.7146 | 4.606 | 5.3206 | 4.8432 | 0.3513 | 0.1234 | 3 | 2.93 | 5.4281 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5149 | 15105.244 | 44264.7648 | Vista Coord | Main | 80Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.2 | 0:240:120 | 0:00 | 2.6688 | 7 | 0.1698 | 4.275 | 4.4448 | 4.3327 | 0.0838 | 0.007 | 3 | 2.6688 | 4.7242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5152 | 15217.665 | 44264.7661 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.0036 | 90.5761 | 99.5797 | 93.5778 | 4.4998 | 20.2484 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5155 | 15510.339 | 44264.7695 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.32 | 0:240:120 | 0:00 | 8.4057 | 7 | 9.9529 | 80.623 | 90.5759 | 84.3142 | 4.708 | 22.1649 | 3 | 8.4057 | 531.4604 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5158 | 15766.847 | 44264.7725 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.52 | 0:240:120 | 0:00 | 6.9731 | 7 | 11.1046 | 61.4751 | 72.5797 | 65.9211 | 5.0597 | 25.601 | 3 | 6.9731 | 45.6758 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5161 | 15969.325 | 44264.7748 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 115.72 | 0:240:120 | 0:00 | 5.9428 | 7 | 11.8577 | 42.7244 | 54.5821 | 47.8143 | 5.168 | 26.7081 | 3 | 5.9428 | 23.6632 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5164 | 16090.803 | 44264.7762 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121 | 0:240:120 | 0:00 | 4.3544 | 7 | 0.5019 | 9.0881 | 9.59 | 9.2568 | 0.2491 | 0.0621 | 3 | 4.3544 | 10.8023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5167 | 16121.654 | 44264.7766 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 122.5796 | 0:240:120 | 0:00 | 4.0245 | 7 | 0.7675 | 8.0953 | 8.8628 | 8.3583 | 0.3417 | 0.1167 | 3 | 4.0245 | 9.2579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5170 | 16148.729 | 44264.7769 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 127.006 | 0:240:120 | 0:00 | 3.3074 | 7 | 0.6292 | 6.1031 | 6.7323 | 6.3019 | 0.2922 | 0.0854 | 3 | 3.3074 | 6.5687 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5173 | 16169.381 | 44264.7772 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.2507 | 0:240:120 | 0:00 | 2.6237 | 7 | 0.3113 | 4.133 | 4.4443 | 4.2832 | 0.1304 | 0.017 | 3 | 2.6237 | 4.609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5176 | 16184.543 | 44264.7773 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.4966 | 0:240:120 | 0:00 | 2.2233 | 7 | 0.1829 | 3.4403 | 3.6232 | 3.5059 | 0.0872 | 0.0076 | 3 | 2.2233 | 3.6572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5179 | 16197.265 | 44264.7775 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.06 | 0:240:120 | 0:00 | 1.7226 | 7 | 0.0826 | 2.47 | 2.5526 | 2.4983 | 0.0407 | 0.0017 | 3 | 1.7226 | 2.6234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5182 | 16207.118 | 44264.7776 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 155.3409 | 0:240:120 | 0:00 | 1.4603 | 7 | 0.0862 | 1.9995 | 2.0857 | 2.0295 | 0.041 | 0.0017 | 3 | 1.4603 | 2.1401 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5185 | 16215.352 | 44264.7777 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 173.1466 | 0:240:120 | 0:00 | 1.046 | 7 | 0.0338 | 1.373 | 1.4068 | 1.3851 | 0.0159 | 0.0003 | 3 | 1.046 | 1.4452 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5188 | 16222.059 | 44264.7778 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 190.1955 | 0:240:120 | 0:00 | 0.8091 | 7 | 0.0319 | 1.0358 | 1.0677 | 1.0469 | 0.0151 | 0.0002 | 3 | 0.8091 | 1.0812 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5191 | 16227.835 | 44264.7778 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 205.678 | 0:240:120 | 0:00 | 0.6641 | 7 | 0.0147 | 0.8366 | 0.8513 | 0.8425 | 0.0065 | 0 | 3 | 0.6641 | 0.8692 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5194 | 16232.954 | 44264.7779 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 224.5188 | 0:240:120 | 0:00 | 0.5399 | 7 | 0.0103 | 0.6758 | 0.6861 | 0.68 | 0.0044 | 0 | 3 | 0.5399 | 0.6937 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5197 | 16237.476 | 44264.7779 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 242.5434 | 0:240:120 | 0:00 | 0.4546 | 7 | 0.0075 | 0.5644 | 0.5719 | 0.5674 | 0.0033 | 0 | 3 | 0.4546 | 0.5762 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5200 | 16242.01 | 44264.778 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 262.194 | 0:240:120 | 0:00 | 0.3855 | 7 | 0.0057 | 0.4754 | 0.4811 | 0.4777 | 0.0024 | 0 | 3 | 0.3855 | 0.4828 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5203 | 16246.227 | 44264.778 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 295.314 | 0:240:120 | 0:00 | 0.304 | 7 | 0.0039 | 0.3726 | 0.3765 | 0.3748 | 0.0015 | 0 | 3 | 0.304 | 0.3748 | P | NP | 0-1-0-0-1-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5206 | 16250.048 | 44264.7781 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 329.508 | 0:240:120 | 0:00 | 0.2479 | 7 | 0.0041 | 0.3034 | 0.3075 | 0.3049 | 0.0017 | 0 | 3 | 0.2479 | 0.3016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5209 | 16253.697 | 44264.7781 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 372.294 | 0:240:120 | 0:00 | 0.2005 | 7 | 0.0033 | 0.2437 | 0.247 | 0.2451 | 0.0012 | 0 | 3 | 0.2005 | 0.2406 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5212 | 16257.383 | 44264.7782 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 408.526 | 0:240:120 | 0:00 | 0.1725 | 7 | 0.0039 | 0.2109 | 0.2148 | 0.2123 | 0.0012 | 0 | 3 | 0.1725 | 0.207 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5215 | 16260.819 | 44264.7782 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 445.484 | 0:240:120 | 0:00 | 0.1511 | 7 | 0.0024 | 0.1845 | 0.1869 | 0.1855 | 0.0009 | 0 | 3 | 0.1511 | 0.1814 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5218 | 16264.043 | 44264.7783 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 497.586 | 0:240:120 | 0:00 | 0.1292 | 7 | 0.0028 | 0.1572 | 0.16 | 0.1582 | 0.0009 | 0 | 3 | 0.1292 | 0.155 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5221 | 16267.316 | 44264.7783 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 552.312 | 0:240:120 | 0:00 | 0.1128 | 7 | 0.0032 | 0.1365 | 0.1397 | 0.138 | 0.001 | 0 | 3 | 0.1128 | 0.1353 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5224 | 16270.511 | 44264.7783 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 620.783 | 0:240:120 | 0:00 | 0.0983 | 7 | 0.0029 | 0.1193 | 0.1222 | 0.1207 | 0.0012 | 0 | 3 | 0.0983 | 0.1179 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5227 | 16273.641 | 44264.7784 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 681.907 | 0:240:120 | 0:00 | 0.089 | 7 | 0.003 | 0.1076 | 0.1106 | 0.109 | 0.0009 | 0 | 3 | 0.089 | 0.1067 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5230 | 16276.539 | 44264.7784 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 775.292 | 0:240:120 | 0:00 | 0.0788 | 7 | 0.0032 | 0.0943 | 0.0975 | 0.0963 | 0.0012 | 0 | 3 | 0.0788 | 0.0946 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5233 | 16279.445 | 44264.7784 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 870.496 | 0:240:120 | 0:00 | 0.0717 | 7 | 0.0013 | 0.0867 | 0.088 | 0.0875 | 0.0006 | 0 | 3 | 0.0717 | 0.0861 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5236 | 16282.312 | 44264.7785 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 973.32 | 0:240:120 | 0:00 | 0.0663 | 7 | 0.0025 | 0.0797 | 0.0822 | 0.0809 | 0.0008 | 0 | 3 | 0.0663 | 0.0796 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5239 | 16285.429 | 44264.7785 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1098.559 | 0:240:120 | 0:00 | 0.0617 | 7 | 0.0035 | 0.0726 | 0.0761 | 0.0746 | 0.001 | 0 | 3 | 0.0617 | 0.0741 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5242 | 16288.517 | 44264.7785 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1254.226 | 0:240:120 | 0:00 | 0.0578 | 7 | 0.0028 | 0.0679 | 0.0707 | 0.0695 | 0.001 | 0 | 3 | 0.0578 | 0.0694 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5245 | 16291.444 | 44264.7786 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1384.928 | 0:240:120 | 0:00 | 0.0555 | 7 | 0.0018 | 0.0649 | 0.0667 | 0.0659 | 0.0007 | 0 | 3 | 0.0555 | 0.0666 | P | NP | 1-1-1-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5248 | 16294.242 | 44264.7786 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1514.954 | 0:240:120 | 0:00 | 0.0538 | 7 | 0.0031 | 0.062 | 0.0651 | 0.0636 | 0.0012 | 0 | 3 | 0.0538 | 0.0645 | P | NP | 0-1-0-0-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5251 | 16297.192 | 44264.7786 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1639.988 | 0:240:120 | 0:00 | 0.0525 | 7 | 0.0032 | 0.0598 | 0.063 | 0.0617 | 0.001 | 0 | 3 | 0.0525 | 0.063 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5254 | 16300.233 | 44264.7787 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1756.91 | 0:240:120 | 0:00 | 0.0515 | 7 | 0.0016 | 0.0595 | 0.0611 | 0.0605 | 0.0007 | 0 | 3 | 0.0515 | 0.0618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5257 | 16303.239 | 44264.7787 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1880.207 | 0:240:120 | 0:00 | 0.0507 | 7 | 0.0029 | 0.0578 | 0.0607 | 0.0592 | 0.0011 | 0 | 3 | 0.0507 | 0.0608 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5260 | 16306.225 | 44264.7787 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1999.598 | 0:240:120 | 0:00 | 0.05 | 7 | 0.0019 | 0.0571 | 0.059 | 0.0581 | 0.0006 | 0 | 3 | 0.05 | 0.06 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5263 | 16309.231 | 44264.7788 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2100.108 | 0:240:120 | 0:00 | 0.0495 | 7 | 0.0025 | 0.0553 | 0.0578 | 0.0569 | 0.0009 | 0 | 3 | 0.0495 | 0.0595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5266 | 16312.109 | 44264.7788 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2212.586 | 0:240:120 | 0:00 | 0.0491 | 7 | 0.0014 | 0.0558 | 0.0572 | 0.0566 | 0.0006 | 0 | 3 | 0.0491 | 0.0591 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5269 | 16315.114 | 44264.7788 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2285.327 | 0:240:120 | 0:00 | 0.0488 | 7 | 0.0026 | 0.0552 | 0.0578 | 0.0565 | 0.0008 | 0 | 3 | 0.0488 | 0.0588 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5272 | 16318.086 | 44264.7789 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2397.696 | 0:240:120 | 0:00 | 0.0485 | 7 | 0.0026 | 0.0541 | 0.0567 | 0.0555 | 0.0008 | 0 | 3 | 0.0485 | 0.0585 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5275 | 16321.076 | 44264.7789 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4126.571 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0042 | 0.0495 | 0.0537 | 0.0517 | 0.0015 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5278 | 16324.007 | 44264.7789 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5004.905 | 0:240:120 | 0:00 | 0.0458 | 7 | 0.0034 | 0.0495 | 0.0529 | 0.0513 | 0.001 | 0 | 3 | 0.0458 | 0.0558 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5281 | 16326.898 | 44264.779 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6001.441 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0036 | 0.0488 | 0.0524 | 0.0507 | 0.0012 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5284 | 16329.991 | 44264.779 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7565.874 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0042 | 0.0477 | 0.0519 | 0.0502 | 0.0011 | 0 | 3 | 0.0453 | 0.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5287 | 16332.864 | 44264.779 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9528.171 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0035 | 0.0482 | 0.0517 | 0.0495 | 0.0012 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5290 | 16399.224 | 44264.7798 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.6 | 0:240:120 | 0:00 | 6.4283 | 7 | 10.7322 | 52.8488 | 63.581 | 57.0906 | 4.8914 | 23.9254 | 3 | 6.4283 | 31.3999 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5293 | 16556.627 | 44264.7816 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.4 | 0:240:120 | 0:00 | 5.0219 | 7 | 9.0177 | 18.5822 | 27.5999 | 21.5916 | 4.5017 | 20.2652 | 3 | 5.0219 | 14.8048 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5296 | 16623.584 | 44264.7824 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.8 | 0:240:120 | 0:00 | 4.1813 | 7 | 0.5001 | 8.5906 | 9.0907 | 8.7584 | 0.2489 | 0.062 | 3 | 4.1813 | 9.963 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5299 | 16652.056 | 44264.7827 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.8 | 0:240:120 | 0:00 | 3.6324 | 7 | 0.5826 | 7.0999 | 7.6825 | 7.317 | 0.2705 | 0.0732 | 3 | 3.6324 | 7.6909 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5302 | 16675.573 | 44264.783 | Vista Coord | Main | 100Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.1 | 0:240:120 | 0:00 | 2.9327 | 7 | 0.9617 | 4.6076 | 5.5693 | 5.0188 | 0.4252 | 0.1808 | 3 | 2.9327 | 5.4357 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5305 | 16790.237 | 44264.7843 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.007 | 90.5709 | 99.5779 | 93.5762 | 4.5003 | 20.2523 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5308 | 17082.684 | 44264.7877 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.32 | 0:240:120 | 0:00 | 8.762 | 7 | 9.0007 | 81.5761 | 90.5768 | 84.7044 | 4.4069 | 19.4209 | 3 | 8.762 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5311 | 17357.226 | 44264.7909 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.98 | 0:240:120 | 0:00 | 8.4057 | 7 | 9.0023 | 81.577 | 90.5793 | 84.5783 | 4.4995 | 20.2454 | 3 | 8.4057 | 531.4604 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5314 | 17622.667 | 44264.794 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 168.3 | 0:240:120 | 0:00 | 7.7705 | 7 | 9.0024 | 72.574 | 81.5764 | 75.5766 | 4.4986 | 20.2378 | 3 | 7.7705 | 101.5883 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5317 | 17852.406 | 44264.7966 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.83 | 0:240:120 | 0:00 | 6.7786 | 7 | 9.2818 | 54.6965 | 63.9783 | 60.7208 | 4.4358 | 19.6765 | 3 | 6.7786 | 39.5832 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5320 | 18037.528 | 44264.7988 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 172.7 | 0:240:120 | 0:00 | 6.1881 | 7 | 9.0004 | 45.5835 | 54.5839 | 49.3978 | 4.1129 | 16.9161 | 3 | 6.1881 | 27.1782 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5323 | 18185.047 | 44264.8005 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 177.1 | 0:240:120 | 0:00 | 5.1215 | 7 | 8.8204 | 27.0958 | 35.9162 | 30.2087 | 4.1495 | 17.2187 | 3 | 5.1215 | 15.5346 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5326 | 18275.453 | 44264.8015 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 180.4 | 0:240:120 | 0:00 | 4.5252 | 7 | 6.5052 | 9.4765 | 15.9817 | 11.6154 | 3.102 | 9.6221 | 3 | 4.5252 | 11.7007 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5329 | 18318.664 | 44264.802 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.5427 | 0:240:120 | 0:00 | 4.0672 | 7 | 0.5049 | 8.5865 | 9.0914 | 8.7575 | 0.2498 | 0.0624 | 3 | 4.0672 | 9.445 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5332 | 18346.098 | 44264.8024 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 190.7642 | 0:240:120 | 0:00 | 3.2845 | 7 | 0.4981 | 6.1029 | 6.601 | 6.315 | 0.2244 | 0.0504 | 3 | 3.2845 | 6.495 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5335 | 18366.406 | 44264.8026 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 199.9294 | 0:240:120 | 0:00 | 2.6206 | 7 | 0.1687 | 4.2759 | 4.4446 | 4.3326 | 0.0828 | 0.0069 | 3 | 2.6206 | 4.601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5338 | 18381.454 | 44264.8028 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.8812 | 0:240:120 | 0:00 | 2.1745 | 7 | 0.1651 | 3.2912 | 3.4563 | 3.3498 | 0.0795 | 0.0063 | 3 | 2.1745 | 3.5493 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5341 | 18394.02 | 44264.8029 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 216.4217 | 0:240:120 | 0:00 | 1.8939 | 7 | 0.1035 | 2.7567 | 2.8602 | 2.8046 | 0.0349 | 0.0012 | 3 | 1.8939 | 2.9597 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5344 | 18405.23 | 44264.803 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 226.1116 | 0:240:120 | 0:00 | 1.617 | 7 | 0.0875 | 2.2992 | 2.3867 | 2.3313 | 0.0394 | 0.0016 | 3 | 1.617 | 2.4244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5347 | 18414.783 | 44264.8031 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 236.5 | 0:240:120 | 0:00 | 1.391 | 7 | 0.0489 | 1.9027 | 1.9516 | 1.9302 | 0.0217 | 0.0005 | 3 | 1.391 | 2.0182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5350 | 18422.955 | 44264.8032 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 248.622 | 0:240:120 | 0:00 | 1.1897 | 7 | 0.0353 | 1.5958 | 1.6311 | 1.6083 | 0.0162 | 0.0003 | 3 | 1.1897 | 1.6773 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5353 | 18430.422 | 44264.8033 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 262.9 | 0:240:120 | 0:00 | 1.0103 | 7 | 0.0239 | 1.3192 | 1.3431 | 1.3289 | 0.0104 | 0.0001 | 3 | 1.0103 | 1.3889 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5356 | 18437.493 | 44264.8034 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 281.182 | 0:240:120 | 0:00 | 0.8406 | 7 | 0.0191 | 1.0828 | 1.1019 | 1.0903 | 0.0086 | 0.0001 | 3 | 0.8406 | 1.1283 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5359 | 18443.476 | 44264.8035 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 295.6151 | 0:240:120 | 0:00 | 0.7385 | 7 | 0.0118 | 0.941 | 0.9528 | 0.9456 | 0.0053 | 0 | 3 | 0.7385 | 0.977 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5362 | 18449.049 | 44264.8035 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 313.0677 | 0:240:120 | 0:00 | 0.6409 | 7 | 0.012 | 0.8062 | 0.8182 | 0.8132 | 0.0048 | 0 | 3 | 0.6409 | 0.836 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5365 | 18454.156 | 44264.8036 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 333.2835 | 0:240:120 | 0:00 | 0.553 | 7 | 0.009 | 0.6942 | 0.7032 | 0.6988 | 0.0034 | 0 | 3 | 0.553 | 0.7119 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5368 | 18458.966 | 44264.8037 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 350.7581 | 0:240:120 | 0:00 | 0.4926 | 7 | 0.0141 | 0.6132 | 0.6273 | 0.6198 | 0.0059 | 0 | 3 | 0.4926 | 0.6282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5371 | 18463.488 | 44264.8037 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 366.8456 | 0:240:120 | 0:00 | 0.4465 | 7 | 0.0103 | 0.5537 | 0.564 | 0.558 | 0.0043 | 0 | 3 | 0.4465 | 0.5652 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5374 | 18467.841 | 44264.8038 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 391.3492 | 0:240:120 | 0:00 | 0.3894 | 7 | 0.0093 | 0.4794 | 0.4887 | 0.4836 | 0.0038 | 0 | 3 | 0.3894 | 0.4881 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5377 | 18472.122 | 44264.8038 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 419.6742 | 0:240:120 | 0:00 | 0.3379 | 7 | 0.0071 | 0.4163 | 0.4234 | 0.4193 | 0.0028 | 0 | 3 | 0.3379 | 0.4195 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5380 | 18476.204 | 44264.8039 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 431.034 | 0:240:120 | 0:00 | 0.3206 | 7 | 0.0063 | 0.3948 | 0.4011 | 0.397 | 0.0027 | 0 | 3 | 0.3206 | 0.3966 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5383 | 18480.125 | 44264.8039 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 459.826 | 0:240:120 | 0:00 | 0.2832 | 7 | 0.0039 | 0.3473 | 0.3512 | 0.3488 | 0.0016 | 0 | 3 | 0.2832 | 0.3475 | NP | NP | 0-0-0-0-0-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5386 | 18483.83 | 44264.8039 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 489.519 | 0:240:120 | 0:00 | 0.2523 | 7 | 0.0049 | 0.3078 | 0.3127 | 0.3101 | 0.002 | 0 | 3 | 0.2523 | 0.3072 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5389 | 18487.452 | 44264.804 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 513.04 | 0:240:120 | 0:00 | 0.2319 | 7 | 0.0058 | 0.2816 | 0.2874 | 0.2847 | 0.0021 | 0 | 3 | 0.2319 | 0.281 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5392 | 18491.107 | 44264.804 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 553.624 | 0:240:120 | 0:00 | 0.2035 | 7 | 0.0047 | 0.247 | 0.2517 | 0.2491 | 0.0019 | 0 | 3 | 0.2035 | 0.2443 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5395 | 18494.468 | 44264.8041 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 593.074 | 0:240:120 | 0:00 | 0.1817 | 7 | 0.004 | 0.2216 | 0.2256 | 0.2232 | 0.0014 | 0 | 3 | 0.1817 | 0.218 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5398 | 18497.774 | 44264.8041 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 636.66 | 0:240:120 | 0:00 | 0.1625 | 7 | 0.0043 | 0.198 | 0.2023 | 0.1994 | 0.0018 | 0 | 3 | 0.1625 | 0.1951 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5401 | 18501.09 | 44264.8041 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 679.896 | 0:240:120 | 0:00 | 0.1473 | 7 | 0.0029 | 0.1794 | 0.1823 | 0.1806 | 0.0013 | 0 | 3 | 0.1473 | 0.1768 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5404 | 18504.576 | 44264.8042 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 729.103 | 0:240:120 | 0:00 | 0.1334 | 7 | 0.0042 | 0.1625 | 0.1667 | 0.164 | 0.0015 | 0 | 3 | 0.1334 | 0.1601 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5407 | 18507.795 | 44264.8042 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 793.371 | 0:240:120 | 0:00 | 0.1191 | 7 | 0.0024 | 0.1453 | 0.1477 | 0.1465 | 0.0008 | 0 | 3 | 0.1191 | 0.143 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5410 | 18511.121 | 44264.8043 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 849.904 | 0:240:120 | 0:00 | 0.1093 | 7 | 0.0029 | 0.1322 | 0.1351 | 0.134 | 0.001 | 0 | 3 | 0.1093 | 0.1312 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5413 | 18514.418 | 44264.8043 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 920.97 | 0:240:120 | 0:00 | 0.0995 | 7 | 0.0027 | 0.1206 | 0.1233 | 0.122 | 0.0009 | 0 | 3 | 0.0995 | 0.1194 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5416 | 18517.566 | 44264.8043 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1001.106 | 0:240:120 | 0:00 | 0.0909 | 7 | 0.003 | 0.1098 | 0.1128 | 0.1112 | 0.0011 | 0 | 3 | 0.0909 | 0.1091 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5419 | 18520.666 | 44264.8044 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1083.684 | 0:240:120 | 0:00 | 0.0841 | 7 | 0.0038 | 0.1006 | 0.1044 | 0.103 | 0.0013 | 0 | 3 | 0.0841 | 0.1009 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5422 | 18523.689 | 44264.8044 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1190.327 | 0:240:120 | 0:00 | 0.0773 | 7 | 0.0019 | 0.0931 | 0.095 | 0.0943 | 0.0007 | 0 | 3 | 0.0773 | 0.0927 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5425 | 18526.652 | 44264.8044 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1339.206 | 0:240:120 | 0:00 | 0.0704 | 7 | 0.0027 | 0.0839 | 0.0866 | 0.0854 | 0.001 | 0 | 3 | 0.0704 | 0.0845 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5428 | 18529.607 | 44264.8045 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1491.074 | 0:240:120 | 0:00 | 0.0654 | 7 | 0.0034 | 0.0771 | 0.0805 | 0.0791 | 0.001 | 0 | 3 | 0.0654 | 0.0785 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5431 | 18532.513 | 44264.8045 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1682.826 | 0:240:120 | 0:00 | 0.061 | 7 | 0.0023 | 0.0726 | 0.0749 | 0.0737 | 0.0009 | 0 | 3 | 0.061 | 0.0732 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5434 | 18535.385 | 44264.8045 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1863.917 | 0:240:120 | 0:00 | 0.058 | 7 | 0.0029 | 0.068 | 0.0709 | 0.0701 | 0.001 | 0 | 3 | 0.058 | 0.0696 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5437 | 18538.38 | 44264.8046 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2049.478 | 0:240:120 | 0:00 | 0.0558 | 7 | 0.0022 | 0.0655 | 0.0677 | 0.0665 | 0.0009 | 0 | 3 | 0.0558 | 0.0669 | P | NP | 1-1-0-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5440 | 18541.482 | 44264.8046 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2244.131 | 0:240:120 | 0:00 | 0.054 | 7 | 0.0029 | 0.0624 | 0.0653 | 0.0638 | 0.0009 | 0 | 3 | 0.054 | 0.0648 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5443 | 18544.356 | 44264.8046 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2488.218 | 0:240:120 | 0:00 | 0.0523 | 7 | 0.0026 | 0.06 | 0.0626 | 0.0616 | 0.0009 | 0 | 3 | 0.0523 | 0.0628 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5446 | 18547.385 | 44264.8047 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2776.17 | 0:240:120 | 0:00 | 0.0509 | 7 | 0.0033 | 0.0572 | 0.0605 | 0.0588 | 0.0013 | 0 | 3 | 0.0509 | 0.061 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5449 | 18550.468 | 44264.8047 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3024.032 | 0:240:120 | 0:00 | 0.0499 | 7 | 0.0035 | 0.0553 | 0.0588 | 0.0574 | 0.0013 | 0 | 3 | 0.0499 | 0.0599 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5452 | 18553.566 | 44264.8048 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3409.364 | 0:240:120 | 0:00 | 0.0489 | 7 | 0.0031 | 0.054 | 0.0571 | 0.056 | 0.001 | 0 | 3 | 0.0489 | 0.0589 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5455 | 18556.552 | 44264.8048 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3721.514 | 0:240:120 | 0:00 | 0.0483 | 7 | 0.003 | 0.0537 | 0.0567 | 0.0551 | 0.0011 | 0 | 3 | 0.0483 | 0.0583 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5458 | 18559.744 | 44264.8048 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3974.242 | 0:240:120 | 0:00 | 0.0479 | 7 | 0.0028 | 0.0525 | 0.0553 | 0.0538 | 0.001 | 0 | 3 | 0.0479 | 0.0579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5461 | 18562.587 | 44264.8049 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4320.05 | 0:240:120 | 0:00 | 0.0474 | 7 | 0.0033 | 0.052 | 0.0553 | 0.0535 | 0.0012 | 0 | 3 | 0.0474 | 0.0574 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5464 | 18565.422 | 44264.8049 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8500 | 0:240:120 | 0:00 | 0.0456 | 7 | 0.0013 | 0.0499 | 0.0512 | 0.0507 | 0.0005 | 0 | 3 | 0.0456 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5467 | 18632.126 | 44264.8057 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 171.8 | 0:240:120 | 0:00 | 6.4596 | 7 | 9.0064 | 54.5767 | 63.5831 | 57.5809 | 4.4995 | 20.2452 | 3 | 6.4596 | 32.0201 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5470 | 18807.49 | 44264.8077 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 174.9 | 0:240:120 | 0:00 | 5.6074 | 7 | 9.0068 | 36.5776 | 45.5844 | 39.5827 | 4.5005 | 20.2541 | 3 | 5.6074 | 19.8 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5473 | 18924.962 | 44264.809 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 178.8 | 0:240:120 | 0:00 | 4.7971 | 7 | 9.2614 | 14.6507 | 23.9121 | 19.1679 | 3.7503 | 14.0649 | 3 | 4.7971 | 13.2988 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5476 | 18984.864 | 44264.8097 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 182 | 0:240:120 | 0:00 | 4.2807 | 7 | 0.5787 | 8.9796 | 9.5583 | 9.2293 | 0.2439 | 0.0595 | 3 | 4.2807 | 10.4366 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5479 | 19014.469 | 44264.8101 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 187.2 | 0:240:120 | 0:00 | 3.6324 | 7 | 0.5134 | 7.1007 | 7.6141 | 7.4327 | 0.247 | 0.061 | 3 | 3.6324 | 7.6909 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5482 | 19037.554 | 44264.8104 | Vista Coord | Main | 150Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 195.3 | 0:240:120 | 0:00 | 2.9219 | 7 | 0.5658 | 4.6201 | 5.1859 | 4.9653 | 0.2403 | 0.0577 | 3 | 2.9219 | 5.4053 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5485 | 19151.343 | 44264.8117 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 220 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.0029 | 90.5748 | 99.5777 | 93.5772 | 4.4993 | 20.2439 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5488 | 19434.734 | 44264.815 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 224.2999 | 0:240:120 | 0:00 | 7.8041 | 7 | 8.9994 | 72.5783 | 81.5777 | 75.5812 | 4.4966 | 20.2197 | 3 | 7.8041 | 106.5043 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5491 | 19646.231 | 44264.8174 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 231.957 | 0:240:120 | 0:00 | 5.8404 | 7 | 0.0313 | 45.5781 | 45.6094 | 45.5862 | 0.0095 | 0.0001 | 3 | 5.8404 | 22.3834 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5494 | 19749.199 | 44264.8186 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 242.9581 | 0:240:120 | 0:00 | 4.2492 | 7 | 0.007 | 9.0859 | 9.0929 | 9.0899 | 0.0021 | 0 | 3 | 4.2492 | 10.2841 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5497 | 19776.829 | 44264.8189 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 254.012 | 0:240:120 | 0:00 | 3.3074 | 7 | 0.1749 | 6.4269 | 6.6018 | 6.5571 | 0.0666 | 0.0044 | 3 | 3.3074 | 6.5687 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
5500 | 19797.135 | 44264.8191 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 266.5014 | 0:240:120 | 0:00 | 2.6237 | 7 | 0.0953 | 4.2771 | 4.3724 | 4.3089 | 0.046 | 0.0021 | 3 | 2.6237 | 4.609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5503 | 19812.172 | 44264.8193 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 276.9921 | 0:240:120 | 0:00 | 2.2234 | 7 | 0.17 | 3.4525 | 3.6225 | 3.5102 | 0.0836 | 0.007 | 3 | 2.2234 | 3.6572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5506 | 19824.729 | 44264.8195 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 296.1211 | 0:240:120 | 0:00 | 1.7226 | 7 | 0.0819 | 2.4712 | 2.5531 | 2.5082 | 0.0357 | 0.0013 | 3 | 1.7226 | 2.6234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5509 | 19834.565 | 44264.8196 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 313.918 | 0:240:120 | 0:00 | 1.4115 | 7 | 0.0518 | 1.9493 | 2.0011 | 1.9678 | 0.0245 | 0.0006 | 3 | 1.4115 | 2.054 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5512 | 19842.695 | 44264.8197 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 346.2943 | 0:240:120 | 0:00 | 1.046 | 7 | 0.0326 | 1.374 | 1.4066 | 1.3955 | 0.0155 | 0.0002 | 3 | 1.046 | 1.4452 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5515 | 19849.397 | 44264.8197 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 380.391 | 0:240:120 | 0:00 | 0.8091 | 7 | 0.0328 | 1.0363 | 1.0691 | 1.0519 | 0.0139 | 0.0002 | 3 | 0.8091 | 1.0812 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5518 | 19855.021 | 44264.8198 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 411.356 | 0:240:120 | 0:00 | 0.6641 | 7 | 0.0179 | 0.8387 | 0.8566 | 0.8482 | 0.0071 | 0.0001 | 3 | 0.6641 | 0.8692 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5521 | 19860.131 | 44264.8199 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 449.0387 | 0:240:120 | 0:00 | 0.5399 | 7 | 0.0135 | 0.673 | 0.6865 | 0.6815 | 0.0058 | 0 | 3 | 0.5399 | 0.6937 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5524 | 19864.882 | 44264.8199 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 485.0857 | 0:240:120 | 0:00 | 0.4546 | 7 | 0.0105 | 0.565 | 0.5755 | 0.5691 | 0.0045 | 0 | 3 | 0.4546 | 0.5762 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5527 | 19869.327 | 44264.82 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 524.387 | 0:240:120 | 0:00 | 0.3855 | 7 | 0.0092 | 0.4753 | 0.4845 | 0.4789 | 0.0038 | 0 | 3 | 0.3855 | 0.4828 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5530 | 19873.429 | 44264.82 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 590.627 | 0:240:120 | 0:00 | 0.304 | 7 | 0.0087 | 0.3714 | 0.3801 | 0.3754 | 0.0032 | 0 | 3 | 0.304 | 0.3748 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
5533 | 19877.226 | 44264.8201 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 659.016 | 0:240:120 | 0:00 | 0.2479 | 7 | 0.0061 | 0.3021 | 0.3082 | 0.305 | 0.0023 | 0 | 3 | 0.2479 | 0.3016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5536 | 19880.854 | 44264.8201 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 744.589 | 0:240:120 | 0:00 | 0.2005 | 7 | 0.0046 | 0.2438 | 0.2484 | 0.2458 | 0.0017 | 0 | 3 | 0.2005 | 0.2406 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5539 | 19884.497 | 44264.8202 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 817.051 | 0:240:120 | 0:00 | 0.1725 | 7 | 0.0028 | 0.2112 | 0.214 | 0.2121 | 0.0012 | 0 | 3 | 0.1725 | 0.207 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5542 | 19887.797 | 44264.8202 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 890.968 | 0:240:120 | 0:00 | 0.1511 | 7 | 0.0037 | 0.1841 | 0.1878 | 0.1858 | 0.0013 | 0 | 3 | 0.1511 | 0.1814 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5545 | 19891.018 | 44264.8202 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 995.172 | 0:240:120 | 0:00 | 0.1292 | 7 | 0.0028 | 0.1572 | 0.16 | 0.1584 | 0.001 | 0 | 3 | 0.1292 | 0.155 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5548 | 19894.223 | 44264.8203 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1104.625 | 0:240:120 | 0:00 | 0.1128 | 7 | 0.0016 | 0.1374 | 0.139 | 0.1382 | 0.0007 | 0 | 3 | 0.1128 | 0.1353 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5551 | 19897.748 | 44264.8203 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1241.566 | 0:240:120 | 0:00 | 0.0983 | 7 | 0.0022 | 0.1194 | 0.1216 | 0.1207 | 0.0008 | 0 | 3 | 0.0983 | 0.1179 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5554 | 19900.846 | 44264.8203 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1363.814 | 0:240:120 | 0:00 | 0.089 | 7 | 0.003 | 0.1075 | 0.1105 | 0.1089 | 0.0012 | 0 | 3 | 0.089 | 0.1067 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5557 | 19903.897 | 44264.8204 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1550.583 | 0:240:120 | 0:00 | 0.0788 | 7 | 0.0028 | 0.0945 | 0.0973 | 0.0959 | 0.0011 | 0 | 3 | 0.0788 | 0.0946 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5560 | 19906.858 | 44264.8204 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1740.992 | 0:240:120 | 0:00 | 0.0717 | 7 | 0.0022 | 0.0868 | 0.089 | 0.0878 | 0.0008 | 0 | 3 | 0.0717 | 0.0861 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5563 | 19909.766 | 44264.8204 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1946.641 | 0:240:120 | 0:00 | 0.0663 | 7 | 0.0024 | 0.0794 | 0.0818 | 0.0809 | 0.0009 | 0 | 3 | 0.0663 | 0.0796 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5566 | 19912.786 | 44264.8205 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2197.118 | 0:240:120 | 0:00 | 0.0617 | 7 | 0.0026 | 0.0725 | 0.0751 | 0.0739 | 0.0009 | 0 | 3 | 0.0617 | 0.0741 | P | NP | 1-1-1-0-1-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5569 | 19915.742 | 44264.8205 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2508.453 | 0:240:120 | 0:00 | 0.0578 | 7 | 0.0032 | 0.067 | 0.0702 | 0.0689 | 0.0012 | 0 | 3 | 0.0578 | 0.0694 | P | NP | 0-1-1-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5572 | 19918.739 | 44264.8206 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2769.855 | 0:240:120 | 0:00 | 0.0555 | 7 | 0.003 | 0.0637 | 0.0667 | 0.0658 | 0.0011 | 0 | 3 | 0.0555 | 0.0666 | P | NP | 1-1-1-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5575 | 19921.552 | 44264.8206 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3029.909 | 0:240:120 | 0:00 | 0.0538 | 7 | 0.003 | 0.0617 | 0.0647 | 0.0635 | 0.0014 | 0 | 3 | 0.0538 | 0.0645 | P | NP | 0-1-0-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5578 | 19924.435 | 44264.8206 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3279.975 | 0:240:120 | 0:00 | 0.0525 | 7 | 0.0021 | 0.0601 | 0.0622 | 0.0613 | 0.0008 | 0 | 3 | 0.0525 | 0.063 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5581 | 19927.352 | 44264.8207 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3513.821 | 0:240:120 | 0:00 | 0.0515 | 7 | 0.0028 | 0.059 | 0.0618 | 0.0604 | 0.001 | 0 | 3 | 0.0515 | 0.0618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5584 | 19930.287 | 44264.8207 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3760.414 | 0:240:120 | 0:00 | 0.0507 | 7 | 0.003 | 0.0573 | 0.0603 | 0.0587 | 0.0012 | 0 | 3 | 0.0507 | 0.0608 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5587 | 19933.274 | 44264.8207 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3999.196 | 0:240:120 | 0:00 | 0.05 | 7 | 0.0031 | 0.0554 | 0.0585 | 0.0575 | 0.001 | 0 | 3 | 0.05 | 0.06 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5590 | 19936.265 | 44264.8208 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4200.216 | 0:240:120 | 0:00 | 0.0495 | 7 | 0.0027 | 0.0554 | 0.0581 | 0.0566 | 0.0009 | 0 | 3 | 0.0495 | 0.0595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5593 | 19939.14 | 44264.8208 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4425.171 | 0:240:120 | 0:00 | 0.0491 | 7 | 0.0036 | 0.0542 | 0.0578 | 0.0562 | 0.0012 | 0 | 3 | 0.0491 | 0.0591 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5596 | 19942.164 | 44264.8208 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4570.654 | 0:240:120 | 0:00 | 0.0488 | 7 | 0.0039 | 0.0542 | 0.0581 | 0.056 | 0.0015 | 0 | 3 | 0.0488 | 0.0588 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5599 | 19945.053 | 44264.8209 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5000 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0033 | 0.0532 | 0.0565 | 0.0548 | 0.0012 | 0 | 3 | 0.0482 | 0.0582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5602 | 19948.05 | 44264.8209 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5126.571 | 0:240:120 | 0:00 | 0.048 | 7 | 0.0027 | 0.0529 | 0.0556 | 0.0546 | 0.0011 | 0 | 3 | 0.048 | 0.058 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5605 | 19951.036 | 44264.8209 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5474.905 | 0:240:120 | 0:00 | 0.0477 | 7 | 0.0037 | 0.0516 | 0.0553 | 0.0535 | 0.0012 | 0 | 3 | 0.0477 | 0.0577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5608 | 19954.028 | 44264.821 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6001.441 | 0:240:120 | 0:00 | 0.0472 | 7 | 0.0029 | 0.0516 | 0.0545 | 0.0531 | 0.001 | 0 | 3 | 0.0472 | 0.0572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5611 | 19956.962 | 44264.821 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7565.874 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0036 | 0.0509 | 0.0545 | 0.0523 | 0.0013 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5614 | 19959.879 | 44264.821 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9528.171 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0053 | 0.0487 | 0.054 | 0.0509 | 0.0015 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5617 | 19990.387 | 44264.8214 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.5 | 0:240:120 | 0:00 | 4.9212 | 7 | 9.0039 | 18.5816 | 27.5855 | 21.5835 | 4.4978 | 20.2299 | 3 | 4.9212 | 14.1071 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5620 | 20056.345 | 44264.8221 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 248.5 | 0:240:120 | 0:00 | 3.7228 | 7 | 0.5029 | 7.5943 | 8.0972 | 7.7626 | 0.2499 | 0.0625 | 3 | 3.7228 | 8.0296 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5623 | 20080.252 | 44264.8224 | Vista Coord | Main | 200Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 260.3 | 0:240:120 | 0:00 | 2.9273 | 7 | 0.0109 | 5.0964 | 5.1073 | 5.1039 | 0.0036 | 0 | 3 | 2.9273 | 5.4205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5626 | 20193.994 | 44264.8237 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 275 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.0011 | 90.576 | 99.5771 | 93.5787 | 4.4981 | 20.2328 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5629 | 20486.433 | 44264.8271 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 276.1 | 0:240:120 | 0:00 | 9.1483 | 7 | 0.01 | 90.5735 | 90.5835 | 90.5774 | 0.0033 | 0 | 3 | 9.1483 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5632 | 20760.925 | 44264.8303 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 277.2 | 0:240:120 | 0:00 | 8.762 | 7 | 8.9999 | 81.5772 | 90.5771 | 87.5804 | 4.4821 | 20.0893 | 3 | 8.762 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5635 | 21017.508 | 44264.8333 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 281.4812 | 0:240:120 | 0:00 | 7.5159 | 7 | 0.1357 | 72.5745 | 72.7102 | 72.5926 | 0.0441 | 0.0019 | 3 | 7.5159 | 74.554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5638 | 21220.148 | 44264.8356 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 288.9183 | 0:240:120 | 0:00 | 6.0048 | 7 | 9.0038 | 45.5791 | 54.5829 | 48.582 | 4.4997 | 20.247 | 3 | 6.0048 | 24.4888 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5641 | 21341.688 | 44264.837 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 300.9127 | 0:240:120 | 0:00 | 4.5016 | 7 | 0.0042 | 9.5848 | 9.589 | 9.5876 | 0.0017 | 0 | 3 | 4.5016 | 11.5718 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5644 | 21370.713 | 44264.8374 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 315.0444 | 0:240:120 | 0:00 | 3.4461 | 7 | 0.4956 | 6.6044 | 7.1 | 6.934 | 0.2458 | 0.0604 | 3 | 3.4461 | 7.0302 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
5647 | 21393.198 | 44264.8376 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 322.3572 | 0:240:120 | 0:00 | 3.0633 | 7 | 0.1089 | 5.601 | 5.7099 | 5.6342 | 0.0469 | 0.0022 | 3 | 3.0633 | 5.8132 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5650 | 21411.922 | 44264.8378 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 329.8394 | 0:240:120 | 0:00 | 2.7451 | 7 | 0.1671 | 4.4418 | 4.6089 | 4.5001 | 0.0814 | 0.0066 | 3 | 2.7451 | 4.9234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5653 | 21427.801 | 44264.838 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 340.7151 | 0:240:120 | 0:00 | 2.3777 | 7 | 0.1658 | 3.7846 | 3.9504 | 3.844 | 0.0802 | 0.0064 | 3 | 2.3777 | 4.0094 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5656 | 21441.613 | 44264.8382 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 350.4446 | 0:240:120 | 0:00 | 2.1176 | 7 | 0.1662 | 3.1257 | 3.2919 | 3.236 | 0.0821 | 0.0067 | 3 | 2.1176 | 3.4255 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5659 | 21453.793 | 44264.8383 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 361.9242 | 0:240:120 | 0:00 | 1.8701 | 7 | 0.0817 | 2.7172 | 2.7989 | 2.7706 | 0.04 | 0.0016 | 3 | 1.8701 | 2.9119 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5662 | 21464.458 | 44264.8384 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 376.1648 | 0:240:120 | 0:00 | 1.6273 | 7 | 0.0835 | 2.3085 | 2.392 | 2.3439 | 0.0366 | 0.0013 | 3 | 1.6273 | 2.4435 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5665 | 21473.934 | 44264.8386 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 393.8308 | 0:240:120 | 0:00 | 1.3949 | 7 | 0.0541 | 1.9025 | 1.9566 | 1.9357 | 0.0243 | 0.0006 | 3 | 1.3949 | 2.0249 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5668 | 21482.477 | 44264.8387 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 414.4811 | 0:240:120 | 0:00 | 1.1887 | 7 | 0.0329 | 1.5974 | 1.6303 | 1.6111 | 0.0152 | 0.0002 | 3 | 1.1887 | 1.6757 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5671 | 21489.791 | 44264.8387 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 440.7887 | 0:240:120 | 0:00 | 0.9934 | 7 | 0.0223 | 1.2982 | 1.3205 | 1.3126 | 0.0104 | 0.0001 | 3 | 0.9934 | 1.3625 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5674 | 21496.335 | 44264.8388 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 464.387 | 0:240:120 | 0:00 | 0.8612 | 7 | 0.039 | 1.1026 | 1.1416 | 1.1206 | 0.0166 | 0.0003 | 3 | 0.8612 | 1.1593 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5677 | 21502.697 | 44264.8389 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 490.7815 | 0:240:120 | 0:00 | 0.7458 | 7 | 0.0288 | 0.941 | 0.9698 | 0.9596 | 0.0135 | 0.0002 | 3 | 0.7458 | 0.9877 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5680 | 21508.285 | 44264.8389 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 514.9903 | 0:240:120 | 0:00 | 0.6616 | 7 | 0.025 | 0.8263 | 0.8513 | 0.8427 | 0.0117 | 0.0001 | 3 | 0.6616 | 0.8656 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5683 | 21513.475 | 44264.839 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 539.0836 | 0:240:120 | 0:00 | 0.593 | 7 | 0.0217 | 0.7407 | 0.7624 | 0.7529 | 0.008 | 0.0001 | 3 | 0.593 | 0.768 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5686 | 21518.303 | 44264.8391 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 564.9886 | 0:240:120 | 0:00 | 0.5319 | 7 | 0.0147 | 0.6634 | 0.6781 | 0.6701 | 0.0061 | 0 | 3 | 0.5319 | 0.6826 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5689 | 21522.996 | 44264.8391 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 593.9945 | 0:240:120 | 0:00 | 0.4755 | 7 | 0.0142 | 0.5875 | 0.6017 | 0.5956 | 0.0059 | 0 | 3 | 0.4755 | 0.6048 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5692 | 21527.411 | 44264.8392 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 626.4478 | 0:240:120 | 0:00 | 0.4239 | 7 | 0.0146 | 0.5212 | 0.5358 | 0.5288 | 0.0061 | 0 | 3 | 0.4239 | 0.5345 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5695 | 21531.797 | 44264.8392 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 655.7551 | 0:240:120 | 0:00 | 0.3851 | 7 | 0.0097 | 0.4741 | 0.4838 | 0.4785 | 0.004 | 0 | 3 | 0.3851 | 0.4824 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5698 | 21535.952 | 44264.8393 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 698.2239 | 0:240:120 | 0:00 | 0.3391 | 7 | 0.0053 | 0.4176 | 0.4229 | 0.4199 | 0.002 | 0 | 3 | 0.3391 | 0.4211 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5701 | 21539.896 | 44264.8393 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 744.0906 | 0:240:120 | 0:00 | 0.2995 | 7 | 0.008 | 0.3667 | 0.3747 | 0.3703 | 0.0034 | 0 | 3 | 0.2995 | 0.3689 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
5704 | 21543.667 | 44264.8394 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 777.916 | 0:240:120 | 0:00 | 0.2753 | 7 | 0.0064 | 0.3357 | 0.3421 | 0.339 | 0.0024 | 0 | 3 | 0.2753 | 0.3373 | NP | NP | 0-0-1-0-0-0-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
5707 | 21547.425 | 44264.8394 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 819.561 | 0:240:120 | 0:00 | 0.2502 | 7 | 0.0055 | 0.3055 | 0.311 | 0.3076 | 0.0024 | 0 | 3 | 0.2502 | 0.3046 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5710 | 21551.015 | 44264.8394 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 867.671 | 0:240:120 | 0:00 | 0.2261 | 7 | 0.0063 | 0.2743 | 0.2806 | 0.2772 | 0.0024 | 0 | 3 | 0.2261 | 0.2734 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5713 | 21554.484 | 44264.8395 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 926.805 | 0:240:120 | 0:00 | 0.2019 | 7 | 0.004 | 0.2459 | 0.2499 | 0.2478 | 0.0014 | 0 | 3 | 0.2019 | 0.2424 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5716 | 21557.891 | 44264.8395 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 990.886 | 0:240:120 | 0:00 | 0.181 | 7 | 0.0044 | 0.2203 | 0.2247 | 0.2222 | 0.0016 | 0 | 3 | 0.181 | 0.2172 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5719 | 21561.356 | 44264.8396 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1069.279 | 0:240:120 | 0:00 | 0.1606 | 7 | 0.0033 | 0.1957 | 0.199 | 0.1973 | 0.0012 | 0 | 3 | 0.1606 | 0.1928 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5722 | 21564.764 | 44264.8396 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1139.522 | 0:240:120 | 0:00 | 0.1461 | 7 | 0.0033 | 0.1775 | 0.1808 | 0.1791 | 0.0012 | 0 | 3 | 0.1461 | 0.1754 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5725 | 21567.923 | 44264.8396 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1232.242 | 0:240:120 | 0:00 | 0.1309 | 7 | 0.0039 | 0.1585 | 0.1624 | 0.1602 | 0.0014 | 0 | 3 | 0.1309 | 0.157 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5728 | 21571.248 | 44264.8397 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1335.289 | 0:240:120 | 0:00 | 0.1177 | 7 | 0.0033 | 0.1426 | 0.1459 | 0.144 | 0.0014 | 0 | 3 | 0.1177 | 0.1412 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5731 | 21574.33 | 44264.8397 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1486.73 | 0:240:120 | 0:00 | 0.1032 | 7 | 0.0031 | 0.1241 | 0.1272 | 0.126 | 0.0011 | 0 | 3 | 0.1032 | 0.1238 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5734 | 21577.378 | 44264.8397 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1611.059 | 0:240:120 | 0:00 | 0.0943 | 7 | 0.003 | 0.1141 | 0.1171 | 0.1155 | 0.0011 | 0 | 3 | 0.0943 | 0.1132 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5737 | 21580.241 | 44264.8398 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1740.331 | 0:240:120 | 0:00 | 0.0871 | 7 | 0.0027 | 0.1052 | 0.1079 | 0.1065 | 0.0008 | 0 | 3 | 0.0871 | 0.1046 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5740 | 21583.322 | 44264.8398 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1848.862 | 0:240:120 | 0:00 | 0.0822 | 7 | 0.0032 | 0.0986 | 0.1018 | 0.1003 | 0.001 | 0 | 3 | 0.0822 | 0.0987 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5743 | 21586.512 | 44264.8399 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1962.115 | 0:240:120 | 0:00 | 0.078 | 7 | 0.0041 | 0.0929 | 0.097 | 0.095 | 0.0013 | 0 | 3 | 0.078 | 0.0936 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5746 | 21589.427 | 44264.8399 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2119.555 | 0:240:120 | 0:00 | 0.0732 | 7 | 0.0029 | 0.0875 | 0.0904 | 0.0891 | 0.0009 | 0 | 3 | 0.0732 | 0.0879 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5749 | 21592.549 | 44264.8399 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2284.858 | 0:240:120 | 0:00 | 0.0692 | 7 | 0.0027 | 0.0827 | 0.0854 | 0.0839 | 0.0009 | 0 | 3 | 0.0692 | 0.0831 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5752 | 21595.54 | 44264.84 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2460.485 | 0:240:120 | 0:00 | 0.0659 | 7 | 0.0025 | 0.0784 | 0.0809 | 0.0799 | 0.0009 | 0 | 3 | 0.0659 | 0.079 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5755 | 21598.466 | 44264.84 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2688.586 | 0:240:120 | 0:00 | 0.0624 | 7 | 0.0027 | 0.0738 | 0.0765 | 0.0752 | 0.0009 | 0 | 3 | 0.0624 | 0.0749 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5758 | 21601.507 | 44264.84 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2898.266 | 0:240:120 | 0:00 | 0.06 | 7 | 0.0031 | 0.0702 | 0.0733 | 0.0718 | 0.0011 | 0 | 3 | 0.06 | 0.072 | P | NP | 0-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5761 | 21604.453 | 44264.8401 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3163.65 | 0:240:120 | 0:00 | 0.0576 | 7 | 0.0033 | 0.0666 | 0.0699 | 0.0686 | 0.0013 | 0 | 3 | 0.0576 | 0.0691 | P | NP | 0-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5764 | 21607.474 | 44264.8401 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3460.546 | 0:240:120 | 0:00 | 0.0555 | 7 | 0.0022 | 0.0644 | 0.0666 | 0.0658 | 0.0009 | 0 | 3 | 0.0555 | 0.0666 | P | NP | 1-1-1-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5767 | 21610.314 | 44264.8401 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3842.005 | 0:240:120 | 0:00 | 0.0535 | 7 | 0.0024 | 0.0616 | 0.064 | 0.0629 | 0.0008 | 0 | 3 | 0.0535 | 0.0642 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5770 | 21613.211 | 44264.8402 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4222.232 | 0:240:120 | 0:00 | 0.052 | 7 | 0.0036 | 0.059 | 0.0626 | 0.0606 | 0.0011 | 0 | 3 | 0.052 | 0.0624 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5773 | 21616.49 | 44264.8402 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4603.071 | 0:240:120 | 0:00 | 0.0509 | 7 | 0.0016 | 0.0582 | 0.0598 | 0.0591 | 0.0006 | 0 | 3 | 0.0509 | 0.0611 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5776 | 21619.612 | 44264.8402 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4950.454 | 0:240:120 | 0:00 | 0.0501 | 7 | 0.0029 | 0.0565 | 0.0594 | 0.0578 | 0.0009 | 0 | 3 | 0.0501 | 0.0601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5779 | 21622.718 | 44264.8403 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5379.656 | 0:240:120 | 0:00 | 0.0493 | 7 | 0.0032 | 0.0547 | 0.0579 | 0.0564 | 0.001 | 0 | 3 | 0.0493 | 0.0593 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5782 | 21625.716 | 44264.8403 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5709.187 | 0:240:120 | 0:00 | 0.0488 | 7 | 0.0025 | 0.0545 | 0.057 | 0.056 | 0.0008 | 0 | 3 | 0.0488 | 0.0588 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5785 | 21628.593 | 44264.8403 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6090.584 | 0:240:120 | 0:00 | 0.0484 | 7 | 0.0035 | 0.0531 | 0.0566 | 0.0549 | 0.0012 | 0 | 3 | 0.0484 | 0.0584 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5788 | 21631.466 | 44264.8404 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6795.504 | 0:240:120 | 0:00 | 0.0477 | 7 | 0.0042 | 0.051 | 0.0552 | 0.0535 | 0.0014 | 0 | 3 | 0.0477 | 0.0577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5791 | 21634.586 | 44264.8404 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7938.079 | 0:240:120 | 0:00 | 0.047 | 7 | 0.0039 | 0.051 | 0.0549 | 0.0526 | 0.0015 | 0 | 3 | 0.047 | 0.057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5794 | 21637.543 | 44264.8404 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9647.669 | 0:240:120 | 0:00 | 0.0463 | 7 | 0.0037 | 0.0504 | 0.0541 | 0.0518 | 0.0012 | 0 | 3 | 0.0463 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5797 | 21640.589 | 44264.8405 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10630.395 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0028 | 0.0504 | 0.0532 | 0.0516 | 0.0009 | 0 | 3 | 0.0461 | 0.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5800 | 21671.116 | 44264.8408 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.9 | 0:240:120 | 0:00 | 5.1541 | 7 | 0.164 | 27.5056 | 27.6696 | 27.5864 | 0.0418 | 0.0017 | 3 | 5.1541 | 15.7832 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5803 | 21737.68 | 44264.8416 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 308 | 0:240:120 | 0:00 | 3.9073 | 7 | 0.503 | 8.0912 | 8.5942 | 8.261 | 0.2494 | 0.0622 | 3 | 3.9073 | 8.762 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5806 | 21764.097 | 44264.8419 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 318.7 | 0:240:120 | 0:00 | 3.2444 | 7 | 0.4992 | 6.1017 | 6.6009 | 6.2702 | 0.2478 | 0.0614 | 3 | 3.2444 | 6.3672 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5809 | 21785.329 | 44264.8422 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 326.1 | 0:240:120 | 0:00 | 2.8962 | 7 | 0.4978 | 4.6098 | 5.1076 | 4.9405 | 0.2477 | 0.0614 | 3 | 2.8962 | 5.3335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5812 | 21802.728 | 44264.8424 | Vista Coord | Main | 250Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 335.3 | 0:240:120 | 0:00 | 2.5487 | 7 | 0.1678 | 4.1118 | 4.2796 | 4.169 | 0.0829 | 0.0069 | 3 | 2.5487 | 4.421 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5815 | 21914.8 | 44264.8437 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 330 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.0017 | 90.5774 | 99.5791 | 95.1788 | 3.9353 | 15.4862 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5818 | 22207.215 | 44264.847 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 332.772 | 0:240:120 | 0:00 | 8.7251 | 7 | 9.0029 | 81.5773 | 90.5802 | 87.5784 | 4.5002 | 20.2515 | 3 | 8.7251 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5821 | 22481.628 | 44264.8502 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 333.883 | 0:240:120 | 0:00 | 8.4257 | 7 | 9.0057 | 81.5735 | 90.5792 | 84.5766 | 4.5 | 20.2498 | 3 | 8.4257 | 605.9736 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5824 | 22740.958 | 44264.8532 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 337.7077 | 0:240:120 | 0:00 | 7.5305 | 7 | 3.3867 | 72.576 | 75.9627 | 73.6218 | 1.5708 | 2.4673 | 3 | 7.5305 | 75.7498 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5827 | 22959.046 | 44264.8557 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 343.3595 | 0:240:120 | 0:00 | 6.4976 | 7 | 9.0007 | 54.5802 | 63.5809 | 58.1419 | 4.1462 | 17.1907 | 3 | 6.4976 | 32.7987 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5830 | 23125.718 | 44264.8577 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 353.2078 | 0:240:120 | 0:00 | 5.224 | 7 | 8.9995 | 27.5858 | 36.5853 | 31.1597 | 4.1528 | 17.2454 | 3 | 5.224 | 16.3314 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5833 | 23210.537 | 44264.8587 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 365.9854 | 0:240:120 | 0:00 | 4.141 | 7 | 0.4989 | 8.5927 | 9.0916 | 8.9244 | 0.2476 | 0.0613 | 3 | 4.141 | 9.777 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5836 | 23238.029 | 44264.859 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 381.5273 | 0:240:120 | 0:00 | 3.2846 | 7 | 0.4993 | 6.1034 | 6.6027 | 6.4343 | 0.2476 | 0.0613 | 3 | 3.2846 | 6.4952 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
5839 | 23258.389 | 44264.8592 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 399.8599 | 0:240:120 | 0:00 | 2.6206 | 7 | 0.1687 | 4.2767 | 4.4454 | 4.3339 | 0.0833 | 0.0069 | 3 | 2.6206 | 4.6009 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5842 | 23273.565 | 44264.8594 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 417.7635 | 0:240:120 | 0:00 | 2.1745 | 7 | 0.1669 | 3.2908 | 3.4577 | 3.4008 | 0.0817 | 0.0067 | 3 | 2.1745 | 3.5492 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5845 | 23286.096 | 44264.8595 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 432.8434 | 0:240:120 | 0:00 | 1.8939 | 7 | 0.1616 | 2.7195 | 2.8811 | 2.8014 | 0.0662 | 0.0044 | 3 | 1.8939 | 2.9597 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5848 | 23296.84 | 44264.8597 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 452.2243 | 0:240:120 | 0:00 | 1.617 | 7 | 0.151 | 2.24 | 2.391 | 2.3167 | 0.0609 | 0.0037 | 3 | 1.617 | 2.4244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5851 | 23306.247 | 44264.8598 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 474.2309 | 0:240:120 | 0:00 | 1.3794 | 7 | 0.0484 | 1.9029 | 1.9513 | 1.9347 | 0.0236 | 0.0006 | 3 | 1.3794 | 1.998 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5854 | 23314.521 | 44264.8599 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 499.4451 | 0:240:120 | 0:00 | 1.1739 | 7 | 0.0323 | 1.5659 | 1.5982 | 1.5864 | 0.0154 | 0.0002 | 3 | 1.1739 | 1.6514 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5857 | 23322.08 | 44264.8599 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 524.9706 | 0:240:120 | 0:00 | 1.0149 | 7 | 0.0545 | 1.3209 | 1.3754 | 1.3457 | 0.0231 | 0.0005 | 3 | 1.0149 | 1.396 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5860 | 23328.558 | 44264.86 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 562.3629 | 0:240:120 | 0:00 | 0.8406 | 7 | 0.0283 | 1.0734 | 1.1017 | 1.092 | 0.0137 | 0.0002 | 3 | 0.8406 | 1.1283 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5863 | 23334.406 | 44264.8601 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 591.2302 | 0:240:120 | 0:00 | 0.7385 | 7 | 0.0152 | 0.9413 | 0.9565 | 0.9493 | 0.0058 | 0 | 3 | 0.7385 | 0.977 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5866 | 23339.929 | 44264.8601 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 626.1354 | 0:240:120 | 0:00 | 0.6409 | 7 | 0.0189 | 0.8071 | 0.826 | 0.8157 | 0.0078 | 0.0001 | 3 | 0.6409 | 0.836 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5869 | 23345.308 | 44264.8602 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 666.567 | 0:240:120 | 0:00 | 0.553 | 7 | 0.0171 | 0.6894 | 0.7065 | 0.6992 | 0.0066 | 0 | 3 | 0.553 | 0.7119 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5872 | 23350.191 | 44264.8603 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 701.5162 | 0:240:120 | 0:00 | 0.4926 | 7 | 0.0135 | 0.6136 | 0.6271 | 0.62 | 0.0057 | 0 | 3 | 0.4926 | 0.6282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5875 | 23354.832 | 44264.8603 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 735.8912 | 0:240:120 | 0:00 | 0.4436 | 7 | 0.0117 | 0.5474 | 0.5591 | 0.5541 | 0.0048 | 0 | 3 | 0.4436 | 0.5613 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5878 | 23359.218 | 44264.8604 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 782.6995 | 0:240:120 | 0:00 | 0.3894 | 7 | 0.0103 | 0.4793 | 0.4896 | 0.4838 | 0.0041 | 0 | 3 | 0.3894 | 0.4881 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5881 | 23363.419 | 44264.8604 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 839.3473 | 0:240:120 | 0:00 | 0.3379 | 7 | 0.0091 | 0.4141 | 0.4232 | 0.4183 | 0.0037 | 0 | 3 | 0.3379 | 0.4195 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5884 | 23367.306 | 44264.8605 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 887.0477 | 0:240:120 | 0:00 | 0.3033 | 7 | 0.0052 | 0.3716 | 0.3768 | 0.374 | 0.002 | 0 | 3 | 0.3033 | 0.3739 | NP | NP | 0-1-1-0-1-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
5887 | 23371.203 | 44264.8605 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 919.652 | 0:240:120 | 0:00 | 0.2832 | 7 | 0.0052 | 0.3465 | 0.3517 | 0.349 | 0.002 | 0 | 3 | 0.2832 | 0.3475 | NP | NP | 0-0-1-0-0-1-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5890 | 23374.978 | 44264.8606 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 979.038 | 0:240:120 | 0:00 | 0.2523 | 7 | 0.0059 | 0.3079 | 0.3138 | 0.3101 | 0.0023 | 0 | 3 | 0.2523 | 0.3072 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5893 | 23378.485 | 44264.8606 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1026.08 | 0:240:120 | 0:00 | 0.2319 | 7 | 0.0053 | 0.2823 | 0.2876 | 0.2848 | 0.0022 | 0 | 3 | 0.2319 | 0.281 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5896 | 23382.206 | 44264.8606 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1100.249 | 0:240:120 | 0:00 | 0.2056 | 7 | 0.0055 | 0.2496 | 0.2551 | 0.2523 | 0.0021 | 0 | 3 | 0.2056 | 0.2471 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5899 | 23385.61 | 44264.8607 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1186.147 | 0:240:120 | 0:00 | 0.1817 | 7 | 0.0037 | 0.2213 | 0.225 | 0.223 | 0.0015 | 0 | 3 | 0.1817 | 0.218 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5902 | 23388.95 | 44264.8607 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1273.321 | 0:240:120 | 0:00 | 0.1625 | 7 | 0.0061 | 0.196 | 0.2021 | 0.1993 | 0.002 | 0 | 3 | 0.1625 | 0.1951 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5905 | 23392.582 | 44264.8608 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1359.792 | 0:240:120 | 0:00 | 0.1473 | 7 | 0.0038 | 0.1775 | 0.1813 | 0.1802 | 0.0012 | 0 | 3 | 0.1473 | 0.1768 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5908 | 23395.852 | 44264.8608 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1458.206 | 0:240:120 | 0:00 | 0.1334 | 7 | 0.0041 | 0.1614 | 0.1655 | 0.1631 | 0.0013 | 0 | 3 | 0.1334 | 0.1601 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5911 | 23398.961 | 44264.8608 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1596.742 | 0:240:120 | 0:00 | 0.1182 | 7 | 0.0033 | 0.1437 | 0.147 | 0.1453 | 0.001 | 0 | 3 | 0.1182 | 0.1418 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5914 | 23402.155 | 44264.8609 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1702.807 | 0:240:120 | 0:00 | 0.1091 | 7 | 0.0045 | 0.1315 | 0.136 | 0.1336 | 0.0017 | 0 | 3 | 0.1091 | 0.1309 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5917 | 23405.454 | 44264.8609 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1830.54 | 0:240:120 | 0:00 | 0.1002 | 7 | 0.0024 | 0.1216 | 0.124 | 0.1227 | 0.0009 | 0 | 3 | 0.1002 | 0.1202 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5920 | 23408.394 | 44264.8609 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2002.211 | 0:240:120 | 0:00 | 0.0909 | 7 | 0.0036 | 0.1093 | 0.1129 | 0.1108 | 0.001 | 0 | 3 | 0.0909 | 0.1091 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5923 | 23411.718 | 44264.861 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2167.368 | 0:240:120 | 0:00 | 0.0841 | 7 | 0.0029 | 0.1015 | 0.1044 | 0.1027 | 0.0009 | 0 | 3 | 0.0841 | 0.1009 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5926 | 23414.804 | 44264.861 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2380.654 | 0:240:120 | 0:00 | 0.0773 | 7 | 0.0017 | 0.0932 | 0.0949 | 0.0941 | 0.0007 | 0 | 3 | 0.0773 | 0.0927 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5929 | 23417.68 | 44264.861 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2678.413 | 0:240:120 | 0:00 | 0.0704 | 7 | 0.0029 | 0.0837 | 0.0866 | 0.0855 | 0.0011 | 0 | 3 | 0.0704 | 0.0845 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5932 | 23420.771 | 44264.8611 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2982.149 | 0:240:120 | 0:00 | 0.0654 | 7 | 0.0032 | 0.0773 | 0.0805 | 0.0789 | 0.0012 | 0 | 3 | 0.0654 | 0.0785 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5935 | 23423.707 | 44264.8611 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3365.653 | 0:240:120 | 0:00 | 0.061 | 7 | 0.0028 | 0.0716 | 0.0744 | 0.0732 | 0.001 | 0 | 3 | 0.061 | 0.0732 | P | NP | 1-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5938 | 23426.762 | 44264.8612 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3727.834 | 0:240:120 | 0:00 | 0.058 | 7 | 0.0028 | 0.0682 | 0.071 | 0.0696 | 0.0011 | 0 | 3 | 0.058 | 0.0696 | P | NP | 0-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5941 | 23429.761 | 44264.8612 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4070.956 | 0:240:120 | 0:00 | 0.0559 | 7 | 0.0029 | 0.0644 | 0.0673 | 0.066 | 0.001 | 0 | 3 | 0.0559 | 0.0671 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5944 | 23432.615 | 44264.8612 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4488.262 | 0:240:120 | 0:00 | 0.054 | 7 | 0.0035 | 0.0616 | 0.0651 | 0.0637 | 0.0012 | 0 | 3 | 0.054 | 0.0648 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5947 | 23435.624 | 44264.8613 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4966.435 | 0:240:120 | 0:00 | 0.0523 | 7 | 0.0027 | 0.0599 | 0.0626 | 0.0614 | 0.0011 | 0 | 3 | 0.0523 | 0.0628 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5950 | 23438.783 | 44264.8613 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5490.34 | 0:240:120 | 0:00 | 0.051 | 7 | 0.0028 | 0.0578 | 0.0606 | 0.0591 | 0.0009 | 0 | 3 | 0.051 | 0.0612 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5953 | 23441.688 | 44264.8613 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5900.064 | 0:240:120 | 0:00 | 0.0502 | 7 | 0.0041 | 0.0556 | 0.0597 | 0.058 | 0.0012 | 0 | 3 | 0.0502 | 0.0602 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5956 | 23444.696 | 44264.8614 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6750.729 | 0:240:120 | 0:00 | 0.049 | 7 | 0.0042 | 0.0536 | 0.0578 | 0.0558 | 0.0014 | 0 | 3 | 0.049 | 0.059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5959 | 23447.96 | 44264.8614 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7443.027 | 0:240:120 | 0:00 | 0.0483 | 7 | 0.0032 | 0.0532 | 0.0564 | 0.0549 | 0.0011 | 0 | 3 | 0.0483 | 0.0583 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5962 | 23450.941 | 44264.8614 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7948.483 | 0:240:120 | 0:00 | 0.0479 | 7 | 0.0035 | 0.0518 | 0.0553 | 0.0537 | 0.0013 | 0 | 3 | 0.0479 | 0.0579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5965 | 23453.894 | 44264.8615 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8640.099 | 0:240:120 | 0:00 | 0.0474 | 7 | 0.0038 | 0.0514 | 0.0552 | 0.0531 | 0.0012 | 0 | 3 | 0.0474 | 0.0574 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5968 | 23456.902 | 44264.8615 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9904.958 | 0:240:120 | 0:00 | 0.0468 | 7 | 0.004 | 0.0505 | 0.0545 | 0.0521 | 0.0013 | 0 | 3 | 0.0468 | 0.0568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5971 | 23459.761 | 44264.8615 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11155.44 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.0029 | 0.0506 | 0.0535 | 0.0517 | 0.0009 | 0 | 3 | 0.0464 | 0.0564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5974 | 23508.089 | 44264.8621 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 348.3 | 0:240:120 | 0:00 | 5.7934 | 7 | 8.9972 | 36.5854 | 45.5826 | 42.7849 | 4.2018 | 17.6554 | 3 | 5.7934 | 21.8277 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5977 | 23620.587 | 44264.8634 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 359.6 | 0:240:120 | 0:00 | 4.6237 | 7 | 8.9989 | 9.5894 | 18.5883 | 12.8088 | 4.3461 | 18.8884 | 3 | 4.6237 | 12.2543 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5980 | 23668.337 | 44264.864 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 373.8 | 0:240:120 | 0:00 | 3.6648 | 7 | 0.2165 | 7.593 | 7.8095 | 7.6432 | 0.0782 | 0.0061 | 3 | 3.6648 | 7.8108 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5983 | 23691.658 | 44264.8642 | Vista Coord | Main | 300Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 390.7 | 0:240:120 | 0:00 | 2.9183 | 7 | 0.499 | 4.6082 | 5.1072 | 4.9406 | 0.2469 | 0.061 | 3 | 2.9183 | 5.3952 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5986 | 23805.354 | 44264.8655 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 385 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.001 | 90.5778 | 99.5788 | 96.5316 | 4.4657 | 19.9427 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5989 | 24106.803 | 44264.869 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 385.99 | 0:240:120 | 0:00 | 9.2944 | 7 | 9.0007 | 90.5756 | 99.5763 | 93.5765 | 4.4996 | 20.2466 | 3 | 9.2944 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5992 | 24399.982 | 44264.8724 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 386.5697 | 0:240:120 | 0:00 | 9.1406 | 7 | 1.7729 | 90.5729 | 92.3458 | 91.0146 | 0.7064 | 0.4991 | 3 | 9.1406 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5995 | 24677.655 | 44264.8756 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 389.8147 | 0:240:120 | 0:00 | 8.3626 | 7 | 9.0029 | 81.5759 | 90.5788 | 84.5775 | 4.4998 | 20.2486 | 3 | 8.3626 | 419.5977 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5998 | 24943.1 | 44264.8787 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 392.2666 | 0:240:120 | 0:00 | 7.8542 | 7 | 9.001 | 72.5783 | 81.5793 | 78.578 | 4.4986 | 20.237 | 3 | 7.8542 | 114.681 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6001 | 25175.529 | 44264.8814 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 398.0493 | 0:240:120 | 0:00 | 6.8613 | 7 | 3.556 | 63.5765 | 67.1325 | 64.5752 | 1.5142 | 2.2928 | 3 | 6.8613 | 42.004 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6004 | 25356.965 | 44264.8835 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 409.013 | 0:240:120 | 0:00 | 5.5148 | 7 | 9.0062 | 36.5779 | 45.5841 | 39.5824 | 4.5005 | 20.2542 | 3 | 5.5148 | 18.8821 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6007 | 25478.459 | 44264.8849 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 415.4755 | 0:240:120 | 0:00 | 4.9333 | 7 | 9.0001 | 18.586 | 27.5861 | 24.5842 | 4.4976 | 20.2286 | 3 | 4.9333 | 14.1888 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6010 | 25545.252 | 44264.8857 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 426.9199 | 0:240:120 | 0:00 | 4.1447 | 7 | 0.4979 | 8.593 | 9.0909 | 8.9245 | 0.2481 | 0.0615 | 3 | 4.1447 | 9.7939 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6013 | 25574.157 | 44264.886 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 435.9377 | 0:240:120 | 0:00 | 3.6724 | 7 | 0.5029 | 7.5933 | 8.0962 | 7.7624 | 0.2495 | 0.0623 | 3 | 3.6724 | 7.8392 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6016 | 25599.096 | 44264.8863 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 448.4139 | 0:240:120 | 0:00 | 3.163 | 7 | 0.4973 | 5.6061 | 6.1034 | 5.9362 | 0.2473 | 0.0612 | 3 | 3.163 | 6.1137 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6019 | 25619.198 | 44264.8865 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 458.3645 | 0:240:120 | 0:00 | 2.8419 | 7 | 0.5006 | 4.6058 | 5.1064 | 4.7815 | 0.2438 | 0.0595 | 3 | 2.8419 | 5.1835 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6022 | 25636.091 | 44264.8867 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 476.4364 | 0:240:120 | 0:00 | 2.3897 | 7 | 0.1665 | 3.785 | 3.9515 | 3.8945 | 0.0817 | 0.0067 | 3 | 2.3897 | 4.0376 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6025 | 25650.655 | 44264.8869 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 492.1246 | 0:240:120 | 0:00 | 2.092 | 7 | 0.1672 | 3.1258 | 3.293 | 3.2361 | 0.082 | 0.0067 | 3 | 2.092 | 3.3706 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6028 | 25662.845 | 44264.887 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 504.625 | 0:240:120 | 0:00 | 1.899 | 7 | 0.1627 | 2.7179 | 2.8806 | 2.7989 | 0.0695 | 0.0048 | 3 | 1.899 | 2.9699 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6031 | 25673.688 | 44264.8872 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 523.9729 | 0:240:120 | 0:00 | 1.6563 | 7 | 0.1642 | 2.3092 | 2.4734 | 2.3902 | 0.0706 | 0.005 | 3 | 1.6563 | 2.4979 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6034 | 25683.65 | 44264.8873 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 537.8428 | 0:240:120 | 0:00 | 1.514 | 7 | 0.0485 | 2.0964 | 2.1449 | 2.1285 | 0.0234 | 0.0005 | 3 | 1.514 | 2.2362 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6037 | 25692.501 | 44264.8874 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 556.7166 | 0:240:120 | 0:00 | 1.3521 | 7 | 0.0493 | 1.8542 | 1.9035 | 1.8867 | 0.0241 | 0.0006 | 3 | 1.3521 | 1.9509 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6040 | 25700.959 | 44264.8875 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 573.848 | 0:240:120 | 0:00 | 1.2297 | 7 | 0.0804 | 1.6296 | 1.71 | 1.6663 | 0.0351 | 0.0012 | 3 | 1.2297 | 1.7436 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6043 | 25708.792 | 44264.8876 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 597.7202 | 0:240:120 | 0:00 | 1.0886 | 7 | 0.0363 | 1.4389 | 1.4752 | 1.4607 | 0.0162 | 0.0003 | 3 | 1.0886 | 1.513 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6046 | 25715.673 | 44264.8876 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 622.5868 | 0:240:120 | 0:00 | 0.9691 | 7 | 0.0453 | 1.2533 | 1.2986 | 1.2751 | 0.0189 | 0.0004 | 3 | 0.9691 | 1.3246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6049 | 25722.309 | 44264.8877 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 643.7607 | 0:240:120 | 0:00 | 0.8842 | 7 | 0.0223 | 1.1412 | 1.1635 | 1.1555 | 0.0101 | 0.0001 | 3 | 0.8842 | 1.1942 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6052 | 25728.505 | 44264.8878 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 667.744 | 0:240:120 | 0:00 | 0.8026 | 7 | 0.0324 | 1.0197 | 1.0521 | 1.0402 | 0.0152 | 0.0002 | 3 | 0.8026 | 1.0715 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6055 | 25734.254 | 44264.8879 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 701.3633 | 0:240:120 | 0:00 | 0.7082 | 7 | 0.0134 | 0.9019 | 0.9153 | 0.9106 | 0.0056 | 0 | 3 | 0.7082 | 0.9329 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6058 | 25739.512 | 44264.8879 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 730.5408 | 0:240:120 | 0:00 | 0.6408 | 7 | 0.0187 | 0.8071 | 0.8258 | 0.816 | 0.0077 | 0.0001 | 3 | 0.6408 | 0.8359 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6061 | 25744.55 | 44264.888 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 768.9264 | 0:240:120 | 0:00 | 0.5677 | 7 | 0.0152 | 0.7108 | 0.726 | 0.7179 | 0.0065 | 0 | 3 | 0.5677 | 0.7324 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6064 | 25749.358 | 44264.888 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 804.2705 | 0:240:120 | 0:00 | 0.5122 | 7 | 0.0173 | 0.6364 | 0.6537 | 0.6448 | 0.0064 | 0 | 3 | 0.5122 | 0.6553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6067 | 25754.039 | 44264.8881 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 836.8536 | 0:240:120 | 0:00 | 0.469 | 7 | 0.0142 | 0.5805 | 0.5947 | 0.5867 | 0.0059 | 0 | 3 | 0.469 | 0.5959 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6070 | 25758.462 | 44264.8881 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 879.9065 | 0:240:120 | 0:00 | 0.4209 | 7 | 0.0102 | 0.5214 | 0.5316 | 0.5254 | 0.0045 | 0 | 3 | 0.4209 | 0.5305 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6073 | 25762.876 | 44264.8882 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 920.162 | 0:240:120 | 0:00 | 0.3833 | 7 | 0.0069 | 0.4728 | 0.4797 | 0.4762 | 0.0027 | 0 | 3 | 0.3833 | 0.4799 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6076 | 25766.977 | 44264.8882 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 978.687 | 0:240:120 | 0:00 | 0.3383 | 7 | 0.0056 | 0.4174 | 0.423 | 0.4194 | 0.0024 | 0 | 3 | 0.3383 | 0.42 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6079 | 25771.124 | 44264.8883 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1044.202 | 0:240:120 | 0:00 | 0.2981 | 7 | 0.0078 | 0.364 | 0.3718 | 0.3679 | 0.0031 | 0 | 3 | 0.2981 | 0.3671 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6082 | 25774.937 | 44264.8883 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1108.297 | 0:240:120 | 0:00 | 0.2666 | 7 | 0.0073 | 0.3247 | 0.332 | 0.328 | 0.0027 | 0 | 3 | 0.2666 | 0.3258 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6085 | 25778.448 | 44264.8884 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1181.254 | 0:240:120 | 0:00 | 0.2375 | 7 | 0.0054 | 0.2896 | 0.295 | 0.2916 | 0.002 | 0 | 3 | 0.2375 | 0.2881 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6088 | 25781.967 | 44264.8884 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1276.236 | 0:240:120 | 0:00 | 0.2077 | 7 | 0.0079 | 0.2503 | 0.2582 | 0.2536 | 0.0025 | 0 | 3 | 0.2077 | 0.2497 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6091 | 25785.412 | 44264.8885 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1357.408 | 0:240:120 | 0:00 | 0.1874 | 7 | 0.0062 | 0.2262 | 0.2324 | 0.229 | 0.0019 | 0 | 3 | 0.1874 | 0.2249 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6094 | 25788.862 | 44264.8885 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1439.222 | 0:240:120 | 0:00 | 0.1707 | 7 | 0.005 | 0.2073 | 0.2123 | 0.2091 | 0.002 | 0 | 3 | 0.1707 | 0.2049 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6097 | 25792.328 | 44264.8885 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1532.361 | 0:240:120 | 0:00 | 0.1551 | 7 | 0.0039 | 0.1871 | 0.191 | 0.1892 | 0.0013 | 0 | 3 | 0.1551 | 0.1861 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6100 | 25795.605 | 44264.8886 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1645.225 | 0:240:120 | 0:00 | 0.1398 | 7 | 0.0021 | 0.1698 | 0.1719 | 0.1709 | 0.0007 | 0 | 3 | 0.1398 | 0.1678 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6103 | 25798.784 | 44264.8886 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1768.25 | 0:240:120 | 0:00 | 0.1266 | 7 | 0.0035 | 0.153 | 0.1565 | 0.1547 | 0.0012 | 0 | 3 | 0.1266 | 0.1519 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6106 | 25801.889 | 44264.8886 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1924.458 | 0:240:120 | 0:00 | 0.1134 | 7 | 0.0029 | 0.1371 | 0.14 | 0.1385 | 0.0009 | 0 | 3 | 0.1134 | 0.1361 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6109 | 25804.95 | 44264.8887 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2070.525 | 0:240:120 | 0:00 | 0.1038 | 7 | 0.0039 | 0.1249 | 0.1288 | 0.1266 | 0.0015 | 0 | 3 | 0.1038 | 0.1246 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6112 | 25808.066 | 44264.8887 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2237.011 | 0:240:120 | 0:00 | 0.0952 | 7 | 0.0027 | 0.1148 | 0.1175 | 0.1158 | 0.0009 | 0 | 3 | 0.0952 | 0.1142 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6115 | 25811.393 | 44264.8888 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2437.176 | 0:240:120 | 0:00 | 0.0871 | 7 | 0.0029 | 0.1054 | 0.1083 | 0.1068 | 0.0009 | 0 | 3 | 0.0871 | 0.1045 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6118 | 25814.269 | 44264.8888 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2646.939 | 0:240:120 | 0:00 | 0.0806 | 7 | 0.0038 | 0.0962 | 0.1 | 0.0981 | 0.0012 | 0 | 3 | 0.0806 | 0.0967 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6121 | 25817.256 | 44264.8888 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2889.817 | 0:240:120 | 0:00 | 0.0748 | 7 | 0.0018 | 0.0896 | 0.0914 | 0.0908 | 0.0007 | 0 | 3 | 0.0748 | 0.0897 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6124 | 25820.222 | 44264.8889 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3122.18 | 0:240:120 | 0:00 | 0.0705 | 7 | 0.0023 | 0.0841 | 0.0864 | 0.0852 | 0.0009 | 0 | 3 | 0.0705 | 0.0845 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6127 | 25823.183 | 44264.8889 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3412.23 | 0:240:120 | 0:00 | 0.0663 | 7 | 0.0027 | 0.0787 | 0.0814 | 0.0802 | 0.001 | 0 | 3 | 0.0663 | 0.0795 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6130 | 25826.373 | 44264.8889 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3721.439 | 0:240:120 | 0:00 | 0.0628 | 7 | 0.0034 | 0.0738 | 0.0772 | 0.0753 | 0.0011 | 0 | 3 | 0.0628 | 0.0754 | P | NP | 1-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6133 | 25829.222 | 44264.889 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4157.41 | 0:240:120 | 0:00 | 0.0593 | 7 | 0.0029 | 0.0696 | 0.0725 | 0.071 | 0.0011 | 0 | 3 | 0.0593 | 0.0711 | P | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6136 | 25832.032 | 44264.889 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4515.231 | 0:240:120 | 0:00 | 0.0571 | 7 | 0.0022 | 0.0661 | 0.0683 | 0.0676 | 0.0009 | 0 | 3 | 0.0571 | 0.0685 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6139 | 25835.215 | 44264.889 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4970.928 | 0:240:120 | 0:00 | 0.055 | 7 | 0.0027 | 0.0635 | 0.0662 | 0.0649 | 0.0008 | 0 | 3 | 0.055 | 0.066 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6142 | 25838.153 | 44264.8891 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5501.29 | 0:240:120 | 0:00 | 0.0531 | 7 | 0.0015 | 0.0621 | 0.0636 | 0.0627 | 0.0006 | 0 | 3 | 0.0531 | 0.0638 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6145 | 25841.071 | 44264.8891 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5925.029 | 0:240:120 | 0:00 | 0.052 | 7 | 0.0025 | 0.0592 | 0.0617 | 0.0603 | 0.0009 | 0 | 3 | 0.052 | 0.0624 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6148 | 25843.927 | 44264.8891 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6570.906 | 0:240:120 | 0:00 | 0.0507 | 7 | 0.003 | 0.0574 | 0.0604 | 0.059 | 0.0011 | 0 | 3 | 0.0507 | 0.0608 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6151 | 25846.836 | 44264.8892 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7334.596 | 0:240:120 | 0:00 | 0.0496 | 7 | 0.0032 | 0.0547 | 0.0579 | 0.0564 | 0.0011 | 0 | 3 | 0.0496 | 0.0596 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6154 | 25849.791 | 44264.8892 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8352.64 | 0:240:120 | 0:00 | 0.0485 | 7 | 0.004 | 0.0528 | 0.0568 | 0.0548 | 0.0013 | 0 | 3 | 0.0485 | 0.0585 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6157 | 25853.041 | 44264.8892 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8934.452 | 0:240:120 | 0:00 | 0.0481 | 7 | 0.0036 | 0.0525 | 0.0561 | 0.0544 | 0.0013 | 0 | 3 | 0.0481 | 0.0581 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6160 | 25856.074 | 44264.8893 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9693.287 | 0:240:120 | 0:00 | 0.0476 | 7 | 0.0022 | 0.0519 | 0.0541 | 0.053 | 0.0007 | 0 | 3 | 0.0476 | 0.0576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6163 | 25859.148 | 44264.8893 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10705.09 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0038 | 0.0508 | 0.0546 | 0.0525 | 0.0012 | 0 | 3 | 0.0471 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6166 | 25862.252 | 44264.8893 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11946.713 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0041 | 0.05 | 0.0541 | 0.0521 | 0.0014 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6169 | 25919.638 | 44264.89 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 403.5 | 0:240:120 | 0:00 | 6.1226 | 7 | 8.9989 | 45.5829 | 54.5818 | 51.4496 | 4.4159 | 19.5 | 3 | 6.1226 | 26.1702 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6172 | 26068.121 | 44264.8917 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 412.2 | 0:240:120 | 0:00 | 5.2128 | 7 | 9.0018 | 27.5834 | 36.5852 | 30.65 | 4.4545 | 19.8424 | 3 | 5.2128 | 16.2421 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6175 | 26153.559 | 44264.8927 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 421.2 | 0:240:120 | 0:00 | 4.5069 | 7 | 0.4231 | 9.1672 | 9.5903 | 9.4861 | 0.1621 | 0.0263 | 3 | 4.5069 | 11.6007 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6178 | 26184.079 | 44264.8931 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 431.4 | 0:240:120 | 0:00 | 3.8968 | 7 | 0.5019 | 8.0921 | 8.594 | 8.2608 | 0.2491 | 0.0621 | 3 | 3.8968 | 8.7188 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6181 | 26211.016 | 44264.8934 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 442.2 | 0:240:120 | 0:00 | 3.3993 | 7 | 0.4993 | 6.6012 | 7.1005 | 6.9325 | 0.2477 | 0.0614 | 3 | 3.3993 | 6.8718 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6184 | 26233.398 | 44264.8936 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 453.4 | 0:240:120 | 0:00 | 2.9943 | 7 | 0.5 | 5.1056 | 5.6056 | 5.4378 | 0.2487 | 0.0619 | 3 | 2.9943 | 5.6115 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6187 | 26251.514 | 44264.8938 | Vista Coord | Main | 350Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 467.4 | 0:240:120 | 0:00 | 2.5981 | 7 | 0.1652 | 4.1151 | 4.2803 | 4.2241 | 0.0816 | 0.0067 | 3 | 2.5981 | 4.5441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6190 | 26364.135 | 44264.8952 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 440 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.003 | 90.5764 | 99.5794 | 96.5781 | 4.5 | 20.25 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6193 | 26665.495 | 44264.8986 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 440.7652 | 0:240:120 | 0:00 | 9.3815 | 7 | 9.0044 | 90.5753 | 99.5797 | 93.6642 | 4.4385 | 19.7007 | 3 | 9.3815 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6196 | 26948.927 | 44264.9019 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 446.7529 | 0:240:120 | 0:00 | 8.1282 | 7 | 5.8104 | 75.7708 | 81.5812 | 79.6871 | 2.838 | 8.0545 | 3 | 8.1282 | 192.0752 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6199 | 27187.398 | 44264.9047 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 451.132 | 0:240:120 | 0:00 | 7.3979 | 7 | 8.071 | 64.5081 | 72.5791 | 70.1524 | 3.6524 | 13.3404 | 3 | 7.3979 | 66.0072 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6202 | 27399.005 | 44264.9071 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 457.3787 | 0:240:120 | 0:00 | 6.5497 | 7 | 8.9985 | 54.5815 | 63.58 | 60.5796 | 4.4975 | 20.2274 | 3 | 6.5497 | 33.9139 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6205 | 27592.33 | 44264.9094 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 457.6693 | 0:240:120 | 0:00 | 6.5147 | 7 | 9.0001 | 54.5822 | 63.5823 | 60.5393 | 4.4681 | 19.9642 | 3 | 6.5147 | 33.1591 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6208 | 27767.85 | 44264.9114 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 465.1955 | 0:240:120 | 0:00 | 5.7181 | 7 | 8.9995 | 36.5837 | 45.5832 | 42.5814 | 4.4977 | 20.229 | 3 | 5.7181 | 20.9743 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6211 | 27889.314 | 44264.9128 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 473.6704 | 0:240:120 | 0:00 | 5.0168 | 7 | 8.999 | 18.5871 | 27.5861 | 24.5837 | 4.4971 | 20.2235 | 3 | 5.0168 | 14.7681 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6214 | 27974.713 | 44264.9138 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 475.6389 | 0:240:120 | 0:00 | 4.8765 | 7 | 8.9995 | 18.5872 | 27.5867 | 21.7844 | 4.3792 | 19.1771 | 3 | 4.8765 | 13.8095 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6217 | 28042.361 | 44264.9146 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 484.6633 | 0:240:120 | 0:00 | 4.3174 | 7 | 0.5017 | 9.0883 | 9.59 | 9.2564 | 0.2491 | 0.062 | 3 | 4.3174 | 10.6173 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6220 | 28073.378 | 44264.9149 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 487.1209 | 0:240:120 | 0:00 | 4.1854 | 7 | 0.499 | 8.5939 | 9.0929 | 8.9252 | 0.2479 | 0.0615 | 3 | 4.1854 | 9.9822 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6223 | 28102.339 | 44264.9153 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 495.4092 | 0:240:120 | 0:00 | 3.7907 | 7 | 0.5005 | 7.5969 | 8.0974 | 7.9287 | 0.2484 | 0.0617 | 3 | 3.7907 | 8.2927 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6226 | 28128.407 | 44264.9156 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 505.4819 | 0:240:120 | 0:00 | 3.3954 | 7 | 0.4979 | 6.6013 | 7.0992 | 6.9319 | 0.2478 | 0.0614 | 3 | 3.3954 | 6.8586 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6229 | 28151.809 | 44264.9158 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 507.9822 | 0:240:120 | 0:00 | 3.3088 | 7 | 0.5144 | 6.103 | 6.6174 | 6.4358 | 0.2494 | 0.0622 | 3 | 3.3088 | 6.5733 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6232 | 28172.679 | 44264.9161 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 521.9621 | 0:240:120 | 0:00 | 2.8909 | 7 | 0.4991 | 4.6085 | 5.1076 | 4.9397 | 0.2481 | 0.0616 | 3 | 2.8909 | 5.3186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6235 | 28190.016 | 44264.9163 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 531.9298 | 0:240:120 | 0:00 | 2.6477 | 7 | 0.1659 | 4.2789 | 4.4448 | 4.3889 | 0.0817 | 0.0067 | 3 | 2.6477 | 4.67 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6238 | 28205.79 | 44264.9165 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 539.1353 | 0:240:120 | 0:00 | 2.494 | 7 | 0.1675 | 3.9488 | 4.1163 | 4.0592 | 0.0822 | 0.0068 | 3 | 2.494 | 4.2868 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6241 | 28220.379 | 44264.9166 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 555.7112 | 0:240:120 | 0:00 | 2.1953 | 7 | 0.3013 | 3.2911 | 3.5924 | 3.443 | 0.1263 | 0.016 | 3 | 2.1953 | 3.595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6244 | 28233.595 | 44264.9168 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 563.1305 | 0:240:120 | 0:00 | 2.0817 | 7 | 0.1777 | 3.1154 | 3.2931 | 3.1844 | 0.0824 | 0.0068 | 3 | 2.0817 | 3.3486 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6247 | 28245.757 | 44264.9169 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 574.5949 | 0:240:120 | 0:00 | 1.9256 | 7 | 0.0836 | 2.798 | 2.8816 | 2.8526 | 0.0407 | 0.0017 | 3 | 1.9256 | 3.0237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6250 | 28256.948 | 44264.9171 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 589.7925 | 0:240:120 | 0:00 | 1.7484 | 7 | 0.164 | 2.4712 | 2.6352 | 2.5529 | 0.0705 | 0.005 | 3 | 1.7484 | 2.6731 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6253 | 28267.705 | 44264.9172 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 599.1492 | 0:240:120 | 0:00 | 1.6532 | 7 | 0.1648 | 2.3081 | 2.4729 | 2.39 | 0.0708 | 0.005 | 3 | 1.6532 | 2.492 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6256 | 28277.568 | 44264.9173 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 614.3071 | 0:240:120 | 0:00 | 1.5171 | 7 | 0.0495 | 2.0954 | 2.1449 | 2.128 | 0.0238 | 0.0006 | 3 | 1.5171 | 2.2417 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6259 | 28286.767 | 44264.9174 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 627.9818 | 0:240:120 | 0:00 | 1.4104 | 7 | 0.0496 | 1.9508 | 2.0004 | 1.9806 | 0.0226 | 0.0005 | 3 | 1.4104 | 2.0521 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6262 | 28295.233 | 44264.9175 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 640.5102 | 0:240:120 | 0:00 | 1.3237 | 7 | 0.0501 | 1.8058 | 1.8559 | 1.8388 | 0.0241 | 0.0006 | 3 | 1.3237 | 1.9022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6265 | 28303.563 | 44264.9176 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 660.2035 | 0:240:120 | 0:00 | 1.205 | 7 | 0.0628 | 1.5984 | 1.6612 | 1.6292 | 0.0269 | 0.0007 | 3 | 1.205 | 1.7026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6268 | 28311.19 | 44264.9177 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 671.4986 | 0:240:120 | 0:00 | 1.145 | 7 | 0.0368 | 1.5291 | 1.5659 | 1.5526 | 0.0164 | 0.0003 | 3 | 1.145 | 1.6042 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6271 | 28318.532 | 44264.9178 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 686.9269 | 0:240:120 | 0:00 | 1.0711 | 7 | 0.0637 | 1.407 | 1.4707 | 1.4371 | 0.0253 | 0.0006 | 3 | 1.0711 | 1.4851 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6274 | 28325.537 | 44264.9179 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 703.8117 | 0:240:120 | 0:00 | 0.9992 | 7 | 0.0447 | 1.298 | 1.3427 | 1.3201 | 0.0188 | 0.0004 | 3 | 0.9992 | 1.3715 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6277 | 28332.159 | 44264.9179 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 735.9396 | 0:240:120 | 0:00 | 0.8836 | 7 | 0.0212 | 1.1414 | 1.1626 | 1.1552 | 0.01 | 0.0001 | 3 | 0.8836 | 1.1932 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6280 | 28338.374 | 44264.918 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 742.1203 | 0:240:120 | 0:00 | 0.864 | 7 | 0.0392 | 1.1028 | 1.142 | 1.1201 | 0.0167 | 0.0003 | 3 | 0.864 | 1.1635 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6283 | 28344.447 | 44264.9181 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 764.1315 | 0:240:120 | 0:00 | 0.7999 | 7 | 0.034 | 1.0186 | 1.0526 | 1.0352 | 0.0142 | 0.0002 | 3 | 0.7999 | 1.0675 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6286 | 28350.196 | 44264.9181 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 786.4364 | 0:240:120 | 0:00 | 0.743 | 7 | 0.0279 | 0.9416 | 0.9695 | 0.9542 | 0.0121 | 0.0001 | 3 | 0.743 | 0.9835 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6289 | 28355.73 | 44264.9182 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 803.4081 | 0:240:120 | 0:00 | 0.7042 | 7 | 0.025 | 0.8901 | 0.9151 | 0.9019 | 0.0105 | 0.0001 | 3 | 0.7042 | 0.927 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6292 | 28361.082 | 44264.9183 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 834.232 | 0:240:120 | 0:00 | 0.6421 | 7 | 0.019 | 0.8069 | 0.8259 | 0.8159 | 0.0082 | 0.0001 | 3 | 0.6421 | 0.8376 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6295 | 28366.168 | 44264.9183 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 839.4276 | 0:240:120 | 0:00 | 0.6325 | 7 | 0.0198 | 0.7969 | 0.8167 | 0.8061 | 0.008 | 0.0001 | 3 | 0.6325 | 0.824 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6298 | 28371.358 | 44264.9184 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 872.4958 | 0:240:120 | 0:00 | 0.5772 | 7 | 0.0179 | 0.7181 | 0.736 | 0.7273 | 0.0074 | 0.0001 | 3 | 0.5772 | 0.7458 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6301 | 28376.15 | 44264.9184 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 883.1642 | 0:240:120 | 0:00 | 0.5611 | 7 | 0.0158 | 0.7031 | 0.7189 | 0.7099 | 0.0066 | 0 | 3 | 0.5611 | 0.7233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6304 | 28380.891 | 44264.9185 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 920.2204 | 0:240:120 | 0:00 | 0.5109 | 7 | 0.0131 | 0.634 | 0.6471 | 0.6416 | 0.0055 | 0 | 3 | 0.5109 | 0.6535 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6307 | 28385.642 | 44264.9185 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 954.8091 | 0:240:120 | 0:00 | 0.4707 | 7 | 0.0142 | 0.5804 | 0.5946 | 0.5891 | 0.0063 | 0 | 3 | 0.4707 | 0.5982 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6310 | 28390.044 | 44264.9186 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 966.5106 | 0:240:120 | 0:00 | 0.4584 | 7 | 0.0106 | 0.57 | 0.5806 | 0.5747 | 0.0045 | 0 | 3 | 0.4584 | 0.5813 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6313 | 28394.398 | 44264.9186 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1007.7864 | 0:240:120 | 0:00 | 0.419 | 7 | 0.0092 | 0.516 | 0.5252 | 0.5213 | 0.0036 | 0 | 3 | 0.419 | 0.5279 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6316 | 28398.636 | 44264.9187 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1011.9538 | 0:240:120 | 0:00 | 0.4153 | 7 | 0.0089 | 0.5128 | 0.5217 | 0.5178 | 0.0035 | 0 | 3 | 0.4153 | 0.523 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6319 | 28402.925 | 44264.9187 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1067.9664 | 0:240:120 | 0:00 | 0.3713 | 7 | 0.0115 | 0.4565 | 0.468 | 0.4623 | 0.0049 | 0 | 3 | 0.3713 | 0.4639 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6322 | 28407.179 | 44264.9188 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1079.6368 | 0:240:120 | 0:00 | 0.3632 | 7 | 0.0097 | 0.4464 | 0.4561 | 0.4511 | 0.0038 | 0 | 3 | 0.3632 | 0.4531 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6325 | 28411.293 | 44264.9188 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1131.7383 | 0:240:120 | 0:00 | 0.3305 | 7 | 0.0087 | 0.4043 | 0.413 | 0.4086 | 0.0034 | 0 | 3 | 0.3305 | 0.4097 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6328 | 28415.291 | 44264.9189 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1132.7635 | 0:240:120 | 0:00 | 0.3299 | 7 | 0.0087 | 0.4045 | 0.4132 | 0.4084 | 0.0036 | 0 | 3 | 0.3299 | 0.4089 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6331 | 28419.449 | 44264.9189 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1176.1563 | 0:240:120 | 0:00 | 0.3066 | 7 | 0.0078 | 0.3745 | 0.3823 | 0.3782 | 0.0031 | 0 | 3 | 0.3066 | 0.3782 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6334 | 28423.333 | 44264.919 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1191.892 | 0:240:120 | 0:00 | 0.2988 | 7 | 0.0052 | 0.3671 | 0.3723 | 0.3689 | 0.0021 | 0 | 3 | 0.2988 | 0.368 | NP | NP | 0-0-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6337 | 28427.241 | 44264.919 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1201.714 | 0:240:120 | 0:00 | 0.2942 | 7 | 0.0079 | 0.3588 | 0.3667 | 0.3628 | 0.003 | 0 | 3 | 0.2942 | 0.3619 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6340 | 28430.95 | 44264.9191 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1272.939 | 0:240:120 | 0:00 | 0.2641 | 7 | 0.0114 | 0.3192 | 0.3306 | 0.3238 | 0.0034 | 0 | 3 | 0.2641 | 0.3227 | NP | NP | 0-1-1-0-0-1-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6343 | 28434.578 | 44264.9191 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1304.4118 | 0:240:120 | 0:00 | 0.2526 | 7 | 0.0063 | 0.3073 | 0.3136 | 0.3101 | 0.0025 | 0 | 3 | 0.2526 | 0.3077 | NP | NP | 0-0-0-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6346 | 28438.263 | 44264.9192 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1334.183 | 0:240:120 | 0:00 | 0.2425 | 7 | 0.0095 | 0.2916 | 0.3011 | 0.2974 | 0.0029 | 0 | 3 | 0.2425 | 0.2946 | NP | NP | 0-0-0-0-0-1-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6349 | 28441.849 | 44264.9192 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1411.577 | 0:240:120 | 0:00 | 0.2196 | 7 | 0.0043 | 0.266 | 0.2703 | 0.2682 | 0.0014 | 0 | 3 | 0.2196 | 0.2651 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6352 | 28445.432 | 44264.9192 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1428.6856 | 0:240:120 | 0:00 | 0.2151 | 7 | 0.0078 | 0.2604 | 0.2682 | 0.2639 | 0.0024 | 0 | 3 | 0.2151 | 0.2593 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6355 | 28448.953 | 44264.9193 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1495.021 | 0:240:120 | 0:00 | 0.1992 | 7 | 0.0052 | 0.2417 | 0.2469 | 0.2435 | 0.0021 | 0 | 3 | 0.1992 | 0.2391 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6358 | 28452.359 | 44264.9193 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1582.0985 | 0:240:120 | 0:00 | 0.1816 | 7 | 0.0053 | 0.2186 | 0.2239 | 0.2218 | 0.0018 | 0 | 3 | 0.1816 | 0.2179 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6361 | 28455.868 | 44264.9194 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1590.025 | 0:240:120 | 0:00 | 0.1801 | 7 | 0.0056 | 0.2188 | 0.2244 | 0.2206 | 0.0018 | 0 | 3 | 0.1801 | 0.2161 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6364 | 28459.196 | 44264.9194 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1682.26 | 0:240:120 | 0:00 | 0.1649 | 7 | 0.0046 | 0.2005 | 0.2051 | 0.2023 | 0.0015 | 0 | 3 | 0.1649 | 0.1978 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6367 | 28462.639 | 44264.9194 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1724.1777 | 0:240:120 | 0:00 | 0.1588 | 7 | 0.0054 | 0.1913 | 0.1967 | 0.1938 | 0.0018 | 0 | 3 | 0.1588 | 0.1905 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6370 | 28465.776 | 44264.9195 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1815.511 | 0:240:120 | 0:00 | 0.147 | 7 | 0.0051 | 0.1777 | 0.1828 | 0.1798 | 0.0019 | 0 | 3 | 0.147 | 0.1764 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6373 | 28469.095 | 44264.9195 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1884.6686 | 0:240:120 | 0:00 | 0.1393 | 7 | 0.0033 | 0.1683 | 0.1716 | 0.1702 | 0.001 | 0 | 3 | 0.1393 | 0.1672 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6376 | 28472.307 | 44264.9196 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1924.842 | 0:240:120 | 0:00 | 0.1353 | 7 | 0.0042 | 0.1631 | 0.1673 | 0.1653 | 0.0013 | 0 | 3 | 0.1353 | 0.1623 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6379 | 28475.741 | 44264.9196 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2051.8738 | 0:240:120 | 0:00 | 0.124 | 7 | 0.0037 | 0.15 | 0.1537 | 0.1517 | 0.0013 | 0 | 3 | 0.124 | 0.1488 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6382 | 28478.884 | 44264.9196 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2055.729 | 0:240:120 | 0:00 | 0.1237 | 7 | 0.0025 | 0.1502 | 0.1527 | 0.1512 | 0.0008 | 0 | 3 | 0.1237 | 0.1484 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6385 | 28482.121 | 44264.9197 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2186.365 | 0:240:120 | 0:00 | 0.1143 | 7 | 0.0041 | 0.1376 | 0.1417 | 0.1397 | 0.0013 | 0 | 3 | 0.1143 | 0.1371 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6388 | 28485.258 | 44264.9197 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2279.0329 | 0:240:120 | 0:00 | 0.1086 | 7 | 0.0017 | 0.1321 | 0.1338 | 0.1327 | 0.0006 | 0 | 3 | 0.1086 | 0.1303 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6391 | 28488.503 | 44264.9197 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2419.427 | 0:240:120 | 0:00 | 0.1012 | 7 | 0.0026 | 0.1217 | 0.1243 | 0.1236 | 0.0009 | 0 | 3 | 0.1012 | 0.1214 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6394 | 28491.597 | 44264.9198 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2476.2701 | 0:240:120 | 0:00 | 0.0986 | 7 | 0.0029 | 0.1195 | 0.1224 | 0.1207 | 0.001 | 0 | 3 | 0.0986 | 0.1183 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6397 | 28494.756 | 44264.9198 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2627.479 | 0:240:120 | 0:00 | 0.0925 | 7 | 0.0027 | 0.111 | 0.1137 | 0.1126 | 0.0011 | 0 | 3 | 0.0925 | 0.1109 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6400 | 28497.712 | 44264.9198 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2766.9663 | 0:240:120 | 0:00 | 0.0877 | 7 | 0.0021 | 0.1058 | 0.1079 | 0.1071 | 0.0008 | 0 | 3 | 0.0877 | 0.1052 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6403 | 28500.546 | 44264.9199 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2901.497 | 0:240:120 | 0:00 | 0.0837 | 7 | 0.0026 | 0.1006 | 0.1032 | 0.1022 | 0.0009 | 0 | 3 | 0.0837 | 0.1005 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6406 | 28503.444 | 44264.9199 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3024.5213 | 0:240:120 | 0:00 | 0.0806 | 7 | 0.003 | 0.0971 | 0.1001 | 0.0986 | 0.0012 | 0 | 3 | 0.0806 | 0.0967 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6409 | 28506.882 | 44264.92 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3108.518 | 0:240:120 | 0:00 | 0.0787 | 7 | 0.0022 | 0.0942 | 0.0964 | 0.0955 | 0.0008 | 0 | 3 | 0.0787 | 0.0944 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6412 | 28509.869 | 44264.92 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3345.9552 | 0:240:120 | 0:00 | 0.074 | 7 | 0.0024 | 0.0883 | 0.0907 | 0.0895 | 0.0008 | 0 | 3 | 0.074 | 0.0888 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6415 | 28512.862 | 44264.92 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3361.756 | 0:240:120 | 0:00 | 0.0737 | 7 | 0.0041 | 0.0869 | 0.091 | 0.0891 | 0.0014 | 0 | 3 | 0.0737 | 0.0885 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6418 | 28516.025 | 44264.9201 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3595.7486 | 0:240:120 | 0:00 | 0.0701 | 7 | 0.0034 | 0.0832 | 0.0866 | 0.0849 | 0.0011 | 0 | 3 | 0.0701 | 0.0841 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6421 | 28519.086 | 44264.9201 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3669.953 | 0:240:120 | 0:00 | 0.069 | 7 | 0.003 | 0.0819 | 0.0849 | 0.0835 | 0.0009 | 0 | 3 | 0.069 | 0.0829 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6424 | 28522.214 | 44264.9201 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3899.1346 | 0:240:120 | 0:00 | 0.0663 | 7 | 0.0029 | 0.0786 | 0.0815 | 0.08 | 0.0009 | 0 | 3 | 0.0663 | 0.0795 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6427 | 28525.123 | 44264.9202 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3956.514 | 0:240:120 | 0:00 | 0.0657 | 7 | 0.0029 | 0.0774 | 0.0803 | 0.079 | 0.0011 | 0 | 3 | 0.0657 | 0.0788 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6430 | 28528.108 | 44264.9202 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4177.6702 | 0:240:120 | 0:00 | 0.0635 | 7 | 0.0025 | 0.0752 | 0.0777 | 0.0765 | 0.0009 | 0 | 3 | 0.0635 | 0.0762 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6433 | 28531.129 | 44264.9202 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4305.728 | 0:240:120 | 0:00 | 0.0624 | 7 | 0.0026 | 0.0739 | 0.0765 | 0.0752 | 0.0009 | 0 | 3 | 0.0624 | 0.0749 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6436 | 28534.191 | 44264.9203 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4566.5329 | 0:240:120 | 0:00 | 0.0605 | 7 | 0.0027 | 0.0713 | 0.074 | 0.0726 | 0.0009 | 0 | 3 | 0.0605 | 0.0726 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6439 | 28537.13 | 44264.9203 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4730.008 | 0:240:120 | 0:00 | 0.0594 | 7 | 0.0033 | 0.0688 | 0.0721 | 0.0708 | 0.0011 | 0 | 3 | 0.0594 | 0.0713 | P | NP | 1-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6442 | 28540.119 | 44264.9203 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4800.6599 | 0:240:120 | 0:00 | 0.059 | 7 | 0.0033 | 0.0686 | 0.0719 | 0.0704 | 0.0011 | 0 | 3 | 0.059 | 0.0708 | P | NP | 0-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6445 | 28542.975 | 44264.9204 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5041.7545 | 0:240:120 | 0:00 | 0.0577 | 7 | 0.0026 | 0.0673 | 0.0699 | 0.0688 | 0.0009 | 0 | 3 | 0.0577 | 0.0692 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6448 | 28545.913 | 44264.9204 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5169.038 | 0:240:120 | 0:00 | 0.057 | 7 | 0.003 | 0.0661 | 0.0691 | 0.0675 | 0.0011 | 0 | 3 | 0.057 | 0.0685 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6451 | 28548.714 | 44264.9204 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5660.627 | 0:240:120 | 0:00 | 0.055 | 7 | 0.0025 | 0.0639 | 0.0664 | 0.065 | 0.0008 | 0 | 3 | 0.055 | 0.066 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6454 | 28551.574 | 44264.9205 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6109.003 | 0:240:120 | 0:00 | 0.0536 | 7 | 0.0025 | 0.0611 | 0.0636 | 0.0628 | 0.0011 | 0 | 3 | 0.0536 | 0.0643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6457 | 28554.614 | 44264.9205 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6788.506 | 0:240:120 | 0:00 | 0.052 | 7 | 0.0038 | 0.0582 | 0.062 | 0.0604 | 0.0012 | 0 | 3 | 0.052 | 0.0624 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6460 | 28557.675 | 44264.9205 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7543.591 | 0:240:120 | 0:00 | 0.0506 | 7 | 0.0029 | 0.0572 | 0.0601 | 0.0588 | 0.001 | 0 | 3 | 0.0506 | 0.0608 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6463 | 28560.473 | 44264.9206 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8470.656 | 0:240:120 | 0:00 | 0.0495 | 7 | 0.0018 | 0.0557 | 0.0575 | 0.0568 | 0.0006 | 0 | 3 | 0.0495 | 0.0595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6466 | 28563.334 | 44264.9206 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9227.931 | 0:240:120 | 0:00 | 0.0488 | 7 | 0.0028 | 0.0539 | 0.0567 | 0.0558 | 0.001 | 0 | 3 | 0.0488 | 0.0588 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6469 | 28566.445 | 44264.9206 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9938.094 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0028 | 0.0527 | 0.0555 | 0.0543 | 0.0011 | 0 | 3 | 0.0482 | 0.0582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6472 | 28569.504 | 44264.9207 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10691.74 | 0:240:120 | 0:00 | 0.0478 | 7 | 0.0037 | 0.0515 | 0.0552 | 0.0534 | 0.0011 | 0 | 3 | 0.0478 | 0.0578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6475 | 28572.422 | 44264.9207 | Vista Coord | Main | 400Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11806.774 | 0:240:120 | 0:00 | 0.0473 | 7 | 0.0033 | 0.0512 | 0.0545 | 0.0529 | 0.0012 | 0 | 3 | 0.0473 | 0.0573 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6478 | 28676.709 | 44264.9219 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 495 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.0026 | 90.5748 | 99.5774 | 95.962 | 4.3514 | 18.9347 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6481 | 28969.071 | 44264.9253 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 498.3473 | 0:240:120 | 0:00 | 8.8781 | 7 | 9.0034 | 81.5764 | 90.5798 | 87.577 | 4.4991 | 20.242 | 3 | 8.8781 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6484 | 29235.235 | 44264.9284 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 502.3722 | 0:240:120 | 0:00 | 8.1648 | 7 | 9.5086 | 72.5822 | 82.0908 | 78.7429 | 4.3916 | 19.2863 | 3 | 8.1648 | 210.321 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6487 | 29473.747 | 44264.9311 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 507.6885 | 0:240:120 | 0:00 | 7.3756 | 7 | 9.001 | 63.58 | 72.581 | 69.5788 | 4.4982 | 20.2337 | 3 | 7.3756 | 64.581 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6490 | 29676.436 | 44264.9335 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 519.0449 | 0:240:120 | 0:00 | 6.0981 | 7 | 8.9998 | 45.5839 | 54.5837 | 51.5812 | 4.4974 | 20.2268 | 3 | 6.0981 | 25.8081 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6493 | 29825.04 | 44264.9352 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 528.3861 | 0:240:120 | 0:00 | 5.3259 | 7 | 8.9992 | 27.5866 | 36.5858 | 33.5833 | 4.4971 | 20.2236 | 3 | 5.3259 | 17.1731 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6496 | 29928.471 | 44264.9364 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 534.4768 | 0:240:120 | 0:00 | 4.9148 | 7 | 9.0007 | 18.5865 | 27.5872 | 24.5846 | 4.4974 | 20.2262 | 3 | 4.9148 | 14.0642 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6499 | 29995.99 | 44264.9372 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 544.0446 | 0:240:120 | 0:00 | 4.3773 | 7 | 0.4992 | 9.0912 | 9.5904 | 9.4221 | 0.2475 | 0.0613 | 3 | 4.3773 | 10.9182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6502 | 30026.697 | 44264.9375 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 556.1006 | 0:240:120 | 0:00 | 3.839 | 7 | 0.9966 | 7.5975 | 8.5941 | 8.0914 | 0.4268 | 0.1822 | 3 | 3.839 | 8.4841 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6505 | 30053.8 | 44264.9379 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 569.0168 | 0:240:120 | 0:00 | 3.3844 | 7 | 0.4982 | 6.6011 | 7.0993 | 6.9292 | 0.2459 | 0.0605 | 3 | 3.3844 | 6.8219 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6508 | 30076.277 | 44264.9381 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 585.8908 | 0:240:120 | 0:00 | 2.9221 | 7 | 0.7548 | 4.6093 | 5.3641 | 5.0199 | 0.3251 | 0.1057 | 3 | 2.9221 | 5.4059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6511 | 30093.951 | 44264.9383 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 603.8945 | 0:240:120 | 0:00 | 2.5421 | 7 | 0.1646 | 4.115 | 4.2796 | 4.1727 | 0.0799 | 0.0064 | 3 | 2.5421 | 4.4046 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6514 | 30109.05 | 44264.9385 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 622.4515 | 0:240:120 | 0:00 | 2.2348 | 7 | 0.1666 | 3.4553 | 3.6219 | 3.565 | 0.0821 | 0.0067 | 3 | 2.2348 | 3.6828 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6517 | 30122.14 | 44264.9386 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 637.5743 | 0:240:120 | 0:00 | 2.0303 | 7 | 0.1676 | 2.9613 | 3.1289 | 3.0693 | 0.0807 | 0.0065 | 3 | 2.0303 | 3.2399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6520 | 30133.83 | 44264.9388 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 660.605 | 0:240:120 | 0:00 | 1.7765 | 7 | 0.0824 | 2.5535 | 2.6359 | 2.6073 | 0.0403 | 0.0016 | 3 | 1.7765 | 2.7274 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6523 | 30144.364 | 44264.9389 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 676.654 | 0:240:120 | 0:00 | 1.631 | 7 | 0.082 | 2.3085 | 2.3905 | 2.3622 | 0.0399 | 0.0016 | 3 | 1.631 | 2.4505 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6526 | 30153.749 | 44264.939 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 709.192 | 0:240:120 | 0:00 | 1.393 | 7 | 0.0493 | 1.9032 | 1.9525 | 1.9355 | 0.0237 | 0.0006 | 3 | 1.393 | 2.0216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6529 | 30162.14 | 44264.9391 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 727.9393 | 0:240:120 | 0:00 | 1.282 | 7 | 0.0963 | 1.7094 | 1.8057 | 1.7576 | 0.0411 | 0.0017 | 3 | 1.282 | 1.8314 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6532 | 30170.092 | 44264.9392 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 750.3089 | 0:240:120 | 0:00 | 1.1686 | 7 | 0.0324 | 1.5656 | 1.598 | 1.5852 | 0.0146 | 0.0002 | 3 | 1.1686 | 1.6426 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6535 | 30177.435 | 44264.9393 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 786.3878 | 0:240:120 | 0:00 | 1.0188 | 7 | 0.0547 | 1.3209 | 1.3756 | 1.346 | 0.0233 | 0.0005 | 3 | 1.0188 | 1.4022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6538 | 30184.108 | 44264.9394 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 815.6456 | 0:240:120 | 0:00 | 0.9202 | 7 | 0.0439 | 1.1857 | 1.2296 | 1.2076 | 0.0187 | 0.0004 | 3 | 0.9202 | 1.249 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6541 | 30190.259 | 44264.9394 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 848.6434 | 0:240:120 | 0:00 | 0.8273 | 7 | 0.0318 | 1.0536 | 1.0854 | 1.0723 | 0.0127 | 0.0002 | 3 | 0.8273 | 1.1084 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6544 | 30196.079 | 44264.9395 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 882.0559 | 0:240:120 | 0:00 | 0.7487 | 7 | 0.0166 | 0.9529 | 0.9695 | 0.9639 | 0.0076 | 0.0001 | 3 | 0.7487 | 0.9919 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6547 | 30201.487 | 44264.9396 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 920.6186 | 0:240:120 | 0:00 | 0.6729 | 7 | 0.0238 | 0.8524 | 0.8762 | 0.8631 | 0.0093 | 0.0001 | 3 | 0.6729 | 0.8818 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6550 | 30206.602 | 44264.9396 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 961.8719 | 0:240:120 | 0:00 | 0.6054 | 7 | 0.0199 | 0.7574 | 0.7773 | 0.7682 | 0.0085 | 0.0001 | 3 | 0.6054 | 0.7855 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6553 | 30211.775 | 44264.9397 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1008.1236 | 0:240:120 | 0:00 | 0.5427 | 7 | 0.0163 | 0.6784 | 0.6947 | 0.6858 | 0.007 | 0 | 3 | 0.5427 | 0.6975 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6556 | 30216.282 | 44264.9397 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1054.3973 | 0:240:120 | 0:00 | 0.4904 | 7 | 0.0152 | 0.6079 | 0.6231 | 0.6158 | 0.0059 | 0 | 3 | 0.4904 | 0.6252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6559 | 30220.938 | 44264.9398 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1123.332 | 0:240:120 | 0:00 | 0.4273 | 7 | 0.0142 | 0.5252 | 0.5394 | 0.5326 | 0.0054 | 0 | 3 | 0.4273 | 0.5391 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6562 | 30225.242 | 44264.9398 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1198.424 | 0:240:120 | 0:00 | 0.3733 | 7 | 0.0085 | 0.4598 | 0.4683 | 0.4636 | 0.0032 | 0 | 3 | 0.3733 | 0.4665 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6565 | 30229.437 | 44264.9399 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1254.741 | 0:240:120 | 0:00 | 0.3402 | 7 | 0.0164 | 0.4125 | 0.4289 | 0.4195 | 0.0047 | 0 | 3 | 0.3402 | 0.4225 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6568 | 30233.384 | 44264.9399 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1365.427 | 0:240:120 | 0:00 | 0.2887 | 7 | 0.0106 | 0.3488 | 0.3594 | 0.3548 | 0.0039 | 0 | 3 | 0.2887 | 0.3547 | NP | NP | 0-0-1-0-0-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6571 | 30237.212 | 44264.94 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1487.429 | 0:240:120 | 0:00 | 0.2465 | 7 | 0.0078 | 0.2979 | 0.3057 | 0.302 | 0.0031 | 0 | 3 | 0.2465 | 0.2998 | NP | NP | 0-0-1-0-1-1-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6574 | 30240.909 | 44264.94 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1576.954 | 0:240:120 | 0:00 | 0.2223 | 7 | 0.0047 | 0.2707 | 0.2754 | 0.2724 | 0.0013 | 0 | 3 | 0.2223 | 0.2685 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6577 | 30244.613 | 44264.9401 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1698.247 | 0:240:120 | 0:00 | 0.196 | 7 | 0.0039 | 0.2375 | 0.2414 | 0.2396 | 0.0013 | 0 | 3 | 0.196 | 0.2352 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6580 | 30247.985 | 44264.9401 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1836.52 | 0:240:120 | 0:00 | 0.1727 | 7 | 0.0065 | 0.2088 | 0.2153 | 0.2114 | 0.0021 | 0 | 3 | 0.1727 | 0.2073 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6583 | 30251.328 | 44264.9401 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1947.056 | 0:240:120 | 0:00 | 0.1579 | 7 | 0.0052 | 0.19 | 0.1952 | 0.1928 | 0.0019 | 0 | 3 | 0.1579 | 0.1894 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6586 | 30254.568 | 44264.9402 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2075.046 | 0:240:120 | 0:00 | 0.1437 | 7 | 0.0033 | 0.1743 | 0.1776 | 0.1755 | 0.0012 | 0 | 3 | 0.1437 | 0.1724 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6589 | 30257.839 | 44264.9402 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2183.925 | 0:240:120 | 0:00 | 0.1337 | 7 | 0.0029 | 0.1621 | 0.165 | 0.1637 | 0.0012 | 0 | 3 | 0.1337 | 0.1604 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6592 | 30261.087 | 44264.9403 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2332.348 | 0:240:120 | 0:00 | 0.1223 | 7 | 0.0022 | 0.1498 | 0.152 | 0.1502 | 0.0008 | 0 | 3 | 0.1223 | 0.1468 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6595 | 30264.516 | 44264.9403 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2444.501 | 0:240:120 | 0:00 | 0.1152 | 7 | 0.0037 | 0.1385 | 0.1422 | 0.1403 | 0.0013 | 0 | 3 | 0.1152 | 0.1382 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6598 | 30267.605 | 44264.9403 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2632.522 | 0:240:120 | 0:00 | 0.1052 | 7 | 0.004 | 0.1267 | 0.1307 | 0.1283 | 0.0013 | 0 | 3 | 0.1052 | 0.1262 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6601 | 30270.714 | 44264.9404 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2808.5 | 0:240:120 | 0:00 | 0.0977 | 7 | 0.0017 | 0.1186 | 0.1203 | 0.1195 | 0.0006 | 0 | 3 | 0.0977 | 0.1172 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6604 | 30273.67 | 44264.9404 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3055 | 0:240:120 | 0:00 | 0.0894 | 7 | 0.0034 | 0.1067 | 0.1101 | 0.1088 | 0.0013 | 0 | 3 | 0.0894 | 0.1072 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6607 | 30276.708 | 44264.9404 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3300 | 0:240:120 | 0:00 | 0.0829 | 7 | 0.003 | 0.0996 | 0.1026 | 0.101 | 0.0011 | 0 | 3 | 0.0829 | 0.0995 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6610 | 30279.708 | 44264.9405 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3585.407 | 0:240:120 | 0:00 | 0.077 | 7 | 0.0036 | 0.0913 | 0.0949 | 0.0934 | 0.0014 | 0 | 3 | 0.077 | 0.0924 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6613 | 30282.594 | 44264.9405 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3849.111 | 0:240:120 | 0:00 | 0.0727 | 7 | 0.0036 | 0.0865 | 0.0901 | 0.0883 | 0.0012 | 0 | 3 | 0.0727 | 0.0873 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6616 | 30285.653 | 44264.9405 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4114.996 | 0:240:120 | 0:00 | 0.0692 | 7 | 0.0029 | 0.0824 | 0.0853 | 0.0839 | 0.0011 | 0 | 3 | 0.0692 | 0.083 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6619 | 30288.583 | 44264.9406 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4459.342 | 0:240:120 | 0:00 | 0.0656 | 7 | 0.004 | 0.0768 | 0.0808 | 0.0788 | 0.0014 | 0 | 3 | 0.0656 | 0.0787 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6622 | 30291.798 | 44264.9406 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4873.021 | 0:240:120 | 0:00 | 0.0622 | 7 | 0.0018 | 0.0742 | 0.076 | 0.075 | 0.0006 | 0 | 3 | 0.0622 | 0.0746 | NP | NP | 0-0-0-0-1-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6625 | 30294.757 | 44264.9406 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5386.563 | 0:240:120 | 0:00 | 0.0591 | 7 | 0.0028 | 0.0692 | 0.072 | 0.0707 | 0.001 | 0 | 3 | 0.0591 | 0.0709 | P | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6628 | 30297.617 | 44264.9407 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5898.557 | 0:240:120 | 0:00 | 0.0567 | 7 | 0.0028 | 0.0661 | 0.0689 | 0.0676 | 0.001 | 0 | 3 | 0.0567 | 0.0681 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6631 | 30300.633 | 44264.9407 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6385.485 | 0:240:120 | 0:00 | 0.055 | 7 | 0.003 | 0.0633 | 0.0663 | 0.0647 | 0.001 | 0 | 3 | 0.055 | 0.066 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6634 | 30303.659 | 44264.9407 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6948.777 | 0:240:120 | 0:00 | 0.0534 | 7 | 0.0015 | 0.062 | 0.0635 | 0.0629 | 0.0006 | 0 | 3 | 0.0534 | 0.0641 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6637 | 30306.671 | 44264.9408 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7538.119 | 0:240:120 | 0:00 | 0.0522 | 7 | 0.0025 | 0.0596 | 0.0621 | 0.0611 | 0.001 | 0 | 3 | 0.0522 | 0.0626 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6640 | 30309.501 | 44264.9408 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8332.521 | 0:240:120 | 0:00 | 0.0509 | 7 | 0.0036 | 0.0571 | 0.0607 | 0.0591 | 0.0013 | 0 | 3 | 0.0509 | 0.061 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6643 | 30312.395 | 44264.9408 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8954.714 | 0:240:120 | 0:00 | 0.0501 | 7 | 0.0028 | 0.0556 | 0.0584 | 0.0577 | 0.0009 | 0 | 3 | 0.0501 | 0.0601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6646 | 30315.371 | 44264.9409 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9734.483 | 0:240:120 | 0:00 | 0.0493 | 7 | 0.0042 | 0.0541 | 0.0583 | 0.0561 | 0.0015 | 0 | 3 | 0.0493 | 0.0593 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6649 | 30318.267 | 44264.9409 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10907.338 | 0:240:120 | 0:00 | 0.0484 | 7 | 0.0036 | 0.0529 | 0.0565 | 0.0548 | 0.0012 | 0 | 3 | 0.0484 | 0.0584 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6652 | 30321.707 | 44264.941 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11431.828 | 0:240:120 | 0:00 | 0.0481 | 7 | 0.0034 | 0.0526 | 0.056 | 0.0545 | 0.0011 | 0 | 3 | 0.0481 | 0.0581 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6655 | 30370.319 | 44264.9415 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 523.7 | 0:240:120 | 0:00 | 5.6887 | 7 | 8.9988 | 36.5862 | 45.585 | 42.4803 | 4.4307 | 19.6311 | 3 | 5.6887 | 20.6536 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6658 | 30494.486 | 44264.943 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 531.4 | 0:240:120 | 0:00 | 5.1147 | 7 | 13.1314 | 18.588 | 31.7194 | 25.6032 | 5.1847 | 26.8814 | 3 | 5.1147 | 15.4838 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6661 | 30576.627 | 44264.9439 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 539.3 | 0:240:120 | 0:00 | 4.6293 | 7 | 8.9982 | 9.5889 | 18.5871 | 15.0037 | 4.1901 | 17.5567 | 3 | 4.6293 | 12.2866 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6664 | 30625.565 | 44264.9445 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 550.1 | 0:240:120 | 0:00 | 4.0905 | 7 | 0.5021 | 8.5908 | 9.0929 | 8.759 | 0.2494 | 0.0622 | 3 | 4.0905 | 9.5489 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6667 | 30654.051 | 44264.9448 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 562.6 | 0:240:120 | 0:00 | 3.597 | 7 | 0.498 | 7.0992 | 7.5972 | 7.4304 | 0.2476 | 0.0613 | 3 | 3.597 | 7.5617 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6670 | 30678.033 | 44264.9451 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 577.5 | 0:240:120 | 0:00 | 3.1365 | 7 | 0.4973 | 5.6063 | 6.1036 | 5.9366 | 0.2474 | 0.0612 | 3 | 3.1365 | 6.0326 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6673 | 30697.575 | 44264.9453 | Vista Coord | Main | 450Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 594.9 | 0:240:120 | 0:00 | 2.7199 | 7 | 0.3312 | 4.2791 | 4.6103 | 4.4442 | 0.1423 | 0.0202 | 3 | 2.7199 | 4.857 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6676 | 30810.142 | 44264.9466 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 550 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.0027 | 90.5755 | 99.5782 | 96.5769 | 4.4999 | 20.2493 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6679 | 31111.597 | 44264.9501 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 551.4762 | 0:240:120 | 0:00 | 9.2827 | 7 | 9.0032 | 90.5746 | 99.5778 | 93.5759 | 4.5005 | 20.2544 | 3 | 9.2827 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6682 | 31403.957 | 44264.9535 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 556.6814 | 0:240:120 | 0:00 | 8.3931 | 7 | 9.0017 | 81.5762 | 90.5779 | 84.6169 | 4.4701 | 19.9814 | 3 | 8.3931 | 493.0023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6685 | 31660.76 | 44264.9565 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 564.2857 | 0:240:120 | 0:00 | 7.353 | 7 | 8.9979 | 63.5819 | 72.5798 | 69.5787 | 4.4975 | 20.2271 | 3 | 7.353 | 63.1854 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6688 | 31872.256 | 44264.9589 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 571.9934 | 0:240:120 | 0:00 | 6.5237 | 7 | 8.9999 | 54.5805 | 63.5804 | 60.5789 | 4.4981 | 20.2325 | 3 | 6.5237 | 33.3496 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6691 | 32047.923 | 44264.9609 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 580.4128 | 0:240:120 | 0:00 | 5.8001 | 7 | 8.9996 | 36.5837 | 45.5833 | 42.5818 | 4.498 | 20.2324 | 3 | 5.8001 | 21.9058 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6694 | 32169.382 | 44264.9623 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 595.1352 | 0:240:120 | 0:00 | 4.8441 | 7 | 9.0056 | 18.5818 | 27.5874 | 21.5861 | 4.5003 | 20.2525 | 3 | 4.8441 | 13.5986 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6697 | 32236.232 | 44264.9631 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 612.7825 | 0:240:120 | 0:00 | 4.029 | 7 | 0.5881 | 8.0956 | 8.6837 | 8.4378 | 0.2579 | 0.0665 | 3 | 4.029 | 9.2774 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6700 | 32263.69 | 44264.9634 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 628.9822 | 0:240:120 | 0:00 | 3.4786 | 7 | 0.8709 | 6.6014 | 7.4723 | 7.0304 | 0.3484 | 0.1214 | 3 | 3.4786 | 7.1421 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6703 | 32287.386 | 44264.9637 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 644.9355 | 0:240:120 | 0:00 | 3.0581 | 7 | 0.9962 | 5.1076 | 6.1038 | 5.6046 | 0.4308 | 0.1856 | 3 | 3.0581 | 5.7979 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6706 | 32306.737 | 44264.9639 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 662.6763 | 0:240:120 | 0:00 | 2.6885 | 7 | 0.166 | 4.2786 | 4.4446 | 4.3882 | 0.0821 | 0.0067 | 3 | 2.6885 | 4.7752 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6709 | 32322.138 | 44264.9641 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 685.1823 | 0:240:120 | 0:00 | 2.3232 | 7 | 0.1659 | 3.6201 | 3.786 | 3.7296 | 0.0817 | 0.0067 | 3 | 2.3232 | 3.883 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6712 | 32335.651 | 44264.9643 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 709.192 | 0:240:120 | 0:00 | 2.0216 | 7 | 0.1688 | 2.9589 | 3.1277 | 3.0155 | 0.0836 | 0.007 | 3 | 2.0216 | 3.2218 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6715 | 32347.115 | 44264.9644 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 741.7443 | 0:240:120 | 0:00 | 1.7106 | 7 | 0.0853 | 2.4686 | 2.5539 | 2.4984 | 0.0411 | 0.0017 | 3 | 1.7106 | 2.6006 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6718 | 32356.964 | 44264.9645 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 773.3649 | 0:240:120 | 0:00 | 1.4814 | 7 | 0.0481 | 2.0485 | 2.0966 | 2.08 | 0.0234 | 0.0005 | 3 | 1.4814 | 2.1776 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6721 | 32365.634 | 44264.9646 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 816.497 | 0:240:120 | 0:00 | 1.245 | 7 | 0.0491 | 1.6608 | 1.7099 | 1.6932 | 0.0238 | 0.0006 | 3 | 1.245 | 1.7691 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6724 | 32373.527 | 44264.9647 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 865.6395 | 0:240:120 | 0:00 | 1.0463 | 7 | 0.0325 | 1.3747 | 1.4072 | 1.3956 | 0.0153 | 0.0002 | 3 | 1.0463 | 1.4457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6727 | 32380.097 | 44264.9648 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 914.8722 | 0:240:120 | 0:00 | 0.8968 | 7 | 0.0237 | 1.1631 | 1.1868 | 1.1786 | 0.011 | 0.0001 | 3 | 0.8968 | 1.2133 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6730 | 32386.217 | 44264.9649 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 958.8645 | 0:240:120 | 0:00 | 0.7919 | 7 | 0.0182 | 1.0179 | 1.0361 | 1.0295 | 0.0083 | 0.0001 | 3 | 0.7919 | 1.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6733 | 32391.904 | 44264.9649 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1010.2301 | 0:240:120 | 0:00 | 0.6939 | 7 | 0.0253 | 0.8775 | 0.9028 | 0.8893 | 0.0107 | 0.0001 | 3 | 0.6939 | 0.9121 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6736 | 32397.268 | 44264.965 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1065.46 | 0:240:120 | 0:00 | 0.6098 | 7 | 0.0198 | 0.7669 | 0.7867 | 0.7761 | 0.0082 | 0.0001 | 3 | 0.6098 | 0.7918 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6739 | 32402.14 | 44264.965 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1124.882 | 0:240:120 | 0:00 | 0.5374 | 7 | 0.0162 | 0.6702 | 0.6864 | 0.6778 | 0.0065 | 0 | 3 | 0.5374 | 0.6902 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6742 | 32406.778 | 44264.9651 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1180.2032 | 0:240:120 | 0:00 | 0.4825 | 7 | 0.0125 | 0.601 | 0.6135 | 0.6069 | 0.0051 | 0 | 3 | 0.4825 | 0.6143 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6745 | 32411.36 | 44264.9651 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1259.0974 | 0:240:120 | 0:00 | 0.4194 | 7 | 0.0154 | 0.5132 | 0.5286 | 0.5216 | 0.0056 | 0 | 3 | 0.4194 | 0.5285 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6748 | 32415.665 | 44264.9652 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1332.0967 | 0:240:120 | 0:00 | 0.373 | 7 | 0.0157 | 0.4527 | 0.4684 | 0.4615 | 0.0053 | 0 | 3 | 0.373 | 0.4661 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6751 | 32419.724 | 44264.9652 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1365.427 | 0:240:120 | 0:00 | 0.3547 | 7 | 0.0097 | 0.4353 | 0.445 | 0.4383 | 0.0034 | 0 | 3 | 0.3547 | 0.4418 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6754 | 32423.6 | 44264.9653 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1467.384 | 0:240:120 | 0:00 | 0.3077 | 7 | 0.0133 | 0.3727 | 0.386 | 0.3789 | 0.0043 | 0 | 3 | 0.3077 | 0.3796 | P | NP | 0-1-1-0-1-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6757 | 32427.249 | 44264.9653 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1563.842 | 0:240:120 | 0:00 | 0.2727 | 7 | 0.0089 | 0.331 | 0.3399 | 0.335 | 0.0028 | 0 | 3 | 0.2727 | 0.3339 | NP | NP | 0-0-1-0-0-1-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6760 | 32430.863 | 44264.9654 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1728.647 | 0:240:120 | 0:00 | 0.2276 | 7 | 0.0055 | 0.2758 | 0.2813 | 0.2785 | 0.0021 | 0 | 3 | 0.2276 | 0.2754 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6763 | 32434.687 | 44264.9654 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1869.396 | 0:240:120 | 0:00 | 0.1991 | 7 | 0.005 | 0.2411 | 0.2461 | 0.2434 | 0.0017 | 0 | 3 | 0.1991 | 0.2389 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6766 | 32438.198 | 44264.9655 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2006.888 | 0:240:120 | 0:00 | 0.1774 | 7 | 0.0041 | 0.2155 | 0.2196 | 0.2169 | 0.0015 | 0 | 3 | 0.1774 | 0.2128 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6769 | 32441.459 | 44264.9655 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2186.205 | 0:240:120 | 0:00 | 0.1554 | 7 | 0.0028 | 0.1883 | 0.1911 | 0.1895 | 0.0011 | 0 | 3 | 0.1554 | 0.1865 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6772 | 32444.745 | 44264.9655 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2369.149 | 0:240:120 | 0:00 | 0.1382 | 7 | 0.0025 | 0.1671 | 0.1696 | 0.1686 | 0.0009 | 0 | 3 | 0.1382 | 0.1659 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6775 | 32447.901 | 44264.9656 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2540.745 | 0:240:120 | 0:00 | 0.1256 | 7 | 0.0032 | 0.1516 | 0.1548 | 0.1532 | 0.0011 | 0 | 3 | 0.1256 | 0.1507 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6778 | 32451.114 | 44264.9656 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2716.252 | 0:240:120 | 0:00 | 0.1151 | 7 | 0.003 | 0.1384 | 0.1414 | 0.14 | 0.001 | 0 | 3 | 0.1151 | 0.1382 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6781 | 32454.367 | 44264.9656 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2906.914 | 0:240:120 | 0:00 | 0.106 | 7 | 0.0029 | 0.1279 | 0.1308 | 0.1295 | 0.0011 | 0 | 3 | 0.106 | 0.1272 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6784 | 32457.858 | 44264.9657 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3146.881 | 0:240:120 | 0:00 | 0.0968 | 7 | 0.0033 | 0.1167 | 0.12 | 0.1182 | 0.0012 | 0 | 3 | 0.0968 | 0.1162 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6787 | 32460.909 | 44264.9657 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3445.993 | 0:240:120 | 0:00 | 0.088 | 7 | 0.0025 | 0.1061 | 0.1086 | 0.1075 | 0.0008 | 0 | 3 | 0.088 | 0.1056 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6790 | 32464.038 | 44264.9658 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3676.35 | 0:240:120 | 0:00 | 0.0827 | 7 | 0.0036 | 0.0984 | 0.102 | 0.1003 | 0.0014 | 0 | 3 | 0.0827 | 0.0992 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6793 | 32467.086 | 44264.9658 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3988.15 | 0:240:120 | 0:00 | 0.0769 | 7 | 0.0031 | 0.0912 | 0.0943 | 0.0932 | 0.0013 | 0 | 3 | 0.0769 | 0.0923 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6796 | 32470.049 | 44264.9658 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4349.03 | 0:240:120 | 0:00 | 0.0718 | 7 | 0.0019 | 0.0868 | 0.0887 | 0.0878 | 0.0006 | 0 | 3 | 0.0718 | 0.0861 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6799 | 32473.038 | 44264.9659 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4693.327 | 0:240:120 | 0:00 | 0.068 | 7 | 0.0029 | 0.0805 | 0.0834 | 0.0821 | 0.0011 | 0 | 3 | 0.068 | 0.0816 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6802 | 32475.887 | 44264.9659 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4970.617 | 0:240:120 | 0:00 | 0.0654 | 7 | 0.0029 | 0.0773 | 0.0802 | 0.0786 | 0.0011 | 0 | 3 | 0.0654 | 0.0785 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6805 | 32478.677 | 44264.9659 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5448.76 | 0:240:120 | 0:00 | 0.062 | 7 | 0.0034 | 0.0723 | 0.0757 | 0.0744 | 0.0012 | 0 | 3 | 0.062 | 0.0744 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6808 | 32481.611 | 44264.966 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5892.404 | 0:240:120 | 0:00 | 0.0595 | 7 | 0.0038 | 0.0692 | 0.073 | 0.0714 | 0.0013 | 0 | 3 | 0.0595 | 0.0714 | P | NP | 0-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6811 | 32484.457 | 44264.966 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6418.894 | 0:240:120 | 0:00 | 0.0572 | 7 | 0.0029 | 0.0663 | 0.0692 | 0.0678 | 0.0011 | 0 | 3 | 0.0572 | 0.0687 | P | NP | 1-1-1-0-1-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6814 | 32487.437 | 44264.966 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7162.309 | 0:240:120 | 0:00 | 0.0548 | 7 | 0.0027 | 0.0634 | 0.0661 | 0.0648 | 0.001 | 0 | 3 | 0.0548 | 0.0658 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6817 | 32490.359 | 44264.9661 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7721.259 | 0:240:120 | 0:00 | 0.0534 | 7 | 0.0022 | 0.0614 | 0.0636 | 0.0627 | 0.0007 | 0 | 3 | 0.0534 | 0.0641 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6820 | 32493.518 | 44264.9661 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8437.535 | 0:240:120 | 0:00 | 0.052 | 7 | 0.0028 | 0.0589 | 0.0617 | 0.0602 | 0.001 | 0 | 3 | 0.052 | 0.0625 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6823 | 32496.537 | 44264.9661 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9326.722 | 0:240:120 | 0:00 | 0.0508 | 7 | 0.0033 | 0.0572 | 0.0605 | 0.059 | 0.0011 | 0 | 3 | 0.0508 | 0.0609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6826 | 32499.663 | 44264.9662 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10086.115 | 0:240:120 | 0:00 | 0.0499 | 7 | 0.0038 | 0.0559 | 0.0597 | 0.0574 | 0.0012 | 0 | 3 | 0.0499 | 0.0599 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6829 | 32502.538 | 44264.9662 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11033.281 | 0:240:120 | 0:00 | 0.0491 | 7 | 0.0036 | 0.0543 | 0.0579 | 0.0559 | 0.0012 | 0 | 3 | 0.0491 | 0.0591 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6832 | 32560.044 | 44264.9669 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 576.2 | 0:240:120 | 0:00 | 6.1421 | 7 | 8.9983 | 45.5837 | 54.582 | 51.5304 | 4.4623 | 19.9121 | 3 | 6.1421 | 26.4648 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6835 | 32708.499 | 44264.9686 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 587.8 | 0:240:120 | 0:00 | 5.2801 | 7 | 8.9993 | 27.5859 | 36.5852 | 33.5823 | 4.4971 | 20.2236 | 3 | 5.2801 | 16.7886 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6838 | 32794.002 | 44264.9696 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 604 | 0:240:120 | 0:00 | 4.3998 | 7 | 0.4975 | 9.0917 | 9.5892 | 9.4226 | 0.2477 | 0.0613 | 3 | 4.3998 | 11.0338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6841 | 32824.08 | 44264.9699 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 620.9 | 0:240:120 | 0:00 | 3.7346 | 7 | 0.4992 | 7.5971 | 8.0963 | 7.9273 | 0.2471 | 0.0611 | 3 | 3.7346 | 8.0747 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6844 | 32849.583 | 44264.9702 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 637 | 0:240:120 | 0:00 | 3.2549 | 7 | 0.5004 | 6.1019 | 6.6023 | 6.4344 | 0.2485 | 0.0617 | 3 | 3.2549 | 6.4004 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6847 | 32870.635 | 44264.9705 | Vista Coord | Main | 500Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 653.8 | 0:240:120 | 0:00 | 2.8626 | 7 | 0.499 | 4.6096 | 5.1086 | 4.8654 | 0.2214 | 0.049 | 3 | 2.8626 | 5.2404 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6850 | 32984.89 | 44264.9718 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 660 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.0018 | 90.5766 | 99.5784 | 96.5729 | 4.4967 | 20.2201 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6853 | 33286.33 | 44264.9753 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 661.1 | 0:240:120 | 0:00 | 9.3892 | 7 | 9.0023 | 90.5752 | 99.5775 | 93.5766 | 4.4999 | 20.2495 | 3 | 9.3892 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6856 | 33578.792 | 44264.9787 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 664.3527 | 0:240:120 | 0:00 | 8.8941 | 7 | 9.0019 | 81.5753 | 90.5772 | 87.5759 | 4.4995 | 20.2452 | 3 | 8.8941 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6859 | 33844.713 | 44264.9817 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 674.8401 | 0:240:120 | 0:00 | 7.5914 | 7 | 9.0079 | 72.5723 | 81.5802 | 75.5771 | 4.5 | 20.2501 | 3 | 7.5914 | 81.1131 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6862 | 34065.079 | 44264.9843 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 694.8634 | 0:240:120 | 0:00 | 5.9065 | 7 | 9.0065 | 45.5765 | 54.583 | 48.5812 | 4.5 | 20.2501 | 3 | 5.9065 | 23.1988 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6865 | 34204.782 | 44264.9859 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 713.2422 | 0:240:120 | 0:00 | 4.8865 | 7 | 9.0036 | 18.5831 | 27.5867 | 21.5864 | 4.4996 | 20.246 | 3 | 4.8865 | 13.8755 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6868 | 34271.723 | 44264.9867 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 734.404 | 0:240:120 | 0:00 | 4.0595 | 7 | 0.8337 | 8.2586 | 9.0923 | 8.6732 | 0.334 | 0.1116 | 3 | 4.0595 | 9.4111 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6871 | 34299.987 | 44264.987 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 757.7746 | 0:240:120 | 0:00 | 3.406 | 7 | 0.4978 | 6.6014 | 7.0992 | 6.932 | 0.2478 | 0.0614 | 3 | 3.406 | 6.8943 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6874 | 34321.602 | 44264.9873 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 788.4481 | 0:240:120 | 0:00 | 2.7968 | 7 | 0.1654 | 4.4448 | 4.6102 | 4.5534 | 0.0813 | 0.0066 | 3 | 2.7968 | 5.0611 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6877 | 34337.484 | 44264.9874 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 821.2204 | 0:240:120 | 0:00 | 2.3351 | 7 | 0.1666 | 3.6205 | 3.7871 | 3.73 | 0.0815 | 0.0066 | 3 | 2.3351 | 3.9104 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6880 | 34350.889 | 44264.9876 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 848.2397 | 0:240:120 | 0:00 | 2.0477 | 7 | 0.1664 | 2.9611 | 3.1275 | 3.0711 | 0.082 | 0.0067 | 3 | 2.0477 | 3.2765 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6883 | 34362.863 | 44264.9877 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 877.9793 | 0:240:120 | 0:00 | 1.7975 | 7 | 0.1645 | 2.5528 | 2.7173 | 2.6349 | 0.0708 | 0.005 | 3 | 1.7975 | 2.7683 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6886 | 34373.217 | 44264.9878 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 908.7617 | 0:240:120 | 0:00 | 1.5906 | 7 | 0.0829 | 2.2266 | 2.3095 | 2.2811 | 0.0404 | 0.0016 | 3 | 1.5906 | 2.3756 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6889 | 34382.677 | 44264.988 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 941.6055 | 0:240:120 | 0:00 | 1.4122 | 7 | 0.0498 | 1.9506 | 2.0004 | 1.98 | 0.0225 | 0.0005 | 3 | 1.4122 | 2.0553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6892 | 34391.184 | 44264.9881 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 987.9386 | 0:240:120 | 0:00 | 1.2138 | 7 | 0.0343 | 1.6269 | 1.6612 | 1.6433 | 0.0141 | 0.0002 | 3 | 1.2138 | 1.7172 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6895 | 34398.724 | 44264.9881 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1043.0673 | 0:240:120 | 0:00 | 1.034 | 7 | 0.0639 | 1.3426 | 1.4065 | 1.3744 | 0.0272 | 0.0007 | 3 | 1.034 | 1.4262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6898 | 34405.508 | 44264.9882 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1111.6699 | 0:240:120 | 0:00 | 0.8671 | 7 | 0.0356 | 1.1057 | 1.1413 | 1.1294 | 0.0162 | 0.0003 | 3 | 0.8671 | 1.1682 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6901 | 34411.507 | 44264.9883 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1176.1563 | 0:240:120 | 0:00 | 0.7486 | 7 | 0.0174 | 0.9529 | 0.9703 | 0.9639 | 0.0081 | 0.0001 | 3 | 0.7486 | 0.9917 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6904 | 34417.195 | 44264.9884 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1262.7098 | 0:240:120 | 0:00 | 0.6283 | 7 | 0.0343 | 0.7794 | 0.8137 | 0.7967 | 0.013 | 0.0002 | 3 | 0.6283 | 0.818 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6907 | 34422.379 | 44264.9884 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1355.6312 | 0:240:120 | 0:00 | 0.5322 | 7 | 0.0297 | 0.6528 | 0.6825 | 0.6674 | 0.0103 | 0.0001 | 3 | 0.5322 | 0.683 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6910 | 34426.946 | 44264.9885 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1444.7928 | 0:240:120 | 0:00 | 0.4618 | 7 | 0.018 | 0.5666 | 0.5846 | 0.5755 | 0.0059 | 0 | 3 | 0.4618 | 0.586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6913 | 34431.404 | 44264.9885 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1515.8858 | 0:240:120 | 0:00 | 0.4165 | 7 | 0.0221 | 0.5038 | 0.5259 | 0.5157 | 0.0069 | 0 | 3 | 0.4165 | 0.5246 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6916 | 34435.567 | 44264.9886 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1575.152 | 0:240:120 | 0:00 | 0.3844 | 7 | 0.0107 | 0.4729 | 0.4836 | 0.4771 | 0.0036 | 0 | 3 | 0.3844 | 0.4814 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6919 | 34439.835 | 44264.9886 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1698.145 | 0:240:120 | 0:00 | 0.3303 | 7 | 0.0108 | 0.401 | 0.4118 | 0.4065 | 0.0043 | 0 | 3 | 0.3303 | 0.4094 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6922 | 34443.714 | 44264.9887 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1825.015 | 0:240:120 | 0:00 | 0.2874 | 7 | 0.0127 | 0.3468 | 0.3595 | 0.352 | 0.0046 | 0 | 3 | 0.2874 | 0.353 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6925 | 34447.651 | 44264.9887 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1940.989 | 0:240:120 | 0:00 | 0.2563 | 7 | 0.0058 | 0.3117 | 0.3175 | 0.3145 | 0.0023 | 0 | 3 | 0.2563 | 0.3125 | NP | NP | 0-0-1-0-0-1-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6928 | 34451.344 | 44264.9888 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2105.7 | 0:240:120 | 0:00 | 0.2217 | 7 | 0.0066 | 0.268 | 0.2746 | 0.2707 | 0.0025 | 0 | 3 | 0.2217 | 0.2678 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6931 | 34454.933 | 44264.9888 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2303.551 | 0:240:120 | 0:00 | 0.1906 | 7 | 0.004 | 0.2315 | 0.2355 | 0.233 | 0.0016 | 0 | 3 | 0.1906 | 0.2287 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6934 | 34458.715 | 44264.9888 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2491.211 | 0:240:120 | 0:00 | 0.1682 | 7 | 0.0063 | 0.2025 | 0.2088 | 0.2053 | 0.002 | 0 | 3 | 0.1682 | 0.2018 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6937 | 34462.003 | 44264.9889 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2719.599 | 0:240:120 | 0:00 | 0.1473 | 7 | 0.0038 | 0.1781 | 0.1819 | 0.1797 | 0.0015 | 0 | 3 | 0.1473 | 0.1768 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6940 | 34465.19 | 44264.9889 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2959.639 | 0:240:120 | 0:00 | 0.1307 | 7 | 0.0033 | 0.1578 | 0.1611 | 0.1591 | 0.0013 | 0 | 3 | 0.1307 | 0.1569 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6943 | 34468.575 | 44264.989 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3200.748 | 0:240:120 | 0:00 | 0.1178 | 7 | 0.0032 | 0.1419 | 0.1451 | 0.1438 | 0.0011 | 0 | 3 | 0.1178 | 0.1414 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6946 | 34471.762 | 44264.989 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3501.489 | 0:240:120 | 0:00 | 0.1055 | 7 | 0.0022 | 0.1275 | 0.1297 | 0.1286 | 0.0008 | 0 | 3 | 0.1055 | 0.1266 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6949 | 34474.871 | 44264.989 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3755 | 0:240:120 | 0:00 | 0.0974 | 7 | 0.0022 | 0.1177 | 0.1199 | 0.119 | 0.0008 | 0 | 3 | 0.0974 | 0.1169 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6952 | 34477.985 | 44264.9891 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4050 | 0:240:120 | 0:00 | 0.0899 | 7 | 0.003 | 0.1073 | 0.1103 | 0.1091 | 0.0012 | 0 | 3 | 0.0899 | 0.1079 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6955 | 34481.019 | 44264.9891 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4500 | 0:240:120 | 0:00 | 0.0812 | 7 | 0.0022 | 0.0973 | 0.0995 | 0.0988 | 0.0008 | 0 | 3 | 0.0812 | 0.0974 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6958 | 34483.982 | 44264.9891 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4993.949 | 0:240:120 | 0:00 | 0.0743 | 7 | 0.0025 | 0.0886 | 0.0911 | 0.0899 | 0.0008 | 0 | 3 | 0.0743 | 0.0892 | NP | NP | 0-1-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6961 | 34487.158 | 44264.9892 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5450 | 0:240:120 | 0:00 | 0.0695 | 7 | 0.003 | 0.0818 | 0.0848 | 0.0838 | 0.0012 | 0 | 3 | 0.0695 | 0.0834 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6964 | 34489.984 | 44264.9892 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5951.586 | 0:240:120 | 0:00 | 0.0655 | 7 | 0.0038 | 0.0766 | 0.0804 | 0.0786 | 0.0014 | 0 | 3 | 0.0655 | 0.0786 | P | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6967 | 34493.072 | 44264.9892 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6620.49 | 0:240:120 | 0:00 | 0.0616 | 7 | 0.0028 | 0.0719 | 0.0747 | 0.0738 | 0.001 | 0 | 3 | 0.0616 | 0.0739 | P | NP | 0-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6970 | 34496.239 | 44264.9893 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7356.886 | 0:240:120 | 0:00 | 0.0584 | 7 | 0.0029 | 0.068 | 0.0709 | 0.0697 | 0.0013 | 0 | 3 | 0.0584 | 0.0701 | P | NP | 1-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6973 | 34499.425 | 44264.9893 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8149.621 | 0:240:120 | 0:00 | 0.0559 | 7 | 0.0034 | 0.0644 | 0.0678 | 0.0661 | 0.001 | 0 | 3 | 0.0559 | 0.0671 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6976 | 34502.634 | 44264.9893 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9295.631 | 0:240:120 | 0:00 | 0.0534 | 7 | 0.0029 | 0.0612 | 0.0641 | 0.0625 | 0.0011 | 0 | 3 | 0.0534 | 0.064 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6979 | 34505.553 | 44264.9894 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10094.985 | 0:240:120 | 0:00 | 0.0521 | 7 | 0.0029 | 0.0591 | 0.062 | 0.0604 | 0.0011 | 0 | 3 | 0.0521 | 0.0625 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6982 | 34508.436 | 44264.9894 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11300.147 | 0:240:120 | 0:00 | 0.0507 | 7 | 0.0032 | 0.0569 | 0.0601 | 0.0585 | 0.0012 | 0 | 3 | 0.0507 | 0.0608 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6985 | 34547.921 | 44264.9899 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 704.1 | 0:240:120 | 0:00 | 5.3486 | 7 | 8.9988 | 27.5858 | 36.5846 | 33.5022 | 4.443 | 19.74 | 3 | 5.3486 | 17.3681 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6988 | 34633.515 | 44264.9909 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 723.8 | 0:240:120 | 0:00 | 4.4383 | 7 | 0.4981 | 9.0915 | 9.5896 | 9.4226 | 0.2475 | 0.0612 | 3 | 4.4383 | 11.2342 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6991 | 34663.517 | 44264.9912 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 746.1 | 0:240:120 | 0:00 | 3.706 | 7 | 0.5021 | 7.5934 | 8.0955 | 7.7627 | 0.2491 | 0.0621 | 3 | 3.706 | 7.9659 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6994 | 34688.998 | 44264.9915 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 773.1 | 0:240:120 | 0:00 | 3.0742 | 7 | 0.9833 | 5.12 | 6.1033 | 5.6452 | 0.3834 | 0.147 | 3 | 3.0742 | 5.8457 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6997 | 34708.177 | 44264.9917 | Vista Coord | Main | 600Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 804.8 | 0:240:120 | 0:00 | 2.5476 | 7 | 0.1677 | 4.1117 | 4.2794 | 4.1689 | 0.0828 | 0.0068 | 3 | 2.5476 | 4.4182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7000 | 34820.085 | 44264.993 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 770 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.0054 | 90.573 | 99.5784 | 95.8832 | 4.2356 | 17.9405 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7003 | 35121.953 | 44264.9965 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 772.2 | 0:240:120 | 0:00 | 9.2648 | 7 | 9.0058 | 90.5731 | 99.5789 | 93.5772 | 4.5004 | 20.2535 | 3 | 9.2648 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7006 | 35414.369 | 44264.9999 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 778.6295 | 0:240:120 | 0:00 | 8.4741 | 7 | 9.0031 | 81.5752 | 90.5783 | 84.5827 | 4.4955 | 20.2096 | 3 | 8.4741 | 912.7277 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7009 | 35670.589 | 44265.0029 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 789.2698 | 0:240:120 | 0:00 | 7.4164 | 7 | 9.0218 | 63.5805 | 72.6023 | 69.5871 | 4.4892 | 20.1531 | 3 | 7.4164 | 67.2285 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7012 | 35882.189 | 44265.0053 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 801.7273 | 0:240:120 | 0:00 | 6.46 | 7 | 9.0055 | 54.5762 | 63.5817 | 57.5797 | 4.5001 | 20.251 | 3 | 6.46 | 32.0283 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7015 | 36048.8 | 44265.0072 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 819.4989 | 0:240:120 | 0:00 | 5.4421 | 7 | 9.203 | 27.587 | 36.79 | 33.6445 | 4.5434 | 20.6426 | 3 | 5.4421 | 18.2004 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7018 | 36134.567 | 44265.0082 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 845.5711 | 0:240:120 | 0:00 | 4.4007 | 7 | 0.4987 | 9.0917 | 9.5904 | 9.4227 | 0.2475 | 0.0613 | 3 | 4.4007 | 11.0387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7021 | 36163.959 | 44265.0086 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 876.1258 | 0:240:120 | 0:00 | 3.5753 | 7 | 0.497 | 7.1 | 7.597 | 7.4305 | 0.2472 | 0.0611 | 3 | 3.5753 | 7.4832 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7024 | 36187.466 | 44265.0088 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 906.8356 | 0:240:120 | 0:00 | 2.9937 | 7 | 0.4971 | 5.1076 | 5.6047 | 5.4379 | 0.2475 | 0.0613 | 3 | 2.9937 | 5.6099 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7027 | 36205.518 | 44265.0091 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 944.5205 | 0:240:120 | 0:00 | 2.4821 | 7 | 0.1665 | 3.9498 | 4.1163 | 4.0594 | 0.0819 | 0.0067 | 3 | 2.4821 | 4.2579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7030 | 36219.628 | 44265.0092 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 988.9209 | 0:240:120 | 0:00 | 2.0533 | 7 | 0.1667 | 2.9607 | 3.1274 | 3.0707 | 0.0825 | 0.0068 | 3 | 2.0533 | 3.2884 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7033 | 36231.152 | 44265.0094 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1035.408 | 0:240:120 | 0:00 | 1.7286 | 7 | 0.0823 | 2.471 | 2.5533 | 2.525 | 0.0402 | 0.0016 | 3 | 1.7286 | 2.635 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7036 | 36241.08 | 44265.0095 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1084.0808 | 0:240:120 | 0:00 | 1.4752 | 7 | 0.0771 | 2.0202 | 2.0973 | 2.0567 | 0.0313 | 0.001 | 3 | 1.4752 | 2.1665 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7039 | 36249.627 | 44265.0096 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1151.7528 | 0:240:120 | 0:00 | 1.2165 | 7 | 0.0318 | 1.6292 | 1.661 | 1.65 | 0.0152 | 0.0002 | 3 | 1.2165 | 1.7217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7042 | 36257.233 | 44265.0097 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1217.2776 | 0:240:120 | 0:00 | 1.0331 | 7 | 0.0563 | 1.343 | 1.3993 | 1.3685 | 0.0241 | 0.0006 | 3 | 1.0331 | 1.4248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7045 | 36264.027 | 44265.0097 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1298.8734 | 0:240:120 | 0:00 | 0.8637 | 7 | 0.0605 | 1.0905 | 1.151 | 1.1234 | 0.0172 | 0.0003 | 3 | 0.8637 | 1.163 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7048 | 36270.152 | 44265.0098 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1385.5193 | 0:240:120 | 0:00 | 0.7305 | 7 | 0.0354 | 0.9217 | 0.9571 | 0.9377 | 0.0118 | 0.0001 | 3 | 0.7305 | 0.9653 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7051 | 36275.326 | 44265.0099 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1476.6257 | 0:240:120 | 0:00 | 0.6247 | 7 | 0.0258 | 0.7739 | 0.7997 | 0.7899 | 0.0091 | 0.0001 | 3 | 0.6247 | 0.8129 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7054 | 36280.367 | 44265.0099 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1560.6338 | 0:240:120 | 0:00 | 0.5487 | 7 | 0.0277 | 0.6746 | 0.7023 | 0.6879 | 0.0107 | 0.0001 | 3 | 0.5487 | 0.7059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7057 | 36285.004 | 44265.01 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1668.4723 | 0:240:120 | 0:00 | 0.4722 | 7 | 0.0209 | 0.5746 | 0.5955 | 0.5873 | 0.0073 | 0.0001 | 3 | 0.4722 | 0.6003 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7060 | 36289.453 | 44265.01 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1778.1852 | 0:240:120 | 0:00 | 0.4118 | 7 | 0.0184 | 0.5006 | 0.519 | 0.5097 | 0.0068 | 0 | 3 | 0.4118 | 0.5182 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7063 | 36293.692 | 44265.0101 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1847.653 | 0:240:120 | 0:00 | 0.3802 | 7 | 0.0066 | 0.4666 | 0.4732 | 0.4702 | 0.0025 | 0 | 3 | 0.3802 | 0.4757 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7066 | 36297.588 | 44265.0101 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2004.409 | 0:240:120 | 0:00 | 0.3228 | 7 | 0.0114 | 0.3905 | 0.4019 | 0.3966 | 0.004 | 0 | 3 | 0.3228 | 0.3995 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7069 | 36301.557 | 44265.0102 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2142.913 | 0:240:120 | 0:00 | 0.2839 | 7 | 0.0069 | 0.3446 | 0.3515 | 0.3478 | 0.0025 | 0 | 3 | 0.2839 | 0.3484 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7072 | 36305.295 | 44265.0102 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2271.932 | 0:240:120 | 0:00 | 0.2548 | 7 | 0.0073 | 0.3077 | 0.315 | 0.3112 | 0.0024 | 0 | 3 | 0.2548 | 0.3105 | NP | NP | 0-0-1-0-1-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7075 | 36308.823 | 44265.0103 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2459.543 | 0:240:120 | 0:00 | 0.2213 | 7 | 0.0066 | 0.2666 | 0.2732 | 0.2702 | 0.0021 | 0 | 3 | 0.2213 | 0.2672 | NP | NP | 0-0-0-0-0-0-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7078 | 36312.534 | 44265.0103 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2626.752 | 0:240:120 | 0:00 | 0.1979 | 7 | 0.005 | 0.2389 | 0.2439 | 0.2416 | 0.0016 | 0 | 3 | 0.1979 | 0.2375 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7081 | 36316.021 | 44265.0103 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2837.731 | 0:240:120 | 0:00 | 0.1746 | 7 | 0.0041 | 0.2116 | 0.2157 | 0.2137 | 0.0013 | 0 | 3 | 0.1746 | 0.2095 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7084 | 36319.621 | 44265.0104 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3020 | 0:240:120 | 0:00 | 0.1586 | 7 | 0.0039 | 0.1911 | 0.195 | 0.1932 | 0.0013 | 0 | 3 | 0.1586 | 0.1903 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7087 | 36322.978 | 44265.0104 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3290 | 0:240:120 | 0:00 | 0.1398 | 7 | 0.0035 | 0.1684 | 0.1719 | 0.1699 | 0.0011 | 0 | 3 | 0.1398 | 0.1678 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7090 | 36326.336 | 44265.0105 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3514.957 | 0:240:120 | 0:00 | 0.1276 | 7 | 0.0022 | 0.1545 | 0.1567 | 0.1555 | 0.0008 | 0 | 3 | 0.1276 | 0.1531 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7093 | 36329.738 | 44265.0105 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3800 | 0:240:120 | 0:00 | 0.1153 | 7 | 0.0024 | 0.1396 | 0.142 | 0.1406 | 0.0008 | 0 | 3 | 0.1153 | 0.1383 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7096 | 36333.042 | 44265.0105 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4055 | 0:240:120 | 0:00 | 0.1064 | 7 | 0.0022 | 0.1286 | 0.1308 | 0.1299 | 0.0007 | 0 | 3 | 0.1064 | 0.1277 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7099 | 36336.076 | 44265.0106 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4350 | 0:240:120 | 0:00 | 0.0982 | 7 | 0.0029 | 0.1187 | 0.1216 | 0.12 | 0.001 | 0 | 3 | 0.0982 | 0.1178 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7102 | 36339.078 | 44265.0106 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4772.749 | 0:240:120 | 0:00 | 0.089 | 7 | 0.0029 | 0.1064 | 0.1093 | 0.1085 | 0.001 | 0 | 3 | 0.089 | 0.1068 | NP | NP | 0-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7105 | 36342.065 | 44265.0106 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5150.713 | 0:240:120 | 0:00 | 0.0826 | 7 | 0.0027 | 0.0988 | 0.1015 | 0.1005 | 0.001 | 0 | 3 | 0.0826 | 0.0992 | NP | NP | 0-1-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7108 | 36345.11 | 44265.0107 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5658.145 | 0:240:120 | 0:00 | 0.0761 | 7 | 0.003 | 0.0906 | 0.0936 | 0.0922 | 0.001 | 0 | 3 | 0.0761 | 0.0913 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
7111 | 36348.126 | 44265.0107 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6241.579 | 0:240:120 | 0:00 | 0.0705 | 7 | 0.0034 | 0.0835 | 0.0869 | 0.0854 | 0.0013 | 0 | 3 | 0.0705 | 0.0846 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
7114 | 36351.005 | 44265.0107 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6778.19 | 0:240:120 | 0:00 | 0.0666 | 7 | 0.0029 | 0.0786 | 0.0815 | 0.0805 | 0.0011 | 0 | 3 | 0.0666 | 0.0799 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
7117 | 36354.162 | 44265.0108 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7461.519 | 0:240:120 | 0:00 | 0.0628 | 7 | 0.0028 | 0.0734 | 0.0762 | 0.075 | 0.0011 | 0 | 3 | 0.0628 | 0.0753 | P | NP | 1-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
7120 | 36357.147 | 44265.0108 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8162.447 | 0:240:120 | 0:00 | 0.0598 | 7 | 0.0027 | 0.0702 | 0.0729 | 0.0716 | 0.0011 | 0 | 3 | 0.0598 | 0.0718 | P | NP | 0-1-1-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
7123 | 36360.107 | 44265.0108 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8892.008 | 0:240:120 | 0:00 | 0.0575 | 7 | 0.0025 | 0.0675 | 0.07 | 0.0688 | 0.0009 | 0 | 3 | 0.0575 | 0.069 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
7126 | 36363.334 | 44265.0109 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9707.025 | 0:240:120 | 0:00 | 0.0555 | 7 | 0.0027 | 0.0634 | 0.0661 | 0.065 | 0.0009 | 0 | 3 | 0.0555 | 0.0665 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7129 | 36366.167 | 44265.0109 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10519.58 | 0:240:120 | 0:00 | 0.0539 | 7 | 0.0027 | 0.062 | 0.0647 | 0.0633 | 0.0009 | 0 | 3 | 0.0539 | 0.0647 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7132 | 36369.226 | 44265.011 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11898.73 | 0:240:120 | 0:00 | 0.0519 | 7 | 0.0021 | 0.059 | 0.0611 | 0.0603 | 0.0008 | 0 | 3 | 0.0519 | 0.0623 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7135 | 36417.666 | 44265.0115 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 810.6 | 0:240:120 | 0:00 | 5.9107 | 7 | 15.7264 | 36.5854 | 52.3118 | 43.7761 | 5.5411 | 30.7035 | 3 | 5.9107 | 23.252 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7138 | 36548.755 | 44265.013 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 832.5 | 0:240:120 | 0:00 | 4.8712 | 7 | 9.0051 | 18.5828 | 27.5879 | 21.5868 | 4.5004 | 20.2535 | 3 | 4.8712 | 13.7752 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7141 | 36615.234 | 44265.0138 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 860.8 | 0:240:120 | 0:00 | 3.9497 | 7 | 0.4992 | 8.0956 | 8.5948 | 8.4264 | 0.2475 | 0.0613 | 3 | 3.9497 | 8.9386 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7144 | 36641.934 | 44265.0141 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 891.5 | 0:240:120 | 0:00 | 3.2605 | 7 | 0.4991 | 6.103 | 6.6021 | 6.4302 | 0.2454 | 0.0602 | 3 | 3.2605 | 6.4183 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7147 | 36662.371 | 44265.0143 | Vista Coord | Main | 700Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 925.7 | 0:240:120 | 0:00 | 2.7159 | 7 | 0.2734 | 4.2785 | 4.5519 | 4.4158 | 0.1105 | 0.0122 | 3 | 2.7159 | 4.8464 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7150 | 36775.003 | 44265.0156 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 880 | 0:240:120 | 0:00 | 9.5688 | 7 | 9.002 | 90.5766 | 99.5786 | 95.2518 | 3.9085 | 15.2765 | 3 | 9.5688 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7153 | 37067.491 | 44265.019 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 889.5018 | 0:240:120 | 0:00 | 8.5099 | 7 | 9.0039 | 81.5759 | 90.5798 | 84.6345 | 4.4588 | 19.8811 | 3 | 8.5099 | 1449.8189 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7156 | 37329.772 | 44265.0221 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 900.7163 | 0:240:120 | 0:00 | 7.5177 | 7 | 9.8239 | 69.2233 | 79.0472 | 73.9272 | 3.4505 | 11.9061 | 3 | 7.5177 | 74.7033 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7159 | 37552.254 | 44265.0246 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 912.0738 | 0:240:120 | 0:00 | 6.7159 | 7 | 8.9999 | 54.5823 | 63.5822 | 60.5802 | 4.4981 | 20.233 | 3 | 6.7159 | 37.8905 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7162 | 37727.9 | 44265.0267 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 932.2929 | 0:240:120 | 0:00 | 5.6304 | 7 | 8.9999 | 36.5839 | 45.5838 | 42.2047 | 4.3001 | 18.491 | 3 | 5.6304 | 20.0363 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7165 | 37840.569 | 44265.028 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 955.9506 | 0:240:120 | 0:00 | 4.7192 | 7 | 8.999 | 9.5898 | 18.5888 | 15.5874 | 4.498 | 20.2319 | 3 | 4.7192 | 12.818 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7168 | 37888.936 | 44265.0285 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 981.2319 | 0:240:120 | 0:00 | 4.0101 | 7 | 0.4986 | 8.0957 | 8.5943 | 8.427 | 0.2477 | 0.0614 | 3 | 4.0101 | 9.1956 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7171 | 37915.466 | 44265.0288 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1016.6915 | 0:240:120 | 0:00 | 3.2965 | 7 | 0.498 | 6.1029 | 6.6009 | 6.4339 | 0.2479 | 0.0615 | 3 | 3.2965 | 6.5337 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
7174 | 37936.297 | 44265.0291 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1053.4326 | 0:240:120 | 0:00 | 2.77 | 7 | 0.1653 | 4.4439 | 4.6092 | 4.5533 | 0.0813 | 0.0066 | 3 | 2.77 | 4.9895 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7177 | 37952.052 | 44265.0293 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1093.7828 | 0:240:120 | 0:00 | 2.3457 | 7 | 0.2046 | 3.6209 | 3.8255 | 3.7344 | 0.0859 | 0.0074 | 3 | 2.3457 | 3.935 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7180 | 37965.373 | 44265.0294 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1139.2414 | 0:240:120 | 0:00 | 1.9907 | 7 | 0.0817 | 2.8801 | 2.9618 | 2.9339 | 0.0397 | 0.0016 | 3 | 1.9907 | 3.1573 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7183 | 37976.598 | 44265.0296 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1181.6442 | 0:240:120 | 0:00 | 1.7375 | 7 | 0.0958 | 2.4711 | 2.5669 | 2.5267 | 0.0417 | 0.0017 | 3 | 1.7375 | 2.652 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7186 | 37986.596 | 44265.0297 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1229.4711 | 0:240:120 | 0:00 | 1.5136 | 7 | 0.1074 | 2.0373 | 2.1447 | 2.1046 | 0.0382 | 0.0015 | 3 | 1.5136 | 2.2353 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7189 | 37995.58 | 44265.0298 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1287.2717 | 0:240:120 | 0:00 | 1.3035 | 7 | 0.0889 | 1.7406 | 1.8295 | 1.7824 | 0.0299 | 0.0009 | 3 | 1.3035 | 1.8678 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7192 | 38003.51 | 44265.0299 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1333.7907 | 0:240:120 | 0:00 | 1.1688 | 7 | 0.0813 | 1.5163 | 1.5976 | 1.5653 | 0.0269 | 0.0007 | 3 | 1.1688 | 1.643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7195 | 38011.005 | 44265.03 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1395.0387 | 0:240:120 | 0:00 | 1.025 | 7 | 0.0863 | 1.3034 | 1.3897 | 1.3498 | 0.0283 | 0.0008 | 3 | 1.025 | 1.412 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7198 | 38017.803 | 44265.03 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1466.7367 | 0:240:120 | 0:00 | 0.8919 | 7 | 0.0517 | 1.1341 | 1.1858 | 1.1586 | 0.0178 | 0.0003 | 3 | 0.8919 | 1.2059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7201 | 38024.046 | 44265.0301 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1540.5104 | 0:240:120 | 0:00 | 0.7835 | 7 | 0.0385 | 0.9908 | 1.0293 | 1.0098 | 0.0122 | 0.0001 | 3 | 0.7835 | 1.0432 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7204 | 38030.016 | 44265.0302 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1617.9944 | 0:240:120 | 0:00 | 0.6921 | 7 | 0.0317 | 0.8651 | 0.8968 | 0.8818 | 0.0113 | 0.0001 | 3 | 0.6921 | 0.9096 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7207 | 38035.384 | 44265.0302 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1706.4883 | 0:240:120 | 0:00 | 0.6084 | 7 | 0.039 | 0.7467 | 0.7857 | 0.7676 | 0.0116 | 0.0001 | 3 | 0.6084 | 0.7897 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7210 | 38040.314 | 44265.0303 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1794.1935 | 0:240:120 | 0:00 | 0.5413 | 7 | 0.0198 | 0.6664 | 0.6862 | 0.678 | 0.007 | 0 | 3 | 0.5413 | 0.6956 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7213 | 38044.937 | 44265.0303 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1890.3489 | 0:240:120 | 0:00 | 0.4814 | 7 | 0.0138 | 0.5937 | 0.6075 | 0.6008 | 0.0053 | 0 | 3 | 0.4814 | 0.6128 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7216 | 38049.423 | 44265.0304 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1999.9936 | 0:240:120 | 0:00 | 0.426 | 7 | 0.0161 | 0.5196 | 0.5357 | 0.5274 | 0.0059 | 0 | 3 | 0.426 | 0.5373 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7219 | 38053.783 | 44265.0304 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2131.5206 | 0:240:120 | 0:00 | 0.3729 | 7 | 0.0117 | 0.454 | 0.4657 | 0.4599 | 0.0043 | 0 | 3 | 0.3729 | 0.466 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7222 | 38058.2 | 44265.0305 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2278.151 | 0:240:120 | 0:00 | 0.3263 | 7 | 0.0121 | 0.3962 | 0.4083 | 0.4016 | 0.0041 | 0 | 3 | 0.3263 | 0.4042 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7225 | 38062.214 | 44265.0305 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2505.226 | 0:240:120 | 0:00 | 0.2721 | 7 | 0.0075 | 0.3287 | 0.3362 | 0.3326 | 0.0027 | 0 | 3 | 0.2721 | 0.333 | P | NP | 0-0-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7228 | 38066.059 | 44265.0306 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2706.467 | 0:240:120 | 0:00 | 0.2365 | 7 | 0.0052 | 0.2869 | 0.2921 | 0.2887 | 0.0021 | 0 | 3 | 0.2365 | 0.2868 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7231 | 38069.669 | 44265.0306 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2973.129 | 0:240:120 | 0:00 | 0.2011 | 7 | 0.0041 | 0.2428 | 0.2469 | 0.2448 | 0.0015 | 0 | 3 | 0.2011 | 0.2413 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7234 | 38073.091 | 44265.0307 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3148.863 | 0:240:120 | 0:00 | 0.183 | 7 | 0.0028 | 0.2218 | 0.2246 | 0.223 | 0.0011 | 0 | 3 | 0.183 | 0.2196 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7237 | 38076.453 | 44265.0307 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3433.924 | 0:240:120 | 0:00 | 0.1598 | 7 | 0.0036 | 0.1935 | 0.1971 | 0.195 | 0.0012 | 0 | 3 | 0.1598 | 0.1917 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7240 | 38079.871 | 44265.0308 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3748.702 | 0:240:120 | 0:00 | 0.1404 | 7 | 0.0033 | 0.1693 | 0.1726 | 0.1706 | 0.0014 | 0 | 3 | 0.1404 | 0.1685 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7243 | 38082.983 | 44265.0308 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4079.537 | 0:240:120 | 0:00 | 0.125 | 7 | 0.003 | 0.1508 | 0.1538 | 0.1522 | 0.0013 | 0 | 3 | 0.125 | 0.15 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7246 | 38086.268 | 44265.0308 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4448.85 | 0:240:120 | 0:00 | 0.1118 | 7 | 0.0033 | 0.1344 | 0.1377 | 0.136 | 0.0013 | 0 | 3 | 0.1118 | 0.1342 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7249 | 38089.268 | 44265.0309 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4940.639 | 0:240:120 | 0:00 | 0.0988 | 7 | 0.0038 | 0.1184 | 0.1222 | 0.1206 | 0.0013 | 0 | 3 | 0.0988 | 0.1186 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7252 | 38092.257 | 44265.0309 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5482.725 | 0:240:120 | 0:00 | 0.0885 | 7 | 0.0028 | 0.1062 | 0.109 | 0.1079 | 0.001 | 0 | 3 | 0.0885 | 0.1062 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7255 | 38095.396 | 44265.0309 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6170.942 | 0:240:120 | 0:00 | 0.0792 | 7 | 0.0027 | 0.0946 | 0.0973 | 0.0959 | 0.0009 | 0 | 3 | 0.0792 | 0.095 | NP | NP | 0-0-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
7258 | 38098.541 | 44265.031 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6962.742 | 0:240:120 | 0:00 | 0.0718 | 7 | 0.0036 | 0.085 | 0.0886 | 0.087 | 0.0015 | 0 | 3 | 0.0718 | 0.0861 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
7261 | 38101.564 | 44265.031 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7892.145 | 0:240:120 | 0:00 | 0.0658 | 7 | 0.0033 | 0.077 | 0.0803 | 0.0793 | 0.0011 | 0 | 3 | 0.0658 | 0.0789 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
7264 | 38104.489 | 44265.031 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8936.271 | 0:240:120 | 0:00 | 0.0612 | 7 | 0.0029 | 0.0714 | 0.0743 | 0.073 | 0.0011 | 0 | 3 | 0.0612 | 0.0734 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
7267 | 38107.642 | 44265.0311 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9961.293 | 0:240:120 | 0:00 | 0.058 | 7 | 0.0029 | 0.0677 | 0.0706 | 0.0691 | 0.0009 | 0 | 3 | 0.058 | 0.0696 | P | NP | 1-1-1-0-1-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7270 | 38110.526 | 44265.0311 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11338.204 | 0:240:120 | 0:00 | 0.055 | 7 | 0.0034 | 0.0629 | 0.0663 | 0.0647 | 0.0013 | 0 | 3 | 0.055 | 0.066 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7273 | 38168.217 | 44265.0318 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 922.2 | 0:240:120 | 0:00 | 6.1271 | 7 | 8.9994 | 45.5831 | 54.5825 | 51.3871 | 4.3891 | 19.2641 | 3 | 6.1271 | 26.2387 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7276 | 38311.533 | 44265.0334 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 944.1 | 0:240:120 | 0:00 | 5.138 | 7 | 13.5968 | 18.5992 | 32.196 | 26.3198 | 5.0841 | 25.8476 | 3 | 5.138 | 15.6599 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7279 | 38386.471 | 44265.0343 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 968.6 | 0:240:120 | 0:00 | 4.3376 | 7 | 0.5017 | 9.0882 | 9.5899 | 9.257 | 0.2493 | 0.0621 | 3 | 4.3376 | 10.7178 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7282 | 38415.964 | 44265.0346 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 999 | 0:240:120 | 0:00 | 3.6204 | 7 | 0.4997 | 7.0979 | 7.5976 | 7.4302 | 0.2479 | 0.0615 | 3 | 3.6204 | 7.6468 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7285 | 38439.461 | 44265.0349 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1035.1 | 0:240:120 | 0:00 | 3.0119 | 7 | 0.4994 | 5.106 | 5.6054 | 5.4379 | 0.2483 | 0.0617 | 3 | 3.0119 | 5.6625 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7288 | 38457.745 | 44265.0351 | Vista Coord | Main | 800Main | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1073.6 | 0:240:120 | 0:00 | 2.542 | 7 | 0.2302 | 4.0508 | 4.281 | 4.1569 | 0.0943 | 0.0089 | 3 | 2.542 | 4.4044 | P | P | P | NP | 0-0-0-0-0-0-0-0-0

## T_Charac-20210315 105136-Compil (hidden)
Index | Time Interval | Timestamp | Curve Family | Type | Amp Type | Test Type | Trip Type | Interrupter# | Start Type | PE | DT1 | DT2 | OCC Freq | Source Freq | Current | Phase A:B:C | X/R:Angle | Expected Time | P_Select | Max Delta | Min Time | Max Time | Average | Std Dev | Variance | Count | Min T Spec | Max T Spec | Ave T Result | T Result | Indiv T | TC Result | Indiv TC
1 | 301.1 | 44270.456 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 18.71 | 0:240:120 | 0:00 | 26.8076 | 7 | 83.7916 | 214.7157 | 298.5073 | 245.1936 | 39.6974 | 1575.882 | 3 | 26.8076 | Inf | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4 | 1084.137 | 44270.4651 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.0842 | 0:240:120 | 0:00 | 23.5783 | 7 | 87.157 | 97.2706 | 184.4276 | 129.7367 | 40.7833 | 1663.2767 | 3 | 23.5783 | 232.6691 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7 | 1513.027 | 44270.47 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.4659 | 0:240:120 | 0:00 | 20.9524 | 7 | 10.0524 | 49.5842 | 59.6366 | 53.0656 | 4.8179 | 23.2122 | 3 | 20.9524 | 113.8164 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10 | 1681.965 | 44270.472 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.8552 | 0:240:120 | 0:00 | 18.7767 | 7 | 5.1134 | 42.6215 | 47.7349 | 44.3499 | 2.5102 | 6.3009 | 3 | 18.7767 | 74.2257 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
13 | 1820.345 | 44270.4736 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 20.2523 | 0:240:120 | 0:00 | 16.946 | 7 | 5.3474 | 35.5242 | 40.8716 | 37.6271 | 2.3 | 5.2898 | 3 | 16.946 | 54.4505 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
16 | 1937.496 | 44270.4749 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 20.6574 | 0:240:120 | 0:00 | 15.3853 | 7 | 4.8908 | 28.7109 | 33.6017 | 30.4284 | 2.3337 | 5.446 | 3 | 15.3853 | 42.6014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
19 | 2033.767 | 44270.476 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 21.0705 | 0:240:120 | 0:00 | 14.04 | 7 | 2.7688 | 23.9699 | 26.7387 | 25.0792 | 1.2522 | 1.5679 | 3 | 14.04 | 34.7153 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
22 | 2113.318 | 44270.477 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 21.4919 | 0:240:120 | 0:00 | 12.8693 | 7 | 1.9417 | 21.5895 | 23.5312 | 22.3536 | 0.8845 | 0.7824 | 3 | 12.8693 | 29.0936 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
25 | 2184.036 | 44270.4778 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 21.9217 | 0:240:120 | 0:00 | 11.8419 | 7 | 1.9055 | 19.1383 | 21.0438 | 19.8703 | 0.8715 | 0.7595 | 3 | 11.8419 | 24.8871 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
28 | 2247.238 | 44270.4785 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 22.3602 | 0:240:120 | 0:00 | 10.9338 | 7 | 2.1525 | 16.5789 | 18.7314 | 17.4548 | 0.9614 | 0.9243 | 3 | 10.9338 | 21.6241 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
31 | 2303.624 | 44270.4792 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 22.8074 | 0:240:120 | 0:00 | 10.1259 | 7 | 1.0549 | 15.1289 | 16.1838 | 15.5624 | 0.4678 | 0.2188 | 3 | 10.1259 | 19.0214 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
34 | 2353.689 | 44270.4797 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.2635 | 0:240:120 | 0:00 | 9.4031 | 7 | 0.9676 | 13.9281 | 14.8957 | 14.2834 | 0.4566 | 0.2084 | 3 | 9.4031 | 16.8989 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
37 | 2399.774 | 44270.4803 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.7288 | 0:240:120 | 0:00 | 8.753 | 7 | 1.1483 | 12.4536 | 13.6019 | 12.9601 | 0.4994 | 0.2494 | 3 | 8.753 | 15.1365 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
40 | 2441.928 | 44270.4808 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.2034 | 0:240:120 | 0:00 | 8.1657 | 7 | 0.8468 | 11.3997 | 12.2465 | 11.7235 | 0.3861 | 0.1491 | 3 | 8.1657 | 13.6511 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
43 | 2480.246 | 44270.4812 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.6874 | 0:240:120 | 0:00 | 7.6328 | 7 | 0.6344 | 10.5617 | 11.1961 | 10.82 | 0.2852 | 0.0813 | 3 | 7.6328 | 12.3832 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
46 | 2515.718 | 44270.4816 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.1812 | 0:240:120 | 0:00 | 7.1475 | 7 | 0.6767 | 9.7171 | 10.3938 | 10.0177 | 0.2854 | 0.0815 | 3 | 7.1475 | 11.2893 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
49 | 2549.01 | 44270.482 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.6848 | 0:240:120 | 0:00 | 6.7041 | 7 | 0.6825 | 8.8984 | 9.5809 | 9.1958 | 0.2925 | 0.0855 | 3 | 6.7041 | 10.3368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
52 | 2579.556 | 44270.4824 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.1985 | 0:240:120 | 0:00 | 6.2976 | 7 | 0.4599 | 8.3357 | 8.7956 | 8.5324 | 0.1987 | 0.0395 | 3 | 6.2976 | 9.5006 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
55 | 2607.99 | 44270.4827 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.7225 | 0:240:120 | 0:00 | 5.9239 | 7 | 0.4801 | 7.7334 | 8.2135 | 7.9532 | 0.2013 | 0.0405 | 3 | 5.9239 | 8.7613 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
58 | 2634.867 | 44270.483 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 27.2569 | 0:240:120 | 0:00 | 5.5794 | 7 | 0.4793 | 7.1767 | 7.656 | 7.3637 | 0.2165 | 0.0469 | 3 | 5.5794 | 8.1036 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
61 | 2659.994 | 44270.4833 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 27.8021 | 0:240:120 | 0:00 | 5.2611 | 7 | 0.3243 | 6.7599 | 7.0842 | 6.8963 | 0.1433 | 0.0205 | 3 | 5.2611 | 7.5152 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
64 | 2683.482 | 44270.4836 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.3581 | 0:240:120 | 0:00 | 4.9664 | 7 | 0.3864 | 6.2856 | 6.672 | 6.4681 | 0.1608 | 0.0259 | 3 | 4.9664 | 6.9862 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
67 | 2705.921 | 44270.4838 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.9253 | 0:240:120 | 0:00 | 4.6928 | 7 | 0.3456 | 5.871 | 6.2166 | 6.0214 | 0.1498 | 0.0224 | 3 | 4.6928 | 6.5085 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
70 | 2726.993 | 44270.4841 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.5038 | 0:240:120 | 0:00 | 4.4385 | 7 | 0.2725 | 5.5452 | 5.8177 | 5.6683 | 0.1163 | 0.0135 | 3 | 4.4385 | 6.0752 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
73 | 2746.651 | 44270.4843 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.0939 | 0:240:120 | 0:00 | 4.2016 | 7 | 0.2813 | 5.1949 | 5.4762 | 5.3229 | 0.1181 | 0.0139 | 3 | 4.2016 | 5.6868 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
76 | 2765.313 | 44270.4845 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.6957 | 0:240:120 | 0:00 | 3.9805 | 7 | 0.2224 | 4.9176 | 5.14 | 5.0031 | 0.0977 | 0.0095 | 3 | 3.9805 | 5.3605 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
79 | 2783.237 | 44270.4847 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.3097 | 0:240:120 | 0:00 | 3.7739 | 7 | 0.2108 | 4.6551 | 4.8659 | 4.749 | 0.0896 | 0.008 | 3 | 3.7739 | 5.0584 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
82 | 2800.409 | 44270.4849 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.9358 | 0:240:120 | 0:00 | 3.5806 | 7 | 0.2217 | 4.3819 | 4.6036 | 4.4872 | 0.0902 | 0.0081 | 3 | 3.5806 | 4.7783 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
85 | 2816.597 | 44270.4851 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.5746 | 0:240:120 | 0:00 | 3.3994 | 7 | 0.1758 | 4.1593 | 4.3351 | 4.2359 | 0.0764 | 0.0058 | 3 | 3.3994 | 4.518 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
88 | 2832.422 | 44270.4853 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.2261 | 0:240:120 | 0:00 | 3.2294 | 7 | 0.1806 | 3.9402 | 4.1208 | 4.0229 | 0.0773 | 0.006 | 3 | 3.2294 | 4.2757 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
91 | 2847.488 | 44270.4855 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.8906 | 0:240:120 | 0:00 | 3.0697 | 7 | 0.1763 | 3.7298 | 3.9061 | 3.8052 | 0.0783 | 0.0061 | 3 | 3.0697 | 4.0497 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
94 | 2861.793 | 44270.4856 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.5684 | 0:240:120 | 0:00 | 2.9195 | 7 | 0.1502 | 3.5485 | 3.6987 | 3.6138 | 0.0649 | 0.0042 | 3 | 2.9195 | 3.8387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
97 | 2875.583 | 44270.4858 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.2598 | 0:240:120 | 0:00 | 2.778 | 7 | 0.1491 | 3.371 | 3.5201 | 3.431 | 0.0658 | 0.0043 | 3 | 2.778 | 3.6412 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
100 | 2888.542 | 44270.4859 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.965 | 0:240:120 | 0:00 | 2.6447 | 7 | 0.1264 | 3.2105 | 3.3369 | 3.2568 | 0.0596 | 0.0036 | 3 | 2.6447 | 3.4562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
103 | 2901.182 | 44270.4861 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.6842 | 0:240:120 | 0:00 | 2.519 | 7 | 0.1172 | 3.0543 | 3.1715 | 3.0996 | 0.0536 | 0.0029 | 3 | 2.519 | 3.2828 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
106 | 2913.49 | 44270.4862 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.4179 | 0:240:120 | 0:00 | 2.4002 | 7 | 0.1181 | 2.8977 | 3.0158 | 2.9417 | 0.0547 | 0.003 | 3 | 2.4002 | 3.1198 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
109 | 2925.252 | 44270.4864 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.1663 | 0:240:120 | 0:00 | 2.288 | 7 | 0.103 | 2.7612 | 2.8642 | 2.8029 | 0.0463 | 0.0021 | 3 | 2.288 | 2.9666 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
112 | 2936.353 | 44270.4865 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.9296 | 0:240:120 | 0:00 | 2.1819 | 7 | 0.1095 | 2.6221 | 2.7316 | 2.6664 | 0.048 | 0.0023 | 3 | 2.1819 | 2.8224 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
115 | 2947.129 | 44270.4866 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.7082 | 0:240:120 | 0:00 | 2.0814 | 7 | 0.0949 | 2.5033 | 2.5982 | 2.5405 | 0.0425 | 0.0018 | 3 | 2.0814 | 2.6866 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
118 | 2957.3 | 44270.4867 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.5024 | 0:240:120 | 0:00 | 1.9863 | 7 | 0.0958 | 2.3828 | 2.4786 | 2.4213 | 0.0428 | 0.0018 | 3 | 1.9863 | 2.5585 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
121 | 2967.497 | 44270.4869 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.3124 | 0:240:120 | 0:00 | 1.8961 | 7 | 0.0811 | 2.2763 | 2.3574 | 2.3077 | 0.0367 | 0.0013 | 3 | 1.8961 | 2.4375 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
124 | 2977.256 | 44270.487 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.1387 | 0:240:120 | 0:00 | 1.8106 | 7 | 0.0777 | 2.1703 | 2.248 | 2.2 | 0.036 | 0.0013 | 3 | 1.8106 | 2.3233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
127 | 2986.704 | 44270.4871 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.9814 | 0:240:120 | 0:00 | 1.7294 | 7 | 0.0699 | 2.0736 | 2.1435 | 2.1 | 0.0321 | 0.001 | 3 | 1.7294 | 2.2152 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
130 | 2995.667 | 44270.4872 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.8411 | 0:240:120 | 0:00 | 1.6524 | 7 | 0.0762 | 1.9773 | 2.0535 | 2.0059 | 0.0349 | 0.0012 | 3 | 1.6524 | 2.113 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
133 | 3004.414 | 44270.4873 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.7179 | 0:240:120 | 0:00 | 1.5792 | 7 | 0.0631 | 1.8909 | 1.954 | 1.9133 | 0.03 | 0.0009 | 3 | 1.5792 | 2.0162 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
136 | 3012.82 | 44270.4874 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.6123 | 0:240:120 | 0:00 | 1.5096 | 7 | 0.0649 | 1.8026 | 1.8675 | 1.8284 | 0.0288 | 0.0008 | 3 | 1.5096 | 1.9245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
139 | 3021.107 | 44270.4875 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.5245 | 0:240:120 | 0:00 | 1.4435 | 7 | 0.058 | 1.7255 | 1.7835 | 1.7463 | 0.0274 | 0.0008 | 3 | 1.4435 | 1.8375 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
142 | 3029.088 | 44270.4876 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.455 | 0:240:120 | 0:00 | 1.3805 | 7 | 0.0562 | 1.6484 | 1.7046 | 1.6683 | 0.0267 | 0.0007 | 3 | 1.3805 | 1.755 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
145 | 3036.935 | 44270.4877 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.4041 | 0:240:120 | 0:00 | 1.3206 | 7 | 0.0511 | 1.578 | 1.6291 | 1.5962 | 0.0243 | 0.0006 | 3 | 1.3206 | 1.6767 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
148 | 3044.7 | 44270.4877 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.3722 | 0:240:120 | 0:00 | 1.2635 | 7 | 0.0537 | 1.5038 | 1.5575 | 1.5239 | 0.0247 | 0.0006 | 3 | 1.2635 | 1.6023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
151 | 3052.157 | 44270.4878 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.3596 | 0:240:120 | 0:00 | 1.2092 | 7 | 0.046 | 1.4433 | 1.4893 | 1.4594 | 0.0216 | 0.0005 | 3 | 1.2092 | 1.5315 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
154 | 3059.304 | 44270.4879 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.3668 | 0:240:120 | 0:00 | 1.1574 | 7 | 0.0464 | 1.3781 | 1.4245 | 1.3948 | 0.0218 | 0.0005 | 3 | 1.1574 | 1.4643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
157 | 3066.129 | 44270.488 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.3941 | 0:240:120 | 0:00 | 1.108 | 7 | 0.0428 | 1.3189 | 1.3617 | 1.3348 | 0.0202 | 0.0004 | 3 | 1.108 | 1.4003 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
160 | 3072.986 | 44270.4881 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.442 | 0:240:120 | 0:00 | 1.0609 | 7 | 0.0388 | 1.2648 | 1.3036 | 1.2782 | 0.0181 | 0.0003 | 3 | 1.0609 | 1.3395 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
163 | 3079.551 | 44270.4881 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.5109 | 0:240:120 | 0:00 | 1.016 | 7 | 0.0413 | 1.2066 | 1.2479 | 1.2216 | 0.0191 | 0.0004 | 3 | 1.016 | 1.2815 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
166 | 3085.974 | 44270.4882 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.6011 | 0:240:120 | 0:00 | 0.9731 | 7 | 0.038 | 1.1561 | 1.1941 | 1.1696 | 0.0178 | 0.0003 | 3 | 0.9731 | 1.2263 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
169 | 3092.404 | 44270.4883 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.7131 | 0:240:120 | 0:00 | 0.9322 | 7 | 0.0343 | 1.1077 | 1.142 | 1.1206 | 0.0153 | 0.0002 | 3 | 0.9322 | 1.1737 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
172 | 3098.593 | 44270.4884 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.8474 | 0:240:120 | 0:00 | 0.8931 | 7 | 0.0342 | 1.0594 | 1.0936 | 1.0721 | 0.0159 | 0.0003 | 3 | 0.8931 | 1.1236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
175 | 3104.647 | 44270.4884 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.0043 | 0:240:120 | 0:00 | 0.8558 | 7 | 0.0279 | 1.0184 | 1.0463 | 1.0283 | 0.0133 | 0.0002 | 3 | 0.8558 | 1.0758 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
178 | 3110.547 | 44270.4885 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.1844 | 0:240:120 | 0:00 | 0.8201 | 7 | 0.0306 | 0.972 | 1.0026 | 0.9841 | 0.013 | 0.0002 | 3 | 0.8201 | 1.0301 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
181 | 3116.368 | 44270.4886 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.3881 | 0:240:120 | 0:00 | 0.786 | 7 | 0.0283 | 0.932 | 0.9603 | 0.9425 | 0.0133 | 0.0002 | 3 | 0.786 | 0.9866 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
184 | 3122.501 | 44270.4886 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.6158 | 0:240:120 | 0:00 | 0.7535 | 7 | 0.0261 | 0.8944 | 0.9205 | 0.9038 | 0.0123 | 0.0002 | 3 | 0.7535 | 0.9451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
187 | 3128.161 | 44270.4887 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.8682 | 0:240:120 | 0:00 | 0.7223 | 7 | 0.0253 | 0.856 | 0.8813 | 0.8656 | 0.0116 | 0.0001 | 3 | 0.7223 | 0.9054 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
190 | 3133.737 | 44270.4888 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.1455 | 0:240:120 | 0:00 | 0.6925 | 7 | 0.025 | 0.8206 | 0.8456 | 0.8295 | 0.0116 | 0.0001 | 3 | 0.6925 | 0.8675 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
193 | 3139.194 | 44270.4888 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.4484 | 0:240:120 | 0:00 | 0.6641 | 7 | 0.0244 | 0.7855 | 0.8099 | 0.7942 | 0.0114 | 0.0001 | 3 | 0.6641 | 0.8314 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
196 | 3144.532 | 44270.4889 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.7774 | 0:240:120 | 0:00 | 0.6368 | 7 | 0.0203 | 0.7552 | 0.7755 | 0.7628 | 0.0094 | 0.0001 | 3 | 0.6368 | 0.7968 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
199 | 3149.56 | 44270.489 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.133 | 0:240:120 | 0:00 | 0.6107 | 7 | 0.0215 | 0.7231 | 0.7446 | 0.7311 | 0.0099 | 0.0001 | 3 | 0.6107 | 0.7637 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
202 | 3154.721 | 44270.489 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.5156 | 0:240:120 | 0:00 | 0.5858 | 7 | 0.0188 | 0.6933 | 0.7121 | 0.7003 | 0.0087 | 0.0001 | 3 | 0.5858 | 0.7321 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
205 | 3159.917 | 44270.4891 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.9259 | 0:240:120 | 0:00 | 0.5619 | 7 | 0.0175 | 0.6652 | 0.6827 | 0.6718 | 0.0081 | 0.0001 | 3 | 0.5619 | 0.7019 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
208 | 3164.768 | 44270.4891 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.3644 | 0:240:120 | 0:00 | 0.539 | 7 | 0.0203 | 0.6371 | 0.6574 | 0.6441 | 0.0089 | 0.0001 | 3 | 0.539 | 0.673 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
211 | 3169.708 | 44270.4892 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.8317 | 0:240:120 | 0:00 | 0.5171 | 7 | 0.0176 | 0.6111 | 0.6287 | 0.6174 | 0.0082 | 0.0001 | 3 | 0.5171 | 0.6454 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
214 | 3174.4 | 44270.4892 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.3284 | 0:240:120 | 0:00 | 0.4962 | 7 | 0.0167 | 0.5864 | 0.6031 | 0.5927 | 0.0075 | 0.0001 | 3 | 0.4962 | 0.619 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
217 | 3178.851 | 44270.4893 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.8549 | 0:240:120 | 0:00 | 0.4761 | 7 | 0.0156 | 0.5632 | 0.5788 | 0.5686 | 0.0072 | 0.0001 | 3 | 0.4761 | 0.5937 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
220 | 3183.253 | 44270.4893 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.412 | 0:240:120 | 0:00 | 0.4568 | 7 | 0.0158 | 0.5395 | 0.5553 | 0.5453 | 0.0071 | 0.0001 | 3 | 0.4568 | 0.5694 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
223 | 3187.867 | 44270.4894 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.0003 | 0:240:120 | 0:00 | 0.4384 | 7 | 0.015 | 0.5172 | 0.5322 | 0.523 | 0.0066 | 0 | 3 | 0.4384 | 0.5462 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
226 | 3192.361 | 44270.4895 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.6203 | 0:240:120 | 0:00 | 0.4207 | 7 | 0.0141 | 0.4959 | 0.51 | 0.5014 | 0.0062 | 0 | 3 | 0.4207 | 0.524 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
229 | 3196.693 | 44270.4895 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.2727 | 0:240:120 | 0:00 | 0.4038 | 7 | 0.0154 | 0.4752 | 0.4906 | 0.4813 | 0.0064 | 0 | 3 | 0.4038 | 0.5028 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
232 | 3200.916 | 44270.4896 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.9581 | 0:240:120 | 0:00 | 0.3876 | 7 | 0.0125 | 0.4568 | 0.4693 | 0.4617 | 0.0053 | 0 | 3 | 0.3876 | 0.4824 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
235 | 3205.032 | 44270.4896 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.6773 | 0:240:120 | 0:00 | 0.372 | 7 | 0.0115 | 0.4392 | 0.4507 | 0.4434 | 0.0052 | 0 | 3 | 0.372 | 0.4629 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
238 | 3209.442 | 44270.4897 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.4309 | 0:240:120 | 0:00 | 0.3571 | 7 | 0.012 | 0.4215 | 0.4335 | 0.4257 | 0.0054 | 0 | 3 | 0.3571 | 0.4442 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
241 | 3213.689 | 44270.4897 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.2195 | 0:240:120 | 0:00 | 0.3428 | 7 | 0.0107 | 0.4045 | 0.4152 | 0.4082 | 0.005 | 0 | 3 | 0.3428 | 0.4263 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
244 | 3217.811 | 44270.4897 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.0439 | 0:240:120 | 0:00 | 0.3291 | 7 | 0.0112 | 0.3877 | 0.3989 | 0.3918 | 0.0049 | 0 | 3 | 0.3291 | 0.4092 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
247 | 3221.848 | 44270.4898 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.9047 | 0:240:120 | 0:00 | 0.316 | 7 | 0.011 | 0.3722 | 0.3832 | 0.3763 | 0.0047 | 0 | 3 | 0.316 | 0.3927 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
250 | 3225.952 | 44270.4898 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.8028 | 0:240:120 | 0:00 | 0.3034 | 7 | 0.0104 | 0.3578 | 0.3682 | 0.3616 | 0.0047 | 0 | 3 | 0.3034 | 0.377 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
253 | 3229.967 | 44270.4899 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.7389 | 0:240:120 | 0:00 | 0.2913 | 7 | 0.0094 | 0.3438 | 0.3532 | 0.3472 | 0.0043 | 0 | 3 | 0.2913 | 0.3618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
256 | 3233.919 | 44270.4899 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.7137 | 0:240:120 | 0:00 | 0.2797 | 7 | 0.0095 | 0.3295 | 0.339 | 0.3333 | 0.0041 | 0 | 3 | 0.2797 | 0.3474 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
259 | 3237.734 | 44270.49 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.7279 | 0:240:120 | 0:00 | 0.2686 | 7 | 0.0093 | 0.3157 | 0.325 | 0.3194 | 0.0041 | 0 | 3 | 0.2686 | 0.3335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
262 | 3241.555 | 44270.49 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.7825 | 0:240:120 | 0:00 | 0.2579 | 7 | 0.0079 | 0.3041 | 0.312 | 0.3071 | 0.0036 | 0 | 3 | 0.2579 | 0.3201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
265 | 3245.359 | 44270.4901 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.8781 | 0:240:120 | 0:00 | 0.2477 | 7 | 0.0088 | 0.2913 | 0.3001 | 0.295 | 0.0036 | 0 | 3 | 0.2477 | 0.3074 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
268 | 3249.179 | 44270.4901 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.0157 | 0:240:120 | 0:00 | 0.2379 | 7 | 0.0078 | 0.2802 | 0.288 | 0.2836 | 0.0032 | 0 | 3 | 0.2379 | 0.2951 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
271 | 3253.024 | 44270.4902 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.196 | 0:240:120 | 0:00 | 0.2284 | 7 | 0.0081 | 0.2692 | 0.2773 | 0.2724 | 0.0034 | 0 | 3 | 0.2284 | 0.2834 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
274 | 3256.7 | 44270.4902 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.4199 | 0:240:120 | 0:00 | 0.2194 | 7 | 0.007 | 0.2589 | 0.2659 | 0.2619 | 0.0028 | 0 | 3 | 0.2194 | 0.2721 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
277 | 3260.443 | 44270.4902 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 115.6883 | 0:240:120 | 0:00 | 0.2107 | 7 | 0.0079 | 0.2477 | 0.2556 | 0.2511 | 0.0034 | 0 | 3 | 0.2107 | 0.2613 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
280 | 3264.205 | 44270.4903 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.0021 | 0:240:120 | 0:00 | 0.2024 | 7 | 0.0072 | 0.2382 | 0.2454 | 0.2413 | 0.0028 | 0 | 3 | 0.2024 | 0.2509 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
283 | 3267.981 | 44270.4903 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.3621 | 0:240:120 | 0:00 | 0.1944 | 7 | 0.0066 | 0.2289 | 0.2355 | 0.2321 | 0.0026 | 0 | 3 | 0.1944 | 0.241 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
286 | 3271.705 | 44270.4904 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 122.7694 | 0:240:120 | 0:00 | 0.1867 | 7 | 0.0063 | 0.2199 | 0.2262 | 0.2229 | 0.0026 | 0 | 3 | 0.1867 | 0.2314 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
289 | 3275.255 | 44270.4904 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.2248 | 0:240:120 | 0:00 | 0.1793 | 7 | 0.0063 | 0.2111 | 0.2174 | 0.2135 | 0.0024 | 0 | 3 | 0.1793 | 0.2223 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
292 | 3278.679 | 44270.4905 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 127.7293 | 0:240:120 | 0:00 | 0.1723 | 7 | 0.0054 | 0.2031 | 0.2085 | 0.2055 | 0.0023 | 0 | 3 | 0.1723 | 0.2135 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
295 | 3282.07 | 44270.4905 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.2839 | 0:240:120 | 0:00 | 0.1655 | 7 | 0.0067 | 0.1942 | 0.2009 | 0.1973 | 0.0026 | 0 | 3 | 0.1655 | 0.205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
298 | 3285.569 | 44270.4905 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 132.8895 | 0:240:120 | 0:00 | 0.159 | 7 | 0.0063 | 0.1861 | 0.1924 | 0.1892 | 0.0024 | 0 | 3 | 0.159 | 0.1969 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
301 | 3289.08 | 44270.4906 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 135.5473 | 0:240:120 | 0:00 | 0.1527 | 7 | 0.0062 | 0.1794 | 0.1856 | 0.1821 | 0.0023 | 0 | 3 | 0.1527 | 0.1891 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
304 | 3292.606 | 44270.4906 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.2583 | 0:240:120 | 0:00 | 0.1467 | 7 | 0.0046 | 0.1732 | 0.1778 | 0.1752 | 0.0017 | 0 | 3 | 0.1467 | 0.1817 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
307 | 3296.183 | 44270.4907 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.0234 | 0:240:120 | 0:00 | 0.1409 | 7 | 0.0052 | 0.1657 | 0.1709 | 0.1678 | 0.002 | 0 | 3 | 0.1409 | 0.1745 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
310 | 3299.612 | 44270.4907 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 143.8439 | 0:240:120 | 0:00 | 0.1354 | 7 | 0.0044 | 0.1595 | 0.1639 | 0.1612 | 0.002 | 0 | 3 | 0.1354 | 0.1676 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
313 | 3303.201 | 44270.4907 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 146.7208 | 0:240:120 | 0:00 | 0.1301 | 7 | 0.0055 | 0.1525 | 0.158 | 0.1555 | 0.0019 | 0 | 3 | 0.1301 | 0.161 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
316 | 3306.634 | 44270.4908 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 149.6552 | 0:240:120 | 0:00 | 0.125 | 7 | 0.0041 | 0.1471 | 0.1512 | 0.1492 | 0.0017 | 0 | 3 | 0.125 | 0.1547 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
319 | 3310.105 | 44270.4908 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 152.6483 | 0:240:120 | 0:00 | 0.1201 | 7 | 0.0039 | 0.1414 | 0.1453 | 0.1433 | 0.0015 | 0 | 3 | 0.1201 | 0.1486 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
322 | 3313.652 | 44270.4909 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 155.7013 | 0:240:120 | 0:00 | 0.1154 | 7 | 0.0051 | 0.1355 | 0.1406 | 0.1379 | 0.0018 | 0 | 3 | 0.1154 | 0.1428 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
325 | 3317.073 | 44270.4909 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 158.8153 | 0:240:120 | 0:00 | 0.1108 | 7 | 0.0046 | 0.13 | 0.1346 | 0.1325 | 0.0016 | 0 | 3 | 0.1108 | 0.1372 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
328 | 3320.509 | 44270.4909 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 161.9916 | 0:240:120 | 0:00 | 0.1065 | 7 | 0.003 | 0.1258 | 0.1288 | 0.1275 | 0.0012 | 0 | 3 | 0.1065 | 0.1318 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
331 | 3323.862 | 44270.491 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.2314 | 0:240:120 | 0:00 | 0.1023 | 7 | 0.0041 | 0.1201 | 0.1242 | 0.122 | 0.0015 | 0 | 3 | 0.1023 | 0.1266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
334 | 3327.056 | 44270.491 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 168.5361 | 0:240:120 | 0:00 | 0.0983 | 7 | 0.0042 | 0.1153 | 0.1195 | 0.1177 | 0.0014 | 0 | 3 | 0.0983 | 0.1216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
337 | 3330.391 | 44270.4911 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 171.9068 | 0:240:120 | 0:00 | 0.0945 | 7 | 0.0042 | 0.111 | 0.1152 | 0.1129 | 0.0016 | 0 | 3 | 0.0945 | 0.1168 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
340 | 3333.595 | 44270.4911 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175.3449 | 0:240:120 | 0:00 | 0.0908 | 7 | 0.0042 | 0.1067 | 0.1109 | 0.1089 | 0.0015 | 0 | 3 | 0.0908 | 0.1123 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
343 | 3336.863 | 44270.4911 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 178.8518 | 0:240:120 | 0:00 | 0.0872 | 7 | 0.004 | 0.1026 | 0.1066 | 0.1049 | 0.0014 | 0 | 3 | 0.0872 | 0.1079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
346 | 3340.114 | 44270.4912 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 182.4289 | 0:240:120 | 0:00 | 0.0838 | 7 | 0.0029 | 0.0988 | 0.1017 | 0.1003 | 0.0011 | 0 | 3 | 0.0838 | 0.1036 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
349 | 3343.322 | 44270.4912 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 186.0774 | 0:240:120 | 0:00 | 0.0805 | 7 | 0.0038 | 0.0943 | 0.0981 | 0.0963 | 0.0013 | 0 | 3 | 0.0805 | 0.0996 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
352 | 3346.501 | 44270.4912 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 189.799 | 0:240:120 | 0:00 | 0.0774 | 7 | 0.0037 | 0.0906 | 0.0943 | 0.0927 | 0.0014 | 0 | 3 | 0.0774 | 0.0957 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
355 | 3349.746 | 44270.4913 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 193.595 | 0:240:120 | 0:00 | 0.0743 | 7 | 0.0039 | 0.0879 | 0.0918 | 0.0898 | 0.0012 | 0 | 3 | 0.0743 | 0.0919 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
358 | 3352.978 | 44270.4913 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 197.4669 | 0:240:120 | 0:00 | 0.0714 | 7 | 0.0026 | 0.0845 | 0.0871 | 0.0857 | 0.0009 | 0 | 3 | 0.0714 | 0.0883 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
361 | 3356.194 | 44270.4913 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 201.4162 | 0:240:120 | 0:00 | 0.0687 | 7 | 0.0027 | 0.0814 | 0.0841 | 0.0828 | 0.001 | 0 | 3 | 0.0687 | 0.0849 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
364 | 3359.452 | 44270.4914 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 205.4445 | 0:240:120 | 0:00 | 0.066 | 7 | 0.0039 | 0.0769 | 0.0808 | 0.079 | 0.0014 | 0 | 3 | 0.066 | 0.0816 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
367 | 3362.706 | 44270.4914 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 209.5534 | 0:240:120 | 0:00 | 0.0634 | 7 | 0.0034 | 0.0747 | 0.0781 | 0.0767 | 0.0013 | 0 | 3 | 0.0634 | 0.0784 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
370 | 3365.982 | 44270.4915 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 213.7445 | 0:240:120 | 0:00 | 0.0609 | 7 | 0.0033 | 0.0712 | 0.0745 | 0.0729 | 0.0013 | 0 | 3 | 0.0609 | 0.0753 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
373 | 3369.204 | 44270.4915 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 218.0194 | 0:240:120 | 0:00 | 0.0585 | 7 | 0.004 | 0.0688 | 0.0728 | 0.071 | 0.0013 | 0 | 3 | 0.0585 | 0.0724 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
376 | 3372.481 | 44270.4915 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 222.3798 | 0:240:120 | 0:00 | 0.0563 | 7 | 0.0024 | 0.0668 | 0.0692 | 0.0683 | 0.001 | 0 | 3 | 0.0563 | 0.0695 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
379 | 3375.732 | 44270.4916 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 226.8274 | 0:240:120 | 0:00 | 0.0541 | 7 | 0.0026 | 0.0643 | 0.0669 | 0.0657 | 0.0009 | 0 | 3 | 0.0541 | 0.0668 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
382 | 3378.956 | 44270.4916 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 231.3639 | 0:240:120 | 0:00 | 0.052 | 7 | 0.0036 | 0.061 | 0.0646 | 0.0631 | 0.0014 | 0 | 3 | 0.052 | 0.0642 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
385 | 3382.186 | 44270.4917 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 235.9912 | 0:240:120 | 0:00 | 0.0499 | 7 | 0.0037 | 0.0579 | 0.0616 | 0.0603 | 0.0012 | 0 | 3 | 0.0499 | 0.0617 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
388 | 3385.396 | 44270.4917 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 240.711 | 0:240:120 | 0:00 | 0.048 | 7 | 0.003 | 0.0567 | 0.0597 | 0.0586 | 0.0011 | 0 | 3 | 0.048 | 0.0593 | P | NP | 1-1-1-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
391 | 3388.635 | 44270.4917 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 245.5252 | 0:240:120 | 0:00 | 0.0461 | 7 | 0.0031 | 0.054 | 0.0571 | 0.0557 | 0.0011 | 0 | 3 | 0.0461 | 0.057 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
394 | 3391.86 | 44270.4918 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 250.4357 | 0:240:120 | 0:00 | 0.0443 | 7 | 0.0025 | 0.0528 | 0.0553 | 0.0539 | 0.0009 | 0 | 3 | 0.0443 | 0.0548 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
397 | 3395.089 | 44270.4918 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 255.4444 | 0:240:120 | 0:00 | 0.0426 | 7 | 0.0034 | 0.0499 | 0.0533 | 0.0519 | 0.001 | 0 | 3 | 0.0426 | 0.0526 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
400 | 3398.322 | 44270.4918 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 260.5533 | 0:240:120 | 0:00 | 0.0409 | 7 | 0.0027 | 0.048 | 0.0507 | 0.0498 | 0.0012 | 0 | 3 | 0.0409 | 0.0509 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
403 | 3401.557 | 44270.4919 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 265.7644 | 0:240:120 | 0:00 | 0.0393 | 7 | 0.0031 | 0.0465 | 0.0496 | 0.0479 | 0.001 | 0 | 3 | 0.0393 | 0.0493 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
406 | 3404.775 | 44270.4919 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 271.0797 | 0:240:120 | 0:00 | 0.0378 | 7 | 0.0029 | 0.0443 | 0.0472 | 0.0462 | 0.0013 | 0 | 3 | 0.0378 | 0.0478 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
409 | 3407.985 | 44270.4919 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 276.5013 | 0:240:120 | 0:00 | 0.0363 | 7 | 0.003 | 0.0421 | 0.0451 | 0.0441 | 0.0011 | 0 | 3 | 0.0363 | 0.0463 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
412 | 3410.969 | 44270.492 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 282.0313 | 0:240:120 | 0:00 | 0.0349 | 7 | 0.0027 | 0.0416 | 0.0443 | 0.043 | 0.001 | 0 | 3 | 0.0349 | 0.0449 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
415 | 3414.111 | 44270.492 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 287.6719 | 0:240:120 | 0:00 | 0.0336 | 7 | 0.0027 | 0.0404 | 0.0431 | 0.0414 | 0.0009 | 0 | 3 | 0.0336 | 0.0436 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
418 | 3417.327 | 44270.4921 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 293.4254 | 0:240:120 | 0:00 | 0.0322 | 7 | 0.0031 | 0.0377 | 0.0408 | 0.0397 | 0.0012 | 0 | 3 | 0.0322 | 0.0422 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
421 | 3420.53 | 44270.4921 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 299.2939 | 0:240:120 | 0:00 | 0.031 | 7 | 0.0027 | 0.0363 | 0.039 | 0.038 | 0.0011 | 0 | 3 | 0.031 | 0.041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
424 | 3423.707 | 44270.4921 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 305.2798 | 0:240:120 | 0:00 | 0.0298 | 7 | 0.003 | 0.0357 | 0.0387 | 0.0372 | 0.001 | 0 | 3 | 0.0298 | 0.0398 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
427 | 3426.932 | 44270.4922 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 311.3854 | 0:240:120 | 0:00 | 0.0286 | 7 | 0.0033 | 0.0338 | 0.0371 | 0.0357 | 0.0012 | 0 | 3 | 0.0286 | 0.0386 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
430 | 3429.965 | 44270.4922 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 317.6131 | 0:240:120 | 0:00 | 0.0275 | 7 | 0.003 | 0.0327 | 0.0357 | 0.0347 | 0.0012 | 0 | 3 | 0.0275 | 0.0375 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
433 | 3432.935 | 44270.4922 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 323.9653 | 0:240:120 | 0:00 | 0.0264 | 7 | 0.0035 | 0.031 | 0.0345 | 0.033 | 0.0012 | 0 | 3 | 0.0264 | 0.0364 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
436 | 3436.13 | 44270.4923 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 330.4446 | 0:240:120 | 0:00 | 0.0254 | 7 | 0.0034 | 0.0301 | 0.0335 | 0.0318 | 0.0011 | 0 | 3 | 0.0254 | 0.0354 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
439 | 3439.403 | 44270.4923 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 337.0535 | 0:240:120 | 0:00 | 0.0244 | 7 | 0.0033 | 0.0293 | 0.0326 | 0.031 | 0.0011 | 0 | 3 | 0.0244 | 0.0344 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
442 | 3442.536 | 44270.4923 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 343.7946 | 0:240:120 | 0:00 | 0.0235 | 7 | 0.0032 | 0.0279 | 0.0311 | 0.0297 | 0.0009 | 0 | 3 | 0.0235 | 0.0335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
445 | 3445.68 | 44270.4924 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 350.6705 | 0:240:120 | 0:00 | 0.0226 | 7 | 0.003 | 0.027 | 0.03 | 0.0287 | 0.0011 | 0 | 3 | 0.0226 | 0.0326 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
448 | 3448.71 | 44270.4924 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 357.6839 | 0:240:120 | 0:00 | 0.0217 | 7 | 0.004 | 0.0255 | 0.0295 | 0.0278 | 0.0013 | 0 | 3 | 0.0217 | 0.0317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
451 | 3451.84 | 44270.4925 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 364.8376 | 0:240:120 | 0:00 | 0.0208 | 7 | 0.0036 | 0.0252 | 0.0288 | 0.0274 | 0.0014 | 0 | 3 | 0.0208 | 0.0308 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
454 | 3454.986 | 44270.4925 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 372.1343 | 0:240:120 | 0:00 | 0.02 | 7 | 0.0032 | 0.0246 | 0.0278 | 0.0263 | 0.0011 | 0 | 3 | 0.02 | 0.03 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
457 | 3457.999 | 44270.4925 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 379.577 | 0:240:120 | 0:00 | 0.0192 | 7 | 0.0028 | 0.0239 | 0.0267 | 0.0255 | 0.001 | 0 | 3 | 0.0192 | 0.0292 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
460 | 3461.117 | 44270.4926 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 387.1685 | 0:240:120 | 0:00 | 0.0185 | 7 | 0.0031 | 0.0226 | 0.0257 | 0.0246 | 0.0012 | 0 | 3 | 0.0185 | 0.0285 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
463 | 3464.239 | 44270.4926 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 394.9119 | 0:240:120 | 0:00 | 0.0178 | 7 | 0.0038 | 0.0219 | 0.0257 | 0.0239 | 0.0012 | 0 | 3 | 0.0178 | 0.0278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
466 | 3467.383 | 44270.4926 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 402.8102 | 0:240:120 | 0:00 | 0.0171 | 7 | 0.0038 | 0.0204 | 0.0242 | 0.0229 | 0.0013 | 0 | 3 | 0.0171 | 0.0271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
469 | 3470.648 | 44270.4927 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 410.8664 | 0:240:120 | 0:00 | 0.0164 | 7 | 0.0042 | 0.0203 | 0.0245 | 0.0226 | 0.0015 | 0 | 3 | 0.0164 | 0.0264 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
472 | 3473.775 | 44270.4927 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 419.0837 | 0:240:120 | 0:00 | 0.0158 | 7 | 0.0036 | 0.0197 | 0.0233 | 0.0219 | 0.0014 | 0 | 3 | 0.0158 | 0.0258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
475 | 3476.879 | 44270.4927 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 427.4654 | 0:240:120 | 0:00 | 0.0152 | 7 | 0.0025 | 0.0199 | 0.0224 | 0.0216 | 0.0011 | 0 | 3 | 0.0152 | 0.0252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
478 | 3479.873 | 44270.4928 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 436.0147 | 0:240:120 | 0:00 | 0.0146 | 7 | 0.0029 | 0.0198 | 0.0227 | 0.0212 | 0.0011 | 0 | 3 | 0.0146 | 0.0246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
481 | 3483.085 | 44270.4928 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 444.735 | 0:240:120 | 0:00 | 0.014 | 7 | 0.0027 | 0.0193 | 0.022 | 0.0208 | 0.0011 | 0 | 3 | 0.014 | 0.024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
484 | 3486.239 | 44270.4929 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 453.6297 | 0:240:120 | 0:00 | 0.0135 | 7 | 0.0034 | 0.0183 | 0.0217 | 0.0202 | 0.0012 | 0 | 3 | 0.0135 | 0.0235 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
487 | 3489.487 | 44270.4929 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 462.7023 | 0:240:120 | 0:00 | 0.0129 | 7 | 0.0029 | 0.0183 | 0.0212 | 0.0199 | 0.0012 | 0 | 3 | 0.0129 | 0.0229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
490 | 3492.529 | 44270.4929 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 471.9563 | 0:240:120 | 0:00 | 0.0124 | 7 | 0.0026 | 0.0177 | 0.0203 | 0.0194 | 0.0009 | 0 | 3 | 0.0124 | 0.0224 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
493 | 3495.652 | 44270.493 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 481.3954 | 0:240:120 | 0:00 | 0.012 | 7 | 0.003 | 0.0181 | 0.0211 | 0.0189 | 0.001 | 0 | 3 | 0.012 | 0.022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
496 | 3498.738 | 44270.493 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 491.0233 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0025 | 0.0175 | 0.02 | 0.0186 | 0.0008 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
499 | 3501.765 | 44270.493 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 500.8438 | 0:240:120 | 0:00 | 0.011 | 7 | 0.0017 | 0.0178 | 0.0195 | 0.0186 | 0.0006 | 0 | 3 | 0.011 | 0.021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
502 | 3504.949 | 44270.4931 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 510.8607 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0016 | 0.0174 | 0.019 | 0.0177 | 0.0005 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
505 | 3508.005 | 44270.4931 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 521.0779 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.0013 | 0.0169 | 0.0182 | 0.0172 | 0.0004 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
508 | 3510.992 | 44270.4931 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 526.3671 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0018 | 0.0164 | 0.0182 | 0.0174 | 0.0008 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
511 | 3514.03 | 44270.4932 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 536.8944 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0013 | 0.0166 | 0.0179 | 0.0171 | 0.0006 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
514 | 3517.105 | 44270.4932 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 547.6323 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0018 | 0.0156 | 0.0174 | 0.0165 | 0.0006 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 1-0-0-0-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
517 | 3520.163 | 44270.4932 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 558.5849 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.003 | 0.0153 | 0.0183 | 0.0165 | 0.0009 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 1-0-0-0-0-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
520 | 3523.329 | 44270.4933 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 569.7566 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0041 | 0.0142 | 0.0183 | 0.016 | 0.0012 | 0 | 3 | 0.0085 | 0.016 | NP | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
523 | 3526.356 | 44270.4933 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 581.1518 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0042 | 0.0139 | 0.0181 | 0.0155 | 0.0015 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
526 | 3529.421 | 44270.4934 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 592.7748 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0041 | 0.0134 | 0.0175 | 0.0151 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
529 | 3532.699 | 44270.4934 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 604.6303 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0038 | 0.0134 | 0.0172 | 0.0152 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
532 | 3535.852 | 44270.4934 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 616.7229 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0043 | 0.0125 | 0.0168 | 0.0148 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
535 | 3539.132 | 44270.4935 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 629.0574 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0052 | 0.0123 | 0.0175 | 0.0148 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
538 | 3542.285 | 44270.4935 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 641.6385 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0041 | 0.0125 | 0.0166 | 0.0145 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
541 | 3545.443 | 44270.4935 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 654.4713 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0042 | 0.012 | 0.0162 | 0.0145 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
544 | 3548.613 | 44270.4936 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 667.5607 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0046 | 0.0121 | 0.0167 | 0.0144 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
547 | 3551.797 | 44270.4936 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 680.9119 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0046 | 0.0117 | 0.0163 | 0.0141 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
550 | 3554.875 | 44270.4936 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 694.5302 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0045 | 0.0117 | 0.0162 | 0.0143 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
553 | 3558.044 | 44270.4937 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 708.4208 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0043 | 0.0117 | 0.016 | 0.014 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
556 | 3561.12 | 44270.4937 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 722.5892 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0047 | 0.0111 | 0.0158 | 0.0136 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
559 | 3564.415 | 44270.4938 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 737.041 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0053 | 0.011 | 0.0163 | 0.0137 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
562 | 3567.51 | 44270.4938 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 751.7818 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0054 | 0.011 | 0.0164 | 0.0137 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
565 | 3570.726 | 44270.4938 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 766.8174 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0052 | 0.0106 | 0.0158 | 0.0133 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
568 | 3573.992 | 44270.4939 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 782.1538 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0052 | 0.0105 | 0.0157 | 0.0134 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
571 | 3577.175 | 44270.4939 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 797.7968 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.0053 | 0.0104 | 0.0157 | 0.0132 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
574 | 3580.358 | 44270.4939 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 813.7528 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0051 | 0.011 | 0.0161 | 0.0133 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
577 | 3583.758 | 44270.494 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 830.0278 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0054 | 0.0106 | 0.016 | 0.0131 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
580 | 3587.025 | 44270.494 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 846.6284 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0052 | 0.0102 | 0.0154 | 0.0132 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
583 | 3590.211 | 44270.4941 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 863.561 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0042 | 0.0103 | 0.0145 | 0.0127 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
586 | 3593.492 | 44270.4941 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 880.8322 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0037 | 0.0104 | 0.0141 | 0.0123 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
589 | 3596.799 | 44270.4941 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 898.4488 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0036 | 0.0107 | 0.0143 | 0.0126 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
592 | 3599.915 | 44270.4942 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 916.4178 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0039 | 0.0102 | 0.0141 | 0.0123 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
595 | 3603.197 | 44270.4942 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 934.7461 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0039 | 0.0099 | 0.0138 | 0.0118 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
598 | 3606.396 | 44270.4942 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 953.4411 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0031 | 0.0101 | 0.0132 | 0.0116 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
601 | 3609.559 | 44270.4943 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 972.5099 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0033 | 0.0099 | 0.0132 | 0.0114 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
604 | 3612.732 | 44270.4943 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 991.9601 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0028 | 0.0103 | 0.0131 | 0.0112 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
607 | 3615.942 | 44270.4944 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1011.7993 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0029 | 0.0097 | 0.0126 | 0.011 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
610 | 3619.106 | 44270.4944 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1032.0353 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0032 | 0.0102 | 0.0134 | 0.0111 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
613 | 3622.296 | 44270.4944 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1052.676 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0041 | 0.0093 | 0.0134 | 0.011 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
616 | 3625.498 | 44270.4945 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1052.7341 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0022 | 0.0099 | 0.0121 | 0.0109 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
619 | 3628.82 | 44270.4945 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1073.7888 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0035 | 0.0093 | 0.0128 | 0.0108 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
622 | 3632.108 | 44270.4945 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1095.2646 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0036 | 0.0092 | 0.0128 | 0.0106 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
625 | 3635.415 | 44270.4946 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1117.1699 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0013 | 0.0107 | 0.012 | 0.0111 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
628 | 3638.713 | 44270.4946 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1139.5133 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.004 | 0.0092 | 0.0132 | 0.0107 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
631 | 3641.899 | 44270.4947 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1162.3035 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0022 | 0.0101 | 0.0123 | 0.0108 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
634 | 3645.099 | 44270.4947 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1185.5496 | 0:240:120 | 0:00 | 0.002 | 7 | 0.003 | 0.0093 | 0.0123 | 0.0108 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
637 | 3648.298 | 44270.4947 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1209.2606 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0028 | 0.0097 | 0.0125 | 0.0106 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
640 | 3651.499 | 44270.4948 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1233.4458 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0028 | 0.0093 | 0.0121 | 0.0105 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
643 | 3654.661 | 44270.4948 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1258.1147 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0023 | 0.0093 | 0.0116 | 0.0101 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
646 | 3657.773 | 44270.4948 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1283.277 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0026 | 0.0089 | 0.0115 | 0.0102 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
649 | 3661.102 | 44270.4949 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1308.9426 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0026 | 0.009 | 0.0116 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
652 | 3664.384 | 44270.4949 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1335.1214 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0012 | 0.0104 | 0.0116 | 0.0107 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
655 | 3667.491 | 44270.495 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1361.8238 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.0094 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
658 | 3670.821 | 44270.495 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1389.0603 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0007 | 0.0101 | 0.0108 | 0.0105 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
661 | 3673.918 | 44270.495 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1416.8415 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.002 | 0.0089 | 0.0109 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
664 | 3677.128 | 44270.4951 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1445.1784 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0015 | 0.0092 | 0.0107 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
667 | 3680.341 | 44270.4951 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1474.0819 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0014 | 0.0099 | 0.0113 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
670 | 3683.673 | 44270.4951 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1503.5636 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0007 | 0.0098 | 0.0105 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
673 | 3686.873 | 44270.4952 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1533.6348 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0015 | 0.0093 | 0.0108 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
676 | 3690.073 | 44270.4952 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1564.3075 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
679 | 3693.195 | 44270.4952 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1595.5937 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0023 | 0.0092 | 0.0115 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
682 | 3696.322 | 44270.4953 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1627.5056 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
685 | 3699.438 | 44270.4953 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1660.0557 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
688 | 3702.652 | 44270.4954 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1693.2568 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0023 | 0.0091 | 0.0114 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
691 | 3705.964 | 44270.4954 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1727.1219 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0004 | 0.0095 | 0.0099 | 0.0097 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
694 | 3709.256 | 44270.4954 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1761.6643 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
697 | 3712.473 | 44270.4955 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1796.8976 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0014 | 0.01 | 0.0114 | 0.0106 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
700 | 3715.675 | 44270.4955 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1832.8356 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
703 | 3719.147 | 44270.4956 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1869.4923 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
706 | 3722.264 | 44270.4956 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1906.8821 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
709 | 3725.516 | 44270.4956 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1945.0198 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.001 | 0.0099 | 0.0109 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
712 | 3728.729 | 44270.4957 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1983.9202 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0021 | 0.0092 | 0.0113 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
715 | 3731.929 | 44270.4957 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2023.5986 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
718 | 3735.157 | 44270.4957 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2064.0706 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
721 | 3738.386 | 44270.4958 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2105.352 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
724 | 3741.605 | 44270.4958 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2147.459 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0011 | 0.0091 | 0.0102 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
727 | 3744.744 | 44270.4958 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2190.4082 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.001 | 0.0098 | 0.0108 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
730 | 3747.896 | 44270.4959 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2234.2164 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.001 | 0.0095 | 0.0105 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
733 | 3751.109 | 44270.4959 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2278.9007 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
736 | 3754.357 | 44270.496 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2324.4787 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
739 | 3757.617 | 44270.496 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2370.9683 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
742 | 3760.933 | 44270.496 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2418.3876 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0019 | 0.0088 | 0.0107 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
745 | 3764.15 | 44270.4961 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2466.7554 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0012 | 0.0099 | 0.0111 | 0.0103 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
748 | 3767.43 | 44270.4961 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2516.0905 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
751 | 3770.651 | 44270.4961 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2566.4123 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.001 | 0.0098 | 0.0108 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
754 | 3773.901 | 44270.4962 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2617.7406 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0015 | 0.0089 | 0.0104 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
757 | 3777.114 | 44270.4962 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2670.0954 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
760 | 3780.441 | 44270.4963 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2723.4973 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0019 | 0.0088 | 0.0107 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
763 | 3783.575 | 44270.4963 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2777.9672 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0024 | 0.0088 | 0.0112 | 0.01 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
766 | 3786.702 | 44270.4963 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2833.5266 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
769 | 3789.843 | 44270.4964 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2890.1971 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0011 | 0.0089 | 0.01 | 0.0093 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
772 | 3793.077 | 44270.4964 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2948.001 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0015 | 0.0098 | 0.0113 | 0.0105 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
775 | 3796.246 | 44270.4964 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3006.9611 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
778 | 3799.502 | 44270.4965 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3067.1003 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
781 | 3802.724 | 44270.4965 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3128.4423 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0019 | 0.0094 | 0.0113 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
784 | 3805.899 | 44270.4966 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3191.0111 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
787 | 3809.046 | 44270.4966 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3254.8313 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
790 | 3812.19 | 44270.4966 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3319.928 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0097 | 0.0113 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
793 | 3815.447 | 44270.4967 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3386.3265 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
796 | 3818.511 | 44270.4967 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3454.0531 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.002 | 0.009 | 0.011 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
799 | 3821.841 | 44270.4967 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3523.1341 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0012 | 0.009 | 0.0102 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
802 | 3824.908 | 44270.4968 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3593.5968 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
805 | 3828.074 | 44270.4968 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3665.4687 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0097 | 0.0113 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
808 | 3831.29 | 44270.4968 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3738.7781 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0003 | 0.0094 | 0.0097 | 0.0095 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
811 | 3834.356 | 44270.4969 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3813.5537 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
814 | 3837.612 | 44270.4969 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3889.8248 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
817 | 3840.864 | 44270.497 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3967.6213 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0006 | 0.0094 | 0.01 | 0.0097 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
820 | 3843.996 | 44270.497 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4046.9737 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
823 | 3847.241 | 44270.497 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4127.9131 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0024 | 0.0088 | 0.0112 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
826 | 3850.498 | 44270.4971 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4210.4714 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0105 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
829 | 3853.741 | 44270.4971 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4294.6808 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0014 | 0.0091 | 0.0105 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
832 | 3856.799 | 44270.4971 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4380.5745 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.0088 | 0.0103 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
835 | 3860.28 | 44270.4972 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4468.1859 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.0096 | 0.0111 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
838 | 3863.426 | 44270.4972 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4557.5497 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0096 | 0.0108 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
841 | 3866.805 | 44270.4973 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4648.7007 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
844 | 3870.034 | 44270.4973 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4741.6747 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
847 | 3873.29 | 44270.4973 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4836.5082 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
850 | 3876.547 | 44270.4974 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4933.2383 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
853 | 3879.816 | 44270.4974 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5031.9031 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
856 | 3883.074 | 44270.4974 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5132.5412 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0014 | 0.0089 | 0.0103 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
859 | 3886.565 | 44270.4975 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5235.192 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.001 | 0.0095 | 0.0105 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
862 | 3889.75 | 44270.4975 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5339.8958 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
865 | 3892.918 | 44270.4976 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5446.6937 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0022 | 0.0088 | 0.011 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
868 | 3896.179 | 44270.4976 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5555.6276 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
871 | 3899.397 | 44270.4976 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5666.7402 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0095 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
874 | 3902.558 | 44270.4977 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5780.075 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
877 | 3905.816 | 44270.4977 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5895.6765 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0014 | 0.0089 | 0.0103 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
880 | 3909.072 | 44270.4977 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6013.59 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.001 | 0.0097 | 0.0107 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
883 | 3912.33 | 44270.4978 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6133.8618 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0021 | 0.009 | 0.0111 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
886 | 3915.734 | 44270.4978 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6256.539 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
889 | 3918.919 | 44270.4979 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6381.6698 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
892 | 3922.086 | 44270.4979 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6509.3032 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.01 | 0.0111 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
895 | 3925.161 | 44270.4979 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6639.4893 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0088 | 0.0105 | 0.0096 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
898 | 3928.544 | 44270.498 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6772.2791 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0091 | 0.011 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
901 | 3931.824 | 44270.498 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6907.7246 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0096 | 0.0109 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
904 | 3935.116 | 44270.498 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7045.8791 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0091 | 0.011 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
907 | 3938.273 | 44270.4981 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7186.7967 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.009 | 0.0109 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
910 | 3941.447 | 44270.4981 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7330.5326 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0088 | 0.0107 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
913 | 3944.598 | 44270.4982 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7477.1433 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0095 | 0.0106 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
916 | 3947.883 | 44270.4982 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7626.6862 | 0:240:120 | 0:00 | 0 | 7 | 0.002 | 0.0089 | 0.0109 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
919 | 3951.155 | 44270.4982 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7779.2199 | 0:240:120 | 0:00 | 0 | 7 | 0.0008 | 0.0094 | 0.0102 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
922 | 3954.238 | 44270.4983 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7934.8043 | 0:240:120 | 0:00 | 0 | 7 | 0.0003 | 0.0093 | 0.0096 | 0.0095 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
925 | 3957.587 | 44270.4983 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8093.5004 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
928 | 3961.074 | 44270.4984 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8255.3704 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
931 | 3964.169 | 44270.4984 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8420.4778 | 0:240:120 | 0:00 | 0 | 7 | 0.0006 | 0.0097 | 0.0103 | 0.01 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
934 | 3967.47 | 44270.4984 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8588.8873 | 0:240:120 | 0:00 | 0 | 7 | 0.0009 | 0.0096 | 0.0105 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
937 | 3970.87 | 44270.4985 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8760.6651 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0096 | 0.0107 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
940 | 3973.947 | 44270.4985 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8935.8784 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0094 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
943 | 3977.135 | 44270.4985 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9114.596 | 0:240:120 | 0:00 | 0 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
946 | 3980.401 | 44270.4986 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9296.8879 | 0:240:120 | 0:00 | 0 | 7 | 0.0008 | 0.0096 | 0.0104 | 0.01 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
949 | 3983.558 | 44270.4986 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9482.8256 | 0:240:120 | 0:00 | 0 | 7 | 0.0008 | 0.0094 | 0.0102 | 0.0098 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
952 | 3986.755 | 44270.4986 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9672.4822 | 0:240:120 | 0:00 | 0 | 7 | 0.0014 | 0.0098 | 0.0112 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
955 | 3990.049 | 44270.4987 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9865.9318 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.0095 | 0.0107 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
958 | 3993.135 | 44270.4987 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10063.2504 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
961 | 3996.641 | 44270.4988 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10264.5154 | 0:240:120 | 0:00 | 0 | 7 | 0.0019 | 0.0089 | 0.0108 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
964 | 3999.926 | 44270.4988 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10469.8057 | 0:240:120 | 0:00 | 0 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
967 | 4003.036 | 44270.4988 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10679.2019 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.01 | 0.0111 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
970 | 4006.446 | 44270.4989 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10892.7859 | 0:240:120 | 0:00 | 0 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
973 | 4009.648 | 44270.4989 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11110.6416 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
976 | 4012.77 | 44270.4989 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11332.8545 | 0:240:120 | 0:00 | 0 | 7 | 0.0022 | 0.0088 | 0.011 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
979 | 4016.191 | 44270.499 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11559.5115 | 0:240:120 | 0:00 | 0 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
982 | 4019.456 | 44270.499 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11790.7018 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
985 | 4121.92 | 44270.5002 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.3 | 0:240:120 | 0:00 | 22.0244 | 7 | 52.1529 | 50.9121 | 103.065 | 68.6251 | 24.5739 | 603.8745 | 3 | 22.0244 | 146.5726 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
988 | 4381.008 | 44270.5032 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.7 | 0:240:120 | 0:00 | 19.5926 | 7 | 5.1427 | 45.1737 | 50.3164 | 47.0427 | 2.4353 | 5.9305 | 3 | 19.5926 | 86.2732 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
991 | 4527.08 | 44270.5049 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 20.1 | 0:240:120 | 0:00 | 17.6085 | 7 | 4.5938 | 38.1455 | 42.7393 | 39.7608 | 2.2131 | 4.8979 | 3 | 17.6085 | 60.6973 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
994 | 4652.146 | 44270.5063 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 20.5 | 0:240:120 | 0:00 | 15.9598 | 7 | 5.5276 | 31.0025 | 36.5301 | 33.139 | 2.5503 | 6.5038 | 3 | 15.9598 | 46.5659 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
997 | 4757.74 | 44270.5076 | Vista Speed | T | 8T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 20.9 | 0:240:120 | 0:00 | 14.5688 | 7 | 4.3705 | 25.2166 | 29.5871 | 26.743 | 2.0732 | 4.2983 | 3 | 14.5688 | 37.6078 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1000 | 5278.935 | 44270.5136 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.2 | 0:240:120 | 0:00 | 39.6836 | 7 | 102.5982 | 355.6105 | 458.2087 | 396.8516 | 46.6402 | 2175.3081 | 3 | 39.6836 | Inf | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1003 | 6537.044 | 44270.5282 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.664 | 0:240:120 | 0:00 | 34.0045 | 7 | 113.7066 | 225.4839 | 339.1905 | 274.3622 | 50.1489 | 2514.9166 | 3 | 34.0045 | 272.498 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1006 | 7414.014 | 44270.5383 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.1373 | 0:240:120 | 0:00 | 29.5976 | 7 | 107.1602 | 88.7633 | 195.9235 | 134.8266 | 46.3722 | 2150.3837 | 3 | 29.5976 | 133.3555 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1009 | 7869.477 | 44270.5436 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.62 | 0:240:120 | 0:00 | 26.0811 | 7 | 8.6937 | 55.2639 | 63.9576 | 58.5737 | 3.7067 | 13.7396 | 3 | 26.0811 | 87.0045 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1012 | 8052.859 | 44270.5457 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.1124 | 0:240:120 | 0:00 | 23.2118 | 7 | 6.4717 | 47.3214 | 53.7931 | 50.1364 | 2.8533 | 8.1413 | 3 | 23.2118 | 63.8513 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1015 | 8209.422 | 44270.5475 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.6147 | 0:240:120 | 0:00 | 20.8279 | 7 | 5.934 | 39.9775 | 45.9115 | 42.5013 | 2.5577 | 6.5417 | 3 | 20.8279 | 49.9771 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1018 | 8342.215 | 44270.5491 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.127 | 0:240:120 | 0:00 | 18.8172 | 7 | 6.5949 | 31.5909 | 38.1858 | 34.4415 | 2.8725 | 8.2511 | 3 | 18.8172 | 40.7423 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1021 | 8451.539 | 44270.5503 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.6495 | 0:240:120 | 0:00 | 17.0998 | 7 | 2.6891 | 27.375 | 30.0641 | 28.388 | 1.2279 | 1.5078 | 3 | 17.0998 | 34.1586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1024 | 8541.214 | 44270.5514 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 27.1825 | 0:240:120 | 0:00 | 15.6169 | 7 | 2.301 | 24.3895 | 26.6905 | 25.4197 | 0.9934 | 0.9868 | 3 | 15.6168 | 29.2318 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1027 | 8621.612 | 44270.5523 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 27.7261 | 0:240:120 | 0:00 | 14.3244 | 7 | 2.3123 | 21.6148 | 23.9271 | 22.7102 | 0.9602 | 0.922 | 3 | 14.3244 | 25.4094 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1030 | 8693.79 | 44270.5531 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.2807 | 0:240:120 | 0:00 | 13.1888 | 7 | 2.5227 | 18.7636 | 21.2863 | 19.9294 | 1.0488 | 1.1 | 3 | 13.1888 | 22.3601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1033 | 8757.718 | 44270.5539 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.8463 | 0:240:120 | 0:00 | 12.1839 | 7 | 1.1891 | 17.1742 | 18.3633 | 17.7319 | 0.5052 | 0.2553 | 3 | 12.1839 | 19.8731 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1036 | 8814.5 | 44270.5545 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.4232 | 0:240:120 | 0:00 | 11.289 | 7 | 1.1467 | 15.7441 | 16.8908 | 16.2786 | 0.4867 | 0.2369 | 3 | 11.289 | 17.8076 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1039 | 8866.847 | 44270.5551 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.0117 | 0:240:120 | 0:00 | 10.4876 | 7 | 1.1873 | 14.2961 | 15.4834 | 14.8359 | 0.5037 | 0.2537 | 3 | 10.4876 | 16.0696 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1042 | 8914.924 | 44270.5557 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.6119 | 0:240:120 | 0:00 | 9.7662 | 7 | 1.0875 | 12.9854 | 14.0729 | 13.4307 | 0.4859 | 0.2361 | 3 | 9.7662 | 14.7202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1045 | 8959.005 | 44270.5562 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.2241 | 0:240:120 | 0:00 | 9.114 | 7 | 0.7417 | 12.133 | 12.8747 | 12.4515 | 0.3268 | 0.1068 | 3 | 9.114 | 13.5375 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1048 | 8999.73 | 44270.5567 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.8486 | 0:240:120 | 0:00 | 8.5219 | 7 | 0.7211 | 11.256 | 11.9771 | 11.5979 | 0.3084 | 0.0951 | 3 | 8.5219 | 12.4931 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1051 | 9037.912 | 44270.5571 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.4856 | 0:240:120 | 0:00 | 7.9824 | 7 | 0.6802 | 10.3972 | 11.0774 | 10.702 | 0.2962 | 0.0877 | 3 | 7.9824 | 11.5649 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1054 | 9073.334 | 44270.5575 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.1353 | 0:240:120 | 0:00 | 7.4891 | 7 | 0.4736 | 9.7139 | 10.1875 | 9.9163 | 0.2089 | 0.0437 | 3 | 7.4891 | 10.7351 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1057 | 9106.479 | 44270.5579 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.798 | 0:240:120 | 0:00 | 7.0367 | 7 | 0.4966 | 9.0819 | 9.5785 | 9.288 | 0.2225 | 0.0495 | 3 | 7.0367 | 9.9894 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1060 | 9137.587 | 44270.5583 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.474 | 0:240:120 | 0:00 | 6.6206 | 7 | 0.5106 | 8.4542 | 8.9648 | 8.678 | 0.2226 | 0.0495 | 3 | 6.6206 | 9.3161 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1063 | 9166.849 | 44270.5586 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.1635 | 0:240:120 | 0:00 | 6.2369 | 7 | 0.4033 | 7.9292 | 8.3325 | 8.0914 | 0.1827 | 0.0334 | 3 | 6.2369 | 8.7057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1066 | 9194.467 | 44270.5589 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.8667 | 0:240:120 | 0:00 | 5.8822 | 7 | 0.3783 | 7.4582 | 7.8365 | 7.6197 | 0.1662 | 0.0276 | 3 | 5.8822 | 8.15 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1069 | 9220.805 | 44270.5592 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.5841 | 0:240:120 | 0:00 | 5.5536 | 7 | 0.3854 | 7.0019 | 7.3873 | 7.1673 | 0.1694 | 0.0287 | 3 | 5.5536 | 7.6425 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1072 | 9245.715 | 44270.5595 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.3157 | 0:240:120 | 0:00 | 5.2486 | 7 | 0.3281 | 6.5766 | 6.9047 | 6.6968 | 0.1522 | 0.0232 | 3 | 5.2486 | 7.1776 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1075 | 9269.143 | 44270.5598 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.0621 | 0:240:120 | 0:00 | 4.9648 | 7 | 0.2654 | 6.2273 | 6.4927 | 6.3328 | 0.1207 | 0.0146 | 3 | 4.9648 | 6.7503 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1078 | 9291.466 | 44270.56 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.8233 | 0:240:120 | 0:00 | 4.7005 | 7 | 0.278 | 5.8612 | 6.1392 | 5.9659 | 0.1286 | 0.0166 | 3 | 4.7005 | 6.3566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1081 | 9312.563 | 44270.5603 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.5998 | 0:240:120 | 0:00 | 4.4538 | 7 | 0.2421 | 5.5239 | 5.766 | 5.6222 | 0.1076 | 0.0116 | 3 | 4.4538 | 5.9929 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1084 | 9332.652 | 44270.5605 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.3918 | 0:240:120 | 0:00 | 4.2231 | 7 | 0.2176 | 5.241 | 5.4586 | 5.324 | 0.1011 | 0.0102 | 3 | 4.2231 | 5.6562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1087 | 9351.859 | 44270.5607 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.1996 | 0:240:120 | 0:00 | 4.0072 | 7 | 0.2314 | 4.9421 | 5.1735 | 5.0311 | 0.1071 | 0.0115 | 3 | 4.0072 | 5.3439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1090 | 9370.411 | 44270.561 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.0236 | 0:240:120 | 0:00 | 3.8049 | 7 | 0.1728 | 4.6936 | 4.8664 | 4.756 | 0.0826 | 0.0068 | 3 | 3.8049 | 5.0536 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1093 | 9387.982 | 44270.5612 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.8641 | 0:240:120 | 0:00 | 3.615 | 7 | 0.1721 | 4.4495 | 4.6216 | 4.5147 | 0.08 | 0.0064 | 3 | 3.615 | 4.7832 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1096 | 9404.605 | 44270.5614 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.7213 | 0:240:120 | 0:00 | 3.4365 | 7 | 0.1766 | 4.2121 | 4.3887 | 4.2758 | 0.0835 | 0.007 | 3 | 3.4365 | 4.531 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1099 | 9420.599 | 44270.5615 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.5958 | 0:240:120 | 0:00 | 3.2686 | 7 | 0.1579 | 4.0029 | 4.1608 | 4.0628 | 0.0729 | 0.0053 | 3 | 3.2686 | 4.2954 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1102 | 9436.252 | 44270.5617 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.4877 | 0:240:120 | 0:00 | 3.1105 | 7 | 0.1542 | 3.8003 | 3.9545 | 3.856 | 0.0726 | 0.0053 | 3 | 3.1105 | 4.0749 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1105 | 9451.177 | 44270.5619 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.3974 | 0:240:120 | 0:00 | 2.9615 | 7 | 0.1335 | 3.611 | 3.7445 | 3.661 | 0.0604 | 0.0036 | 3 | 2.9615 | 3.8683 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1108 | 9465.245 | 44270.5621 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.3254 | 0:240:120 | 0:00 | 2.8208 | 7 | 0.1302 | 3.4312 | 3.5614 | 3.4806 | 0.0601 | 0.0036 | 3 | 2.8208 | 3.6745 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1111 | 9478.753 | 44270.5622 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.2719 | 0:240:120 | 0:00 | 2.6881 | 7 | 0.1187 | 3.2652 | 3.3839 | 3.3075 | 0.0567 | 0.0032 | 3 | 2.6881 | 3.4925 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1114 | 9491.949 | 44270.5624 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.2373 | 0:240:120 | 0:00 | 2.5626 | 7 | 0.1073 | 3.1205 | 3.2278 | 3.1581 | 0.051 | 0.0026 | 3 | 2.5626 | 3.3213 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1117 | 9504.602 | 44270.5625 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.2221 | 0:240:120 | 0:00 | 2.4438 | 7 | 0.1096 | 2.9555 | 3.0651 | 2.9944 | 0.0524 | 0.0027 | 3 | 2.4438 | 3.1601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1120 | 9516.624 | 44270.5627 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.2265 | 0:240:120 | 0:00 | 2.3315 | 7 | 0.1034 | 2.8182 | 2.9216 | 2.859 | 0.047 | 0.0022 | 3 | 2.3315 | 3.0083 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1123 | 9528.322 | 44270.5628 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.2511 | 0:240:120 | 0:00 | 2.225 | 7 | 0.0925 | 2.6879 | 2.7804 | 2.7213 | 0.044 | 0.0019 | 3 | 2.225 | 2.865 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1126 | 9539.66 | 44270.5629 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.2961 | 0:240:120 | 0:00 | 2.1241 | 7 | 0.0834 | 2.5645 | 2.6479 | 2.5937 | 0.0402 | 0.0016 | 3 | 2.1241 | 2.7298 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1129 | 9550.764 | 44270.563 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.362 | 0:240:120 | 0:00 | 2.0284 | 7 | 0.0774 | 2.4505 | 2.5279 | 2.4776 | 0.0375 | 0.0014 | 3 | 2.0284 | 2.602 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1132 | 9561.692 | 44270.5632 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.4492 | 0:240:120 | 0:00 | 1.9376 | 7 | 0.0718 | 2.3371 | 2.4089 | 2.3628 | 0.0341 | 0.0012 | 3 | 1.9376 | 2.4812 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1135 | 9571.762 | 44270.5633 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.5582 | 0:240:120 | 0:00 | 1.8514 | 7 | 0.0801 | 2.223 | 2.3031 | 2.2515 | 0.038 | 0.0014 | 3 | 1.8514 | 2.3668 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1138 | 9581.535 | 44270.5634 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.6894 | 0:240:120 | 0:00 | 1.7694 | 7 | 0.0675 | 2.1265 | 2.194 | 2.1504 | 0.0321 | 0.001 | 3 | 1.7694 | 2.2585 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1141 | 9591.18 | 44270.5635 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.8432 | 0:240:120 | 0:00 | 1.6916 | 7 | 0.0677 | 2.0279 | 2.0956 | 2.0539 | 0.0308 | 0.0009 | 3 | 1.6916 | 2.1559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1144 | 9600.312 | 44270.5636 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.02 | 0:240:120 | 0:00 | 1.6175 | 7 | 0.0636 | 1.9371 | 2.0007 | 1.963 | 0.0275 | 0.0008 | 3 | 1.6175 | 2.0586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1147 | 9609.232 | 44270.5637 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.2204 | 0:240:120 | 0:00 | 1.547 | 7 | 0.0651 | 1.8502 | 1.9153 | 1.8739 | 0.0297 | 0.0009 | 3 | 1.547 | 1.9662 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1150 | 9618.044 | 44270.5638 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.4448 | 0:240:120 | 0:00 | 1.4799 | 7 | 0.053 | 1.7725 | 1.8255 | 1.7932 | 0.0239 | 0.0006 | 3 | 1.4799 | 1.8785 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1153 | 9626.661 | 44270.5639 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.6937 | 0:240:120 | 0:00 | 1.416 | 7 | 0.0538 | 1.6917 | 1.7455 | 1.712 | 0.0247 | 0.0006 | 3 | 1.416 | 1.7953 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1156 | 9634.856 | 44270.564 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.9676 | 0:240:120 | 0:00 | 1.3551 | 7 | 0.0505 | 1.6186 | 1.6691 | 1.6375 | 0.0235 | 0.0006 | 3 | 1.3551 | 1.7161 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1159 | 9642.72 | 44270.5641 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.267 | 0:240:120 | 0:00 | 1.2971 | 7 | 0.0474 | 1.5489 | 1.5963 | 1.5668 | 0.0218 | 0.0005 | 3 | 1.2971 | 1.6408 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1162 | 9650.379 | 44270.5642 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.5923 | 0:240:120 | 0:00 | 1.2418 | 7 | 0.0449 | 1.482 | 1.5269 | 1.4984 | 0.0212 | 0.0004 | 3 | 1.2418 | 1.5692 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1165 | 9658.036 | 44270.5643 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.9442 | 0:240:120 | 0:00 | 1.1891 | 7 | 0.0447 | 1.4153 | 1.46 | 1.4339 | 0.0195 | 0.0004 | 3 | 1.1891 | 1.501 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1168 | 9665.444 | 44270.5644 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.323 | 0:240:120 | 0:00 | 1.1387 | 7 | 0.0427 | 1.3551 | 1.3978 | 1.3714 | 0.0186 | 0.0003 | 3 | 1.1387 | 1.4362 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1171 | 9673.082 | 44270.5645 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.7295 | 0:240:120 | 0:00 | 1.0907 | 7 | 0.0366 | 1.2995 | 1.3361 | 1.3122 | 0.0175 | 0.0003 | 3 | 1.0907 | 1.3743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1174 | 9680.311 | 44270.5645 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.1641 | 0:240:120 | 0:00 | 1.0449 | 7 | 0.0337 | 1.2451 | 1.2788 | 1.2569 | 0.0162 | 0.0003 | 3 | 1.0449 | 1.3154 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1177 | 9687.268 | 44270.5646 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.6274 | 0:240:120 | 0:00 | 1.0011 | 7 | 0.0348 | 1.1907 | 1.2255 | 1.2033 | 0.0165 | 0.0003 | 3 | 1.0011 | 1.2593 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1180 | 9694.12 | 44270.5647 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.1199 | 0:240:120 | 0:00 | 0.9593 | 7 | 0.0316 | 1.1411 | 1.1727 | 1.1525 | 0.015 | 0.0002 | 3 | 0.9593 | 1.2057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1183 | 9700.628 | 44270.5648 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.6423 | 0:240:120 | 0:00 | 0.9193 | 7 | 0.0313 | 1.0927 | 1.124 | 1.104 | 0.0144 | 0.0002 | 3 | 0.9193 | 1.1546 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1186 | 9707.05 | 44270.5649 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.1952 | 0:240:120 | 0:00 | 0.8811 | 7 | 0.0296 | 1.0465 | 1.0761 | 1.0571 | 0.0139 | 0.0002 | 3 | 0.8811 | 1.1059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1189 | 9713.269 | 44270.5649 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.7791 | 0:240:120 | 0:00 | 0.8446 | 7 | 0.0284 | 1.003 | 1.0314 | 1.0127 | 0.0138 | 0.0002 | 3 | 0.8446 | 1.0593 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1192 | 9719.49 | 44270.565 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.3946 | 0:240:120 | 0:00 | 0.8097 | 7 | 0.0261 | 0.9625 | 0.9886 | 0.9717 | 0.0123 | 0.0002 | 3 | 0.8097 | 1.0149 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1195 | 9725.428 | 44270.5651 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.0425 | 0:240:120 | 0:00 | 0.7764 | 7 | 0.0244 | 0.9213 | 0.9457 | 0.9302 | 0.0114 | 0.0001 | 3 | 0.7764 | 0.9725 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1198 | 9731.55 | 44270.5651 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.7234 | 0:240:120 | 0:00 | 0.7444 | 7 | 0.0246 | 0.8834 | 0.908 | 0.8918 | 0.0117 | 0.0001 | 3 | 0.7444 | 0.9319 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1201 | 9737.345 | 44270.5652 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.4379 | 0:240:120 | 0:00 | 0.7139 | 7 | 0.0239 | 0.8462 | 0.8701 | 0.8544 | 0.0114 | 0.0001 | 3 | 0.7139 | 0.8932 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1204 | 9742.999 | 44270.5653 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.1866 | 0:240:120 | 0:00 | 0.6847 | 7 | 0.0221 | 0.8115 | 0.8336 | 0.8192 | 0.0106 | 0.0001 | 3 | 0.6847 | 0.8562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1207 | 9748.539 | 44270.5653 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.9703 | 0:240:120 | 0:00 | 0.6567 | 7 | 0.0212 | 0.7779 | 0.7991 | 0.7851 | 0.0101 | 0.0001 | 3 | 0.6567 | 0.8208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1210 | 9753.813 | 44270.5654 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.7898 | 0:240:120 | 0:00 | 0.63 | 7 | 0.0188 | 0.747 | 0.7658 | 0.7535 | 0.0087 | 0.0001 | 3 | 0.63 | 0.7869 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1213 | 9759.166 | 44270.5655 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.6455 | 0:240:120 | 0:00 | 0.6043 | 7 | 0.0192 | 0.7158 | 0.735 | 0.7227 | 0.0091 | 0.0001 | 3 | 0.6043 | 0.7545 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1216 | 9764.42 | 44270.5655 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.5385 | 0:240:120 | 0:00 | 0.5798 | 7 | 0.0188 | 0.6864 | 0.7052 | 0.6928 | 0.009 | 0.0001 | 3 | 0.5798 | 0.7236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1219 | 9769.611 | 44270.5656 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.4692 | 0:240:120 | 0:00 | 0.5563 | 7 | 0.0172 | 0.6589 | 0.6761 | 0.6647 | 0.0081 | 0.0001 | 3 | 0.5563 | 0.6939 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1222 | 9774.757 | 44270.5656 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.4386 | 0:240:120 | 0:00 | 0.5338 | 7 | 0.0176 | 0.6308 | 0.6484 | 0.6373 | 0.0079 | 0.0001 | 3 | 0.5338 | 0.6656 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1225 | 9779.759 | 44270.5657 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.4474 | 0:240:120 | 0:00 | 0.5122 | 7 | 0.0158 | 0.6063 | 0.6221 | 0.6116 | 0.0075 | 0.0001 | 3 | 0.5122 | 0.6384 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1228 | 9785.015 | 44270.5658 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.4963 | 0:240:120 | 0:00 | 0.4915 | 7 | 0.0149 | 0.5816 | 0.5965 | 0.5871 | 0.0069 | 0 | 3 | 0.4915 | 0.6124 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1231 | 9789.845 | 44270.5658 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.5863 | 0:240:120 | 0:00 | 0.4717 | 7 | 0.0159 | 0.5574 | 0.5733 | 0.5635 | 0.0068 | 0 | 3 | 0.4717 | 0.5875 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1234 | 9794.681 | 44270.5659 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 108.718 | 0:240:120 | 0:00 | 0.4528 | 7 | 0.013 | 0.5359 | 0.5489 | 0.5406 | 0.0059 | 0 | 3 | 0.4528 | 0.5637 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1237 | 9799.514 | 44270.5659 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.8923 | 0:240:120 | 0:00 | 0.4346 | 7 | 0.0138 | 0.5137 | 0.5275 | 0.5188 | 0.006 | 0 | 3 | 0.4346 | 0.5409 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1240 | 9804.299 | 44270.566 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.1102 | 0:240:120 | 0:00 | 0.4172 | 7 | 0.0129 | 0.4927 | 0.5056 | 0.4973 | 0.0057 | 0 | 3 | 0.4172 | 0.519 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1243 | 9808.884 | 44270.566 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 115.3724 | 0:240:120 | 0:00 | 0.4004 | 7 | 0.0125 | 0.473 | 0.4855 | 0.4779 | 0.0055 | 0 | 3 | 0.4004 | 0.4981 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1246 | 9813.528 | 44270.5661 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.6798 | 0:240:120 | 0:00 | 0.3844 | 7 | 0.0114 | 0.4545 | 0.4659 | 0.4587 | 0.0053 | 0 | 3 | 0.3844 | 0.478 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1249 | 9817.973 | 44270.5661 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.0334 | 0:240:120 | 0:00 | 0.3691 | 7 | 0.0114 | 0.4359 | 0.4473 | 0.4401 | 0.0053 | 0 | 3 | 0.3691 | 0.4588 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1252 | 9822.194 | 44270.5662 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 122.4341 | 0:240:120 | 0:00 | 0.3543 | 7 | 0.0115 | 0.4184 | 0.4299 | 0.423 | 0.0051 | 0 | 3 | 0.3543 | 0.4403 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1255 | 9826.553 | 44270.5662 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.8828 | 0:240:120 | 0:00 | 0.3402 | 7 | 0.0113 | 0.4009 | 0.4122 | 0.4052 | 0.0048 | 0 | 3 | 0.3402 | 0.4227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1258 | 9831.09 | 44270.5663 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 127.3804 | 0:240:120 | 0:00 | 0.3266 | 7 | 0.0095 | 0.3858 | 0.3953 | 0.3895 | 0.0041 | 0 | 3 | 0.3266 | 0.4057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1261 | 9835.502 | 44270.5663 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 129.9281 | 0:240:120 | 0:00 | 0.3136 | 7 | 0.0089 | 0.3709 | 0.3798 | 0.3742 | 0.004 | 0 | 3 | 0.3136 | 0.3895 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1264 | 9839.549 | 44270.5664 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 132.5266 | 0:240:120 | 0:00 | 0.3012 | 7 | 0.0093 | 0.3557 | 0.365 | 0.3594 | 0.004 | 0 | 3 | 0.3012 | 0.3739 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1267 | 9843.768 | 44270.5664 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 135.1771 | 0:240:120 | 0:00 | 0.2892 | 7 | 0.0092 | 0.3411 | 0.3503 | 0.3449 | 0.0039 | 0 | 3 | 0.2892 | 0.359 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1270 | 9848.123 | 44270.5665 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.8807 | 0:240:120 | 0:00 | 0.2777 | 7 | 0.0077 | 0.3286 | 0.3363 | 0.3314 | 0.0034 | 0 | 3 | 0.2777 | 0.3447 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1273 | 9852.239 | 44270.5665 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 140.6383 | 0:240:120 | 0:00 | 0.2667 | 7 | 0.0079 | 0.3148 | 0.3227 | 0.3178 | 0.0035 | 0 | 3 | 0.2667 | 0.3309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1276 | 9856.348 | 44270.5666 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 143.4511 | 0:240:120 | 0:00 | 0.2562 | 7 | 0.0065 | 0.303 | 0.3095 | 0.3057 | 0.0028 | 0 | 3 | 0.2562 | 0.3178 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1279 | 9860.319 | 44270.5666 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 146.3201 | 0:240:120 | 0:00 | 0.246 | 7 | 0.0076 | 0.2911 | 0.2987 | 0.294 | 0.0034 | 0 | 3 | 0.246 | 0.3051 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1282 | 9864.646 | 44270.5667 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 149.2465 | 0:240:120 | 0:00 | 0.2363 | 7 | 0.0079 | 0.2791 | 0.287 | 0.2825 | 0.0033 | 0 | 3 | 0.2363 | 0.293 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1285 | 9868.383 | 44270.5667 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 152.2314 | 0:240:120 | 0:00 | 0.2269 | 7 | 0.0064 | 0.2686 | 0.275 | 0.271 | 0.0028 | 0 | 3 | 0.2269 | 0.2814 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1288 | 9872.486 | 44270.5668 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 155.276 | 0:240:120 | 0:00 | 0.218 | 7 | 0.0066 | 0.2574 | 0.264 | 0.2599 | 0.003 | 0 | 3 | 0.218 | 0.2702 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1291 | 9876.492 | 44270.5668 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 158.3816 | 0:240:120 | 0:00 | 0.2094 | 7 | 0.0056 | 0.2476 | 0.2532 | 0.2499 | 0.0023 | 0 | 3 | 0.2094 | 0.2595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1294 | 9880.289 | 44270.5669 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 161.5492 | 0:240:120 | 0:00 | 0.2011 | 7 | 0.006 | 0.2374 | 0.2434 | 0.2402 | 0.0023 | 0 | 3 | 0.2011 | 0.2492 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1297 | 9884.035 | 44270.5669 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.7802 | 0:240:120 | 0:00 | 0.1932 | 7 | 0.0062 | 0.2279 | 0.2341 | 0.2305 | 0.0026 | 0 | 3 | 0.1932 | 0.2394 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1300 | 9887.797 | 44270.5669 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 168.0758 | 0:240:120 | 0:00 | 0.1856 | 7 | 0.005 | 0.219 | 0.224 | 0.2212 | 0.002 | 0 | 3 | 0.1856 | 0.2299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1303 | 9891.585 | 44270.567 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 171.4373 | 0:240:120 | 0:00 | 0.1783 | 7 | 0.0062 | 0.2103 | 0.2165 | 0.213 | 0.0022 | 0 | 3 | 0.1783 | 0.2208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1306 | 9895.149 | 44270.567 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 174.8661 | 0:240:120 | 0:00 | 0.1713 | 7 | 0.0047 | 0.2019 | 0.2066 | 0.204 | 0.0018 | 0 | 3 | 0.1713 | 0.2121 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1309 | 9898.567 | 44270.5671 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 178.3634 | 0:240:120 | 0:00 | 0.1645 | 7 | 0.0054 | 0.194 | 0.1994 | 0.1962 | 0.0022 | 0 | 3 | 0.1645 | 0.2037 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1312 | 9902.213 | 44270.5671 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 181.9306 | 0:240:120 | 0:00 | 0.1581 | 7 | 0.004 | 0.1871 | 0.1911 | 0.189 | 0.0014 | 0 | 3 | 0.1581 | 0.1957 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1315 | 9905.711 | 44270.5672 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 185.5693 | 0:240:120 | 0:00 | 0.1518 | 7 | 0.0052 | 0.1789 | 0.1841 | 0.1816 | 0.0018 | 0 | 3 | 0.1518 | 0.188 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1318 | 9909.336 | 44270.5672 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 189.2806 | 0:240:120 | 0:00 | 0.1459 | 7 | 0.0038 | 0.1728 | 0.1766 | 0.1751 | 0.0014 | 0 | 3 | 0.1459 | 0.1806 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1321 | 9913.323 | 44270.5672 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 193.0663 | 0:240:120 | 0:00 | 0.1401 | 7 | 0.005 | 0.1652 | 0.1702 | 0.1679 | 0.0017 | 0 | 3 | 0.1401 | 0.1735 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1324 | 9916.906 | 44270.5673 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 196.9276 | 0:240:120 | 0:00 | 0.1346 | 7 | 0.0046 | 0.159 | 0.1636 | 0.161 | 0.0017 | 0 | 3 | 0.1346 | 0.1666 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1327 | 9920.469 | 44270.5673 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 200.8661 | 0:240:120 | 0:00 | 0.1294 | 7 | 0.005 | 0.152 | 0.157 | 0.1545 | 0.0018 | 0 | 3 | 0.1294 | 0.1601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1330 | 9923.941 | 44270.5674 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 204.8835 | 0:240:120 | 0:00 | 0.1243 | 7 | 0.0033 | 0.1467 | 0.15 | 0.1485 | 0.0011 | 0 | 3 | 0.1243 | 0.1538 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1333 | 9927.384 | 44270.5674 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.9811 | 0:240:120 | 0:00 | 0.1194 | 7 | 0.0042 | 0.1407 | 0.1449 | 0.1432 | 0.0015 | 0 | 3 | 0.1194 | 0.1478 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1336 | 9931.157 | 44270.5674 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 213.1607 | 0:240:120 | 0:00 | 0.1147 | 7 | 0.0038 | 0.1349 | 0.1387 | 0.137 | 0.0015 | 0 | 3 | 0.1147 | 0.142 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1339 | 9934.694 | 44270.5675 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 217.424 | 0:240:120 | 0:00 | 0.1102 | 7 | 0.0042 | 0.13 | 0.1342 | 0.1322 | 0.0016 | 0 | 3 | 0.1102 | 0.1364 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1342 | 9938.33 | 44270.5675 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 221.7724 | 0:240:120 | 0:00 | 0.1059 | 7 | 0.0037 | 0.1246 | 0.1283 | 0.1265 | 0.0012 | 0 | 3 | 0.1059 | 0.131 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1345 | 9941.731 | 44270.5676 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 226.2079 | 0:240:120 | 0:00 | 0.1018 | 7 | 0.0047 | 0.1189 | 0.1236 | 0.1216 | 0.0015 | 0 | 3 | 0.1018 | 0.1259 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1348 | 9945.124 | 44270.5676 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 230.732 | 0:240:120 | 0:00 | 0.0978 | 7 | 0.004 | 0.1152 | 0.1192 | 0.1172 | 0.0014 | 0 | 3 | 0.0978 | 0.121 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1351 | 9948.782 | 44270.5677 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 235.3467 | 0:240:120 | 0:00 | 0.094 | 7 | 0.0028 | 0.111 | 0.1138 | 0.1129 | 0.0011 | 0 | 3 | 0.094 | 0.1162 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1354 | 9952.171 | 44270.5677 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 240.0536 | 0:240:120 | 0:00 | 0.0903 | 7 | 0.0041 | 0.1058 | 0.1099 | 0.1079 | 0.0014 | 0 | 3 | 0.0903 | 0.1117 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1357 | 9955.707 | 44270.5677 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 244.8547 | 0:240:120 | 0:00 | 0.0868 | 7 | 0.0035 | 0.1024 | 0.1059 | 0.1047 | 0.0012 | 0 | 3 | 0.0868 | 0.1073 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1360 | 9959.089 | 44270.5678 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 249.7518 | 0:240:120 | 0:00 | 0.0834 | 7 | 0.0027 | 0.0985 | 0.1012 | 0.1002 | 0.0011 | 0 | 3 | 0.0834 | 0.1031 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1363 | 9962.551 | 44270.5678 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 254.7468 | 0:240:120 | 0:00 | 0.0801 | 7 | 0.0028 | 0.0944 | 0.0972 | 0.096 | 0.0012 | 0 | 3 | 0.0801 | 0.0991 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1366 | 9966.319 | 44270.5679 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 259.8418 | 0:240:120 | 0:00 | 0.077 | 7 | 0.0032 | 0.0911 | 0.0943 | 0.093 | 0.0012 | 0 | 3 | 0.077 | 0.0952 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1369 | 9969.976 | 44270.5679 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 265.0386 | 0:240:120 | 0:00 | 0.074 | 7 | 0.0013 | 0.0883 | 0.0896 | 0.0891 | 0.0005 | 0 | 3 | 0.074 | 0.0915 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1372 | 9973.526 | 44270.5679 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 270.3394 | 0:240:120 | 0:00 | 0.0711 | 7 | 0.002 | 0.084 | 0.086 | 0.0851 | 0.0007 | 0 | 3 | 0.0711 | 0.0879 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1375 | 9976.904 | 44270.568 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 275.7461 | 0:240:120 | 0:00 | 0.0683 | 7 | 0.0036 | 0.0805 | 0.0841 | 0.0826 | 0.0013 | 0 | 3 | 0.0683 | 0.0845 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1378 | 9980.38 | 44270.568 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 281.2611 | 0:240:120 | 0:00 | 0.0657 | 7 | 0.0027 | 0.078 | 0.0807 | 0.0796 | 0.001 | 0 | 3 | 0.0657 | 0.0812 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1381 | 9983.788 | 44270.5681 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 286.8863 | 0:240:120 | 0:00 | 0.0631 | 7 | 0.0031 | 0.074 | 0.0771 | 0.076 | 0.0013 | 0 | 3 | 0.0631 | 0.078 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1384 | 9987.171 | 44270.5681 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 292.624 | 0:240:120 | 0:00 | 0.0606 | 7 | 0.0037 | 0.0708 | 0.0745 | 0.0731 | 0.0015 | 0 | 3 | 0.0606 | 0.0749 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1387 | 9990.605 | 44270.5681 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 298.4765 | 0:240:120 | 0:00 | 0.0583 | 7 | 0.003 | 0.0687 | 0.0717 | 0.0706 | 0.0011 | 0 | 3 | 0.0583 | 0.072 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1390 | 9994.02 | 44270.5682 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 304.446 | 0:240:120 | 0:00 | 0.056 | 7 | 0.0023 | 0.0666 | 0.0689 | 0.068 | 0.0011 | 0 | 3 | 0.056 | 0.0692 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1393 | 9997.427 | 44270.5682 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 310.5349 | 0:240:120 | 0:00 | 0.0538 | 7 | 0.004 | 0.0626 | 0.0666 | 0.0652 | 0.0016 | 0 | 3 | 0.0538 | 0.0665 | P | NP | 1-1-1-0-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1396 | 10001.01 | 44270.5683 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 316.7456 | 0:240:120 | 0:00 | 0.0517 | 7 | 0.0026 | 0.0608 | 0.0634 | 0.0627 | 0.0009 | 0 | 3 | 0.0517 | 0.0639 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1399 | 10004.646 | 44270.5683 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 323.0806 | 0:240:120 | 0:00 | 0.0497 | 7 | 0.0032 | 0.0586 | 0.0618 | 0.0606 | 0.0011 | 0 | 3 | 0.0497 | 0.0614 | P | NP | 1-1-1-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1402 | 10008.057 | 44270.5683 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 329.5422 | 0:240:120 | 0:00 | 0.0478 | 7 | 0.003 | 0.0562 | 0.0592 | 0.0581 | 0.0013 | 0 | 3 | 0.0478 | 0.059 | P | NP | 0-1-0-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1405 | 10011.342 | 44270.5684 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 336.133 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0022 | 0.0541 | 0.0563 | 0.0555 | 0.0008 | 0 | 3 | 0.0459 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1408 | 10014.735 | 44270.5684 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 342.8557 | 0:240:120 | 0:00 | 0.0441 | 7 | 0.0031 | 0.0516 | 0.0547 | 0.0536 | 0.0014 | 0 | 3 | 0.0441 | 0.0545 | P | NP | 1-1-1-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1411 | 10017.962 | 44270.5685 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 349.7128 | 0:240:120 | 0:00 | 0.0424 | 7 | 0.0014 | 0.0512 | 0.0526 | 0.052 | 0.0006 | 0 | 3 | 0.0424 | 0.0524 | P | NP | 1-1-1-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
1414 | 10021.565 | 44270.5685 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 356.707 | 0:240:120 | 0:00 | 0.0407 | 7 | 0.0033 | 0.0473 | 0.0506 | 0.0494 | 0.0012 | 0 | 3 | 0.0407 | 0.0507 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1417 | 10024.884 | 44270.5685 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 363.8412 | 0:240:120 | 0:00 | 0.0392 | 7 | 0.0028 | 0.0462 | 0.049 | 0.0479 | 0.001 | 0 | 3 | 0.0392 | 0.0492 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1420 | 10028.201 | 44270.5686 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 371.118 | 0:240:120 | 0:00 | 0.0376 | 7 | 0.003 | 0.0443 | 0.0473 | 0.0459 | 0.0011 | 0 | 3 | 0.0376 | 0.0476 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1423 | 10031.404 | 44270.5686 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 378.5404 | 0:240:120 | 0:00 | 0.0362 | 7 | 0.0027 | 0.0429 | 0.0456 | 0.0444 | 0.0008 | 0 | 3 | 0.0362 | 0.0462 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1426 | 10034.441 | 44270.5686 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 386.1112 | 0:240:120 | 0:00 | 0.0348 | 7 | 0.0037 | 0.0407 | 0.0444 | 0.0427 | 0.0013 | 0 | 3 | 0.0348 | 0.0448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1429 | 10037.793 | 44270.5687 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 393.8334 | 0:240:120 | 0:00 | 0.0334 | 7 | 0.0028 | 0.0399 | 0.0427 | 0.0412 | 0.001 | 0 | 3 | 0.0334 | 0.0434 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1432 | 10041.074 | 44270.5687 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 401.7101 | 0:240:120 | 0:00 | 0.0321 | 7 | 0.0033 | 0.0379 | 0.0412 | 0.0398 | 0.0012 | 0 | 3 | 0.0321 | 0.0421 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1435 | 10044.47 | 44270.5688 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 409.7443 | 0:240:120 | 0:00 | 0.0308 | 7 | 0.0033 | 0.0365 | 0.0398 | 0.0385 | 0.0012 | 0 | 3 | 0.0308 | 0.0408 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1438 | 10047.669 | 44270.5688 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 417.9392 | 0:240:120 | 0:00 | 0.0296 | 7 | 0.0024 | 0.0358 | 0.0382 | 0.0371 | 0.0008 | 0 | 3 | 0.0296 | 0.0396 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1441 | 10050.737 | 44270.5688 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 426.2979 | 0:240:120 | 0:00 | 0.0285 | 7 | 0.0033 | 0.033 | 0.0363 | 0.0352 | 0.0012 | 0 | 3 | 0.0285 | 0.0385 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1444 | 10053.862 | 44270.5689 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 434.8239 | 0:240:120 | 0:00 | 0.0274 | 7 | 0.0037 | 0.0322 | 0.0359 | 0.0341 | 0.0013 | 0 | 3 | 0.0274 | 0.0374 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1447 | 10057.406 | 44270.5689 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 443.5204 | 0:240:120 | 0:00 | 0.0263 | 7 | 0.0034 | 0.0313 | 0.0347 | 0.0336 | 0.0013 | 0 | 3 | 0.0263 | 0.0363 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1450 | 10060.667 | 44270.5689 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 452.3908 | 0:240:120 | 0:00 | 0.0253 | 7 | 0.0028 | 0.0305 | 0.0333 | 0.0319 | 0.0011 | 0 | 3 | 0.0253 | 0.0353 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1453 | 10063.835 | 44270.569 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 461.4386 | 0:240:120 | 0:00 | 0.0243 | 7 | 0.0025 | 0.0292 | 0.0317 | 0.0307 | 0.001 | 0 | 3 | 0.0243 | 0.0343 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1456 | 10067.375 | 44270.569 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 470.6674 | 0:240:120 | 0:00 | 0.0234 | 7 | 0.0032 | 0.0277 | 0.0309 | 0.0296 | 0.0012 | 0 | 3 | 0.0234 | 0.0334 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1459 | 10070.681 | 44270.5691 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 480.0807 | 0:240:120 | 0:00 | 0.0225 | 7 | 0.0026 | 0.0273 | 0.0299 | 0.0289 | 0.001 | 0 | 3 | 0.0225 | 0.0325 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1462 | 10074.186 | 44270.5691 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 489.6823 | 0:240:120 | 0:00 | 0.0216 | 7 | 0.0029 | 0.0258 | 0.0287 | 0.028 | 0.001 | 0 | 3 | 0.0216 | 0.0316 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1465 | 10077.638 | 44270.5691 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 499.476 | 0:240:120 | 0:00 | 0.0207 | 7 | 0.0028 | 0.0253 | 0.0281 | 0.0269 | 0.001 | 0 | 3 | 0.0207 | 0.0307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1468 | 10080.882 | 44270.5692 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 509.4655 | 0:240:120 | 0:00 | 0.0199 | 7 | 0.0036 | 0.024 | 0.0276 | 0.026 | 0.0014 | 0 | 3 | 0.0199 | 0.0299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1471 | 10084.116 | 44270.5692 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 519.6548 | 0:240:120 | 0:00 | 0.0192 | 7 | 0.0027 | 0.0242 | 0.0269 | 0.0254 | 0.001 | 0 | 3 | 0.0192 | 0.0292 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1474 | 10087.302 | 44270.5693 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 530.0479 | 0:240:120 | 0:00 | 0.0184 | 7 | 0.0037 | 0.0223 | 0.026 | 0.0245 | 0.0013 | 0 | 3 | 0.0184 | 0.0284 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1477 | 10090.485 | 44270.5693 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 540.6489 | 0:240:120 | 0:00 | 0.0177 | 7 | 0.0037 | 0.022 | 0.0257 | 0.0239 | 0.0012 | 0 | 3 | 0.0177 | 0.0277 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1480 | 10093.603 | 44270.5693 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 551.4618 | 0:240:120 | 0:00 | 0.017 | 7 | 0.0037 | 0.0213 | 0.025 | 0.0233 | 0.0011 | 0 | 3 | 0.017 | 0.027 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1483 | 10096.813 | 44270.5694 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 562.4911 | 0:240:120 | 0:00 | 0.0164 | 7 | 0.0039 | 0.0207 | 0.0246 | 0.0228 | 0.0015 | 0 | 3 | 0.0164 | 0.0264 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1486 | 10100.074 | 44270.5694 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 573.7409 | 0:240:120 | 0:00 | 0.0157 | 7 | 0.0033 | 0.0199 | 0.0232 | 0.022 | 0.0011 | 0 | 3 | 0.0157 | 0.0257 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1489 | 10103.144 | 44270.5694 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 585.2157 | 0:240:120 | 0:00 | 0.0151 | 7 | 0.0036 | 0.02 | 0.0236 | 0.0219 | 0.0012 | 0 | 3 | 0.0151 | 0.0251 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1492 | 10106.253 | 44270.5695 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 596.92 | 0:240:120 | 0:00 | 0.0145 | 7 | 0.0038 | 0.0189 | 0.0227 | 0.021 | 0.0014 | 0 | 3 | 0.0145 | 0.0245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1495 | 10109.454 | 44270.5695 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 608.8584 | 0:240:120 | 0:00 | 0.014 | 7 | 0.0041 | 0.0186 | 0.0227 | 0.0208 | 0.0014 | 0 | 3 | 0.014 | 0.024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1498 | 10112.646 | 44270.5695 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 621.0356 | 0:240:120 | 0:00 | 0.0134 | 7 | 0.0039 | 0.0182 | 0.0221 | 0.0204 | 0.0013 | 0 | 3 | 0.0134 | 0.0234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1501 | 10115.835 | 44270.5696 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 633.4563 | 0:240:120 | 0:00 | 0.0129 | 7 | 0.0034 | 0.0179 | 0.0213 | 0.0198 | 0.0011 | 0 | 3 | 0.0129 | 0.0229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1504 | 10118.943 | 44270.5696 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 646.1254 | 0:240:120 | 0:00 | 0.0124 | 7 | 0.0021 | 0.0185 | 0.0206 | 0.0195 | 0.0008 | 0 | 3 | 0.0124 | 0.0224 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1507 | 10122.138 | 44270.5697 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 659.0479 | 0:240:120 | 0:00 | 0.0119 | 7 | 0.0016 | 0.0185 | 0.0201 | 0.0195 | 0.0005 | 0 | 3 | 0.0119 | 0.0219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1510 | 10125.221 | 44270.5697 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 672.2289 | 0:240:120 | 0:00 | 0.0114 | 7 | 0.002 | 0.0178 | 0.0198 | 0.0187 | 0.0008 | 0 | 3 | 0.0114 | 0.0214 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1513 | 10128.312 | 44270.5697 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 685.6735 | 0:240:120 | 0:00 | 0.011 | 7 | 0.0022 | 0.0174 | 0.0196 | 0.0182 | 0.0007 | 0 | 3 | 0.011 | 0.021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1516 | 10131.66 | 44270.5698 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 699.387 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0014 | 0.0171 | 0.0185 | 0.018 | 0.0006 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1519 | 10134.843 | 44270.5698 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 713.3747 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.001 | 0.0168 | 0.0178 | 0.0176 | 0.0003 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1522 | 10138.181 | 44270.5698 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 719.0888 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0004 | 0.0174 | 0.0178 | 0.0175 | 0.0002 | 0 | 3 | 0.01 | 0.02 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1525 | 10141.284 | 44270.5699 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 733.4706 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0025 | 0.0157 | 0.0182 | 0.0171 | 0.0009 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-1-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1528 | 10144.475 | 44270.5699 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 748.14 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0022 | 0.0159 | 0.0181 | 0.0167 | 0.0008 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 0-0-0-1-1-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
1531 | 10147.678 | 44270.57 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 763.1028 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0025 | 0.0153 | 0.0178 | 0.0166 | 0.0008 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 0-0-0-0-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
1534 | 10150.874 | 44270.57 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 778.3648 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.003 | 0.0147 | 0.0177 | 0.0158 | 0.001 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-1-1-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
1537 | 10153.963 | 44270.57 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 793.9321 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0035 | 0.0136 | 0.0171 | 0.0153 | 0.0013 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1540 | 10157.103 | 44270.5701 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 809.8108 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.002 | 0.015 | 0.017 | 0.0156 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1543 | 10160.291 | 44270.5701 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 826.007 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0033 | 0.0132 | 0.0165 | 0.0149 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1546 | 10163.408 | 44270.5701 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 842.5271 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0043 | 0.0123 | 0.0166 | 0.0149 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1549 | 10166.531 | 44270.5702 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 859.3777 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0047 | 0.0121 | 0.0168 | 0.0146 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1552 | 10169.724 | 44270.5702 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 876.5652 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0052 | 0.0122 | 0.0174 | 0.0145 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1555 | 10173.043 | 44270.5702 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 894.0965 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0044 | 0.0123 | 0.0167 | 0.0144 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1558 | 10176.45 | 44270.5703 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 911.9785 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0041 | 0.0119 | 0.016 | 0.0143 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1561 | 10179.863 | 44270.5703 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 930.218 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0047 | 0.0115 | 0.0162 | 0.0142 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
1564 | 10183.142 | 44270.5704 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 948.8224 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0042 | 0.0118 | 0.016 | 0.0139 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1567 | 10186.442 | 44270.5704 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 967.7988 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0053 | 0.0118 | 0.0171 | 0.014 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1570 | 10189.813 | 44270.5704 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 987.1548 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0046 | 0.0114 | 0.016 | 0.0138 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1573 | 10192.883 | 44270.5705 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1006.8979 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0045 | 0.0114 | 0.0159 | 0.0138 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1576 | 10196.087 | 44270.5705 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1027.0359 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0038 | 0.012 | 0.0158 | 0.0137 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1579 | 10199.19 | 44270.5706 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1047.5766 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0041 | 0.0114 | 0.0155 | 0.0134 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1582 | 10202.377 | 44270.5706 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1068.5281 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0045 | 0.0108 | 0.0153 | 0.0132 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1585 | 10205.542 | 44270.5706 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1089.8987 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.004 | 0.0113 | 0.0153 | 0.0135 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1588 | 10208.86 | 44270.5707 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1111.6967 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0048 | 0.0104 | 0.0152 | 0.0129 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1591 | 10212.058 | 44270.5707 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1133.9306 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0048 | 0.0105 | 0.0153 | 0.0129 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1594 | 10215.152 | 44270.5707 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1156.6092 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0055 | 0.0104 | 0.0159 | 0.0131 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1597 | 10218.35 | 44270.5708 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1179.7414 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0046 | 0.0107 | 0.0153 | 0.013 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1600 | 10221.444 | 44270.5708 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1203.3362 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0045 | 0.0105 | 0.015 | 0.0125 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1603 | 10224.606 | 44270.5708 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1227.4029 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0036 | 0.0111 | 0.0147 | 0.0127 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1606 | 10227.818 | 44270.5709 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1251.951 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0029 | 0.0107 | 0.0136 | 0.0122 | 0.0009 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1609 | 10231.087 | 44270.5709 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1276.99 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0034 | 0.0101 | 0.0135 | 0.0118 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1612 | 10234.406 | 44270.571 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1302.5298 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0037 | 0.0102 | 0.0139 | 0.0115 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1615 | 10237.595 | 44270.571 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1328.5804 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0027 | 0.0104 | 0.0131 | 0.0114 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1618 | 10240.691 | 44270.571 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1355.152 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0044 | 0.0092 | 0.0136 | 0.0113 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1621 | 10243.98 | 44270.5711 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1382.2551 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0035 | 0.009 | 0.0125 | 0.0108 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1624 | 10247.122 | 44270.5711 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1409.9002 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0036 | 0.0093 | 0.0129 | 0.0109 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1627 | 10250.533 | 44270.5711 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1438.0982 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0041 | 0.009 | 0.0131 | 0.0107 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1630 | 10253.654 | 44270.5712 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1438.1776 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0022 | 0.01 | 0.0122 | 0.0112 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1633 | 10256.949 | 44270.5712 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1466.9411 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0024 | 0.0098 | 0.0122 | 0.0107 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1636 | 10260.412 | 44270.5713 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1496.28 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0016 | 0.0104 | 0.012 | 0.011 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1639 | 10263.85 | 44270.5713 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1526.2056 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0028 | 0.0092 | 0.012 | 0.0105 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1642 | 10267.06 | 44270.5713 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1556.7297 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0032 | 0.0093 | 0.0125 | 0.0108 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1645 | 10270.327 | 44270.5714 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1587.8643 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0021 | 0.0101 | 0.0122 | 0.0109 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1648 | 10273.492 | 44270.5714 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1619.6215 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0041 | 0.009 | 0.0131 | 0.0108 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1651 | 10276.738 | 44270.5714 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1652.014 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0041 | 0.0089 | 0.013 | 0.0105 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1654 | 10279.98 | 44270.5715 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1685.0543 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0012 | 0.0103 | 0.0115 | 0.0107 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1657 | 10283.172 | 44270.5715 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1718.7553 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0025 | 0.0098 | 0.0123 | 0.0107 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1660 | 10286.372 | 44270.5716 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1753.1304 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0035 | 0.0091 | 0.0126 | 0.0106 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1663 | 10289.458 | 44270.5716 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1788.1931 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0029 | 0.009 | 0.0119 | 0.0106 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1666 | 10292.67 | 44270.5716 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1823.9569 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.002 | 0.0099 | 0.0119 | 0.0107 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1669 | 10295.966 | 44270.5717 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1860.4361 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0029 | 0.009 | 0.0119 | 0.0102 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1672 | 10299.172 | 44270.5717 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1897.6448 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0022 | 0.009 | 0.0112 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1675 | 10302.372 | 44270.5717 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1935.5977 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0024 | 0.0089 | 0.0113 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1678 | 10305.554 | 44270.5718 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1974.3096 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0019 | 0.0091 | 0.011 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1681 | 10309.083 | 44270.5718 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2013.7958 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0024 | 0.0089 | 0.0113 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1684 | 10312.276 | 44270.5719 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2054.0717 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0015 | 0.0094 | 0.0109 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1687 | 10315.362 | 44270.5719 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2095.1532 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1690 | 10318.663 | 44270.5719 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2137.0562 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0024 | 0.009 | 0.0114 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1693 | 10322.089 | 44270.572 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2179.7974 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0008 | 0.0098 | 0.0106 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1696 | 10325.386 | 44270.572 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2223.3933 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0024 | 0.0091 | 0.0115 | 0.0103 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1699 | 10328.574 | 44270.572 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2267.8612 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0012 | 0.0091 | 0.0103 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1702 | 10331.713 | 44270.5721 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2313.2184 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0024 | 0.009 | 0.0114 | 0.01 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1705 | 10335.856 | 44270.5721 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2359.4828 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0012 | 0.0089 | 0.0101 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1708 | 10338.952 | 44270.5722 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2406.6724 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0022 | 0.0092 | 0.0114 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1711 | 10342.351 | 44270.5722 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2454.8059 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1714 | 10345.645 | 44270.5722 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2503.902 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1717 | 10348.745 | 44270.5723 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2553.98 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1720 | 10351.93 | 44270.5723 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2605.0596 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1723 | 10355.266 | 44270.5724 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2657.1608 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0014 | 0.0089 | 0.0103 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1726 | 10358.531 | 44270.5724 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2710.304 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0019 | 0.009 | 0.0109 | 0.0096 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1729 | 10361.653 | 44270.5724 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2764.5101 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0011 | 0.0094 | 0.0105 | 0.0097 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1732 | 10364.854 | 44270.5725 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2819.8003 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.01 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1735 | 10368.372 | 44270.5725 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2876.1963 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0014 | 0.0088 | 0.0102 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1738 | 10371.543 | 44270.5725 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2933.7202 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0094 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1741 | 10374.851 | 44270.5726 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2992.3947 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0015 | 0.0095 | 0.011 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1744 | 10378.275 | 44270.5726 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3052.2425 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0018 | 0.009 | 0.0108 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1747 | 10381.565 | 44270.5727 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3113.2874 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0008 | 0.0097 | 0.0105 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1750 | 10384.661 | 44270.5727 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3175.5531 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1753 | 10387.778 | 44270.5727 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3239.0642 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0015 | 0.0096 | 0.0111 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1756 | 10391.214 | 44270.5728 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3303.8455 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0012 | 0.0093 | 0.0105 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1759 | 10394.425 | 44270.5728 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3369.9224 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1762 | 10397.524 | 44270.5728 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3437.3209 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.001 | 0.0101 | 0.0111 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1765 | 10400.732 | 44270.5729 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3506.0673 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1768 | 10404.043 | 44270.5729 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3576.1886 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0009 | 0.0098 | 0.0107 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1771 | 10407.258 | 44270.573 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3647.7124 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0005 | 0.0102 | 0.0107 | 0.0104 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1774 | 10410.424 | 44270.573 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3720.6666 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0023 | 0.009 | 0.0113 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1777 | 10413.809 | 44270.573 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3795.08 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1780 | 10416.784 | 44270.5731 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3870.9816 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0011 | 0.0097 | 0.0108 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1783 | 10420.233 | 44270.5731 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3948.4012 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1786 | 10423.723 | 44270.5731 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4027.3692 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1789 | 10426.859 | 44270.5732 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4107.9166 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0013 | 0.0096 | 0.0109 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1792 | 10430.055 | 44270.5732 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4190.0749 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0088 | 0.0104 | 0.0094 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1795 | 10433.252 | 44270.5733 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4273.8764 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0015 | 0.0096 | 0.0111 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1798 | 10436.356 | 44270.5733 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4359.354 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1801 | 10439.476 | 44270.5733 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4446.541 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1804 | 10442.9 | 44270.5734 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4535.4719 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1807 | 10446.163 | 44270.5734 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4626.1813 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1810 | 10449.247 | 44270.5734 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4718.7049 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1813 | 10452.362 | 44270.5735 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4813.079 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1816 | 10455.456 | 44270.5735 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4909.3406 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1819 | 10458.961 | 44270.5736 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5007.5274 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1822 | 10462.072 | 44270.5736 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5107.678 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1825 | 10465.349 | 44270.5736 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5209.8315 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1828 | 10468.474 | 44270.5737 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5314.0282 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0022 | 0.0088 | 0.011 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1831 | 10471.808 | 44270.5737 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5420.3087 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1834 | 10474.913 | 44270.5737 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5528.7149 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0003 | 0.0095 | 0.0098 | 0.0097 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1837 | 10478.263 | 44270.5738 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5639.2892 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.001 | 0.0094 | 0.0104 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1840 | 10481.46 | 44270.5738 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5752.075 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1843 | 10484.904 | 44270.5739 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5867.1165 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0005 | 0.0099 | 0.0104 | 0.0102 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1846 | 10488.097 | 44270.5739 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5984.4588 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.001 | 0.0093 | 0.0103 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1849 | 10491.429 | 44270.5739 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6104.148 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0021 | 0.0089 | 0.011 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1852 | 10494.514 | 44270.574 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6226.2309 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0009 | 0.0098 | 0.0107 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1855 | 10497.601 | 44270.574 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6350.7556 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1858 | 10500.785 | 44270.574 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6477.7707 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1861 | 10504.092 | 44270.5741 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6607.3261 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0014 | 0.0087 | 0.0101 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1864 | 10507.523 | 44270.5741 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6739.4726 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0006 | 0.0092 | 0.0098 | 0.0094 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1867 | 10510.923 | 44270.5742 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6874.2621 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.001 | 0.0097 | 0.0107 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1870 | 10514.119 | 44270.5742 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7011.7473 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0006 | 0.01 | 0.0106 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1873 | 10517.204 | 44270.5742 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7151.9822 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1876 | 10520.315 | 44270.5743 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7295.0219 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1879 | 10523.4 | 44270.5743 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7440.9223 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1882 | 10526.513 | 44270.5743 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7589.7408 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.01 | 0.0111 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1885 | 10529.61 | 44270.5744 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7741.5356 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1888 | 10533.164 | 44270.5744 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7896.3663 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0006 | 0.0096 | 0.0102 | 0.0098 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1891 | 10536.24 | 44270.5745 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8054.2936 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.009 | 0.0106 | 0.0095 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1894 | 10539.77 | 44270.5745 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8215.3795 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0091 | 0.0102 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1897 | 10542.946 | 44270.5745 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8379.6871 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0008 | 0.0095 | 0.0103 | 0.0099 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1900 | 10546.058 | 44270.5746 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8547.2808 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1903 | 10549.272 | 44270.5746 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8718.2265 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0099 | 0.0111 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1906 | 10552.475 | 44270.5746 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8892.591 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1909 | 10555.678 | 44270.5747 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9070.4428 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1912 | 10558.875 | 44270.5747 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9251.8517 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.0088 | 0.0103 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1915 | 10561.995 | 44270.5747 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9436.8887 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1918 | 10565.174 | 44270.5748 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9625.6265 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0009 | 0.0092 | 0.0101 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1921 | 10568.382 | 44270.5748 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9818.139 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1924 | 10571.613 | 44270.5749 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10014.5018 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1927 | 10574.689 | 44270.5749 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10214.7918 | 0:240:120 | 0:00 | 0 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1930 | 10578.007 | 44270.5749 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10419.0876 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1933 | 10581.214 | 44270.575 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10627.4694 | 0:240:120 | 0:00 | 0 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1936 | 10584.416 | 44270.575 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10840.0188 | 0:240:120 | 0:00 | 0 | 7 | 0.002 | 0.0088 | 0.0108 | 0.0095 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1939 | 10587.621 | 44270.575 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11056.8192 | 0:240:120 | 0:00 | 0 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1942 | 10590.85 | 44270.5751 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11277.9555 | 0:240:120 | 0:00 | 0 | 7 | 0.0012 | 0.0088 | 0.01 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1945 | 10594.262 | 44270.5751 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11503.5146 | 0:240:120 | 0:00 | 0 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1948 | 10597.56 | 44270.5752 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11733.585 | 0:240:120 | 0:00 | 0 | 7 | 0.0016 | 0.009 | 0.0106 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1951 | 10601.1 | 44270.5752 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11968.2566 | 0:240:120 | 0:00 | 0 | 7 | 0.0015 | 0.0095 | 0.011 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1954 | 10856.331 | 44270.5782 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.9 | 0:240:120 | 0:00 | 31.6652 | 7 | 119.7698 | 148.5259 | 268.2957 | 197.1761 | 49.0937 | 2410.1903 | 3 | 31.6652 | 179.5901 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1957 | 11515.024 | 44270.5858 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.4 | 0:240:120 | 0:00 | 27.5828 | 7 | 66.5356 | 58.1753 | 124.7109 | 80.811 | 32.2652 | 1041.0426 | 3 | 27.5828 | 103.5017 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1960 | 11822.908 | 44270.5893 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.9 | 0:240:120 | 0:00 | 24.3752 | 7 | 6.0434 | 50.8496 | 56.893 | 53.2499 | 2.7452 | 7.5361 | 3 | 24.3752 | 72.1924 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1963 | 11988.27 | 44270.5913 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.4 | 0:240:120 | 0:00 | 21.7898 | 7 | 5.2927 | 43.453 | 48.7457 | 45.5344 | 2.3863 | 5.6944 | 3 | 21.7898 | 55.1302 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1966 | 12130.328 | 44270.5929 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.9 | 0:240:120 | 0:00 | 19.6628 | 7 | 6.1619 | 35.4994 | 41.6613 | 38.0821 | 2.7397 | 7.5059 | 3 | 19.6628 | 44.3998 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1969 | 12250.983 | 44270.5943 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.4 | 0:240:120 | 0:00 | 17.8832 | 7 | 6.2779 | 28.3316 | 34.6095 | 30.7289 | 2.8789 | 8.2881 | 3 | 17.8832 | 37.0327 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1972 | 12351.259 | 44270.5955 | Vista Speed | T | 10T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.9 | 0:240:120 | 0:00 | 16.3729 | 7 | 2.1943 | 25.7837 | 27.978 | 26.8324 | 0.8938 | 0.799 | 3 | 16.3729 | 31.6652 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1975 | 12951.628 | 44270.6024 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.04 | 0:240:120 | 0:00 | 51.5767 | 7 | 99.5901 | 440.8185 | 540.4086 | 482.5616 | 44.5367 | 1983.5181 | 3 | 51.5767 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1978 | 14461.227 | 44270.6199 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.6408 | 0:240:120 | 0:00 | 42.5234 | 7 | 96.914 | 329.3251 | 426.2391 | 366.0998 | 45.4368 | 2064.4986 | 3 | 42.5234 | 301.2904 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1981 | 15629.806 | 44270.6334 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.2536 | 0:240:120 | 0:00 | 35.9569 | 7 | 97.5868 | 216.2451 | 313.8319 | 255.2144 | 44.2161 | 1955.0643 | 3 | 35.9569 | 147.1089 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1984 | 16448.506 | 44270.6429 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.8787 | 0:240:120 | 0:00 | 30.9798 | 7 | 89.1906 | 99.9257 | 189.1163 | 137.7443 | 39.4893 | 1559.4045 | 3 | 30.9798 | 95.9984 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1987 | 16893.889 | 44270.648 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.5163 | 0:240:120 | 0:00 | 27.0799 | 7 | 11.363 | 53.1957 | 64.5587 | 57.512 | 5.2244 | 27.2941 | 3 | 27.0799 | 70.5108 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1990 | 17077.482 | 44270.6502 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.1666 | 0:240:120 | 0:00 | 23.944 | 7 | 5.4799 | 46.1485 | 51.6284 | 48.7577 | 2.3245 | 5.4032 | 3 | 23.944 | 55.2495 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1993 | 17229.425 | 44270.6519 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.8299 | 0:240:120 | 0:00 | 21.3694 | 7 | 5.9899 | 39.465 | 45.4549 | 42.098 | 2.6308 | 6.9212 | 3 | 21.3694 | 45.0948 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1996 | 17362.248 | 44270.6535 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.5065 | 0:240:120 | 0:00 | 19.2193 | 7 | 5.7846 | 33.031 | 38.8156 | 35.1776 | 2.7159 | 7.3759 | 3 | 19.2193 | 37.856 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1999 | 17474.192 | 44270.6548 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.1966 | 0:240:120 | 0:00 | 17.3981 | 7 | 4.3403 | 26.7591 | 31.0994 | 28.4385 | 1.9703 | 3.8821 | 3 | 17.3981 | 32.4384 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2002 | 17565.81 | 44270.6558 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.9006 | 0:240:120 | 0:00 | 15.8367 | 7 | 1.971 | 24.4885 | 26.4595 | 25.3167 | 0.884 | 0.7815 | 3 | 15.8367 | 28.2345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2005 | 17645.882 | 44270.6567 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.6186 | 0:240:120 | 0:00 | 14.4844 | 7 | 1.7932 | 22.2614 | 24.0546 | 22.9282 | 0.8418 | 0.7087 | 3 | 14.4844 | 24.8799 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2008 | 17718.703 | 44270.6576 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.351 | 0:240:120 | 0:00 | 13.3025 | 7 | 1.9347 | 19.608 | 21.5427 | 20.3463 | 0.9051 | 0.8193 | 3 | 13.3025 | 22.1428 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2011 | 17784.289 | 44270.6583 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.098 | 0:240:120 | 0:00 | 12.2616 | 7 | 1.7519 | 17.3452 | 19.0971 | 17.9616 | 0.8168 | 0.6672 | 3 | 12.2616 | 19.8687 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2014 | 17842.417 | 44270.659 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.8599 | 0:240:120 | 0:00 | 11.3386 | 7 | 1.0012 | 16.0148 | 17.016 | 16.378 | 0.4782 | 0.2287 | 3 | 11.3386 | 17.9506 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2017 | 17895.199 | 44270.6596 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.6371 | 0:240:120 | 0:00 | 10.515 | 7 | 0.9028 | 14.7425 | 15.6453 | 15.1173 | 0.4021 | 0.1617 | 3 | 10.515 | 16.3123 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2020 | 17944.263 | 44270.6602 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.4299 | 0:240:120 | 0:00 | 9.7762 | 7 | 1.0741 | 13.4235 | 14.4976 | 13.8353 | 0.4948 | 0.2448 | 3 | 9.7762 | 14.8977 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2023 | 17989.142 | 44270.6607 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.2385 | 0:240:120 | 0:00 | 9.1103 | 7 | 0.8153 | 12.2634 | 13.0787 | 12.5557 | 0.3917 | 0.1534 | 3 | 9.1103 | 13.6647 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2026 | 18030.428 | 44270.6612 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.0633 | 0:240:120 | 0:00 | 8.5074 | 7 | 0.5852 | 11.4392 | 12.0244 | 11.6478 | 0.2818 | 0.0794 | 3 | 8.5074 | 12.5815 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2029 | 18069.105 | 44270.6616 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.9045 | 0:240:120 | 0:00 | 7.9594 | 7 | 0.5994 | 10.6042 | 11.2036 | 10.8214 | 0.2752 | 0.0757 | 3 | 7.9594 | 11.6228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2032 | 18105.063 | 44270.6621 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.7626 | 0:240:120 | 0:00 | 7.4594 | 7 | 0.6588 | 9.7537 | 10.4125 | 10.004 | 0.3029 | 0.0917 | 3 | 7.4594 | 10.7691 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2035 | 18138.527 | 44270.6624 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.6379 | 0:240:120 | 0:00 | 7.0019 | 7 | 0.4624 | 9.1526 | 9.615 | 9.3207 | 0.2178 | 0.0474 | 3 | 7.0019 | 10.0046 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2038 | 18169.597 | 44270.6628 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.5306 | 0:240:120 | 0:00 | 6.5818 | 7 | 0.4383 | 8.5636 | 9.0019 | 8.7289 | 0.2041 | 0.0416 | 3 | 6.5818 | 9.3165 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2041 | 18199.148 | 44270.6631 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.4412 | 0:240:120 | 0:00 | 6.1952 | 7 | 0.4826 | 7.9537 | 8.4363 | 8.1446 | 0.2155 | 0.0464 | 3 | 6.1952 | 8.6943 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2044 | 18227.046 | 44270.6635 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.3701 | 0:240:120 | 0:00 | 5.8383 | 7 | 0.3224 | 7.4867 | 7.8091 | 7.5962 | 0.156 | 0.0243 | 3 | 5.8383 | 8.1295 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2047 | 18253.31 | 44270.6638 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.3175 | 0:240:120 | 0:00 | 5.5082 | 7 | 0.2959 | 7.0541 | 7.35 | 7.1618 | 0.1407 | 0.0198 | 3 | 5.5082 | 7.6148 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2050 | 18277.97 | 44270.6641 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.2838 | 0:240:120 | 0:00 | 5.2022 | 7 | 0.3345 | 6.5981 | 6.9326 | 6.7312 | 0.1519 | 0.0231 | 3 | 5.2022 | 7.1442 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2053 | 18301.385 | 44270.6643 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.2695 | 0:240:120 | 0:00 | 4.918 | 7 | 0.2625 | 6.2109 | 6.4734 | 6.3018 | 0.1268 | 0.0161 | 3 | 4.918 | 6.7126 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2056 | 18323.382 | 44270.6646 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.2749 | 0:240:120 | 0:00 | 4.6534 | 7 | 0.2188 | 5.8852 | 6.104 | 5.9626 | 0.1055 | 0.0111 | 3 | 4.6534 | 6.3157 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2059 | 18344.479 | 44270.6648 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.3004 | 0:240:120 | 0:00 | 4.4068 | 7 | 0.2677 | 5.5156 | 5.7833 | 5.6143 | 0.1266 | 0.016 | 3 | 4.4068 | 5.9497 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2062 | 18364.405 | 44270.6651 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.3464 | 0:240:120 | 0:00 | 4.1765 | 7 | 0.1767 | 5.2325 | 5.4092 | 5.2936 | 0.0858 | 0.0074 | 3 | 4.1765 | 5.6113 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2065 | 18383.301 | 44270.6653 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.4133 | 0:240:120 | 0:00 | 3.9612 | 7 | 0.2049 | 4.9458 | 5.1507 | 5.0181 | 0.0977 | 0.0095 | 3 | 3.9612 | 5.2978 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2068 | 18401.844 | 44270.6655 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.5016 | 0:240:120 | 0:00 | 3.7595 | 7 | 0.2169 | 4.6437 | 4.8606 | 4.735 | 0.094 | 0.0088 | 3 | 3.7595 | 5.0069 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2071 | 18419.456 | 44270.6657 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.6116 | 0:240:120 | 0:00 | 3.5703 | 7 | 0.1566 | 4.425 | 4.5816 | 4.4843 | 0.0714 | 0.0051 | 3 | 3.5703 | 4.7362 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2074 | 18436.025 | 44270.6659 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.7438 | 0:240:120 | 0:00 | 3.3928 | 7 | 0.1515 | 4.2013 | 4.3528 | 4.2551 | 0.0713 | 0.0051 | 3 | 3.3928 | 4.484 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2077 | 18452.113 | 44270.6661 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.8987 | 0:240:120 | 0:00 | 3.2258 | 7 | 0.1464 | 3.9695 | 4.1159 | 4.0237 | 0.0673 | 0.0045 | 3 | 3.2258 | 4.2487 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2080 | 18467.324 | 44270.6662 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.0767 | 0:240:120 | 0:00 | 3.0687 | 7 | 0.1302 | 3.7834 | 3.9136 | 3.8275 | 0.0633 | 0.004 | 3 | 3.0687 | 4.0286 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2083 | 18481.953 | 44270.6664 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.2782 | 0:240:120 | 0:00 | 2.9208 | 7 | 0.1537 | 3.5626 | 3.7163 | 3.6267 | 0.0671 | 0.0045 | 3 | 2.9208 | 3.8227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2086 | 18495.852 | 44270.6666 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.5038 | 0:240:120 | 0:00 | 2.7812 | 7 | 0.1193 | 3.3959 | 3.5152 | 3.4502 | 0.0485 | 0.0024 | 3 | 2.7812 | 3.6297 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2089 | 18509.206 | 44270.6667 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.7539 | 0:240:120 | 0:00 | 2.6496 | 7 | 0.1166 | 3.2304 | 3.347 | 3.2774 | 0.0525 | 0.0028 | 3 | 2.6496 | 3.4485 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2092 | 18522.268 | 44270.6669 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.0289 | 0:240:120 | 0:00 | 2.5252 | 7 | 0.1037 | 3.0809 | 3.1846 | 3.1178 | 0.0495 | 0.0024 | 3 | 2.5252 | 3.2782 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2095 | 18534.575 | 44270.667 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.3295 | 0:240:120 | 0:00 | 2.4076 | 7 | 0.1 | 2.9286 | 3.0286 | 2.9698 | 0.0429 | 0.0018 | 3 | 2.4076 | 3.1181 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2098 | 18546.809 | 44270.6672 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.6561 | 0:240:120 | 0:00 | 2.2963 | 7 | 0.0927 | 2.7902 | 2.8829 | 2.824 | 0.0442 | 0.002 | 3 | 2.2963 | 2.9673 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2101 | 18558.2 | 44270.6673 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.0092 | 0:240:120 | 0:00 | 2.191 | 7 | 0.0871 | 2.655 | 2.7421 | 2.6907 | 0.0384 | 0.0015 | 3 | 2.191 | 2.8251 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2104 | 18569.326 | 44270.6674 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.3894 | 0:240:120 | 0:00 | 2.0912 | 7 | 0.0882 | 2.531 | 2.6192 | 2.5637 | 0.041 | 0.0017 | 3 | 2.0912 | 2.6909 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2107 | 18580.049 | 44270.6676 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.7972 | 0:240:120 | 0:00 | 1.9965 | 7 | 0.0735 | 2.42 | 2.4935 | 2.4457 | 0.0351 | 0.0012 | 3 | 1.9965 | 2.5643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2110 | 18590.457 | 44270.6677 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.2331 | 0:240:120 | 0:00 | 1.9068 | 7 | 0.0734 | 2.3037 | 2.3771 | 2.3282 | 0.0362 | 0.0013 | 3 | 1.9068 | 2.4445 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2113 | 18600.519 | 44270.6678 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.6978 | 0:240:120 | 0:00 | 1.8216 | 7 | 0.0665 | 2.1994 | 2.2659 | 2.2226 | 0.0321 | 0.001 | 3 | 1.8216 | 2.3313 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2116 | 18610.244 | 44270.6679 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.1918 | 0:240:120 | 0:00 | 1.7406 | 7 | 0.0652 | 2.097 | 2.1622 | 2.12 | 0.0314 | 0.001 | 3 | 1.7406 | 2.2241 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2119 | 18619.636 | 44270.668 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.7156 | 0:240:120 | 0:00 | 1.6637 | 7 | 0.0555 | 2.0072 | 2.0627 | 2.0266 | 0.027 | 0.0007 | 3 | 1.6637 | 2.1226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2122 | 18628.931 | 44270.6681 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.2699 | 0:240:120 | 0:00 | 1.5906 | 7 | 0.0602 | 1.9121 | 1.9723 | 1.9337 | 0.0284 | 0.0008 | 3 | 1.5906 | 2.0263 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2125 | 18638.021 | 44270.6682 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.8553 | 0:240:120 | 0:00 | 1.5211 | 7 | 0.0516 | 1.8288 | 1.8804 | 1.8465 | 0.0247 | 0.0006 | 3 | 1.5211 | 1.935 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2128 | 18646.821 | 44270.6683 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.4724 | 0:240:120 | 0:00 | 1.4549 | 7 | 0.0538 | 1.7445 | 1.7983 | 1.7651 | 0.0247 | 0.0006 | 3 | 1.4549 | 1.8484 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2131 | 18655.039 | 44270.6684 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.1219 | 0:240:120 | 0:00 | 1.3919 | 7 | 0.0462 | 1.6705 | 1.7167 | 1.6866 | 0.0224 | 0.0005 | 3 | 1.3919 | 1.7661 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2134 | 18663.156 | 44270.6685 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.8043 | 0:240:120 | 0:00 | 1.3319 | 7 | 0.0447 | 1.5955 | 1.6402 | 1.6114 | 0.0213 | 0.0005 | 3 | 1.3319 | 1.688 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2137 | 18671.275 | 44270.6686 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.5204 | 0:240:120 | 0:00 | 1.2747 | 7 | 0.0479 | 1.5234 | 1.5713 | 1.5409 | 0.0224 | 0.0005 | 3 | 1.2747 | 1.6137 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2140 | 18679.131 | 44270.6687 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.2708 | 0:240:120 | 0:00 | 1.2202 | 7 | 0.0415 | 1.4599 | 1.5014 | 1.4756 | 0.0193 | 0.0004 | 3 | 1.2202 | 1.543 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2143 | 18686.641 | 44270.6688 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.0562 | 0:240:120 | 0:00 | 1.1682 | 7 | 0.0407 | 1.3964 | 1.4371 | 1.4106 | 0.0197 | 0.0004 | 3 | 1.1682 | 1.4758 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2146 | 18693.824 | 44270.6689 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.8773 | 0:240:120 | 0:00 | 1.1187 | 7 | 0.0379 | 1.3375 | 1.3754 | 1.3505 | 0.0183 | 0.0003 | 3 | 1.1187 | 1.4118 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2149 | 18700.96 | 44270.669 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.7349 | 0:240:120 | 0:00 | 1.0714 | 7 | 0.0325 | 1.2809 | 1.3134 | 1.2924 | 0.0155 | 0.0002 | 3 | 1.0714 | 1.3508 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2152 | 18708.17 | 44270.669 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.6296 | 0:240:120 | 0:00 | 1.0262 | 7 | 0.0346 | 1.2245 | 1.2591 | 1.2368 | 0.0164 | 0.0003 | 3 | 1.0262 | 1.2927 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2155 | 18714.812 | 44270.6691 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.5622 | 0:240:120 | 0:00 | 0.9832 | 7 | 0.0317 | 1.1729 | 1.2046 | 1.1843 | 0.0146 | 0.0002 | 3 | 0.9832 | 1.2374 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2158 | 18721.577 | 44270.6692 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.5334 | 0:240:120 | 0:00 | 0.942 | 7 | 0.0275 | 1.1247 | 1.1522 | 1.1339 | 0.0136 | 0.0002 | 3 | 0.942 | 1.1846 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2161 | 18728.134 | 44270.6693 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.5441 | 0:240:120 | 0:00 | 0.9027 | 7 | 0.0288 | 1.0755 | 1.1043 | 1.0856 | 0.0136 | 0.0002 | 3 | 0.9027 | 1.1343 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2164 | 18734.381 | 44270.6693 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.595 | 0:240:120 | 0:00 | 0.8651 | 7 | 0.0263 | 1.0309 | 1.0572 | 1.0405 | 0.0123 | 0.0002 | 3 | 0.8651 | 1.0863 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2167 | 18740.959 | 44270.6694 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.6869 | 0:240:120 | 0:00 | 0.8292 | 7 | 0.024 | 0.9872 | 1.0112 | 0.9962 | 0.0112 | 0.0001 | 3 | 0.8292 | 1.0405 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2170 | 18746.87 | 44270.6695 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 108.8206 | 0:240:120 | 0:00 | 0.7949 | 7 | 0.0255 | 0.947 | 0.9725 | 0.9557 | 0.0118 | 0.0001 | 3 | 0.7949 | 0.9967 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2173 | 18753.085 | 44270.6696 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.997 | 0:240:120 | 0:00 | 0.7621 | 7 | 0.0233 | 0.9072 | 0.9305 | 0.9154 | 0.0108 | 0.0001 | 3 | 0.7621 | 0.955 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2176 | 18758.946 | 44270.6696 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.2169 | 0:240:120 | 0:00 | 0.7307 | 7 | 0.0226 | 0.8692 | 0.8918 | 0.8775 | 0.0107 | 0.0001 | 3 | 0.7307 | 0.9151 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2179 | 18764.651 | 44270.6697 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 115.4813 | 0:240:120 | 0:00 | 0.7007 | 7 | 0.0219 | 0.8317 | 0.8536 | 0.8397 | 0.0101 | 0.0001 | 3 | 0.7007 | 0.877 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2182 | 18770.426 | 44270.6698 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.7909 | 0:240:120 | 0:00 | 0.672 | 7 | 0.02 | 0.7988 | 0.8188 | 0.8054 | 0.0096 | 0.0001 | 3 | 0.672 | 0.8406 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2185 | 18775.911 | 44270.6698 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.1467 | 0:240:120 | 0:00 | 0.6445 | 7 | 0.0191 | 0.7656 | 0.7847 | 0.7724 | 0.0091 | 0.0001 | 3 | 0.6445 | 0.8057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2188 | 18781.417 | 44270.6699 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 122.5497 | 0:240:120 | 0:00 | 0.6182 | 7 | 0.0187 | 0.7336 | 0.7523 | 0.7409 | 0.0083 | 0.0001 | 3 | 0.6182 | 0.7724 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2191 | 18787.281 | 44270.6699 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.0007 | 0:240:120 | 0:00 | 0.593 | 7 | 0.0177 | 0.703 | 0.7207 | 0.7098 | 0.0077 | 0.0001 | 3 | 0.593 | 0.7406 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2194 | 18792.331 | 44270.67 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 127.5007 | 0:240:120 | 0:00 | 0.5689 | 7 | 0.0165 | 0.6755 | 0.692 | 0.6813 | 0.0075 | 0.0001 | 3 | 0.5689 | 0.7102 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2197 | 18797.73 | 44270.6701 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.0507 | 0:240:120 | 0:00 | 0.5458 | 7 | 0.016 | 0.6475 | 0.6635 | 0.653 | 0.0075 | 0.0001 | 3 | 0.5458 | 0.681 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2200 | 18802.578 | 44270.6701 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 132.6517 | 0:240:120 | 0:00 | 0.5237 | 7 | 0.0136 | 0.6223 | 0.6359 | 0.6269 | 0.0065 | 0 | 3 | 0.5237 | 0.6532 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2203 | 18807.899 | 44270.6702 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 135.3047 | 0:240:120 | 0:00 | 0.5025 | 7 | 0.0145 | 0.5963 | 0.6108 | 0.6014 | 0.0065 | 0 | 3 | 0.5025 | 0.6265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2206 | 18812.988 | 44270.6702 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.0108 | 0:240:120 | 0:00 | 0.4822 | 7 | 0.0137 | 0.5718 | 0.5855 | 0.5769 | 0.0064 | 0 | 3 | 0.4822 | 0.6009 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2209 | 18817.795 | 44270.6703 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 140.771 | 0:240:120 | 0:00 | 0.4628 | 7 | 0.0127 | 0.5489 | 0.5616 | 0.5535 | 0.006 | 0 | 3 | 0.4628 | 0.5765 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2212 | 18823.238 | 44270.6704 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 143.5865 | 0:240:120 | 0:00 | 0.4441 | 7 | 0.0123 | 0.5274 | 0.5397 | 0.5317 | 0.0056 | 0 | 3 | 0.4441 | 0.5531 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2215 | 18827.918 | 44270.6704 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 146.4582 | 0:240:120 | 0:00 | 0.4263 | 7 | 0.0119 | 0.5055 | 0.5174 | 0.5099 | 0.0052 | 0 | 3 | 0.4263 | 0.5307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2218 | 18832.603 | 44270.6705 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 149.3874 | 0:240:120 | 0:00 | 0.4092 | 7 | 0.0115 | 0.485 | 0.4965 | 0.4889 | 0.0055 | 0 | 3 | 0.4092 | 0.5092 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2221 | 18837.023 | 44270.6705 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 152.3751 | 0:240:120 | 0:00 | 0.3928 | 7 | 0.0114 | 0.4663 | 0.4777 | 0.47 | 0.0051 | 0 | 3 | 0.3928 | 0.4886 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2224 | 18841.477 | 44270.6706 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 155.4226 | 0:240:120 | 0:00 | 0.377 | 7 | 0.0102 | 0.4469 | 0.4571 | 0.4506 | 0.0045 | 0 | 3 | 0.377 | 0.4689 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2227 | 18845.892 | 44270.6706 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 158.5311 | 0:240:120 | 0:00 | 0.362 | 7 | 0.0115 | 0.4283 | 0.4398 | 0.4326 | 0.0049 | 0 | 3 | 0.362 | 0.45 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2230 | 18850.077 | 44270.6707 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 161.7017 | 0:240:120 | 0:00 | 0.3475 | 7 | 0.009 | 0.4122 | 0.4212 | 0.4154 | 0.0041 | 0 | 3 | 0.3475 | 0.4319 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2233 | 18854.241 | 44270.6707 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.9357 | 0:240:120 | 0:00 | 0.3336 | 7 | 0.0092 | 0.395 | 0.4042 | 0.3987 | 0.0039 | 0 | 3 | 0.3336 | 0.4146 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2236 | 18858.753 | 44270.6708 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 168.2344 | 0:240:120 | 0:00 | 0.3203 | 7 | 0.0082 | 0.3798 | 0.388 | 0.3832 | 0.0034 | 0 | 3 | 0.3203 | 0.3979 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2239 | 18863.182 | 44270.6708 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 171.5991 | 0:240:120 | 0:00 | 0.3076 | 7 | 0.0074 | 0.3649 | 0.3723 | 0.3676 | 0.0032 | 0 | 3 | 0.3076 | 0.382 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2242 | 18867.279 | 44270.6709 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175.0311 | 0:240:120 | 0:00 | 0.2953 | 7 | 0.007 | 0.3499 | 0.3569 | 0.3526 | 0.003 | 0 | 3 | 0.2953 | 0.3667 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2245 | 18871.497 | 44270.6709 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 178.5317 | 0:240:120 | 0:00 | 0.2836 | 7 | 0.0067 | 0.3367 | 0.3434 | 0.3395 | 0.0026 | 0 | 3 | 0.2836 | 0.3521 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2248 | 18875.686 | 44270.671 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 182.1024 | 0:240:120 | 0:00 | 0.2723 | 7 | 0.0065 | 0.3231 | 0.3296 | 0.3253 | 0.0031 | 0 | 3 | 0.2723 | 0.338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2251 | 18880.174 | 44270.671 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 185.7444 | 0:240:120 | 0:00 | 0.2615 | 7 | 0.0073 | 0.3097 | 0.317 | 0.3123 | 0.0033 | 0 | 3 | 0.2615 | 0.3245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2254 | 18884.345 | 44270.6711 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 189.4593 | 0:240:120 | 0:00 | 0.2512 | 7 | 0.0056 | 0.2974 | 0.303 | 0.2998 | 0.0023 | 0 | 3 | 0.2512 | 0.3116 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2257 | 18888.324 | 44270.6711 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 193.2485 | 0:240:120 | 0:00 | 0.2412 | 7 | 0.0063 | 0.2858 | 0.2921 | 0.2883 | 0.0026 | 0 | 3 | 0.2412 | 0.2992 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2260 | 18892.317 | 44270.6712 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 197.1134 | 0:240:120 | 0:00 | 0.2317 | 7 | 0.0057 | 0.2742 | 0.2799 | 0.2767 | 0.0023 | 0 | 3 | 0.2317 | 0.2873 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2263 | 18896.29 | 44270.6712 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 201.0557 | 0:240:120 | 0:00 | 0.2225 | 7 | 0.0057 | 0.2629 | 0.2686 | 0.2653 | 0.0021 | 0 | 3 | 0.2225 | 0.2759 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2266 | 18900.144 | 44270.6713 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 205.0768 | 0:240:120 | 0:00 | 0.2137 | 7 | 0.005 | 0.253 | 0.258 | 0.2554 | 0.002 | 0 | 3 | 0.2137 | 0.2649 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2269 | 18903.959 | 44270.6713 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 209.1784 | 0:240:120 | 0:00 | 0.2053 | 7 | 0.0062 | 0.242 | 0.2482 | 0.245 | 0.0024 | 0 | 3 | 0.2053 | 0.2544 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2272 | 18907.728 | 44270.6713 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 213.3619 | 0:240:120 | 0:00 | 0.1972 | 7 | 0.0052 | 0.2335 | 0.2387 | 0.2358 | 0.0021 | 0 | 3 | 0.1972 | 0.2444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2275 | 18911.62 | 44270.6714 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 217.6292 | 0:240:120 | 0:00 | 0.1894 | 7 | 0.005 | 0.2243 | 0.2293 | 0.2266 | 0.0018 | 0 | 3 | 0.1894 | 0.2347 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2278 | 18915.256 | 44270.6714 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 221.9818 | 0:240:120 | 0:00 | 0.1819 | 7 | 0.0055 | 0.215 | 0.2205 | 0.2178 | 0.0018 | 0 | 3 | 0.1819 | 0.2254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2281 | 18918.996 | 44270.6715 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 226.4214 | 0:240:120 | 0:00 | 0.1748 | 7 | 0.0046 | 0.2065 | 0.2111 | 0.2087 | 0.0017 | 0 | 3 | 0.1748 | 0.2165 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2284 | 18922.721 | 44270.6715 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 230.9498 | 0:240:120 | 0:00 | 0.1679 | 7 | 0.0041 | 0.1991 | 0.2032 | 0.2007 | 0.0016 | 0 | 3 | 0.1679 | 0.2079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2287 | 18926.323 | 44270.6716 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 235.5688 | 0:240:120 | 0:00 | 0.1613 | 7 | 0.0051 | 0.1902 | 0.1953 | 0.1928 | 0.0017 | 0 | 3 | 0.1613 | 0.1997 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2290 | 18929.733 | 44270.6716 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 240.2802 | 0:240:120 | 0:00 | 0.1549 | 7 | 0.0041 | 0.1835 | 0.1876 | 0.1851 | 0.0015 | 0 | 3 | 0.1549 | 0.1919 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2293 | 18933.329 | 44270.6716 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 245.0858 | 0:240:120 | 0:00 | 0.1488 | 7 | 0.0042 | 0.176 | 0.1802 | 0.1782 | 0.0014 | 0 | 3 | 0.1488 | 0.1843 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2296 | 18937.05 | 44270.6717 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 249.9875 | 0:240:120 | 0:00 | 0.143 | 7 | 0.0041 | 0.1691 | 0.1732 | 0.1714 | 0.0015 | 0 | 3 | 0.143 | 0.177 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2299 | 18940.51 | 44270.6717 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 254.9873 | 0:240:120 | 0:00 | 0.1374 | 7 | 0.0042 | 0.1629 | 0.1671 | 0.1647 | 0.0015 | 0 | 3 | 0.1374 | 0.1701 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2302 | 18944.11 | 44270.6718 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 260.087 | 0:240:120 | 0:00 | 0.132 | 7 | 0.003 | 0.1563 | 0.1593 | 0.1577 | 0.0013 | 0 | 3 | 0.132 | 0.1634 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2305 | 18947.631 | 44270.6718 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 265.2887 | 0:240:120 | 0:00 | 0.1268 | 7 | 0.0039 | 0.1494 | 0.1533 | 0.1517 | 0.0014 | 0 | 3 | 0.1268 | 0.1569 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2308 | 18951.167 | 44270.6718 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 270.5945 | 0:240:120 | 0:00 | 0.1218 | 7 | 0.004 | 0.1433 | 0.1473 | 0.1453 | 0.0016 | 0 | 3 | 0.1218 | 0.1508 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2311 | 18954.679 | 44270.6719 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 276.0064 | 0:240:120 | 0:00 | 0.1171 | 7 | 0.003 | 0.1384 | 0.1414 | 0.1402 | 0.0014 | 0 | 3 | 0.1171 | 0.1448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2314 | 18958.134 | 44270.6719 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 281.5265 | 0:240:120 | 0:00 | 0.1125 | 7 | 0.0038 | 0.1327 | 0.1365 | 0.1346 | 0.0014 | 0 | 3 | 0.1125 | 0.1392 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2317 | 18961.549 | 44270.672 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 287.1571 | 0:240:120 | 0:00 | 0.1081 | 7 | 0.0023 | 0.1284 | 0.1307 | 0.1296 | 0.0009 | 0 | 3 | 0.1081 | 0.1337 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2320 | 18964.908 | 44270.672 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 292.9002 | 0:240:120 | 0:00 | 0.1038 | 7 | 0.0034 | 0.1229 | 0.1263 | 0.1247 | 0.0012 | 0 | 3 | 0.1038 | 0.1284 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2323 | 18968.497 | 44270.672 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 298.7582 | 0:240:120 | 0:00 | 0.0998 | 7 | 0.0028 | 0.1185 | 0.1213 | 0.1199 | 0.0011 | 0 | 3 | 0.0998 | 0.1234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2326 | 18971.871 | 44270.6721 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 304.7334 | 0:240:120 | 0:00 | 0.0959 | 7 | 0.004 | 0.1127 | 0.1167 | 0.115 | 0.0015 | 0 | 3 | 0.0959 | 0.1186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2329 | 18975.3 | 44270.6721 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 310.828 | 0:240:120 | 0:00 | 0.0921 | 7 | 0.0038 | 0.1085 | 0.1123 | 0.1107 | 0.0012 | 0 | 3 | 0.0921 | 0.1139 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2332 | 18978.725 | 44270.6722 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 317.0446 | 0:240:120 | 0:00 | 0.0885 | 7 | 0.0028 | 0.1043 | 0.1071 | 0.1061 | 0.0013 | 0 | 3 | 0.0885 | 0.1095 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2335 | 18982.329 | 44270.6722 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 323.3855 | 0:240:120 | 0:00 | 0.085 | 7 | 0.0042 | 0.1003 | 0.1045 | 0.1026 | 0.0014 | 0 | 3 | 0.085 | 0.1052 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2338 | 18985.645 | 44270.6722 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 329.8532 | 0:240:120 | 0:00 | 0.0817 | 7 | 0.0024 | 0.0969 | 0.0993 | 0.0982 | 0.0008 | 0 | 3 | 0.0817 | 0.1011 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2341 | 18989.046 | 44270.6723 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 336.4503 | 0:240:120 | 0:00 | 0.0785 | 7 | 0.0041 | 0.0928 | 0.0969 | 0.0945 | 0.0014 | 0 | 3 | 0.0785 | 0.0971 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2344 | 18992.285 | 44270.6723 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 343.1793 | 0:240:120 | 0:00 | 0.0755 | 7 | 0.0029 | 0.0893 | 0.0922 | 0.0905 | 0.001 | 0 | 3 | 0.0755 | 0.0933 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2347 | 18995.693 | 44270.6724 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 350.0429 | 0:240:120 | 0:00 | 0.0725 | 7 | 0.0028 | 0.0859 | 0.0887 | 0.0874 | 0.0008 | 0 | 3 | 0.0725 | 0.0896 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2350 | 18999.373 | 44270.6724 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 357.0437 | 0:240:120 | 0:00 | 0.0697 | 7 | 0.0042 | 0.0815 | 0.0857 | 0.0843 | 0.0016 | 0 | 3 | 0.0697 | 0.0861 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2353 | 19002.758 | 44270.6724 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 364.1846 | 0:240:120 | 0:00 | 0.067 | 7 | 0.0026 | 0.0789 | 0.0815 | 0.0802 | 0.0009 | 0 | 3 | 0.067 | 0.0828 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2356 | 19006.474 | 44270.6725 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 371.4683 | 0:240:120 | 0:00 | 0.0643 | 7 | 0.003 | 0.0761 | 0.0791 | 0.0778 | 0.0011 | 0 | 3 | 0.0643 | 0.0795 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2359 | 19009.892 | 44270.6725 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 378.8977 | 0:240:120 | 0:00 | 0.0618 | 7 | 0.0023 | 0.0733 | 0.0756 | 0.0746 | 0.0008 | 0 | 3 | 0.0618 | 0.0764 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2362 | 19013.489 | 44270.6726 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 386.4756 | 0:240:120 | 0:00 | 0.0594 | 7 | 0.0023 | 0.071 | 0.0733 | 0.0721 | 0.0008 | 0 | 3 | 0.0594 | 0.0734 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2365 | 19016.923 | 44270.6726 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 394.2051 | 0:240:120 | 0:00 | 0.0571 | 7 | 0.0022 | 0.0682 | 0.0704 | 0.0694 | 0.0007 | 0 | 3 | 0.0571 | 0.0706 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2368 | 19020.313 | 44270.6726 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 402.0892 | 0:240:120 | 0:00 | 0.0549 | 7 | 0.0032 | 0.0653 | 0.0685 | 0.0669 | 0.0012 | 0 | 3 | 0.0549 | 0.0678 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2371 | 19023.732 | 44270.6727 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 410.131 | 0:240:120 | 0:00 | 0.0527 | 7 | 0.0042 | 0.0615 | 0.0657 | 0.0639 | 0.0015 | 0 | 3 | 0.0527 | 0.0652 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2374 | 19027.471 | 44270.6727 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 418.3336 | 0:240:120 | 0:00 | 0.0507 | 7 | 0.0014 | 0.0609 | 0.0623 | 0.0616 | 0.0006 | 0 | 3 | 0.0507 | 0.0626 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2377 | 19030.849 | 44270.6728 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 426.7003 | 0:240:120 | 0:00 | 0.0487 | 7 | 0.0016 | 0.0586 | 0.0602 | 0.0595 | 0.0007 | 0 | 3 | 0.0487 | 0.0602 | P | NP | 1-1-1-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
2380 | 19034.39 | 44270.6728 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 435.2343 | 0:240:120 | 0:00 | 0.0468 | 7 | 0.0026 | 0.0552 | 0.0578 | 0.0569 | 0.0009 | 0 | 3 | 0.0468 | 0.0578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2383 | 19037.761 | 44270.6728 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 443.939 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0023 | 0.0532 | 0.0555 | 0.0545 | 0.0009 | 0 | 3 | 0.045 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2386 | 19041.153 | 44270.6729 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 452.8178 | 0:240:120 | 0:00 | 0.0432 | 7 | 0.0027 | 0.0512 | 0.0539 | 0.0528 | 0.001 | 0 | 3 | 0.0432 | 0.0534 | P | NP | 1-1-1-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2389 | 19044.551 | 44270.6729 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 461.8741 | 0:240:120 | 0:00 | 0.0415 | 7 | 0.002 | 0.0497 | 0.0517 | 0.0507 | 0.0006 | 0 | 3 | 0.0415 | 0.0515 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2392 | 19048.024 | 44270.673 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 471.1116 | 0:240:120 | 0:00 | 0.0399 | 7 | 0.0027 | 0.0473 | 0.05 | 0.049 | 0.001 | 0 | 3 | 0.0399 | 0.0499 | P | NP | 0-1-1-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2395 | 19051.302 | 44270.673 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 480.5338 | 0:240:120 | 0:00 | 0.0384 | 7 | 0.0027 | 0.0457 | 0.0484 | 0.047 | 0.0011 | 0 | 3 | 0.0384 | 0.0484 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2398 | 19054.765 | 44270.673 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 490.1445 | 0:240:120 | 0:00 | 0.0369 | 7 | 0.0027 | 0.0442 | 0.0469 | 0.0453 | 0.001 | 0 | 3 | 0.0369 | 0.0469 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2401 | 19057.909 | 44270.6731 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 499.9474 | 0:240:120 | 0:00 | 0.0354 | 7 | 0.0027 | 0.0423 | 0.045 | 0.0436 | 0.001 | 0 | 3 | 0.0354 | 0.0454 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2404 | 19061.185 | 44270.6731 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 509.9464 | 0:240:120 | 0:00 | 0.0341 | 7 | 0.0014 | 0.0409 | 0.0423 | 0.0418 | 0.0006 | 0 | 3 | 0.0341 | 0.0441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2407 | 19064.459 | 44270.6732 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 520.1453 | 0:240:120 | 0:00 | 0.0327 | 7 | 0.0031 | 0.0386 | 0.0417 | 0.0406 | 0.0013 | 0 | 3 | 0.0327 | 0.0427 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2410 | 19067.71 | 44270.6732 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 530.5482 | 0:240:120 | 0:00 | 0.0315 | 7 | 0.0018 | 0.0377 | 0.0395 | 0.0389 | 0.0007 | 0 | 3 | 0.0315 | 0.0415 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2413 | 19070.928 | 44270.6732 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 541.1591 | 0:240:120 | 0:00 | 0.0302 | 7 | 0.0034 | 0.0359 | 0.0393 | 0.0378 | 0.0014 | 0 | 3 | 0.0302 | 0.0402 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2416 | 19074.252 | 44270.6733 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 551.9823 | 0:240:120 | 0:00 | 0.0291 | 7 | 0.003 | 0.0344 | 0.0374 | 0.036 | 0.0011 | 0 | 3 | 0.0291 | 0.0391 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2419 | 19077.557 | 44270.6733 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 563.022 | 0:240:120 | 0:00 | 0.0279 | 7 | 0.0016 | 0.0343 | 0.0359 | 0.0351 | 0.0006 | 0 | 3 | 0.0279 | 0.0379 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2422 | 19080.671 | 44270.6733 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 574.2824 | 0:240:120 | 0:00 | 0.0268 | 7 | 0.0026 | 0.0319 | 0.0345 | 0.0337 | 0.001 | 0 | 3 | 0.0268 | 0.0368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2425 | 19084.054 | 44270.6734 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 585.7681 | 0:240:120 | 0:00 | 0.0258 | 7 | 0.003 | 0.0309 | 0.0339 | 0.0326 | 0.0011 | 0 | 3 | 0.0258 | 0.0358 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2428 | 19087.143 | 44270.6734 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 597.4834 | 0:240:120 | 0:00 | 0.0248 | 7 | 0.0035 | 0.0297 | 0.0332 | 0.0314 | 0.0013 | 0 | 3 | 0.0248 | 0.0348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2431 | 19090.344 | 44270.6735 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 609.4331 | 0:240:120 | 0:00 | 0.0238 | 7 | 0.0025 | 0.0291 | 0.0316 | 0.0303 | 0.0007 | 0 | 3 | 0.0238 | 0.0338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2434 | 19093.623 | 44270.6735 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 621.6218 | 0:240:120 | 0:00 | 0.0229 | 7 | 0.0031 | 0.0275 | 0.0306 | 0.0292 | 0.0012 | 0 | 3 | 0.0229 | 0.0329 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2437 | 19096.858 | 44270.6735 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 634.0542 | 0:240:120 | 0:00 | 0.022 | 7 | 0.0031 | 0.0261 | 0.0292 | 0.0279 | 0.0011 | 0 | 3 | 0.022 | 0.032 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2440 | 19100.12 | 44270.6736 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 646.7353 | 0:240:120 | 0:00 | 0.0212 | 7 | 0.0031 | 0.0253 | 0.0284 | 0.0272 | 0.0013 | 0 | 3 | 0.0212 | 0.0312 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2443 | 19103.315 | 44270.6736 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 659.67 | 0:240:120 | 0:00 | 0.0203 | 7 | 0.0041 | 0.024 | 0.0281 | 0.0263 | 0.0015 | 0 | 3 | 0.0203 | 0.0303 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2446 | 19106.491 | 44270.6736 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 672.8634 | 0:240:120 | 0:00 | 0.0195 | 7 | 0.0029 | 0.024 | 0.0269 | 0.0253 | 0.001 | 0 | 3 | 0.0195 | 0.0295 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2449 | 19109.553 | 44270.6737 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 686.3207 | 0:240:120 | 0:00 | 0.0188 | 7 | 0.0028 | 0.0234 | 0.0262 | 0.025 | 0.001 | 0 | 3 | 0.0188 | 0.0288 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2452 | 19113 | 44270.6737 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 700.0471 | 0:240:120 | 0:00 | 0.018 | 7 | 0.0028 | 0.0222 | 0.025 | 0.024 | 0.0012 | 0 | 3 | 0.018 | 0.028 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2455 | 19116.039 | 44270.6738 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 714.048 | 0:240:120 | 0:00 | 0.0173 | 7 | 0.003 | 0.0216 | 0.0246 | 0.0235 | 0.0011 | 0 | 3 | 0.0173 | 0.0273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2458 | 19119.103 | 44270.6738 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 728.329 | 0:240:120 | 0:00 | 0.0167 | 7 | 0.0038 | 0.0204 | 0.0242 | 0.0227 | 0.0014 | 0 | 3 | 0.0167 | 0.0267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2461 | 19122.317 | 44270.6738 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 742.8955 | 0:240:120 | 0:00 | 0.016 | 7 | 0.0027 | 0.0208 | 0.0235 | 0.0223 | 0.001 | 0 | 3 | 0.016 | 0.026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2464 | 19125.979 | 44270.6739 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 757.7535 | 0:240:120 | 0:00 | 0.0154 | 7 | 0.0043 | 0.0196 | 0.0239 | 0.0217 | 0.0017 | 0 | 3 | 0.0154 | 0.0254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2467 | 19129.142 | 44270.6739 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 772.9085 | 0:240:120 | 0:00 | 0.0148 | 7 | 0.0036 | 0.019 | 0.0226 | 0.0209 | 0.0015 | 0 | 3 | 0.0148 | 0.0248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2470 | 19132.197 | 44270.6739 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 788.3667 | 0:240:120 | 0:00 | 0.0142 | 7 | 0.0037 | 0.019 | 0.0227 | 0.0211 | 0.0013 | 0 | 3 | 0.0142 | 0.0242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2473 | 19135.567 | 44270.674 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 804.134 | 0:240:120 | 0:00 | 0.0137 | 7 | 0.0036 | 0.0186 | 0.0222 | 0.0205 | 0.0012 | 0 | 3 | 0.0137 | 0.0237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2476 | 19138.834 | 44270.674 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 820.2167 | 0:240:120 | 0:00 | 0.0131 | 7 | 0.0022 | 0.0192 | 0.0214 | 0.0203 | 0.0007 | 0 | 3 | 0.0131 | 0.0231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2479 | 19142.22 | 44270.6741 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 836.621 | 0:240:120 | 0:00 | 0.0126 | 7 | 0.0031 | 0.0187 | 0.0218 | 0.0197 | 0.0011 | 0 | 3 | 0.0126 | 0.0226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2482 | 19145.379 | 44270.6741 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 853.3535 | 0:240:120 | 0:00 | 0.0121 | 7 | 0.0023 | 0.0178 | 0.0201 | 0.019 | 0.0012 | 0 | 3 | 0.0121 | 0.0221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2485 | 19148.469 | 44270.6741 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 870.4205 | 0:240:120 | 0:00 | 0.0117 | 7 | 0.0021 | 0.0177 | 0.0198 | 0.0189 | 0.0007 | 0 | 3 | 0.0117 | 0.0217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2488 | 19151.866 | 44270.6742 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 887.8289 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.0018 | 0.0176 | 0.0194 | 0.0185 | 0.0008 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2491 | 19155.048 | 44270.6742 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 905.5855 | 0:240:120 | 0:00 | 0.0108 | 7 | 0.0017 | 0.0173 | 0.019 | 0.0179 | 0.0005 | 0 | 3 | 0.0108 | 0.0208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2494 | 19158.11 | 44270.6742 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 923.6972 | 0:240:120 | 0:00 | 0.0104 | 7 | 0.0014 | 0.0174 | 0.0188 | 0.0179 | 0.0004 | 0 | 3 | 0.0104 | 0.0204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2497 | 19161.151 | 44270.6743 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 940.1758 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0018 | 0.0164 | 0.0182 | 0.0175 | 0.0007 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2500 | 19164.227 | 44270.6743 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 958.9793 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0012 | 0.0167 | 0.0179 | 0.0171 | 0.0005 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2503 | 19167.733 | 44270.6744 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 978.1589 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0023 | 0.0151 | 0.0174 | 0.0163 | 0.0008 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2506 | 19170.873 | 44270.6744 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 997.7221 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0025 | 0.0153 | 0.0178 | 0.0163 | 0.0008 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 1-1-0-0-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
2509 | 19174.053 | 44270.6744 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1017.6765 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0034 | 0.0144 | 0.0178 | 0.0158 | 0.0011 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2512 | 19177.513 | 44270.6745 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1038.03 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0047 | 0.0135 | 0.0182 | 0.0156 | 0.0016 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2515 | 19180.592 | 44270.6745 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1058.7906 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0035 | 0.0137 | 0.0172 | 0.0153 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2518 | 19183.785 | 44270.6745 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1079.9664 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0042 | 0.0129 | 0.0171 | 0.015 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2521 | 19187.381 | 44270.6746 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1101.5658 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0047 | 0.0125 | 0.0172 | 0.0148 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2524 | 19190.643 | 44270.6746 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1123.5971 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0041 | 0.0128 | 0.0169 | 0.0146 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2527 | 19193.72 | 44270.6747 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1146.069 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0041 | 0.0123 | 0.0164 | 0.0145 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2530 | 19196.902 | 44270.6747 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1168.9904 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0042 | 0.0122 | 0.0164 | 0.0145 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2533 | 19200.093 | 44270.6747 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1192.3702 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0051 | 0.0116 | 0.0167 | 0.0143 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2536 | 19203.236 | 44270.6748 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1216.2176 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0052 | 0.0115 | 0.0167 | 0.0142 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2539 | 19206.438 | 44270.6748 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1240.542 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0044 | 0.0114 | 0.0158 | 0.0137 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2542 | 19209.569 | 44270.6748 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1265.3528 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0046 | 0.0116 | 0.0162 | 0.0139 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2545 | 19212.966 | 44270.6749 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1290.6599 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.005 | 0.0111 | 0.0161 | 0.0136 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2548 | 19216.149 | 44270.6749 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1316.4731 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0052 | 0.0109 | 0.0161 | 0.0137 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2551 | 19219.534 | 44270.675 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1342.8025 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0042 | 0.0116 | 0.0158 | 0.0136 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2554 | 19222.919 | 44270.675 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1369.6586 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0052 | 0.0114 | 0.0166 | 0.0136 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2557 | 19226.424 | 44270.675 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1397.0518 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0052 | 0.0112 | 0.0164 | 0.0135 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2560 | 19229.815 | 44270.6751 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1424.9928 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.0051 | 0.0113 | 0.0164 | 0.0133 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2563 | 19232.971 | 44270.6751 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1453.4926 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0046 | 0.0105 | 0.0151 | 0.013 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2566 | 19236.147 | 44270.6751 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1482.5625 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0052 | 0.0104 | 0.0156 | 0.0131 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2569 | 19239.629 | 44270.6752 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1512.2138 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0052 | 0.0105 | 0.0157 | 0.0128 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2572 | 19242.963 | 44270.6752 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1542.458 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0037 | 0.0107 | 0.0144 | 0.0128 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2575 | 19246.157 | 44270.6753 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1573.3072 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.003 | 0.0108 | 0.0138 | 0.0124 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2578 | 19249.613 | 44270.6753 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1604.7733 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0031 | 0.0103 | 0.0134 | 0.0122 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2581 | 19253.329 | 44270.6753 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1636.8688 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0036 | 0.0101 | 0.0137 | 0.0118 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2584 | 19256.933 | 44270.6754 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1669.6062 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0036 | 0.0102 | 0.0138 | 0.0118 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2587 | 19259.998 | 44270.6754 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1702.9983 | 0:240:120 | 0:00 | 0.003 | 7 | 0.003 | 0.01 | 0.013 | 0.0113 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2590 | 19263.249 | 44270.6755 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1737.0583 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.003 | 0.0102 | 0.0132 | 0.0115 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2593 | 19266.735 | 44270.6755 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1771.7994 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0041 | 0.0099 | 0.014 | 0.0117 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2596 | 19270.481 | 44270.6755 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1807.2354 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0041 | 0.0098 | 0.0139 | 0.0117 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2599 | 19273.521 | 44270.6756 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1843.3801 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0044 | 0.0092 | 0.0136 | 0.011 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2602 | 19276.682 | 44270.6756 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1880.2477 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0028 | 0.0101 | 0.0129 | 0.0111 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2605 | 19280.069 | 44270.6757 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1880.3516 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0042 | 0.0097 | 0.0139 | 0.0113 | 0.0017 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2608 | 19283.534 | 44270.6757 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1917.9586 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0041 | 0.0091 | 0.0132 | 0.0113 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2611 | 19286.809 | 44270.6757 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1956.3178 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0029 | 0.0097 | 0.0126 | 0.0111 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2614 | 19289.985 | 44270.6758 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1995.4441 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0041 | 0.0089 | 0.013 | 0.0109 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2617 | 19293.254 | 44270.6758 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2035.353 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0041 | 0.0092 | 0.0133 | 0.011 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2620 | 19296.445 | 44270.6758 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2076.0601 | 0:240:120 | 0:00 | 0.002 | 7 | 0.004 | 0.0095 | 0.0135 | 0.0111 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2623 | 19299.479 | 44270.6759 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2117.5813 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0026 | 0.009 | 0.0116 | 0.0104 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2626 | 19302.535 | 44270.6759 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2159.9329 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0024 | 0.0093 | 0.0117 | 0.0106 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2629 | 19305.922 | 44270.676 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2203.1316 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0017 | 0.01 | 0.0117 | 0.0111 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2632 | 19309.185 | 44270.676 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2247.1942 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0029 | 0.0091 | 0.012 | 0.0106 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2635 | 19312.357 | 44270.676 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2292.1381 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0017 | 0.0098 | 0.0115 | 0.0107 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2638 | 19315.434 | 44270.6761 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2337.9808 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.001 | 0.01 | 0.011 | 0.0107 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2641 | 19318.627 | 44270.6761 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2384.7404 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0007 | 0.0101 | 0.0108 | 0.0105 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2644 | 19321.806 | 44270.6761 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2432.4353 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0013 | 0.0102 | 0.0115 | 0.0105 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2647 | 19324.966 | 44270.6762 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2481.084 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.002 | 0.0095 | 0.0115 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2650 | 19328.137 | 44270.6762 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2530.7056 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0019 | 0.0094 | 0.0113 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2653 | 19331.319 | 44270.6762 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2581.3198 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0012 | 0.01 | 0.0112 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2656 | 19334.692 | 44270.6763 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2632.9461 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2659 | 19338.118 | 44270.6763 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2685.6051 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0005 | 0.01 | 0.0105 | 0.0103 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2662 | 19341.341 | 44270.6764 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2739.3172 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.001 | 0.0099 | 0.0109 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2665 | 19344.513 | 44270.6764 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2794.1035 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2668 | 19347.616 | 44270.6764 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2849.9856 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2671 | 19350.982 | 44270.6765 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2906.9853 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0023 | 0.0091 | 0.0114 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2674 | 19354.885 | 44270.6765 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2965.125 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2677 | 19357.953 | 44270.6766 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3024.4275 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2680 | 19361.238 | 44270.6766 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3084.9161 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2683 | 19364.592 | 44270.6766 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3146.6144 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2686 | 19367.9 | 44270.6767 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3209.5467 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2689 | 19371.293 | 44270.6767 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3273.7376 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0012 | 0.009 | 0.0102 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2692 | 19374.414 | 44270.6767 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3339.2123 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0015 | 0.0092 | 0.0107 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2695 | 19377.485 | 44270.6768 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3405.9966 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2698 | 19380.652 | 44270.6768 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3474.1165 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2701 | 19383.806 | 44270.6769 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3543.5989 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2704 | 19386.963 | 44270.6769 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3614.4708 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2707 | 19390.126 | 44270.6769 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3686.7603 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0017 | 0.0097 | 0.0114 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2710 | 19393.268 | 44270.677 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3760.4955 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2713 | 19396.51 | 44270.677 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3835.7054 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0013 | 0.0095 | 0.0108 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2716 | 19399.674 | 44270.677 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3912.4195 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2719 | 19402.918 | 44270.6771 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3990.6679 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2722 | 19406.048 | 44270.6771 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4070.4812 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2725 | 19409.228 | 44270.6771 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4151.8908 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0011 | 0.009 | 0.0101 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2728 | 19412.49 | 44270.6772 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4234.9287 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0015 | 0.0096 | 0.0111 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2731 | 19415.555 | 44270.6772 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4319.6272 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0019 | 0.0094 | 0.0113 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2734 | 19418.961 | 44270.6773 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4406.0198 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2737 | 19422.262 | 44270.6773 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4494.1402 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0014 | 0.0098 | 0.0112 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2740 | 19425.534 | 44270.6773 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4584.023 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0021 | 0.0089 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2743 | 19428.942 | 44270.6774 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4675.7034 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2746 | 19432.166 | 44270.6774 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4769.2175 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.002 | 0.0093 | 0.0113 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2749 | 19435.458 | 44270.6775 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4864.6019 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0019 | 0.0094 | 0.0113 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2752 | 19438.633 | 44270.6775 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4961.8939 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0011 | 0.0093 | 0.0104 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2755 | 19441.847 | 44270.6775 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5061.1318 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0097 | 0.0113 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2758 | 19445.06 | 44270.6776 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5162.3544 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0019 | 0.0088 | 0.0107 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2761 | 19448.601 | 44270.6776 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5265.6015 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2764 | 19451.741 | 44270.6776 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5370.9135 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2767 | 19454.986 | 44270.6777 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5478.3318 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0014 | 0.0089 | 0.0103 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2770 | 19458.381 | 44270.6777 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5587.8984 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2773 | 19461.653 | 44270.6778 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5699.6564 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.002 | 0.0092 | 0.0112 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2776 | 19464.926 | 44270.6778 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5813.6495 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0007 | 0.0097 | 0.0104 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2779 | 19468.33 | 44270.6778 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5929.9225 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2782 | 19471.597 | 44270.6779 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6048.521 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2785 | 19474.836 | 44270.6779 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6169.4914 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0015 | 0.0097 | 0.0112 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2788 | 19478.078 | 44270.6779 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6292.8812 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2791 | 19481.251 | 44270.678 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6418.7388 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0012 | 0.0093 | 0.0105 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2794 | 19484.292 | 44270.678 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6547.1136 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0008 | 0.01 | 0.0108 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2797 | 19487.678 | 44270.6781 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6678.0559 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0018 | 0.0091 | 0.0109 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2800 | 19490.848 | 44270.6781 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6811.617 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.0088 | 0.0105 | 0.0096 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2803 | 19494.017 | 44270.6781 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6947.8493 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0021 | 0.0089 | 0.011 | 0.01 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2806 | 19497.073 | 44270.6782 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7086.8063 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2809 | 19500.62 | 44270.6782 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7228.5425 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0005 | 0.0098 | 0.0103 | 0.0101 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2812 | 19504.076 | 44270.6782 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7373.1133 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2815 | 19507.337 | 44270.6783 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7520.5756 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2818 | 19510.416 | 44270.6783 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7670.9871 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.002 | 0.009 | 0.011 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2821 | 19513.576 | 44270.6784 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7824.4068 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0003 | 0.0094 | 0.0097 | 0.0096 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2824 | 19516.869 | 44270.6784 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7980.895 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2827 | 19520.012 | 44270.6784 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8140.5129 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2830 | 19523.175 | 44270.6785 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8303.3231 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0096 | 0.0108 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2833 | 19526.261 | 44270.6785 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8469.3896 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0007 | 0.0096 | 0.0103 | 0.01 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2836 | 19529.324 | 44270.6785 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8638.7774 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.0095 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2839 | 19532.925 | 44270.6786 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8811.5529 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2842 | 19536.313 | 44270.6786 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8987.784 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2845 | 19539.479 | 44270.6787 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9167.5397 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0004 | 0.0094 | 0.0098 | 0.0096 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2848 | 19542.64 | 44270.6787 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9350.8905 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2851 | 19545.904 | 44270.6787 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9537.9083 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0003 | 0.0096 | 0.0099 | 0.0097 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2854 | 19548.978 | 44270.6788 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9728.6664 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.0088 | 0.0099 | 0.0093 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2857 | 19552.385 | 44270.6788 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9923.2398 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0017 | 0.0088 | 0.0105 | 0.0096 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2860 | 19555.814 | 44270.6788 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10121.7046 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2863 | 19559.075 | 44270.6789 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10324.1386 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.0088 | 0.0103 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2866 | 19562.244 | 44270.6789 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10530.6214 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0009 | 0.0096 | 0.0105 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2869 | 19565.407 | 44270.679 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10741.2338 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2872 | 19568.583 | 44270.679 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10956.0585 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0011 | 0.009 | 0.0101 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2875 | 19571.865 | 44270.679 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11175.1797 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0015 | 0.0089 | 0.0104 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2878 | 19575.325 | 44270.6791 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11398.6833 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0006 | 0.0093 | 0.0099 | 0.0096 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2881 | 19578.45 | 44270.6791 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11626.657 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0021 | 0.0088 | 0.0109 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2884 | 19581.651 | 44270.6791 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11859.1901 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0005 | 0.0098 | 0.0103 | 0.0101 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2887 | 19940.407 | 44270.6833 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.9 | 0:240:120 | 0:00 | 39.4905 | 7 | 101.2945 | 270.9185 | 372.213 | 315.3126 | 40.3094 | 1624.8459 | 3 | 39.4905 | 209.118 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2890 | 20918.102 | 44270.6946 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.6 | 0:240:120 | 0:00 | 33.0293 | 7 | 81.8808 | 152.1701 | 234.0509 | 185.9253 | 36.5881 | 1338.6918 | 3 | 33.0293 | 113.7088 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2893 | 21509.062 | 44270.7015 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.2 | 0:240:120 | 0:00 | 28.8931 | 7 | 64.3497 | 56.4874 | 120.8371 | 78.8578 | 31.1547 | 970.6137 | 3 | 28.8931 | 81.2669 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2896 | 21808.833 | 44270.7049 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.8 | 0:240:120 | 0:00 | 25.6239 | 7 | 4.7048 | 50.4018 | 55.1066 | 52.3688 | 2.0841 | 4.3437 | 3 | 25.6239 | 62.9648 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2899 | 21970.511 | 44270.7068 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.5 | 0:240:120 | 0:00 | 22.5831 | 7 | 5.7182 | 42.7841 | 48.5023 | 45.4474 | 2.4308 | 5.9089 | 3 | 22.5831 | 49.6567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2902 | 22112.325 | 44270.7084 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.2 | 0:240:120 | 0:00 | 20.1424 | 7 | 5.8352 | 35.9087 | 41.7439 | 38.223 | 2.6425 | 6.9827 | 3 | 20.1424 | 40.8422 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2905 | 22232.628 | 44270.7098 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.9 | 0:240:120 | 0:00 | 18.1412 | 7 | 5.1948 | 28.684 | 33.8788 | 31.0013 | 2.2419 | 5.0263 | 3 | 18.1412 | 34.5774 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2908 | 22331.624 | 44270.711 | Vista Speed | T | 12T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.5 | 0:240:120 | 0:00 | 16.6929 | 7 | 2.0792 | 25.8013 | 27.8805 | 26.6348 | 0.8901 | 0.7922 | 3 | 16.6929 | 30.4929 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2911 | 23209.909 | 44270.7211 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.136 | 0:240:120 | 0:00 | 62.929 | 7 | 27.3038 | 548.0719 | 575.3757 | 561.543 | 14.4125 | 207.721 | 3 | 62.929 | 9999999 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2914 | 25386.29 | 44270.7463 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.8787 | 0:240:120 | 0:00 | 51.0464 | 7 | 109.5441 | 427.8159 | 537.36 | 472.5809 | 49.6414 | 2464.2677 | 3 | 51.0464 | 670.9521 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2917 | 26880.018 | 44270.7636 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.6363 | 0:240:120 | 0:00 | 42.6647 | 7 | 110.4738 | 306.0531 | 416.5269 | 345.6839 | 53.0941 | 2818.9833 | 3 | 42.6647 | 217.0262 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2920 | 28006.028 | 44270.7766 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.409 | 0:240:120 | 0:00 | 36.4397 | 7 | 106.4609 | 184.28 | 290.7409 | 220.8936 | 52.2018 | 2725.028 | 3 | 36.4397 | 127.3723 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2923 | 28734.345 | 44270.7851 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.1972 | 0:240:120 | 0:00 | 31.6372 | 7 | 81.3641 | 62.998 | 144.3621 | 90.1 | 40.4209 | 1633.8496 | 3 | 31.6372 | 89.0845 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2926 | 29085.332 | 44270.7891 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.0011 | 0:240:120 | 0:00 | 27.8222 | 7 | 4.3551 | 55.992 | 60.3471 | 57.5488 | 2.0567 | 4.23 | 3 | 27.8222 | 67.8615 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2929 | 29262.324 | 44270.7912 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.8212 | 0:240:120 | 0:00 | 24.7209 | 7 | 5.0538 | 48.1333 | 53.1871 | 50.3723 | 2.1822 | 4.7621 | 3 | 24.7209 | 54.3823 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2932 | 29418.319 | 44270.793 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.6576 | 0:240:120 | 0:00 | 22.1518 | 7 | 6.2585 | 40.2254 | 46.4839 | 42.4789 | 3.0076 | 9.0456 | 3 | 22.1518 | 45.0687 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2935 | 29553.37 | 44270.7946 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.5107 | 0:240:120 | 0:00 | 19.9904 | 7 | 5.9204 | 33.2654 | 39.1858 | 35.2557 | 2.9243 | 8.5513 | 3 | 19.9904 | 38.2528 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2938 | 29664.935 | 44270.7958 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.381 | 0:240:120 | 0:00 | 18.1482 | 7 | 1.835 | 28.4813 | 30.3163 | 29.2707 | 0.7822 | 0.6119 | 3 | 18.1482 | 33.0523 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2941 | 29756.343 | 44270.7969 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.2686 | 0:240:120 | 0:00 | 16.5604 | 7 | 2.1172 | 25.7444 | 27.8616 | 26.4739 | 1.04 | 1.0815 | 3 | 16.5604 | 28.9565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2944 | 29840.02 | 44270.7979 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.1739 | 0:240:120 | 0:00 | 15.1787 | 7 | 1.6045 | 23.3165 | 24.921 | 23.8978 | 0.7606 | 0.5784 | 3 | 15.1787 | 25.6497 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2947 | 29915.244 | 44270.7987 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.0974 | 0:240:120 | 0:00 | 13.9664 | 7 | 2.1247 | 20.2998 | 22.4245 | 21.0899 | 1.0027 | 1.0054 | 3 | 13.9664 | 22.9258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2950 | 29982.579 | 44270.7995 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.0394 | 0:240:120 | 0:00 | 12.8948 | 7 | 1.0274 | 18.4832 | 19.5106 | 18.8602 | 0.4854 | 0.2356 | 3 | 12.8948 | 20.6448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2953 | 30042.487 | 44270.8002 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.0002 | 0:240:120 | 0:00 | 11.9417 | 7 | 1.0734 | 16.9958 | 18.0692 | 17.3579 | 0.5316 | 0.2826 | 3 | 11.9417 | 18.7083 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2956 | 30098.151 | 44270.8009 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.9802 | 0:240:120 | 0:00 | 11.0888 | 7 | 0.9529 | 15.5296 | 16.4825 | 15.8658 | 0.4603 | 0.2118 | 3 | 11.0888 | 17.0448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2959 | 30149.165 | 44270.8015 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.9798 | 0:240:120 | 0:00 | 10.3219 | 7 | 0.9215 | 14.135 | 15.0565 | 14.4913 | 0.4174 | 0.1742 | 3 | 10.3219 | 15.6015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2962 | 30196.037 | 44270.802 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.9994 | 0:240:120 | 0:00 | 9.6291 | 7 | 0.6225 | 13.1269 | 13.7494 | 13.3359 | 0.3088 | 0.0953 | 3 | 9.6291 | 14.3384 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2965 | 30239.31 | 44270.8025 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.0394 | 0:240:120 | 0:00 | 9.0005 | 7 | 0.6358 | 12.1749 | 12.8107 | 12.3906 | 0.3147 | 0.099 | 3 | 9.0005 | 13.2244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2968 | 30279.827 | 44270.803 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.1001 | 0:240:120 | 0:00 | 8.4281 | 7 | 0.6398 | 11.2174 | 11.8572 | 11.4449 | 0.3095 | 0.0958 | 3 | 8.4281 | 12.2355 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2971 | 30317.444 | 44270.8034 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.1821 | 0:240:120 | 0:00 | 7.9051 | 7 | 0.5383 | 10.3678 | 10.9061 | 10.5534 | 0.2633 | 0.0693 | 3 | 7.9051 | 11.3522 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2974 | 30352.268 | 44270.8038 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.2858 | 0:240:120 | 0:00 | 7.4256 | 7 | 0.4261 | 9.7353 | 10.1614 | 9.8957 | 0.1986 | 0.0394 | 3 | 7.4256 | 10.5592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2977 | 30384.97 | 44270.8042 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.4115 | 0:240:120 | 0:00 | 6.9849 | 7 | 0.4237 | 9.106 | 9.5297 | 9.2609 | 0.2007 | 0.0403 | 3 | 6.9849 | 9.8437 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2980 | 30415.811 | 44270.8045 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.5597 | 0:240:120 | 0:00 | 6.5786 | 7 | 0.4263 | 8.4718 | 8.8981 | 8.6158 | 0.2112 | 0.0446 | 3 | 6.5786 | 9.1955 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2983 | 30444.669 | 44270.8049 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.7309 | 0:240:120 | 0:00 | 6.2032 | 7 | 0.2992 | 8.0266 | 8.3258 | 8.1278 | 0.1481 | 0.0219 | 3 | 6.2032 | 8.6059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2986 | 30472.125 | 44270.8052 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.9255 | 0:240:120 | 0:00 | 5.8556 | 7 | 0.3965 | 7.4539 | 7.8504 | 7.6275 | 0.1667 | 0.0278 | 3 | 5.8556 | 8.0677 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2989 | 30498.414 | 44270.8055 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.1441 | 0:240:120 | 0:00 | 5.533 | 7 | 0.3251 | 6.9968 | 7.3219 | 7.1117 | 0.1542 | 0.0238 | 3 | 5.533 | 7.5749 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2992 | 30522.773 | 44270.8058 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.3869 | 0:240:120 | 0:00 | 5.2331 | 7 | 0.2468 | 6.6394 | 6.8862 | 6.7329 | 0.1148 | 0.0132 | 3 | 5.2331 | 7.1222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2995 | 30546.225 | 44270.806 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.6547 | 0:240:120 | 0:00 | 4.9537 | 7 | 0.2744 | 6.2386 | 6.513 | 6.3527 | 0.122 | 0.0149 | 3 | 4.9537 | 6.7053 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2998 | 30568.496 | 44270.8063 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.9478 | 0:240:120 | 0:00 | 4.6931 | 7 | 0.2307 | 5.8924 | 6.1231 | 5.9731 | 0.1118 | 0.0125 | 3 | 4.6931 | 6.3204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3001 | 30589.473 | 44270.8065 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.2667 | 0:240:120 | 0:00 | 4.4495 | 7 | 0.2004 | 5.5699 | 5.7703 | 5.6456 | 0.0933 | 0.0087 | 3 | 4.4495 | 5.9642 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3004 | 30609.321 | 44270.8068 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.6121 | 0:240:120 | 0:00 | 4.2215 | 7 | 0.2301 | 5.2507 | 5.4808 | 5.3559 | 0.0947 | 0.009 | 3 | 4.2215 | 5.6339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3007 | 30628.481 | 44270.807 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.9843 | 0:240:120 | 0:00 | 4.0078 | 7 | 0.1593 | 4.9928 | 5.1521 | 5.0483 | 0.0771 | 0.0059 | 3 | 4.0078 | 5.3269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3010 | 30646.789 | 44270.8072 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.384 | 0:240:120 | 0:00 | 3.8074 | 7 | 0.1424 | 4.7366 | 4.879 | 4.7855 | 0.0695 | 0.0048 | 3 | 3.8074 | 5.0412 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3013 | 30664.213 | 44270.8074 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.8117 | 0:240:120 | 0:00 | 3.619 | 7 | 0.1566 | 4.4741 | 4.6307 | 4.5274 | 0.0751 | 0.0056 | 3 | 3.619 | 4.7747 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3016 | 30680.836 | 44270.8076 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.2679 | 0:240:120 | 0:00 | 3.4419 | 7 | 0.1343 | 4.2485 | 4.3828 | 4.2955 | 0.0651 | 0.0042 | 3 | 3.4419 | 4.5258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3019 | 30696.713 | 44270.8078 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.7533 | 0:240:120 | 0:00 | 3.2751 | 7 | 0.1313 | 4.0371 | 4.1684 | 4.0807 | 0.0633 | 0.004 | 3 | 3.2751 | 4.2929 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3022 | 30712.009 | 44270.808 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.2683 | 0:240:120 | 0:00 | 3.118 | 7 | 0.1113 | 3.833 | 3.9443 | 3.8702 | 0.0542 | 0.0029 | 3 | 3.118 | 4.0748 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3025 | 30726.736 | 44270.8081 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.8137 | 0:240:120 | 0:00 | 2.9697 | 7 | 0.1017 | 3.6497 | 3.7514 | 3.6856 | 0.0479 | 0.0023 | 3 | 2.9697 | 3.8703 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3028 | 30740.672 | 44270.8083 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.39 | 0:240:120 | 0:00 | 2.8297 | 7 | 0.1277 | 3.4464 | 3.5741 | 3.4979 | 0.0574 | 0.0033 | 3 | 2.8297 | 3.6781 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3031 | 30754.23 | 44270.8085 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.9978 | 0:240:120 | 0:00 | 2.6974 | 7 | 0.0974 | 3.2977 | 3.3951 | 3.3308 | 0.048 | 0.0023 | 3 | 2.6974 | 3.4975 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3034 | 30767.222 | 44270.8086 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.6377 | 0:240:120 | 0:00 | 2.5722 | 7 | 0.1036 | 3.1246 | 3.2282 | 3.1696 | 0.0447 | 0.002 | 3 | 2.5722 | 3.3275 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3037 | 30779.986 | 44270.8088 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.3105 | 0:240:120 | 0:00 | 2.4538 | 7 | 0.0864 | 2.9895 | 3.0759 | 3.0191 | 0.042 | 0.0018 | 3 | 2.4538 | 3.1673 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3040 | 30792.039 | 44270.8089 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.0167 | 0:240:120 | 0:00 | 2.3416 | 7 | 0.0901 | 2.8408 | 2.9309 | 2.8734 | 0.0429 | 0.0018 | 3 | 2.3416 | 3.0163 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3043 | 30803.553 | 44270.809 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.757 | 0:240:120 | 0:00 | 2.2353 | 7 | 0.0749 | 2.7093 | 2.7842 | 2.7378 | 0.0343 | 0.0012 | 3 | 2.2353 | 2.8737 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3046 | 30814.645 | 44270.8092 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.5322 | 0:240:120 | 0:00 | 2.1345 | 7 | 0.077 | 2.5852 | 2.6622 | 2.6142 | 0.0347 | 0.0012 | 3 | 2.1345 | 2.739 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3049 | 30825.446 | 44270.8093 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.3428 | 0:240:120 | 0:00 | 2.0388 | 7 | 0.072 | 2.4655 | 2.5375 | 2.4929 | 0.0329 | 0.0011 | 3 | 2.0388 | 2.6116 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3052 | 30835.883 | 44270.8094 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.1897 | 0:240:120 | 0:00 | 1.948 | 7 | 0.0723 | 2.3531 | 2.4254 | 2.3805 | 0.0329 | 0.0011 | 3 | 1.948 | 2.4911 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3055 | 30845.994 | 44270.8095 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.0734 | 0:240:120 | 0:00 | 1.8617 | 7 | 0.0656 | 2.2423 | 2.3079 | 2.2688 | 0.0294 | 0.0009 | 3 | 1.8617 | 2.3769 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3058 | 30855.869 | 44270.8096 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.9949 | 0:240:120 | 0:00 | 1.7797 | 7 | 0.0618 | 2.1426 | 2.2044 | 2.1674 | 0.0274 | 0.0007 | 3 | 1.7797 | 2.2688 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3061 | 30865.788 | 44270.8097 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.9548 | 0:240:120 | 0:00 | 1.7017 | 7 | 0.0504 | 2.0532 | 2.1036 | 2.0702 | 0.0244 | 0.0006 | 3 | 1.7017 | 2.1662 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3064 | 30875.438 | 44270.8099 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.9539 | 0:240:120 | 0:00 | 1.6274 | 7 | 0.0609 | 1.9533 | 2.0142 | 1.9781 | 0.0269 | 0.0007 | 3 | 1.6274 | 2.069 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3067 | 30884.347 | 44270.81 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.993 | 0:240:120 | 0:00 | 1.5568 | 7 | 0.0457 | 1.8743 | 1.92 | 1.8902 | 0.0219 | 0.0005 | 3 | 1.5568 | 1.9766 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3070 | 30893.081 | 44270.8101 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.0728 | 0:240:120 | 0:00 | 1.4895 | 7 | 0.0532 | 1.7845 | 1.8377 | 1.806 | 0.0233 | 0.0005 | 3 | 1.4895 | 1.8889 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3073 | 30901.524 | 44270.8102 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 108.1943 | 0:240:120 | 0:00 | 1.4255 | 7 | 0.049 | 1.7089 | 1.7579 | 1.7281 | 0.022 | 0.0005 | 3 | 1.4255 | 1.8055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3076 | 30909.606 | 44270.8103 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.3582 | 0:240:120 | 0:00 | 1.3644 | 7 | 0.0465 | 1.6338 | 1.6803 | 1.6524 | 0.0209 | 0.0004 | 3 | 1.3644 | 1.7262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3079 | 30917.6 | 44270.8103 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.5654 | 0:240:120 | 0:00 | 1.3062 | 7 | 0.0438 | 1.564 | 1.6078 | 1.581 | 0.0196 | 0.0004 | 3 | 1.3062 | 1.6508 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3082 | 30925.227 | 44270.8104 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.8167 | 0:240:120 | 0:00 | 1.2507 | 7 | 0.0397 | 1.4966 | 1.5363 | 1.5121 | 0.018 | 0.0003 | 3 | 1.2507 | 1.5791 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3085 | 30932.654 | 44270.8105 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.113 | 0:240:120 | 0:00 | 1.1977 | 7 | 0.0387 | 1.4317 | 1.4704 | 1.4467 | 0.0175 | 0.0003 | 3 | 1.1977 | 1.5107 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3088 | 30939.811 | 44270.8106 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.4553 | 0:240:120 | 0:00 | 1.1471 | 7 | 0.0313 | 1.3734 | 1.4047 | 1.3843 | 0.0151 | 0.0002 | 3 | 1.1471 | 1.4457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3091 | 30946.979 | 44270.8107 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.8444 | 0:240:120 | 0:00 | 1.0989 | 7 | 0.0341 | 1.3131 | 1.3472 | 1.3254 | 0.0157 | 0.0002 | 3 | 1.0989 | 1.3836 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3094 | 30953.927 | 44270.8108 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.2812 | 0:240:120 | 0:00 | 1.0528 | 7 | 0.0288 | 1.2577 | 1.2865 | 1.2678 | 0.0139 | 0.0002 | 3 | 1.0528 | 1.3245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3097 | 30960.635 | 44270.8108 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.7669 | 0:240:120 | 0:00 | 1.0088 | 7 | 0.0296 | 1.2042 | 1.2338 | 1.2153 | 0.0131 | 0.0002 | 3 | 1.0088 | 1.2682 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3100 | 30967.093 | 44270.8109 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 129.3022 | 0:240:120 | 0:00 | 0.9668 | 7 | 0.0269 | 1.1549 | 1.1818 | 1.1647 | 0.0126 | 0.0002 | 3 | 0.9668 | 1.2144 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3103 | 30973.434 | 44270.811 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131.8883 | 0:240:120 | 0:00 | 0.9266 | 7 | 0.0271 | 1.1048 | 1.1319 | 1.1145 | 0.013 | 0.0002 | 3 | 0.9266 | 1.1631 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3106 | 30979.758 | 44270.8111 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.526 | 0:240:120 | 0:00 | 0.8882 | 7 | 0.0256 | 1.0584 | 1.084 | 1.0682 | 0.0115 | 0.0001 | 3 | 0.8882 | 1.1141 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3109 | 30985.868 | 44270.8111 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.2165 | 0:240:120 | 0:00 | 0.8515 | 7 | 0.0239 | 1.0138 | 1.0377 | 1.0231 | 0.0109 | 0.0001 | 3 | 0.8515 | 1.0674 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3112 | 30991.937 | 44270.8112 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 139.9609 | 0:240:120 | 0:00 | 0.8164 | 7 | 0.0222 | 0.9737 | 0.9959 | 0.9818 | 0.0103 | 0.0001 | 3 | 0.8164 | 1.0227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3115 | 30997.729 | 44270.8113 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.7601 | 0:240:120 | 0:00 | 0.7828 | 7 | 0.0213 | 0.9324 | 0.9537 | 0.9404 | 0.01 | 0.0001 | 3 | 0.7828 | 0.98 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3118 | 31003.517 | 44270.8113 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 145.6153 | 0:240:120 | 0:00 | 0.7507 | 7 | 0.0221 | 0.8934 | 0.9155 | 0.9017 | 0.0101 | 0.0001 | 3 | 0.7507 | 0.9393 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3121 | 31009.13 | 44270.8114 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.5276 | 0:240:120 | 0:00 | 0.7199 | 7 | 0.0188 | 0.8578 | 0.8766 | 0.8646 | 0.0089 | 0.0001 | 3 | 0.7199 | 0.9003 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3124 | 31014.774 | 44270.8115 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 151.4981 | 0:240:120 | 0:00 | 0.6905 | 7 | 0.0176 | 0.8222 | 0.8398 | 0.8286 | 0.0082 | 0.0001 | 3 | 0.6905 | 0.8631 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3127 | 31020.422 | 44270.8115 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 154.5281 | 0:240:120 | 0:00 | 0.6624 | 7 | 0.0169 | 0.7886 | 0.8055 | 0.7948 | 0.0078 | 0.0001 | 3 | 0.6624 | 0.8275 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3130 | 31025.775 | 44270.8116 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 157.6187 | 0:240:120 | 0:00 | 0.6354 | 7 | 0.0176 | 0.7561 | 0.7737 | 0.7624 | 0.008 | 0.0001 | 3 | 0.6354 | 0.7934 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3133 | 31030.864 | 44270.8117 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.771 | 0:240:120 | 0:00 | 0.6096 | 7 | 0.015 | 0.725 | 0.74 | 0.7311 | 0.0066 | 0 | 3 | 0.6096 | 0.7608 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3136 | 31035.968 | 44270.8117 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 163.9865 | 0:240:120 | 0:00 | 0.5849 | 7 | 0.0169 | 0.6942 | 0.7111 | 0.7009 | 0.0072 | 0.0001 | 3 | 0.5849 | 0.7296 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3139 | 31041.201 | 44270.8118 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 167.2662 | 0:240:120 | 0:00 | 0.5612 | 7 | 0.0144 | 0.667 | 0.6814 | 0.6724 | 0.0066 | 0 | 3 | 0.5612 | 0.6998 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3142 | 31046.272 | 44270.8118 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.6115 | 0:240:120 | 0:00 | 0.5385 | 7 | 0.0141 | 0.6411 | 0.6552 | 0.6462 | 0.0065 | 0 | 3 | 0.5385 | 0.6713 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3145 | 31051.373 | 44270.8119 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 174.0237 | 0:240:120 | 0:00 | 0.5168 | 7 | 0.0123 | 0.6151 | 0.6274 | 0.6194 | 0.0056 | 0 | 3 | 0.5168 | 0.6439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3148 | 31056.141 | 44270.812 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 177.5042 | 0:240:120 | 0:00 | 0.496 | 7 | 0.0133 | 0.5892 | 0.6025 | 0.5942 | 0.0054 | 0 | 3 | 0.496 | 0.6178 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3151 | 31060.996 | 44270.812 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 181.0543 | 0:240:120 | 0:00 | 0.476 | 7 | 0.0097 | 0.5659 | 0.5756 | 0.5697 | 0.0043 | 0 | 3 | 0.476 | 0.5927 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3154 | 31065.938 | 44270.8121 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 184.6754 | 0:240:120 | 0:00 | 0.4569 | 7 | 0.0109 | 0.5425 | 0.5534 | 0.5468 | 0.0046 | 0 | 3 | 0.4569 | 0.5687 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3157 | 31070.556 | 44270.8121 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 188.3689 | 0:240:120 | 0:00 | 0.4386 | 7 | 0.0093 | 0.5211 | 0.5304 | 0.5241 | 0.0043 | 0 | 3 | 0.4386 | 0.5457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3160 | 31075.023 | 44270.8122 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 192.1363 | 0:240:120 | 0:00 | 0.421 | 7 | 0.0083 | 0.5001 | 0.5084 | 0.5035 | 0.0035 | 0 | 3 | 0.421 | 0.5237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3163 | 31079.818 | 44270.8122 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 195.979 | 0:240:120 | 0:00 | 0.4041 | 7 | 0.0086 | 0.4799 | 0.4885 | 0.4832 | 0.0038 | 0 | 3 | 0.4041 | 0.5026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3166 | 31084.214 | 44270.8123 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 199.8986 | 0:240:120 | 0:00 | 0.388 | 7 | 0.0086 | 0.4614 | 0.47 | 0.4645 | 0.0036 | 0 | 3 | 0.388 | 0.4823 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3169 | 31088.587 | 44270.8123 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 203.8966 | 0:240:120 | 0:00 | 0.3725 | 7 | 0.0079 | 0.4427 | 0.4506 | 0.4454 | 0.0035 | 0 | 3 | 0.3725 | 0.4629 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3172 | 31092.888 | 44270.8124 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 207.9745 | 0:240:120 | 0:00 | 0.3576 | 7 | 0.0083 | 0.4242 | 0.4325 | 0.4274 | 0.0035 | 0 | 3 | 0.3576 | 0.4444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3175 | 31097.058 | 44270.8124 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 212.134 | 0:240:120 | 0:00 | 0.3434 | 7 | 0.0072 | 0.4082 | 0.4154 | 0.4109 | 0.003 | 0 | 3 | 0.3434 | 0.4265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3178 | 31101.256 | 44270.8125 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 216.3767 | 0:240:120 | 0:00 | 0.3297 | 7 | 0.0066 | 0.3918 | 0.3984 | 0.3943 | 0.0028 | 0 | 3 | 0.3297 | 0.4095 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3181 | 31105.561 | 44270.8125 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 220.7042 | 0:240:120 | 0:00 | 0.3166 | 7 | 0.0062 | 0.376 | 0.3822 | 0.3788 | 0.0025 | 0 | 3 | 0.3166 | 0.3931 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3184 | 31109.793 | 44270.8126 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 225.1183 | 0:240:120 | 0:00 | 0.304 | 7 | 0.0058 | 0.3617 | 0.3675 | 0.364 | 0.0022 | 0 | 3 | 0.304 | 0.3774 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3187 | 31113.834 | 44270.8126 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 229.6206 | 0:240:120 | 0:00 | 0.292 | 7 | 0.0046 | 0.3473 | 0.3519 | 0.3493 | 0.0018 | 0 | 3 | 0.292 | 0.3623 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3190 | 31117.945 | 44270.8127 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.2131 | 0:240:120 | 0:00 | 0.2804 | 7 | 0.0049 | 0.3338 | 0.3387 | 0.3358 | 0.0021 | 0 | 3 | 0.2804 | 0.3479 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3193 | 31122 | 44270.8127 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 238.8973 | 0:240:120 | 0:00 | 0.2693 | 7 | 0.0062 | 0.319 | 0.3252 | 0.3218 | 0.0025 | 0 | 3 | 0.2693 | 0.334 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3196 | 31125.986 | 44270.8128 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 243.6753 | 0:240:120 | 0:00 | 0.2586 | 7 | 0.0053 | 0.3067 | 0.312 | 0.309 | 0.0022 | 0 | 3 | 0.2586 | 0.3208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3199 | 31129.939 | 44270.8128 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 248.5488 | 0:240:120 | 0:00 | 0.2484 | 7 | 0.0051 | 0.2944 | 0.2995 | 0.2967 | 0.0021 | 0 | 3 | 0.2484 | 0.308 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3202 | 31133.885 | 44270.8129 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 253.5197 | 0:240:120 | 0:00 | 0.2386 | 7 | 0.0052 | 0.283 | 0.2882 | 0.2857 | 0.0019 | 0 | 3 | 0.2386 | 0.2958 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3205 | 31137.879 | 44270.8129 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 258.5901 | 0:240:120 | 0:00 | 0.2291 | 7 | 0.0048 | 0.2713 | 0.2761 | 0.2735 | 0.0016 | 0 | 3 | 0.2291 | 0.2841 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3208 | 31141.603 | 44270.8129 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 263.7619 | 0:240:120 | 0:00 | 0.2201 | 7 | 0.0042 | 0.2611 | 0.2653 | 0.2631 | 0.0015 | 0 | 3 | 0.2201 | 0.2728 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3211 | 31145.897 | 44270.813 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 269.0372 | 0:240:120 | 0:00 | 0.2114 | 7 | 0.0042 | 0.251 | 0.2552 | 0.2528 | 0.0015 | 0 | 3 | 0.2114 | 0.262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3214 | 31149.999 | 44270.813 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 274.4179 | 0:240:120 | 0:00 | 0.2031 | 7 | 0.0053 | 0.2406 | 0.2459 | 0.2427 | 0.0021 | 0 | 3 | 0.2031 | 0.2516 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3217 | 31153.78 | 44270.8131 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 279.9063 | 0:240:120 | 0:00 | 0.1951 | 7 | 0.004 | 0.2315 | 0.2355 | 0.2335 | 0.0015 | 0 | 3 | 0.1951 | 0.2417 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3220 | 31157.524 | 44270.8131 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 285.5044 | 0:240:120 | 0:00 | 0.1874 | 7 | 0.0038 | 0.2221 | 0.2259 | 0.2242 | 0.0015 | 0 | 3 | 0.1874 | 0.2321 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3223 | 31161.228 | 44270.8132 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 291.2145 | 0:240:120 | 0:00 | 0.18 | 7 | 0.0042 | 0.2124 | 0.2166 | 0.2149 | 0.0014 | 0 | 3 | 0.18 | 0.223 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3226 | 31165.146 | 44270.8132 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 297.0388 | 0:240:120 | 0:00 | 0.1729 | 7 | 0.0043 | 0.2052 | 0.2095 | 0.2072 | 0.0015 | 0 | 3 | 0.1729 | 0.2142 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3229 | 31168.627 | 44270.8133 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 302.9796 | 0:240:120 | 0:00 | 0.1661 | 7 | 0.0037 | 0.1971 | 0.2008 | 0.1988 | 0.0013 | 0 | 3 | 0.1661 | 0.2057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3232 | 31171.921 | 44270.8133 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 309.0392 | 0:240:120 | 0:00 | 0.1596 | 7 | 0.0041 | 0.1889 | 0.193 | 0.1908 | 0.0014 | 0 | 3 | 0.1596 | 0.1976 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3235 | 31175.495 | 44270.8133 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 315.2199 | 0:240:120 | 0:00 | 0.1533 | 7 | 0.0042 | 0.1814 | 0.1856 | 0.1836 | 0.0013 | 0 | 3 | 0.1533 | 0.1898 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3238 | 31179.008 | 44270.8134 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 321.5243 | 0:240:120 | 0:00 | 0.1473 | 7 | 0.0029 | 0.1752 | 0.1781 | 0.1766 | 0.001 | 0 | 3 | 0.1473 | 0.1824 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3241 | 31182.404 | 44270.8134 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 327.9548 | 0:240:120 | 0:00 | 0.1415 | 7 | 0.0041 | 0.1677 | 0.1718 | 0.1696 | 0.0015 | 0 | 3 | 0.1415 | 0.1752 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3244 | 31185.707 | 44270.8135 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 334.5139 | 0:240:120 | 0:00 | 0.136 | 7 | 0.0041 | 0.1613 | 0.1654 | 0.1635 | 0.0014 | 0 | 3 | 0.136 | 0.1683 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3247 | 31189.377 | 44270.8135 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 341.2042 | 0:240:120 | 0:00 | 0.1307 | 7 | 0.0032 | 0.1551 | 0.1583 | 0.1565 | 0.0013 | 0 | 3 | 0.1307 | 0.1617 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3250 | 31192.782 | 44270.8135 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 348.0283 | 0:240:120 | 0:00 | 0.1255 | 7 | 0.0035 | 0.1487 | 0.1522 | 0.1504 | 0.0013 | 0 | 3 | 0.1255 | 0.1553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3253 | 31196.091 | 44270.8136 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 354.9888 | 0:240:120 | 0:00 | 0.1206 | 7 | 0.0031 | 0.1429 | 0.146 | 0.1443 | 0.0011 | 0 | 3 | 0.1206 | 0.1492 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3256 | 31199.473 | 44270.8136 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 362.0886 | 0:240:120 | 0:00 | 0.1159 | 7 | 0.0027 | 0.1369 | 0.1396 | 0.1385 | 0.0009 | 0 | 3 | 0.1159 | 0.1434 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3259 | 31202.883 | 44270.8136 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 369.3304 | 0:240:120 | 0:00 | 0.1113 | 7 | 0.003 | 0.1315 | 0.1345 | 0.133 | 0.0011 | 0 | 3 | 0.1113 | 0.1377 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3262 | 31206.201 | 44270.8137 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 376.717 | 0:240:120 | 0:00 | 0.107 | 7 | 0.0032 | 0.1265 | 0.1297 | 0.1284 | 0.0014 | 0 | 3 | 0.107 | 0.1323 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3265 | 31209.533 | 44270.8137 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 384.2513 | 0:240:120 | 0:00 | 0.1028 | 7 | 0.0022 | 0.1222 | 0.1244 | 0.1232 | 0.0008 | 0 | 3 | 0.1028 | 0.1272 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3268 | 31212.831 | 44270.8138 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 391.9364 | 0:240:120 | 0:00 | 0.0988 | 7 | 0.0031 | 0.1168 | 0.1199 | 0.1184 | 0.0011 | 0 | 3 | 0.0988 | 0.1222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3271 | 31216.272 | 44270.8138 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 399.7751 | 0:240:120 | 0:00 | 0.0949 | 7 | 0.0029 | 0.112 | 0.1149 | 0.1135 | 0.0012 | 0 | 3 | 0.0949 | 0.1174 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3274 | 31219.556 | 44270.8138 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 407.7706 | 0:240:120 | 0:00 | 0.0912 | 7 | 0.0033 | 0.1079 | 0.1112 | 0.1097 | 0.0012 | 0 | 3 | 0.0912 | 0.1128 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3277 | 31223.338 | 44270.8139 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 415.926 | 0:240:120 | 0:00 | 0.0876 | 7 | 0.0017 | 0.1043 | 0.106 | 0.1052 | 0.0008 | 0 | 3 | 0.0876 | 0.1084 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3280 | 31226.627 | 44270.8139 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 424.2445 | 0:240:120 | 0:00 | 0.0842 | 7 | 0.0028 | 0.1002 | 0.103 | 0.1017 | 0.0009 | 0 | 3 | 0.0842 | 0.1041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3283 | 31229.97 | 44270.814 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 432.7294 | 0:240:120 | 0:00 | 0.0809 | 7 | 0.0026 | 0.096 | 0.0986 | 0.0975 | 0.001 | 0 | 3 | 0.0809 | 0.1001 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3286 | 31233.197 | 44270.814 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 441.384 | 0:240:120 | 0:00 | 0.0778 | 7 | 0.003 | 0.0918 | 0.0948 | 0.0932 | 0.0011 | 0 | 3 | 0.0778 | 0.0961 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3289 | 31236.71 | 44270.814 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 450.2117 | 0:240:120 | 0:00 | 0.0747 | 7 | 0.003 | 0.0881 | 0.0911 | 0.0897 | 0.0011 | 0 | 3 | 0.0747 | 0.0924 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3292 | 31240.039 | 44270.8141 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 459.2159 | 0:240:120 | 0:00 | 0.0718 | 7 | 0.0036 | 0.0854 | 0.089 | 0.0871 | 0.0013 | 0 | 3 | 0.0718 | 0.0888 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3295 | 31243.387 | 44270.8141 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 468.4002 | 0:240:120 | 0:00 | 0.069 | 7 | 0.003 | 0.0813 | 0.0843 | 0.0831 | 0.0013 | 0 | 3 | 0.069 | 0.0853 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3298 | 31247.073 | 44270.8142 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 477.7682 | 0:240:120 | 0:00 | 0.0663 | 7 | 0.0021 | 0.079 | 0.0811 | 0.08 | 0.0008 | 0 | 3 | 0.0663 | 0.082 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3301 | 31250.586 | 44270.8142 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 487.3236 | 0:240:120 | 0:00 | 0.0637 | 7 | 0.0039 | 0.0748 | 0.0787 | 0.0764 | 0.0014 | 0 | 3 | 0.0637 | 0.0788 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3304 | 31253.917 | 44270.8142 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 497.0701 | 0:240:120 | 0:00 | 0.0612 | 7 | 0.0024 | 0.0733 | 0.0757 | 0.0747 | 0.0008 | 0 | 3 | 0.0612 | 0.0757 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3307 | 31257.385 | 44270.8143 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 507.0115 | 0:240:120 | 0:00 | 0.0589 | 7 | 0.0027 | 0.0701 | 0.0728 | 0.0714 | 0.001 | 0 | 3 | 0.0589 | 0.0727 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3310 | 31260.684 | 44270.8143 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 517.1517 | 0:240:120 | 0:00 | 0.0566 | 7 | 0.0032 | 0.067 | 0.0702 | 0.0686 | 0.0012 | 0 | 3 | 0.0566 | 0.0699 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3313 | 31263.906 | 44270.8144 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 527.4947 | 0:240:120 | 0:00 | 0.0544 | 7 | 0.0032 | 0.064 | 0.0672 | 0.0659 | 0.0012 | 0 | 3 | 0.0544 | 0.0672 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3316 | 31267.185 | 44270.8144 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 538.0446 | 0:240:120 | 0:00 | 0.0522 | 7 | 0.0031 | 0.0616 | 0.0647 | 0.0634 | 0.0012 | 0 | 3 | 0.0522 | 0.0645 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3319 | 31270.666 | 44270.8144 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 548.8055 | 0:240:120 | 0:00 | 0.0502 | 7 | 0.0027 | 0.0597 | 0.0624 | 0.0615 | 0.0011 | 0 | 3 | 0.0502 | 0.062 | P | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3322 | 31273.944 | 44270.8145 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 559.7816 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0022 | 0.0573 | 0.0595 | 0.0585 | 0.0008 | 0 | 3 | 0.0482 | 0.0596 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3325 | 31277.134 | 44270.8145 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 570.9773 | 0:240:120 | 0:00 | 0.0464 | 7 | 0.003 | 0.0548 | 0.0578 | 0.0565 | 0.0009 | 0 | 3 | 0.0464 | 0.0573 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3328 | 31280.315 | 44270.8145 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 582.3968 | 0:240:120 | 0:00 | 0.0446 | 7 | 0.0033 | 0.0525 | 0.0558 | 0.0541 | 0.0012 | 0 | 3 | 0.0446 | 0.0551 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3331 | 31283.615 | 44270.8146 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 594.0448 | 0:240:120 | 0:00 | 0.0428 | 7 | 0.0034 | 0.0502 | 0.0536 | 0.0523 | 0.0012 | 0 | 3 | 0.0428 | 0.0529 | P | NP | 0-1-0-0-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3334 | 31286.926 | 44270.8146 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 605.9257 | 0:240:120 | 0:00 | 0.0412 | 7 | 0.0035 | 0.0481 | 0.0516 | 0.0501 | 0.0013 | 0 | 3 | 0.0412 | 0.0512 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3337 | 31290.126 | 44270.8147 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 618.0442 | 0:240:120 | 0:00 | 0.0395 | 7 | 0.0027 | 0.0467 | 0.0494 | 0.0484 | 0.001 | 0 | 3 | 0.0395 | 0.0495 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3340 | 31293.315 | 44270.8147 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 630.4051 | 0:240:120 | 0:00 | 0.038 | 7 | 0.0025 | 0.0452 | 0.0477 | 0.0466 | 0.0011 | 0 | 3 | 0.038 | 0.048 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3343 | 31296.587 | 44270.8147 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 643.0132 | 0:240:120 | 0:00 | 0.0365 | 7 | 0.003 | 0.0432 | 0.0462 | 0.0447 | 0.0011 | 0 | 3 | 0.0365 | 0.0465 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3346 | 31300.012 | 44270.8148 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 655.8734 | 0:240:120 | 0:00 | 0.0351 | 7 | 0.0016 | 0.0419 | 0.0435 | 0.0429 | 0.0006 | 0 | 3 | 0.0351 | 0.0451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3349 | 31303.633 | 44270.8148 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 668.9909 | 0:240:120 | 0:00 | 0.0337 | 7 | 0.0029 | 0.0397 | 0.0426 | 0.0415 | 0.0012 | 0 | 3 | 0.0337 | 0.0437 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3352 | 31306.793 | 44270.8149 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 682.3707 | 0:240:120 | 0:00 | 0.0324 | 7 | 0.0022 | 0.0386 | 0.0408 | 0.0399 | 0.0007 | 0 | 3 | 0.0324 | 0.0424 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3355 | 31309.806 | 44270.8149 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 696.0181 | 0:240:120 | 0:00 | 0.0312 | 7 | 0.003 | 0.0369 | 0.0399 | 0.0388 | 0.0009 | 0 | 3 | 0.0312 | 0.0412 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3358 | 31313.138 | 44270.8149 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 709.9385 | 0:240:120 | 0:00 | 0.03 | 7 | 0.0031 | 0.0357 | 0.0388 | 0.0372 | 0.0011 | 0 | 3 | 0.03 | 0.04 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3361 | 31316.468 | 44270.815 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 724.1372 | 0:240:120 | 0:00 | 0.0288 | 7 | 0.0038 | 0.0332 | 0.037 | 0.0356 | 0.0013 | 0 | 3 | 0.0288 | 0.0388 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3364 | 31319.657 | 44270.815 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 738.62 | 0:240:120 | 0:00 | 0.0277 | 7 | 0.0039 | 0.0327 | 0.0366 | 0.0346 | 0.0012 | 0 | 3 | 0.0277 | 0.0377 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3367 | 31322.986 | 44270.815 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 753.3924 | 0:240:120 | 0:00 | 0.0266 | 7 | 0.003 | 0.0314 | 0.0344 | 0.0334 | 0.001 | 0 | 3 | 0.0266 | 0.0366 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3370 | 31326.117 | 44270.8151 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 768.4602 | 0:240:120 | 0:00 | 0.0256 | 7 | 0.0025 | 0.0309 | 0.0334 | 0.0322 | 0.001 | 0 | 3 | 0.0256 | 0.0356 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3373 | 31329.108 | 44270.8151 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 783.8294 | 0:240:120 | 0:00 | 0.0246 | 7 | 0.0026 | 0.029 | 0.0316 | 0.0308 | 0.001 | 0 | 3 | 0.0246 | 0.0346 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3376 | 31332.108 | 44270.8151 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 799.506 | 0:240:120 | 0:00 | 0.0236 | 7 | 0.0028 | 0.0283 | 0.0311 | 0.03 | 0.001 | 0 | 3 | 0.0236 | 0.0336 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3379 | 31335.352 | 44270.8152 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 815.4962 | 0:240:120 | 0:00 | 0.0227 | 7 | 0.0022 | 0.0278 | 0.03 | 0.029 | 0.0008 | 0 | 3 | 0.0227 | 0.0327 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3382 | 31338.546 | 44270.8152 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 831.8061 | 0:240:120 | 0:00 | 0.0218 | 7 | 0.003 | 0.0262 | 0.0292 | 0.028 | 0.0011 | 0 | 3 | 0.0218 | 0.0318 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3385 | 31341.545 | 44270.8153 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 848.4422 | 0:240:120 | 0:00 | 0.021 | 7 | 0.0034 | 0.0247 | 0.0281 | 0.0268 | 0.0013 | 0 | 3 | 0.021 | 0.031 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3388 | 31344.542 | 44270.8153 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 865.411 | 0:240:120 | 0:00 | 0.0201 | 7 | 0.0036 | 0.024 | 0.0276 | 0.0264 | 0.0012 | 0 | 3 | 0.0201 | 0.0301 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3391 | 31347.754 | 44270.8153 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 882.7193 | 0:240:120 | 0:00 | 0.0194 | 7 | 0.0031 | 0.024 | 0.0271 | 0.0256 | 0.0011 | 0 | 3 | 0.0194 | 0.0294 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3394 | 31350.738 | 44270.8154 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 900.3736 | 0:240:120 | 0:00 | 0.0186 | 7 | 0.0038 | 0.0223 | 0.0261 | 0.0242 | 0.0011 | 0 | 3 | 0.0186 | 0.0286 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3397 | 31353.832 | 44270.8154 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 918.3811 | 0:240:120 | 0:00 | 0.0179 | 7 | 0.0031 | 0.0223 | 0.0254 | 0.0244 | 0.0011 | 0 | 3 | 0.0179 | 0.0279 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3400 | 31356.963 | 44270.8154 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 936.7487 | 0:240:120 | 0:00 | 0.0172 | 7 | 0.0039 | 0.0217 | 0.0256 | 0.0239 | 0.0014 | 0 | 3 | 0.0172 | 0.0272 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3403 | 31360.151 | 44270.8155 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 955.4837 | 0:240:120 | 0:00 | 0.0165 | 7 | 0.0022 | 0.0223 | 0.0245 | 0.0233 | 0.0007 | 0 | 3 | 0.0165 | 0.0265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3406 | 31363.34 | 44270.8155 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 974.5934 | 0:240:120 | 0:00 | 0.0159 | 7 | 0.0041 | 0.02 | 0.0241 | 0.0224 | 0.0017 | 0 | 3 | 0.0159 | 0.0259 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3409 | 31366.635 | 44270.8155 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 994.0853 | 0:240:120 | 0:00 | 0.0153 | 7 | 0.003 | 0.0198 | 0.0228 | 0.0219 | 0.0011 | 0 | 3 | 0.0153 | 0.0253 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3412 | 31369.862 | 44270.8156 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1013.967 | 0:240:120 | 0:00 | 0.0147 | 7 | 0.004 | 0.0192 | 0.0232 | 0.0215 | 0.0015 | 0 | 3 | 0.0147 | 0.0247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3415 | 31373.066 | 44270.8156 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1034.2463 | 0:240:120 | 0:00 | 0.0141 | 7 | 0.003 | 0.0194 | 0.0224 | 0.0213 | 0.0011 | 0 | 3 | 0.0141 | 0.0241 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3418 | 31376.579 | 44270.8157 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1054.9312 | 0:240:120 | 0:00 | 0.0135 | 7 | 0.0036 | 0.0187 | 0.0223 | 0.0206 | 0.0012 | 0 | 3 | 0.0135 | 0.0235 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3421 | 31379.65 | 44270.8157 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1076.0299 | 0:240:120 | 0:00 | 0.013 | 7 | 0.0033 | 0.018 | 0.0213 | 0.0199 | 0.0012 | 0 | 3 | 0.013 | 0.023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3424 | 31382.902 | 44270.8157 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1097.5505 | 0:240:120 | 0:00 | 0.0125 | 7 | 0.0034 | 0.0182 | 0.0216 | 0.02 | 0.0011 | 0 | 3 | 0.0125 | 0.0225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3427 | 31386.119 | 44270.8158 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1119.5015 | 0:240:120 | 0:00 | 0.012 | 7 | 0.0027 | 0.0186 | 0.0213 | 0.0197 | 0.0009 | 0 | 3 | 0.012 | 0.022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3430 | 31389.319 | 44270.8158 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1141.8915 | 0:240:120 | 0:00 | 0.0116 | 7 | 0.0025 | 0.0181 | 0.0206 | 0.0192 | 0.001 | 0 | 3 | 0.0116 | 0.0216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3433 | 31392.331 | 44270.8158 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1164.7293 | 0:240:120 | 0:00 | 0.0111 | 7 | 0.0018 | 0.0175 | 0.0193 | 0.0184 | 0.0006 | 0 | 3 | 0.0111 | 0.0211 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3436 | 31395.553 | 44270.8159 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1188.0239 | 0:240:120 | 0:00 | 0.0107 | 7 | 0.0012 | 0.0177 | 0.0189 | 0.0181 | 0.0005 | 0 | 3 | 0.0107 | 0.0207 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3439 | 31398.571 | 44270.8159 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1211.7844 | 0:240:120 | 0:00 | 0.0103 | 7 | 0.0021 | 0.0171 | 0.0192 | 0.0181 | 0.0006 | 0 | 3 | 0.0103 | 0.0203 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3442 | 31401.534 | 44270.8159 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1227.7273 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0011 | 0.0167 | 0.0178 | 0.0172 | 0.0004 | 0 | 3 | 0.01 | 0.02 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3445 | 31404.714 | 44270.816 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1252.2819 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0019 | 0.0163 | 0.0182 | 0.0174 | 0.0005 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3448 | 31407.843 | 44270.816 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1277.3275 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0021 | 0.016 | 0.0181 | 0.017 | 0.0008 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 1-0-0-0-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
3451 | 31411.158 | 44270.8161 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1302.8741 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0018 | 0.016 | 0.0178 | 0.0166 | 0.0007 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 1-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3454 | 31414.27 | 44270.8161 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1328.9315 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0017 | 0.0149 | 0.0166 | 0.0158 | 0.0007 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3457 | 31417.25 | 44270.8161 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1355.5102 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0026 | 0.0145 | 0.0171 | 0.0156 | 0.001 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3460 | 31420.431 | 44270.8162 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1382.6204 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0028 | 0.0142 | 0.017 | 0.0153 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3463 | 31423.868 | 44270.8162 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1410.2728 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0041 | 0.0129 | 0.017 | 0.015 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3466 | 31427.192 | 44270.8162 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1438.4782 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0036 | 0.0131 | 0.0167 | 0.0146 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3469 | 31430.515 | 44270.8163 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1467.2478 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0039 | 0.0122 | 0.0161 | 0.0141 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3472 | 31433.807 | 44270.8163 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1496.5928 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0041 | 0.0121 | 0.0162 | 0.0144 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3475 | 31437.126 | 44270.8164 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1526.5246 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0052 | 0.0113 | 0.0165 | 0.0142 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3478 | 31440.308 | 44270.8164 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1557.0551 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.004 | 0.0114 | 0.0154 | 0.014 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3481 | 31443.388 | 44270.8164 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1588.1962 | 0:240:120 | 0:00 | 0.006 | 7 | 0.004 | 0.0117 | 0.0157 | 0.014 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3484 | 31446.408 | 44270.8165 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1619.9601 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0041 | 0.0116 | 0.0157 | 0.0138 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3487 | 31449.519 | 44270.8165 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1652.3593 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0049 | 0.0111 | 0.016 | 0.0139 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3490 | 31452.708 | 44270.8165 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1685.4065 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0051 | 0.0112 | 0.0163 | 0.0136 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3493 | 31456.349 | 44270.8166 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1719.1146 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.005 | 0.0109 | 0.0159 | 0.0134 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3496 | 31459.62 | 44270.8166 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1753.4969 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0054 | 0.0109 | 0.0163 | 0.0134 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3499 | 31462.71 | 44270.8167 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1788.5669 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0038 | 0.0111 | 0.0149 | 0.0133 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3502 | 31465.707 | 44270.8167 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1824.3382 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0035 | 0.0113 | 0.0148 | 0.0134 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3505 | 31468.818 | 44270.8167 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1860.825 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.0053 | 0.0105 | 0.0158 | 0.0133 | 0.0022 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3508 | 31471.912 | 44270.8168 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1898.0415 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0041 | 0.0113 | 0.0154 | 0.0134 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3511 | 31475.026 | 44270.8168 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1936.0023 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0038 | 0.011 | 0.0148 | 0.0129 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3514 | 31478.241 | 44270.8168 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1974.7224 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0048 | 0.0104 | 0.0152 | 0.013 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3517 | 31481.657 | 44270.8169 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2014.2168 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0033 | 0.011 | 0.0143 | 0.0128 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3520 | 31484.937 | 44270.8169 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2054.5011 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0028 | 0.0113 | 0.0141 | 0.0122 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3523 | 31487.926 | 44270.8169 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2095.5912 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0032 | 0.0104 | 0.0136 | 0.0124 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3526 | 31491.004 | 44270.817 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2137.503 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0037 | 0.01 | 0.0137 | 0.0117 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3529 | 31494.081 | 44270.817 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2180.253 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0033 | 0.0103 | 0.0136 | 0.0118 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3532 | 31497.425 | 44270.8171 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2223.8581 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0035 | 0.0099 | 0.0134 | 0.0113 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3535 | 31500.487 | 44270.8171 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2268.3353 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0026 | 0.01 | 0.0126 | 0.0113 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3538 | 31503.572 | 44270.8171 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2313.702 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0025 | 0.0101 | 0.0126 | 0.0112 | 0.0008 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3541 | 31506.675 | 44270.8172 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2359.976 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0029 | 0.0093 | 0.0122 | 0.0107 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3544 | 31509.867 | 44270.8172 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2407.1755 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0029 | 0.0095 | 0.0124 | 0.0107 | 0.0009 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3547 | 31513.075 | 44270.8172 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2455.319 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0027 | 0.0095 | 0.0122 | 0.0107 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3550 | 31516.073 | 44270.8173 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2455.4546 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0041 | 0.0092 | 0.0133 | 0.0108 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3553 | 31519.173 | 44270.8173 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2504.5637 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0028 | 0.0092 | 0.012 | 0.0106 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3556 | 31522.804 | 44270.8174 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2554.655 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0027 | 0.009 | 0.0117 | 0.0104 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3559 | 31525.986 | 44270.8174 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2605.7481 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0026 | 0.009 | 0.0116 | 0.0102 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3562 | 31529.172 | 44270.8174 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2657.8631 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0031 | 0.009 | 0.0121 | 0.0105 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3565 | 31532.239 | 44270.8175 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2711.0203 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0036 | 0.0089 | 0.0125 | 0.0101 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3568 | 31535.448 | 44270.8175 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2765.2407 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0022 | 0.0093 | 0.0115 | 0.0102 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3571 | 31538.452 | 44270.8175 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2820.5456 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0029 | 0.0094 | 0.0123 | 0.0105 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3574 | 31541.648 | 44270.8176 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2876.9565 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0027 | 0.0093 | 0.012 | 0.0105 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3577 | 31545.053 | 44270.8176 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2934.4956 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.003 | 0.0092 | 0.0122 | 0.0102 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3580 | 31548.125 | 44270.8176 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2993.1855 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0011 | 0.0097 | 0.0108 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3583 | 31551.123 | 44270.8177 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3053.0492 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0013 | 0.0099 | 0.0112 | 0.0107 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3586 | 31554.534 | 44270.8177 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3114.1102 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0011 | 0.0101 | 0.0112 | 0.0106 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3589 | 31557.724 | 44270.8178 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3176.3924 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0015 | 0.0093 | 0.0108 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3592 | 31560.794 | 44270.8178 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3239.9203 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0026 | 0.0089 | 0.0115 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3595 | 31563.983 | 44270.8178 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3304.7187 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.002 | 0.0094 | 0.0114 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3598 | 31567.06 | 44270.8179 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3370.813 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0013 | 0.0096 | 0.0109 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3601 | 31570.375 | 44270.8179 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3438.2293 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0015 | 0.0094 | 0.0109 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3604 | 31573.452 | 44270.8179 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3506.9939 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0016 | 0.0097 | 0.0113 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3607 | 31576.554 | 44270.818 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3577.1338 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0013 | 0.0095 | 0.0108 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3610 | 31580.076 | 44270.818 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3648.6764 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0018 | 0.0094 | 0.0112 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3613 | 31583.476 | 44270.8181 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3721.65 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0018 | 0.0091 | 0.0109 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3616 | 31586.462 | 44270.8181 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3796.083 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3619 | 31589.621 | 44270.8181 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3872.0046 | 0:240:120 | 0:00 | 0.001 | 7 | 0.001 | 0.0099 | 0.0109 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3622 | 31592.729 | 44270.8182 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3949.4447 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3625 | 31596.049 | 44270.8182 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4028.4336 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3628 | 31599.265 | 44270.8182 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4109.0023 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0022 | 0.0089 | 0.0111 | 0.0096 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3631 | 31602.273 | 44270.8183 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4191.1823 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0019 | 0.0095 | 0.0114 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3634 | 31605.277 | 44270.8183 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4275.006 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0009 | 0.0097 | 0.0106 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3637 | 31608.61 | 44270.8183 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4360.5061 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0015 | 0.009 | 0.0105 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3640 | 31611.682 | 44270.8184 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4447.7162 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0011 | 0.0094 | 0.0105 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3643 | 31614.993 | 44270.8184 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4536.6705 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0055 | 0.0095 | 0.015 | 0.0103 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
3646 | 31618.299 | 44270.8185 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4627.4039 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0044 | 0.01 | 0.0144 | 0.0109 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3649 | 31621.487 | 44270.8185 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4719.952 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0012 | 0.0093 | 0.0105 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3652 | 31624.491 | 44270.8185 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4814.3511 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0013 | 0.01 | 0.0113 | 0.0105 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3655 | 31627.718 | 44270.8186 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4910.6381 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3658 | 31630.925 | 44270.8186 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5008.8508 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3661 | 31633.999 | 44270.8186 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5109.0279 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3664 | 31637.322 | 44270.8187 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5211.2084 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0014 | 0.0095 | 0.0109 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3667 | 31640.411 | 44270.8187 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5315.4326 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0017 | 0.0089 | 0.0106 | 0.0097 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3670 | 31643.504 | 44270.8187 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5421.7412 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3673 | 31646.663 | 44270.8188 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5530.1761 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0017 | 0.0093 | 0.011 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3676 | 31649.767 | 44270.8188 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5640.7796 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3679 | 31652.762 | 44270.8189 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5753.5952 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3682 | 31655.768 | 44270.8189 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5868.6671 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0015 | 0.0089 | 0.0104 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3685 | 31658.854 | 44270.8189 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5986.0404 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3688 | 31661.953 | 44270.819 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6105.7612 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3691 | 31664.957 | 44270.819 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6227.8765 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0013 | 0.0099 | 0.0112 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3694 | 31668.08 | 44270.819 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6352.434 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3697 | 31671.239 | 44270.8191 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6479.4827 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0014 | 0.0089 | 0.0103 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3700 | 31674.428 | 44270.8191 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6609.0723 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3703 | 31677.414 | 44270.8191 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6741.2538 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.0094 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3706 | 31680.408 | 44270.8192 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6876.0788 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3709 | 31683.378 | 44270.8192 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7013.6004 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0017 | 0.0093 | 0.011 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3712 | 31686.48 | 44270.8192 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7153.8724 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0088 | 0.0104 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3715 | 31689.579 | 44270.8193 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7296.9499 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3718 | 31692.609 | 44270.8193 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7442.8889 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0012 | 0.0088 | 0.01 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3721 | 31695.935 | 44270.8194 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7591.7466 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.001 | 0.01 | 0.011 | 0.0106 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3724 | 31698.933 | 44270.8194 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7743.5816 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3727 | 31701.929 | 44270.8194 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7898.4532 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.002 | 0.0091 | 0.0111 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3730 | 31705.133 | 44270.8195 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8056.4223 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3733 | 31708.61 | 44270.8195 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8217.5507 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0013 | 0.0096 | 0.0109 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3736 | 31711.631 | 44270.8195 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8381.9017 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0013 | 0.0099 | 0.0112 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3739 | 31714.746 | 44270.8196 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8549.5398 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3742 | 31717.93 | 44270.8196 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8720.5306 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0012 | 0.0093 | 0.0105 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3745 | 31721.052 | 44270.8196 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8894.9412 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0019 | 0.0088 | 0.0107 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3748 | 31724.431 | 44270.8197 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9072.84 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3751 | 31727.551 | 44270.8197 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9254.2968 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0002 | 0.0101 | 0.0103 | 0.0102 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3754 | 31730.777 | 44270.8198 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9439.3827 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.002 | 0.0089 | 0.0109 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3757 | 31733.773 | 44270.8198 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9628.1704 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3760 | 31736.875 | 44270.8198 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9820.7338 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0014 | 0.0098 | 0.0112 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3763 | 31739.937 | 44270.8199 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10017.1485 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3766 | 31743.109 | 44270.8199 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10217.4914 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3769 | 31746.183 | 44270.8199 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10421.8413 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0096 | 0.0109 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3772 | 31749.254 | 44270.82 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10630.2781 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3775 | 31752.523 | 44270.82 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10842.8837 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0007 | 0.0097 | 0.0104 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3778 | 31755.709 | 44270.82 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11059.7413 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.002 | 0.009 | 0.011 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3781 | 31759.016 | 44270.8201 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11280.9362 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0013 | 0.0095 | 0.0108 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3784 | 31762.208 | 44270.8201 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11506.5549 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3787 | 31765.403 | 44270.8202 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11736.686 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3790 | 31768.812 | 44270.8202 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11971.4197 | 0:240:120 | 0:00 | 0.0001 | 7 | 0.0012 | 0.0091 | 0.0103 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3793 | 32105.831 | 44270.8241 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39 | 0:240:120 | 0:00 | 39.5049 | 7 | 113.7473 | 240.8839 | 354.6312 | 279.4446 | 50.8585 | 2586.5853 | 3 | 39.5049 | 163.2313 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3796 | 33040.714 | 44270.8349 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.8 | 0:240:120 | 0:00 | 33.8998 | 7 | 107.4218 | 120.1241 | 227.5459 | 156.7451 | 51.9802 | 2701.9376 | 3 | 33.8998 | 105.0809 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3799 | 33567.586 | 44270.841 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.6 | 0:240:120 | 0:00 | 29.6128 | 7 | 13.1928 | 59.5002 | 72.693 | 63.775 | 6.2752 | 39.3787 | 3 | 29.6128 | 77.0682 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3802 | 33771.982 | 44270.8434 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.4 | 0:240:120 | 0:00 | 26.2298 | 7 | 4.5332 | 52.0339 | 56.5671 | 53.9155 | 1.9754 | 3.9021 | 3 | 26.2298 | 60.5936 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3805 | 33937.702 | 44270.8453 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.2 | 0:240:120 | 0:00 | 23.4935 | 7 | 5.1333 | 44.6542 | 49.7875 | 46.8838 | 2.2294 | 4.9704 | 3 | 23.4935 | 49.751 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3808 | 34083.171 | 44270.847 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.1 | 0:240:120 | 0:00 | 20.9811 | 7 | 6.2804 | 36.6121 | 42.8925 | 38.758 | 3.093 | 9.5665 | 3 | 20.9811 | 41.2734 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3811 | 34206.97 | 44270.8484 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.9 | 0:240:120 | 0:00 | 19.1267 | 7 | 5.1348 | 29.9786 | 35.1134 | 31.7005 | 2.5287 | 6.3942 | 3 | 19.1267 | 35.7504 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3814 | 34309.447 | 44270.8496 | Vista Speed | T | 15T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.8 | 0:240:120 | 0:00 | 17.3662 | 7 | 1.9105 | 27.0451 | 28.9556 | 27.8263 | 0.8534 | 0.7283 | 3 | 17.3662 | 30.9935 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3817 | 35207.189 | 44270.86 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.75 | 0:240:120 | 0:00 | 64.2676 | 7 | 90.3479 | 581.1702 | 671.5181 | 606.5965 | 40.1589 | 1612.7389 | 3 | 64.2676 | 9999999 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3820 | 37103.446 | 44270.8819 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.685 | 0:240:120 | 0:00 | 52.1322 | 7 | 98.0342 | 451.974 | 550.0082 | 489.5377 | 45.5718 | 2076.7933 | 3 | 52.1322 | 685.224 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3823 | 38634.896 | 44270.8997 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.6387 | 0:240:120 | 0:00 | 43.5723 | 7 | 108.2747 | 320.1114 | 428.3861 | 358.7788 | 52.2275 | 2727.7147 | 3 | 43.5723 | 221.6425 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3826 | 39798.693 | 44270.9131 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.6115 | 0:240:120 | 0:00 | 37.2148 | 7 | 116.7066 | 187.4207 | 304.1273 | 228.0386 | 56.9347 | 3241.5565 | 3 | 37.2148 | 130.0816 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3829 | 40576.781 | 44270.9221 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.6037 | 0:240:120 | 0:00 | 32.3101 | 7 | 103.1651 | 64.4126 | 167.5777 | 98.8515 | 51.3259 | 2634.3439 | 3 | 32.3101 | 90.9795 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3832 | 40976.045 | 44270.9268 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.6158 | 0:240:120 | 0:00 | 28.4141 | 7 | 4.2529 | 57.5463 | 61.7992 | 58.9498 | 2.0852 | 4.3481 | 3 | 28.4141 | 69.3049 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3835 | 41156.858 | 44270.9289 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.6481 | 0:240:120 | 0:00 | 25.2467 | 7 | 3.4992 | 50.7411 | 54.2403 | 51.9353 | 1.7217 | 2.9644 | 3 | 25.2467 | 55.5391 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3838 | 41315.768 | 44270.9307 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.7011 | 0:240:120 | 0:00 | 22.623 | 7 | 5.7073 | 41.772 | 47.4793 | 44.0725 | 2.5875 | 6.6953 | 3 | 22.623 | 46.0274 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3841 | 41453.877 | 44270.9323 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.7751 | 0:240:120 | 0:00 | 20.4157 | 7 | 6.2943 | 34.0415 | 40.3358 | 36.1631 | 3.085 | 9.517 | 3 | 20.4157 | 39.0665 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3844 | 41568.177 | 44270.9336 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.8706 | 0:240:120 | 0:00 | 18.5342 | 7 | 1.367 | 29.4794 | 30.8464 | 29.9596 | 0.6451 | 0.4162 | 3 | 18.5342 | 33.7553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3847 | 41661.361 | 44270.9347 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.988 | 0:240:120 | 0:00 | 16.9126 | 7 | 2.1163 | 26.3407 | 28.457 | 27.1797 | 0.9667 | 0.9344 | 3 | 16.9126 | 29.5725 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3850 | 41747.127 | 44270.9357 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.1277 | 0:240:120 | 0:00 | 15.5016 | 7 | 1.5565 | 24.003 | 25.5595 | 24.5215 | 0.7709 | 0.5943 | 3 | 15.5016 | 26.1953 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3853 | 41824.023 | 44270.9366 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.2903 | 0:240:120 | 0:00 | 14.2634 | 7 | 2.0157 | 20.8867 | 22.9024 | 21.6998 | 0.9084 | 0.8252 | 3 | 14.2634 | 23.4135 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3856 | 41892.5 | 44270.9374 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.4761 | 0:240:120 | 0:00 | 13.1691 | 7 | 0.7767 | 18.9596 | 19.7363 | 19.2432 | 0.3618 | 0.1309 | 3 | 13.1691 | 21.084 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3859 | 41953.261 | 44270.9381 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.6856 | 0:240:120 | 0:00 | 12.1957 | 7 | 1.0908 | 17.3656 | 18.4564 | 17.743 | 0.5353 | 0.2865 | 3 | 12.1957 | 19.1062 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3862 | 42009.73 | 44270.9387 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.9193 | 0:240:120 | 0:00 | 11.3247 | 7 | 1.0813 | 15.7364 | 16.8177 | 16.2432 | 0.4578 | 0.2096 | 3 | 11.3247 | 17.4074 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3865 | 42061.708 | 44270.9393 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.1777 | 0:240:120 | 0:00 | 10.5415 | 7 | 0.842 | 14.5042 | 15.3462 | 14.8276 | 0.3771 | 0.1422 | 3 | 10.5415 | 15.9334 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3868 | 42109.478 | 44270.9399 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.4613 | 0:240:120 | 0:00 | 9.8339 | 7 | 0.628 | 13.4077 | 14.0357 | 13.6189 | 0.3115 | 0.097 | 3 | 9.8339 | 14.6434 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3871 | 42153.668 | 44270.9404 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.7705 | 0:240:120 | 0:00 | 9.1919 | 7 | 0.6522 | 12.4327 | 13.0849 | 12.661 | 0.3177 | 0.1009 | 3 | 9.1919 | 13.5057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3874 | 42195.031 | 44270.9409 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.1059 | 0:240:120 | 0:00 | 8.6074 | 7 | 0.6519 | 11.4557 | 12.1076 | 11.688 | 0.3149 | 0.0991 | 3 | 8.6074 | 12.4957 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3877 | 42233.28 | 44270.9413 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.468 | 0:240:120 | 0:00 | 8.0732 | 7 | 0.5391 | 10.5889 | 11.128 | 10.7768 | 0.2634 | 0.0694 | 3 | 8.0732 | 11.5937 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3880 | 42269.041 | 44270.9417 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.8574 | 0:240:120 | 0:00 | 7.5836 | 7 | 0.425 | 9.9485 | 10.3735 | 10.1112 | 0.1981 | 0.0392 | 3 | 7.5836 | 10.7838 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3883 | 42302.514 | 44270.9421 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.2746 | 0:240:120 | 0:00 | 7.1334 | 7 | 0.4289 | 9.2995 | 9.7284 | 9.4456 | 0.2117 | 0.0448 | 3 | 7.1334 | 10.0531 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3886 | 42334.063 | 44270.9425 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.72 | 0:240:120 | 0:00 | 6.7185 | 7 | 0.4308 | 8.6532 | 9.084 | 8.7982 | 0.214 | 0.0458 | 3 | 6.7185 | 9.3911 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3889 | 42363.526 | 44270.9428 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.1944 | 0:240:120 | 0:00 | 6.3352 | 7 | 0.2955 | 8.1998 | 8.4953 | 8.2988 | 0.1472 | 0.0217 | 3 | 6.3352 | 8.7889 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3892 | 42391.532 | 44270.9431 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.6983 | 0:240:120 | 0:00 | 5.9802 | 7 | 0.3091 | 7.6822 | 7.9913 | 7.7948 | 0.1455 | 0.0212 | 3 | 5.9802 | 8.2393 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3895 | 42418.433 | 44270.9435 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.2323 | 0:240:120 | 0:00 | 5.6507 | 7 | 0.3043 | 7.145 | 7.4493 | 7.2531 | 0.1463 | 0.0214 | 3 | 5.6507 | 7.736 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3898 | 42443.491 | 44270.9437 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.7969 | 0:240:120 | 0:00 | 5.3444 | 7 | 0.2254 | 6.806 | 7.0314 | 6.8825 | 0.1114 | 0.0124 | 3 | 5.3444 | 7.2737 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3901 | 42467.073 | 44270.944 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.3929 | 0:240:120 | 0:00 | 5.0591 | 7 | 0.2492 | 6.3707 | 6.6199 | 6.4671 | 0.1128 | 0.0127 | 3 | 5.0591 | 6.8479 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3904 | 42489.579 | 44270.9443 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.0207 | 0:240:120 | 0:00 | 4.7929 | 7 | 0.2327 | 6.0194 | 6.2521 | 6.1012 | 0.1128 | 0.0127 | 3 | 4.7929 | 6.4548 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3907 | 42510.901 | 44270.9445 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.6812 | 0:240:120 | 0:00 | 4.5441 | 7 | 0.1831 | 5.6869 | 5.87 | 5.7548 | 0.0851 | 0.0072 | 3 | 4.5441 | 6.0911 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3910 | 42531.369 | 44270.9448 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.3748 | 0:240:120 | 0:00 | 4.3113 | 7 | 0.2385 | 5.3533 | 5.5918 | 5.4608 | 0.099 | 0.0098 | 3 | 4.3113 | 5.7537 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3913 | 42551.005 | 44270.945 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.1023 | 0:240:120 | 0:00 | 4.0931 | 7 | 0.156 | 5.1049 | 5.2609 | 5.1569 | 0.0772 | 0.006 | 3 | 4.0931 | 5.4402 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3916 | 42569.564 | 44270.9452 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.8643 | 0:240:120 | 0:00 | 3.8884 | 7 | 0.1354 | 4.838 | 4.9734 | 4.8842 | 0.0664 | 0.0044 | 3 | 3.8884 | 5.1484 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3919 | 42587.289 | 44270.9454 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.6616 | 0:240:120 | 0:00 | 3.696 | 7 | 0.1418 | 4.5706 | 4.7124 | 4.6201 | 0.0684 | 0.0047 | 3 | 3.696 | 4.8762 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3922 | 42604.273 | 44270.9456 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.4948 | 0:240:120 | 0:00 | 3.5151 | 7 | 0.1261 | 4.3398 | 4.4659 | 4.3837 | 0.0603 | 0.0036 | 3 | 3.5151 | 4.622 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3925 | 42620.751 | 44270.9458 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.3647 | 0:240:120 | 0:00 | 3.3448 | 7 | 0.1211 | 4.123 | 4.2441 | 4.1643 | 0.0583 | 0.0034 | 3 | 3.3448 | 4.3843 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3928 | 42636.535 | 44270.946 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.272 | 0:240:120 | 0:00 | 3.1843 | 7 | 0.1033 | 3.9148 | 4.0181 | 3.9494 | 0.0513 | 0.0026 | 3 | 3.1843 | 4.1615 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3931 | 42651.343 | 44270.9462 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.2175 | 0:240:120 | 0:00 | 3.0328 | 7 | 0.1143 | 3.7145 | 3.8288 | 3.7626 | 0.0497 | 0.0025 | 3 | 3.0328 | 3.9526 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3934 | 42665.58 | 44270.9463 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.2018 | 0:240:120 | 0:00 | 2.8899 | 7 | 0.1304 | 3.5198 | 3.6502 | 3.5748 | 0.0574 | 0.0033 | 3 | 2.8899 | 3.7564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3937 | 42679.316 | 44270.9465 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.2259 | 0:240:120 | 0:00 | 2.7547 | 7 | 0.086 | 3.3697 | 3.4557 | 3.399 | 0.0419 | 0.0018 | 3 | 2.7547 | 3.5719 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3940 | 42692.447 | 44270.9466 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.2904 | 0:240:120 | 0:00 | 2.6269 | 7 | 0.1049 | 3.1911 | 3.296 | 3.2355 | 0.0467 | 0.0022 | 3 | 2.6269 | 3.3983 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3943 | 42705.111 | 44270.9468 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.3962 | 0:240:120 | 0:00 | 2.506 | 7 | 0.0799 | 3.0535 | 3.1334 | 3.081 | 0.0381 | 0.0015 | 3 | 2.506 | 3.2347 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3946 | 42717.371 | 44270.9469 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.5441 | 0:240:120 | 0:00 | 2.3914 | 7 | 0.0939 | 2.9001 | 2.994 | 2.938 | 0.042 | 0.0018 | 3 | 2.3914 | 3.0804 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3949 | 42729.07 | 44270.9471 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.735 | 0:240:120 | 0:00 | 2.2829 | 7 | 0.0768 | 2.7616 | 2.8384 | 2.796 | 0.0323 | 0.001 | 3 | 2.2829 | 2.9348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3952 | 42740.562 | 44270.9472 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.9697 | 0:240:120 | 0:00 | 2.1799 | 7 | 0.0704 | 2.6392 | 2.7096 | 2.6687 | 0.0304 | 0.0009 | 3 | 2.1799 | 2.7972 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3955 | 42751.348 | 44270.9473 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.2491 | 0:240:120 | 0:00 | 2.0822 | 7 | 0.0677 | 2.5178 | 2.5855 | 2.5439 | 0.0302 | 0.0009 | 3 | 2.0822 | 2.6671 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3958 | 42761.981 | 44270.9474 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.5741 | 0:240:120 | 0:00 | 1.9894 | 7 | 0.0654 | 2.4015 | 2.4669 | 2.429 | 0.0278 | 0.0008 | 3 | 1.9894 | 2.544 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3961 | 42772.245 | 44270.9476 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.9455 | 0:240:120 | 0:00 | 1.9013 | 7 | 0.0587 | 2.2895 | 2.3482 | 2.3148 | 0.0248 | 0.0006 | 3 | 1.9013 | 2.4275 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3964 | 42782.121 | 44270.9477 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.3645 | 0:240:120 | 0:00 | 1.8175 | 7 | 0.059 | 2.1878 | 2.2468 | 2.2128 | 0.026 | 0.0007 | 3 | 1.8175 | 2.317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3967 | 42791.926 | 44270.9478 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.8317 | 0:240:120 | 0:00 | 1.7379 | 7 | 0.0542 | 2.0949 | 2.1491 | 2.1141 | 0.0256 | 0.0007 | 3 | 1.7379 | 2.2123 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3970 | 42801.417 | 44270.9479 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.3484 | 0:240:120 | 0:00 | 1.6621 | 7 | 0.0561 | 1.9937 | 2.0498 | 2.0181 | 0.0236 | 0.0006 | 3 | 1.6621 | 2.113 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3973 | 42810.377 | 44270.948 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.9153 | 0:240:120 | 0:00 | 1.5899 | 7 | 0.0465 | 1.9139 | 1.9604 | 1.9308 | 0.0219 | 0.0005 | 3 | 1.5899 | 2.0186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3976 | 42819.249 | 44270.9481 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.5336 | 0:240:120 | 0:00 | 1.5212 | 7 | 0.0467 | 1.8236 | 1.8703 | 1.8428 | 0.021 | 0.0004 | 3 | 1.5212 | 1.9291 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3979 | 42827.782 | 44270.9482 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.2043 | 0:240:120 | 0:00 | 1.4558 | 7 | 0.0458 | 1.7453 | 1.7911 | 1.763 | 0.0202 | 0.0004 | 3 | 1.4558 | 1.8439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3982 | 42835.978 | 44270.9483 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.9284 | 0:240:120 | 0:00 | 1.3934 | 7 | 0.0478 | 1.6675 | 1.7153 | 1.6865 | 0.0207 | 0.0004 | 3 | 1.3934 | 1.763 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3985 | 42843.95 | 44270.9484 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.707 | 0:240:120 | 0:00 | 1.334 | 7 | 0.0466 | 1.5947 | 1.6413 | 1.6137 | 0.0205 | 0.0004 | 3 | 1.334 | 1.6859 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3988 | 42851.997 | 44270.9485 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.5411 | 0:240:120 | 0:00 | 1.2773 | 7 | 0.0391 | 1.5283 | 1.5674 | 1.5438 | 0.0176 | 0.0003 | 3 | 1.2773 | 1.6127 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3991 | 42860.111 | 44270.9486 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.4319 | 0:240:120 | 0:00 | 1.2232 | 7 | 0.0357 | 1.4626 | 1.4983 | 1.4771 | 0.0161 | 0.0003 | 3 | 1.2232 | 1.5429 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3994 | 42867.684 | 44270.9487 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.3806 | 0:240:120 | 0:00 | 1.1715 | 7 | 0.0336 | 1.4023 | 1.4359 | 1.415 | 0.0149 | 0.0002 | 3 | 1.1715 | 1.4764 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3997 | 42874.775 | 44270.9487 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.3882 | 0:240:120 | 0:00 | 1.1223 | 7 | 0.0324 | 1.341 | 1.3734 | 1.354 | 0.0143 | 0.0002 | 3 | 1.1223 | 1.4131 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4000 | 42881.739 | 44270.9488 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.456 | 0:240:120 | 0:00 | 1.0752 | 7 | 0.0337 | 1.2817 | 1.3154 | 1.2951 | 0.015 | 0.0002 | 3 | 1.0752 | 1.3527 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4003 | 42888.388 | 44270.9489 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 159.5851 | 0:240:120 | 0:00 | 1.0303 | 7 | 0.0246 | 1.2324 | 1.257 | 1.242 | 0.0111 | 0.0001 | 3 | 1.0303 | 1.2951 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4006 | 42895.047 | 44270.949 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 162.7768 | 0:240:120 | 0:00 | 0.9873 | 7 | 0.0243 | 1.1799 | 1.2042 | 1.1894 | 0.0103 | 0.0001 | 3 | 0.9873 | 1.2402 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4009 | 42901.667 | 44270.9491 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.0323 | 0:240:120 | 0:00 | 0.9463 | 7 | 0.0229 | 1.1289 | 1.1518 | 1.1384 | 0.0101 | 0.0001 | 3 | 0.9463 | 1.1878 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4012 | 42907.979 | 44270.9491 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.353 | 0:240:120 | 0:00 | 0.9071 | 7 | 0.0222 | 1.0824 | 1.1046 | 1.0909 | 0.0102 | 0.0001 | 3 | 0.9071 | 1.1378 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4015 | 42914.199 | 44270.9492 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 172.74 | 0:240:120 | 0:00 | 0.8696 | 7 | 0.0239 | 1.0354 | 1.0593 | 1.0447 | 0.0106 | 0.0001 | 3 | 0.8696 | 1.0901 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4018 | 42920.377 | 44270.9493 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176.1948 | 0:240:120 | 0:00 | 0.8338 | 7 | 0.0171 | 0.9952 | 1.0123 | 1.0017 | 0.0076 | 0.0001 | 3 | 0.8338 | 1.0445 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4021 | 42926.335 | 44270.9493 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 179.7187 | 0:240:120 | 0:00 | 0.7995 | 7 | 0.0221 | 0.9515 | 0.9736 | 0.9602 | 0.0096 | 0.0001 | 3 | 0.7995 | 1.0009 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4024 | 42932.273 | 44270.9494 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.3131 | 0:240:120 | 0:00 | 0.7667 | 7 | 0.0198 | 0.9116 | 0.9314 | 0.9195 | 0.0087 | 0.0001 | 3 | 0.7667 | 0.9593 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4027 | 42937.91 | 44270.9495 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 186.9793 | 0:240:120 | 0:00 | 0.7353 | 7 | 0.0166 | 0.8755 | 0.8921 | 0.8822 | 0.0074 | 0.0001 | 3 | 0.7353 | 0.9195 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4030 | 42943.618 | 44270.9495 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 190.7189 | 0:240:120 | 0:00 | 0.7052 | 7 | 0.016 | 0.8389 | 0.8549 | 0.8455 | 0.0069 | 0 | 3 | 0.7052 | 0.8814 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4033 | 42949.174 | 44270.9496 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.5333 | 0:240:120 | 0:00 | 0.6765 | 7 | 0.0163 | 0.806 | 0.8223 | 0.8118 | 0.0071 | 0.0001 | 3 | 0.6765 | 0.8451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4036 | 42954.566 | 44270.9497 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 198.424 | 0:240:120 | 0:00 | 0.6489 | 7 | 0.0125 | 0.7731 | 0.7856 | 0.7778 | 0.0056 | 0 | 3 | 0.6489 | 0.8103 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4039 | 42959.834 | 44270.9497 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 202.3925 | 0:240:120 | 0:00 | 0.6226 | 7 | 0.0143 | 0.7406 | 0.7549 | 0.7461 | 0.0065 | 0 | 3 | 0.6226 | 0.777 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4042 | 42965.035 | 44270.9498 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 206.4403 | 0:240:120 | 0:00 | 0.5973 | 7 | 0.0133 | 0.7103 | 0.7236 | 0.7158 | 0.0056 | 0 | 3 | 0.5973 | 0.7452 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4045 | 42970.272 | 44270.9498 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 210.5691 | 0:240:120 | 0:00 | 0.5731 | 7 | 0.0122 | 0.6811 | 0.6933 | 0.6858 | 0.0054 | 0 | 3 | 0.5731 | 0.7147 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4048 | 42975.309 | 44270.9499 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 214.7805 | 0:240:120 | 0:00 | 0.55 | 7 | 0.012 | 0.6535 | 0.6655 | 0.6586 | 0.0052 | 0 | 3 | 0.55 | 0.6855 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4051 | 42980.309 | 44270.95 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 219.0761 | 0:240:120 | 0:00 | 0.5278 | 7 | 0.0123 | 0.627 | 0.6393 | 0.6317 | 0.0053 | 0 | 3 | 0.5278 | 0.6576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4054 | 42985.041 | 44270.95 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.4576 | 0:240:120 | 0:00 | 0.5065 | 7 | 0.0099 | 0.6028 | 0.6127 | 0.6066 | 0.004 | 0 | 3 | 0.5065 | 0.6309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4057 | 42990.092 | 44270.9501 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 227.9268 | 0:240:120 | 0:00 | 0.4861 | 7 | 0.0098 | 0.5781 | 0.5879 | 0.5817 | 0.0042 | 0 | 3 | 0.4861 | 0.6053 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4060 | 42995.008 | 44270.9501 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 232.4853 | 0:240:120 | 0:00 | 0.4666 | 7 | 0.008 | 0.555 | 0.563 | 0.5582 | 0.0034 | 0 | 3 | 0.4666 | 0.5808 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4063 | 42999.648 | 44270.9502 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.135 | 0:240:120 | 0:00 | 0.4479 | 7 | 0.0074 | 0.5334 | 0.5408 | 0.536 | 0.0035 | 0 | 3 | 0.4479 | 0.5573 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4066 | 43004.306 | 44270.9502 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 241.8777 | 0:240:120 | 0:00 | 0.4299 | 7 | 0.0075 | 0.5105 | 0.518 | 0.5133 | 0.0035 | 0 | 3 | 0.4299 | 0.5348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4069 | 43008.682 | 44270.9503 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.7153 | 0:240:120 | 0:00 | 0.4127 | 7 | 0.0073 | 0.4907 | 0.498 | 0.4936 | 0.0033 | 0 | 3 | 0.4127 | 0.5132 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4072 | 43013.263 | 44270.9503 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 251.6496 | 0:240:120 | 0:00 | 0.3962 | 7 | 0.0063 | 0.4711 | 0.4774 | 0.4733 | 0.0029 | 0 | 3 | 0.3962 | 0.4926 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4075 | 43017.88 | 44270.9504 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.6826 | 0:240:120 | 0:00 | 0.3804 | 7 | 0.0068 | 0.4517 | 0.4585 | 0.4549 | 0.0026 | 0 | 3 | 0.3804 | 0.4728 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4078 | 43022.24 | 44270.9504 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 261.8162 | 0:240:120 | 0:00 | 0.3653 | 7 | 0.0055 | 0.4347 | 0.4402 | 0.4366 | 0.0026 | 0 | 3 | 0.3653 | 0.4538 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4081 | 43026.507 | 44270.9505 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 267.0526 | 0:240:120 | 0:00 | 0.3507 | 7 | 0.0049 | 0.4167 | 0.4216 | 0.4188 | 0.0019 | 0 | 3 | 0.3507 | 0.4356 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4084 | 43030.965 | 44270.9505 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 272.3936 | 0:240:120 | 0:00 | 0.3367 | 7 | 0.0052 | 0.3999 | 0.4051 | 0.4018 | 0.0025 | 0 | 3 | 0.3367 | 0.4182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4087 | 43035.324 | 44270.9506 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 277.8415 | 0:240:120 | 0:00 | 0.3234 | 7 | 0.0062 | 0.3844 | 0.3906 | 0.3866 | 0.0025 | 0 | 3 | 0.3234 | 0.4015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4090 | 43039.886 | 44270.9507 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 283.3983 | 0:240:120 | 0:00 | 0.3105 | 7 | 0.0049 | 0.369 | 0.3739 | 0.3709 | 0.002 | 0 | 3 | 0.3105 | 0.3854 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4093 | 43044.068 | 44270.9507 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 289.0663 | 0:240:120 | 0:00 | 0.2982 | 7 | 0.0049 | 0.3538 | 0.3587 | 0.356 | 0.0019 | 0 | 3 | 0.2982 | 0.37 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4096 | 43047.921 | 44270.9507 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.8476 | 0:240:120 | 0:00 | 0.2864 | 7 | 0.0045 | 0.3406 | 0.3451 | 0.3421 | 0.0019 | 0 | 3 | 0.2864 | 0.3553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4099 | 43051.893 | 44270.9508 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 300.7445 | 0:240:120 | 0:00 | 0.275 | 7 | 0.0054 | 0.3259 | 0.3313 | 0.3283 | 0.0022 | 0 | 3 | 0.275 | 0.3412 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4102 | 43055.839 | 44270.9508 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 306.7594 | 0:240:120 | 0:00 | 0.2641 | 7 | 0.0042 | 0.3134 | 0.3176 | 0.3156 | 0.0016 | 0 | 3 | 0.2641 | 0.3276 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4105 | 43059.771 | 44270.9509 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 312.8946 | 0:240:120 | 0:00 | 0.2537 | 7 | 0.0037 | 0.3014 | 0.3051 | 0.3028 | 0.0017 | 0 | 3 | 0.2537 | 0.3146 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4108 | 43063.727 | 44270.9509 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 319.1525 | 0:240:120 | 0:00 | 0.2436 | 7 | 0.0034 | 0.2899 | 0.2933 | 0.2915 | 0.0013 | 0 | 3 | 0.2436 | 0.3021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4111 | 43067.423 | 44270.951 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 325.5356 | 0:240:120 | 0:00 | 0.234 | 7 | 0.0037 | 0.2782 | 0.2819 | 0.2796 | 0.0017 | 0 | 3 | 0.234 | 0.2901 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4114 | 43071.235 | 44270.951 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 332.0463 | 0:240:120 | 0:00 | 0.2248 | 7 | 0.0032 | 0.2666 | 0.2698 | 0.268 | 0.0012 | 0 | 3 | 0.2248 | 0.2786 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4117 | 43075.189 | 44270.9511 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 338.6872 | 0:240:120 | 0:00 | 0.2159 | 7 | 0.0042 | 0.2562 | 0.2604 | 0.2582 | 0.0013 | 0 | 3 | 0.2159 | 0.2676 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4120 | 43079.001 | 44270.9511 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 345.461 | 0:240:120 | 0:00 | 0.2074 | 7 | 0.0045 | 0.2461 | 0.2506 | 0.2478 | 0.0019 | 0 | 3 | 0.2074 | 0.257 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4123 | 43082.937 | 44270.9511 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 352.3702 | 0:240:120 | 0:00 | 0.1992 | 7 | 0.0046 | 0.2366 | 0.2412 | 0.2385 | 0.0017 | 0 | 3 | 0.1992 | 0.2468 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4126 | 43086.746 | 44270.9512 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 359.4176 | 0:240:120 | 0:00 | 0.1914 | 7 | 0.0036 | 0.2278 | 0.2314 | 0.2289 | 0.0015 | 0 | 3 | 0.1914 | 0.2371 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4129 | 43090.592 | 44270.9512 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 366.6059 | 0:240:120 | 0:00 | 0.1839 | 7 | 0.0041 | 0.2183 | 0.2224 | 0.2198 | 0.0015 | 0 | 3 | 0.1839 | 0.2277 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4132 | 43094.555 | 44270.9513 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 373.938 | 0:240:120 | 0:00 | 0.1766 | 7 | 0.003 | 0.2099 | 0.2129 | 0.2111 | 0.0013 | 0 | 3 | 0.1766 | 0.2187 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4135 | 43097.999 | 44270.9513 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 381.4168 | 0:240:120 | 0:00 | 0.1697 | 7 | 0.0035 | 0.2018 | 0.2053 | 0.2031 | 0.0014 | 0 | 3 | 0.1697 | 0.2101 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4138 | 43101.494 | 44270.9514 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 389.0451 | 0:240:120 | 0:00 | 0.163 | 7 | 0.0036 | 0.1935 | 0.1971 | 0.195 | 0.0014 | 0 | 3 | 0.163 | 0.2018 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4141 | 43105.123 | 44270.9514 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 396.826 | 0:240:120 | 0:00 | 0.1566 | 7 | 0.0027 | 0.1865 | 0.1892 | 0.1875 | 0.0011 | 0 | 3 | 0.1566 | 0.1939 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4144 | 43108.459 | 44270.9514 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 404.7626 | 0:240:120 | 0:00 | 0.1505 | 7 | 0.0032 | 0.1791 | 0.1823 | 0.1805 | 0.0012 | 0 | 3 | 0.1505 | 0.1862 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4147 | 43111.938 | 44270.9515 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 412.8578 | 0:240:120 | 0:00 | 0.1445 | 7 | 0.0039 | 0.1713 | 0.1752 | 0.1731 | 0.0014 | 0 | 3 | 0.1445 | 0.1789 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4150 | 43115.314 | 44270.9515 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 421.115 | 0:240:120 | 0:00 | 0.1389 | 7 | 0.0029 | 0.1646 | 0.1675 | 0.1659 | 0.0012 | 0 | 3 | 0.1389 | 0.1719 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4153 | 43118.698 | 44270.9516 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 429.5373 | 0:240:120 | 0:00 | 0.1334 | 7 | 0.0029 | 0.1585 | 0.1614 | 0.1597 | 0.001 | 0 | 3 | 0.1334 | 0.1651 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4156 | 43122.174 | 44270.9516 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 438.128 | 0:240:120 | 0:00 | 0.1282 | 7 | 0.0035 | 0.1518 | 0.1553 | 0.1531 | 0.0014 | 0 | 3 | 0.1282 | 0.1586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4159 | 43125.494 | 44270.9516 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 446.8906 | 0:240:120 | 0:00 | 0.1232 | 7 | 0.0037 | 0.1454 | 0.1491 | 0.1474 | 0.0011 | 0 | 3 | 0.1232 | 0.1524 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4162 | 43128.892 | 44270.9517 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 455.8284 | 0:240:120 | 0:00 | 0.1184 | 7 | 0.0021 | 0.1409 | 0.143 | 0.1419 | 0.0008 | 0 | 3 | 0.1184 | 0.1464 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4165 | 43132.153 | 44270.9517 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 464.945 | 0:240:120 | 0:00 | 0.1137 | 7 | 0.0024 | 0.1349 | 0.1373 | 0.1361 | 0.0009 | 0 | 3 | 0.1137 | 0.1407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4168 | 43135.427 | 44270.9518 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 474.2439 | 0:240:120 | 0:00 | 0.1093 | 7 | 0.0033 | 0.1298 | 0.1331 | 0.1308 | 0.0013 | 0 | 3 | 0.1093 | 0.1352 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4171 | 43138.874 | 44270.9518 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 483.7287 | 0:240:120 | 0:00 | 0.105 | 7 | 0.0029 | 0.1246 | 0.1275 | 0.126 | 0.0009 | 0 | 3 | 0.105 | 0.1299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4174 | 43142.338 | 44270.9518 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 493.4033 | 0:240:120 | 0:00 | 0.1009 | 7 | 0.0017 | 0.1202 | 0.1219 | 0.1209 | 0.0007 | 0 | 3 | 0.1009 | 0.1248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4177 | 43145.633 | 44270.9519 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 503.2714 | 0:240:120 | 0:00 | 0.0969 | 7 | 0.0032 | 0.1151 | 0.1183 | 0.1167 | 0.0012 | 0 | 3 | 0.0969 | 0.1199 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4180 | 43148.971 | 44270.9519 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 513.3368 | 0:240:120 | 0:00 | 0.0931 | 7 | 0.0029 | 0.1103 | 0.1132 | 0.1119 | 0.0011 | 0 | 3 | 0.0931 | 0.1152 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4183 | 43152.257 | 44270.952 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 523.6035 | 0:240:120 | 0:00 | 0.0895 | 7 | 0.0029 | 0.1065 | 0.1094 | 0.1078 | 0.001 | 0 | 3 | 0.0895 | 0.1107 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4186 | 43155.577 | 44270.952 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 534.0756 | 0:240:120 | 0:00 | 0.086 | 7 | 0.0039 | 0.1016 | 0.1055 | 0.1037 | 0.0013 | 0 | 3 | 0.086 | 0.1063 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4189 | 43158.763 | 44270.952 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 544.7571 | 0:240:120 | 0:00 | 0.0826 | 7 | 0.0022 | 0.0982 | 0.1004 | 0.0995 | 0.0008 | 0 | 3 | 0.0826 | 0.1022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4192 | 43162.056 | 44270.9521 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 555.6523 | 0:240:120 | 0:00 | 0.0794 | 7 | 0.003 | 0.0941 | 0.0971 | 0.0955 | 0.0012 | 0 | 3 | 0.0794 | 0.0982 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4195 | 43165.783 | 44270.9521 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 566.7653 | 0:240:120 | 0:00 | 0.0763 | 7 | 0.0023 | 0.0905 | 0.0928 | 0.0915 | 0.0009 | 0 | 3 | 0.0763 | 0.0943 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4198 | 43169.315 | 44270.9521 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 578.1006 | 0:240:120 | 0:00 | 0.0733 | 7 | 0.0017 | 0.0875 | 0.0892 | 0.0886 | 0.0006 | 0 | 3 | 0.0733 | 0.0907 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4201 | 43172.664 | 44270.9522 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 589.6626 | 0:240:120 | 0:00 | 0.0705 | 7 | 0.003 | 0.0837 | 0.0867 | 0.0851 | 0.001 | 0 | 3 | 0.0705 | 0.0871 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4204 | 43175.99 | 44270.9522 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 601.4559 | 0:240:120 | 0:00 | 0.0677 | 7 | 0.0033 | 0.0801 | 0.0834 | 0.0814 | 0.0013 | 0 | 3 | 0.0677 | 0.0837 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4207 | 43179.464 | 44270.9523 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 613.485 | 0:240:120 | 0:00 | 0.0651 | 7 | 0.003 | 0.0771 | 0.0801 | 0.0787 | 0.0011 | 0 | 3 | 0.0651 | 0.0804 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4210 | 43182.811 | 44270.9523 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 625.7547 | 0:240:120 | 0:00 | 0.0625 | 7 | 0.0024 | 0.0737 | 0.0761 | 0.0753 | 0.001 | 0 | 3 | 0.0625 | 0.0773 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4213 | 43186.321 | 44270.9523 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 638.2698 | 0:240:120 | 0:00 | 0.0601 | 7 | 0.0023 | 0.0712 | 0.0735 | 0.0725 | 0.0008 | 0 | 3 | 0.0601 | 0.0743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4216 | 43189.956 | 44270.9524 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 651.0352 | 0:240:120 | 0:00 | 0.0578 | 7 | 0.0035 | 0.0678 | 0.0713 | 0.0696 | 0.0013 | 0 | 3 | 0.0578 | 0.0714 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4219 | 43193.18 | 44270.9524 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 664.0559 | 0:240:120 | 0:00 | 0.0555 | 7 | 0.0036 | 0.065 | 0.0686 | 0.0667 | 0.0013 | 0 | 3 | 0.0555 | 0.0686 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4222 | 43196.692 | 44270.9525 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 677.337 | 0:240:120 | 0:00 | 0.0533 | 7 | 0.0029 | 0.063 | 0.0659 | 0.0646 | 0.001 | 0 | 3 | 0.0533 | 0.0659 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4225 | 43200.073 | 44270.9525 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 690.8837 | 0:240:120 | 0:00 | 0.0513 | 7 | 0.0032 | 0.0599 | 0.0631 | 0.0617 | 0.0011 | 0 | 3 | 0.0513 | 0.0633 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4228 | 43203.402 | 44270.9525 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 704.7014 | 0:240:120 | 0:00 | 0.0493 | 7 | 0.0015 | 0.0585 | 0.06 | 0.0596 | 0.0006 | 0 | 3 | 0.0493 | 0.0609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4231 | 43206.871 | 44270.9526 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 718.7954 | 0:240:120 | 0:00 | 0.0473 | 7 | 0.0036 | 0.0551 | 0.0587 | 0.0571 | 0.0013 | 0 | 3 | 0.0473 | 0.0585 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4234 | 43210.349 | 44270.9526 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 733.1714 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0036 | 0.0533 | 0.0569 | 0.0552 | 0.0014 | 0 | 3 | 0.0455 | 0.0562 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4237 | 43213.59 | 44270.9527 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 747.8348 | 0:240:120 | 0:00 | 0.0437 | 7 | 0.003 | 0.0514 | 0.0544 | 0.0533 | 0.0012 | 0 | 3 | 0.0437 | 0.054 | P | NP | 0-1-0-0-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
4240 | 43216.738 | 44270.9527 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 762.7915 | 0:240:120 | 0:00 | 0.042 | 7 | 0.0033 | 0.0495 | 0.0528 | 0.0514 | 0.0011 | 0 | 3 | 0.042 | 0.052 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4243 | 43220.006 | 44270.9527 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 778.0473 | 0:240:120 | 0:00 | 0.0404 | 7 | 0.0023 | 0.0483 | 0.0506 | 0.0496 | 0.0008 | 0 | 3 | 0.0404 | 0.0504 | P | NP | 0-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4246 | 43223.064 | 44270.9528 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 793.6083 | 0:240:120 | 0:00 | 0.0388 | 7 | 0.003 | 0.046 | 0.049 | 0.0475 | 0.0013 | 0 | 3 | 0.0388 | 0.0488 | P | NP | 1-1-1-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4249 | 43226.21 | 44270.9528 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 809.4804 | 0:240:120 | 0:00 | 0.0373 | 7 | 0.0032 | 0.044 | 0.0472 | 0.0456 | 0.0011 | 0 | 3 | 0.0373 | 0.0473 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4252 | 43229.352 | 44270.9528 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 825.67 | 0:240:120 | 0:00 | 0.0359 | 7 | 0.0026 | 0.0419 | 0.0445 | 0.0436 | 0.0011 | 0 | 3 | 0.0359 | 0.0459 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4255 | 43232.597 | 44270.9529 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 842.1834 | 0:240:120 | 0:00 | 0.0345 | 7 | 0.0028 | 0.0411 | 0.0439 | 0.0422 | 0.001 | 0 | 3 | 0.0345 | 0.0445 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4258 | 43236.05 | 44270.9529 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 859.0271 | 0:240:120 | 0:00 | 0.0331 | 7 | 0.0028 | 0.0391 | 0.0419 | 0.0408 | 0.0011 | 0 | 3 | 0.0331 | 0.0431 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4261 | 43239.338 | 44270.953 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 876.2076 | 0:240:120 | 0:00 | 0.0318 | 7 | 0.003 | 0.0372 | 0.0402 | 0.0389 | 0.001 | 0 | 3 | 0.0318 | 0.0418 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4264 | 43242.588 | 44270.953 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 893.7318 | 0:240:120 | 0:00 | 0.0306 | 7 | 0.0025 | 0.0365 | 0.039 | 0.038 | 0.0009 | 0 | 3 | 0.0306 | 0.0406 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4267 | 43245.939 | 44270.953 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 911.6064 | 0:240:120 | 0:00 | 0.0294 | 7 | 0.0037 | 0.0344 | 0.0381 | 0.0366 | 0.0014 | 0 | 3 | 0.0294 | 0.0394 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4270 | 43249.228 | 44270.9531 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 929.8386 | 0:240:120 | 0:00 | 0.0283 | 7 | 0.0028 | 0.0334 | 0.0362 | 0.035 | 0.0009 | 0 | 3 | 0.0283 | 0.0383 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4273 | 43252.416 | 44270.9531 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 948.4353 | 0:240:120 | 0:00 | 0.0272 | 7 | 0.0029 | 0.0327 | 0.0356 | 0.0341 | 0.0009 | 0 | 3 | 0.0272 | 0.0372 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4276 | 43255.792 | 44270.9532 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 967.404 | 0:240:120 | 0:00 | 0.0261 | 7 | 0.0028 | 0.0306 | 0.0334 | 0.0326 | 0.001 | 0 | 3 | 0.0261 | 0.0361 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4279 | 43259.141 | 44270.9532 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 986.7521 | 0:240:120 | 0:00 | 0.0251 | 7 | 0.0016 | 0.0312 | 0.0328 | 0.0321 | 0.0006 | 0 | 3 | 0.0251 | 0.0351 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4282 | 43262.475 | 44270.9532 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1006.4872 | 0:240:120 | 0:00 | 0.0241 | 7 | 0.002 | 0.0295 | 0.0315 | 0.0309 | 0.0008 | 0 | 3 | 0.0241 | 0.0341 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4285 | 43265.889 | 44270.9533 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1026.6169 | 0:240:120 | 0:00 | 0.0232 | 7 | 0.003 | 0.0275 | 0.0305 | 0.0294 | 0.001 | 0 | 3 | 0.0232 | 0.0332 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4288 | 43269.136 | 44270.9533 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1047.1492 | 0:240:120 | 0:00 | 0.0223 | 7 | 0.0032 | 0.0263 | 0.0295 | 0.0282 | 0.001 | 0 | 3 | 0.0223 | 0.0323 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4291 | 43271.94 | 44270.9533 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1068.0922 | 0:240:120 | 0:00 | 0.0214 | 7 | 0.0029 | 0.0258 | 0.0287 | 0.0275 | 0.0012 | 0 | 3 | 0.0214 | 0.0314 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4294 | 43275.13 | 44270.9534 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1089.4541 | 0:240:120 | 0:00 | 0.0206 | 7 | 0.0028 | 0.0252 | 0.028 | 0.0268 | 0.0008 | 0 | 3 | 0.0206 | 0.0306 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4297 | 43278.468 | 44270.9534 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1111.2432 | 0:240:120 | 0:00 | 0.0198 | 7 | 0.003 | 0.0245 | 0.0275 | 0.0258 | 0.0009 | 0 | 3 | 0.0198 | 0.0298 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4300 | 43281.839 | 44270.9535 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1133.468 | 0:240:120 | 0:00 | 0.019 | 7 | 0.0018 | 0.0242 | 0.026 | 0.0254 | 0.0008 | 0 | 3 | 0.019 | 0.029 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4303 | 43284.946 | 44270.9535 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1156.1374 | 0:240:120 | 0:00 | 0.0183 | 7 | 0.0031 | 0.0227 | 0.0258 | 0.0244 | 0.0011 | 0 | 3 | 0.0183 | 0.0283 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4306 | 43287.991 | 44270.9535 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1179.2601 | 0:240:120 | 0:00 | 0.0176 | 7 | 0.0024 | 0.0232 | 0.0256 | 0.0245 | 0.0008 | 0 | 3 | 0.0176 | 0.0276 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4309 | 43291.368 | 44270.9536 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1202.8453 | 0:240:120 | 0:00 | 0.0169 | 7 | 0.0036 | 0.0213 | 0.0249 | 0.0234 | 0.0011 | 0 | 3 | 0.0169 | 0.0269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4312 | 43294.634 | 44270.9536 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1226.9022 | 0:240:120 | 0:00 | 0.0162 | 7 | 0.0027 | 0.0211 | 0.0238 | 0.0229 | 0.0011 | 0 | 3 | 0.0162 | 0.0262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4315 | 43297.652 | 44270.9536 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1251.4403 | 0:240:120 | 0:00 | 0.0156 | 7 | 0.0029 | 0.0209 | 0.0238 | 0.0224 | 0.001 | 0 | 3 | 0.0156 | 0.0256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4318 | 43300.588 | 44270.9537 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1276.4691 | 0:240:120 | 0:00 | 0.015 | 7 | 0.003 | 0.0197 | 0.0227 | 0.0217 | 0.001 | 0 | 3 | 0.015 | 0.025 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4321 | 43303.536 | 44270.9537 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1301.9985 | 0:240:120 | 0:00 | 0.0144 | 7 | 0.0025 | 0.0202 | 0.0227 | 0.0215 | 0.0009 | 0 | 3 | 0.0144 | 0.0244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4324 | 43306.55 | 44270.9537 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1328.0384 | 0:240:120 | 0:00 | 0.0138 | 7 | 0.0029 | 0.0192 | 0.0221 | 0.021 | 0.0012 | 0 | 3 | 0.0138 | 0.0238 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4327 | 43310.145 | 44270.9538 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1354.5992 | 0:240:120 | 0:00 | 0.0133 | 7 | 0.004 | 0.0183 | 0.0223 | 0.0205 | 0.0014 | 0 | 3 | 0.0133 | 0.0233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4330 | 43313.388 | 44270.9538 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1381.6912 | 0:240:120 | 0:00 | 0.0128 | 7 | 0.0037 | 0.0182 | 0.0219 | 0.0202 | 0.0014 | 0 | 3 | 0.0128 | 0.0228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4333 | 43316.564 | 44270.9539 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1409.325 | 0:240:120 | 0:00 | 0.0123 | 7 | 0.004 | 0.0175 | 0.0215 | 0.0193 | 0.0013 | 0 | 3 | 0.0123 | 0.0223 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4336 | 43319.741 | 44270.9539 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1437.5115 | 0:240:120 | 0:00 | 0.0118 | 7 | 0.0028 | 0.0174 | 0.0202 | 0.0187 | 0.0011 | 0 | 3 | 0.0118 | 0.0218 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4339 | 43322.947 | 44270.9539 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1466.2617 | 0:240:120 | 0:00 | 0.0113 | 7 | 0.0025 | 0.0173 | 0.0198 | 0.0186 | 0.001 | 0 | 3 | 0.0113 | 0.0213 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4342 | 43325.963 | 44270.954 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1495.587 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0023 | 0.0177 | 0.02 | 0.0186 | 0.0007 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4345 | 43328.945 | 44270.954 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1525.4987 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0017 | 0.0173 | 0.019 | 0.018 | 0.0006 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4348 | 43332.122 | 44270.954 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1556.0087 | 0:240:120 | 0:00 | 0.0101 | 7 | 0.0015 | 0.0173 | 0.0188 | 0.0178 | 0.0005 | 0 | 3 | 0.0101 | 0.0201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4351 | 43335.216 | 44270.9541 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1561.9082 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0019 | 0.0164 | 0.0183 | 0.0172 | 0.0006 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4354 | 43338.507 | 44270.9541 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1593.1464 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0015 | 0.0165 | 0.018 | 0.017 | 0.0006 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4357 | 43341.438 | 44270.9541 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1625.0093 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0011 | 0.0163 | 0.0174 | 0.0167 | 0.0003 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4360 | 43344.4 | 44270.9542 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1657.5095 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0021 | 0.0158 | 0.0179 | 0.0168 | 0.0008 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 0-0-0-1-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4363 | 43347.471 | 44270.9542 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1690.6597 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0027 | 0.0149 | 0.0176 | 0.0161 | 0.0009 | 0 | 3 | 0.0085 | 0.016 | NP | NP | 1-0-1-1-0-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4366 | 43350.422 | 44270.9542 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1724.4729 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0028 | 0.0146 | 0.0174 | 0.0158 | 0.0009 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-0-0-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4369 | 43353.777 | 44270.9543 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1758.9624 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0036 | 0.0142 | 0.0178 | 0.0157 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
4372 | 43356.967 | 44270.9543 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1794.1416 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0035 | 0.0132 | 0.0167 | 0.0149 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4375 | 43360.157 | 44270.9544 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1830.0245 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0029 | 0.0127 | 0.0156 | 0.0144 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4378 | 43363.861 | 44270.9544 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1866.6249 | 0:240:120 | 0:00 | 0.007 | 7 | 0.004 | 0.0124 | 0.0164 | 0.0143 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4381 | 43367.234 | 44270.9544 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1903.9574 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0051 | 0.0119 | 0.017 | 0.0142 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4384 | 43370.3 | 44270.9545 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1942.0366 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0047 | 0.0117 | 0.0164 | 0.0142 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4387 | 43373.374 | 44270.9545 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1980.8773 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0052 | 0.0113 | 0.0165 | 0.0139 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4390 | 43376.751 | 44270.9546 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2020.4949 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0052 | 0.0114 | 0.0166 | 0.014 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4393 | 43379.722 | 44270.9546 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2060.9048 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0052 | 0.0117 | 0.0169 | 0.0139 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4396 | 43382.895 | 44270.9546 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2102.1229 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0055 | 0.0111 | 0.0166 | 0.0138 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4399 | 43386.272 | 44270.9547 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2144.1653 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0046 | 0.0108 | 0.0154 | 0.0134 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4402 | 43389.271 | 44270.9547 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2187.0486 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0056 | 0.0107 | 0.0163 | 0.0133 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4405 | 43392.241 | 44270.9547 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2230.7896 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0045 | 0.0109 | 0.0154 | 0.0134 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4408 | 43395.758 | 44270.9548 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2275.4054 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0052 | 0.0104 | 0.0156 | 0.0131 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4411 | 43399.047 | 44270.9548 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2320.9135 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0052 | 0.0103 | 0.0155 | 0.0128 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4414 | 43402.056 | 44270.9548 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2367.3318 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.0043 | 0.0108 | 0.0151 | 0.0131 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4417 | 43405.217 | 44270.9549 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2414.6784 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0034 | 0.0112 | 0.0146 | 0.0128 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4420 | 43408.487 | 44270.9549 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2462.972 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0033 | 0.0114 | 0.0147 | 0.0129 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4423 | 43411.446 | 44270.955 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2512.2314 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0052 | 0.0102 | 0.0154 | 0.0127 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4426 | 43415.04 | 44270.955 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2562.476 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0042 | 0.0106 | 0.0148 | 0.0128 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4429 | 43418.078 | 44270.955 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2613.7256 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0045 | 0.0101 | 0.0146 | 0.0123 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4432 | 43421.149 | 44270.9551 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2666.0001 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0041 | 0.0109 | 0.015 | 0.0128 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4435 | 43424.312 | 44270.9551 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2719.3201 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0023 | 0.0112 | 0.0135 | 0.0123 | 0.0009 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4438 | 43427.526 | 44270.9551 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2773.7065 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0035 | 0.0103 | 0.0138 | 0.0121 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4441 | 43430.494 | 44270.9552 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2829.1806 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0031 | 0.01 | 0.0131 | 0.0115 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4444 | 43433.463 | 44270.9552 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2885.7642 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0032 | 0.0097 | 0.0129 | 0.0111 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4447 | 43437.04 | 44270.9552 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2943.4795 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0029 | 0.0096 | 0.0125 | 0.0111 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4450 | 43440.13 | 44270.9553 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3002.3491 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0031 | 0.0094 | 0.0125 | 0.0107 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4453 | 43443.23 | 44270.9553 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3062.3961 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0045 | 0.01 | 0.0145 | 0.0116 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4456 | 43446.254 | 44270.9554 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3123.644 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.003 | 0.0096 | 0.0126 | 0.0107 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4459 | 43449.189 | 44270.9554 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3123.8165 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0032 | 0.0096 | 0.0128 | 0.0106 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4462 | 43452.15 | 44270.9554 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3186.2928 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0032 | 0.0097 | 0.0129 | 0.0106 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4465 | 43455.134 | 44270.9555 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3250.0187 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0033 | 0.0093 | 0.0126 | 0.0106 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4468 | 43458.296 | 44270.9555 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3315.0191 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0036 | 0.0093 | 0.0129 | 0.0105 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4471 | 43461.362 | 44270.9555 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3381.3194 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0033 | 0.0091 | 0.0124 | 0.0104 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4474 | 43464.433 | 44270.9556 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3448.9458 | 0:240:120 | 0:00 | 0.002 | 7 | 0.003 | 0.0092 | 0.0122 | 0.0105 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4477 | 43467.686 | 44270.9556 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3517.9247 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0028 | 0.009 | 0.0118 | 0.0103 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4480 | 43471.06 | 44270.9556 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3588.2832 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0041 | 0.0103 | 0.0144 | 0.0112 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4483 | 43474.05 | 44270.9557 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3660.0489 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0019 | 0.0099 | 0.0118 | 0.0107 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4486 | 43477.1 | 44270.9557 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3733.2499 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0023 | 0.0094 | 0.0117 | 0.0104 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4489 | 43480.154 | 44270.9557 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3807.9149 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0023 | 0.0091 | 0.0114 | 0.0102 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4492 | 43483.12 | 44270.9558 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3884.0732 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0051 | 0.0099 | 0.015 | 0.0111 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4495 | 43486.116 | 44270.9558 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3961.7546 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.006 | 0.009 | 0.015 | 0.0105 | 0.0019 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4498 | 43489.198 | 44270.9559 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4040.9897 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4501 | 43492.307 | 44270.9559 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4121.8095 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0053 | 0.0098 | 0.0151 | 0.0113 | 0.0022 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4504 | 43495.785 | 44270.9559 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4204.2457 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.004 | 0.0101 | 0.0141 | 0.0109 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4507 | 43499.257 | 44270.956 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4288.3306 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0004 | 0.0096 | 0.01 | 0.0098 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4510 | 43502.456 | 44270.956 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4374.0972 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4513 | 43505.7 | 44270.956 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4461.5792 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0095 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4516 | 43508.767 | 44270.9561 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4550.8108 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0053 | 0.009 | 0.0143 | 0.0106 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4519 | 43511.762 | 44270.9561 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4641.827 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0015 | 0.009 | 0.0105 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4522 | 43515.226 | 44270.9562 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4734.6635 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0053 | 0.0097 | 0.015 | 0.0109 | 0.0023 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4525 | 43518.233 | 44270.9562 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4829.3568 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0039 | 0.0101 | 0.014 | 0.0107 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4528 | 43521.391 | 44270.9562 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4925.9439 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0007 | 0.0098 | 0.0105 | 0.0101 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4531 | 43524.374 | 44270.9563 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5024.4628 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4534 | 43527.793 | 44270.9563 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5124.9521 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0053 | 0.0089 | 0.0142 | 0.0105 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4537 | 43531.032 | 44270.9563 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5227.4511 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0018 | 0.0096 | 0.0114 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4540 | 43534.022 | 44270.9564 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5332.0001 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0006 | 0.0101 | 0.0107 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4543 | 43537.304 | 44270.9564 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5438.6401 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4546 | 43540.383 | 44270.9564 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5547.4129 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.006 | 0.009 | 0.015 | 0.0105 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4549 | 43543.473 | 44270.9565 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5658.3612 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0015 | 0.0096 | 0.0111 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4552 | 43546.995 | 44270.9565 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5771.5284 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4555 | 43550.072 | 44270.9566 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5886.959 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0009 | 0.0097 | 0.0106 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4558 | 43553.355 | 44270.9566 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6004.6982 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0018 | 0.0091 | 0.0109 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4561 | 43556.648 | 44270.9566 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6124.7921 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0005 | 0.0099 | 0.0104 | 0.0101 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4564 | 43559.726 | 44270.9567 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6247.288 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0003 | 0.0095 | 0.0098 | 0.0097 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4567 | 43562.787 | 44270.9567 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6372.2337 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0014 | 0.0099 | 0.0113 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4570 | 43565.969 | 44270.9567 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6499.6784 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0015 | 0.0098 | 0.0113 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4573 | 43569.118 | 44270.9568 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6629.672 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4576 | 43572.102 | 44270.9568 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6762.2654 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0005 | 0.0094 | 0.0099 | 0.0096 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4579 | 43575.3 | 44270.9568 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6897.5107 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4582 | 43578.381 | 44270.9569 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7035.4609 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4585 | 43581.35 | 44270.9569 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7176.1702 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4588 | 43584.337 | 44270.957 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7319.6936 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0012 | 0.0099 | 0.0111 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4591 | 43587.366 | 44270.957 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7466.0874 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4594 | 43590.306 | 44270.957 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7615.4092 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.002 | 0.0091 | 0.0111 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4597 | 43593.388 | 44270.9571 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7767.7174 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4600 | 43596.475 | 44270.9571 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7923.0717 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4603 | 43599.453 | 44270.9571 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8081.5331 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0018 | 0.0096 | 0.0114 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4606 | 43602.436 | 44270.9572 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8243.1638 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0006 | 0.0097 | 0.0103 | 0.01 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4609 | 43605.472 | 44270.9572 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8408.0271 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4612 | 43608.564 | 44270.9572 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8576.1876 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0024 | 0.0089 | 0.0113 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4615 | 43611.82 | 44270.9573 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8747.7114 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0004 | 0.0103 | 0.0107 | 0.0106 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4618 | 43615.097 | 44270.9573 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8922.6656 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.002 | 0.0088 | 0.0108 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4621 | 43618.14 | 44270.9573 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9101.1189 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0018 | 0.0089 | 0.0107 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4624 | 43621.116 | 44270.9574 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9283.1413 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4627 | 43624.169 | 44270.9574 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9468.8041 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.002 | 0.009 | 0.011 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4630 | 43627.118 | 44270.9574 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9658.1802 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0018 | 0.0088 | 0.0106 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4633 | 43630.183 | 44270.9575 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9851.3438 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4636 | 43633.26 | 44270.9575 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10048.3707 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0004 | 0.0097 | 0.0101 | 0.0098 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4639 | 43636.332 | 44270.9576 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10249.3381 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0019 | 0.0094 | 0.0113 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4642 | 43639.593 | 44270.9576 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10454.3249 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.001 | 0.0101 | 0.0111 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4645 | 43642.891 | 44270.9576 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10663.4114 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0024 | 0.0088 | 0.0112 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4648 | 43645.881 | 44270.9577 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10876.6796 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4651 | 43649.256 | 44270.9577 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11094.2132 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0016 | 0.0097 | 0.0113 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4654 | 43652.556 | 44270.9577 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11316.0974 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0007 | 0.0097 | 0.0104 | 0.0101 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4657 | 43655.415 | 44270.9578 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11542.4194 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0012 | 0.0093 | 0.0105 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4660 | 43658.693 | 44270.9578 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11773.2678 | 0:240:120 | 0:00 | 0.0002 | 7 | 0.0011 | 0.0101 | 0.0112 | 0.0105 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4663 | 44014.748 | 44270.9619 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.1 | 0:240:120 | 0:00 | 40.3227 | 7 | 119.6154 | 247.2566 | 366.872 | 290.7424 | 53.8332 | 2898.0129 | 3 | 40.3227 | 166.3925 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4666 | 44986.8 | 44270.9732 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.1 | 0:240:120 | 0:00 | 34.639 | 7 | 111.9006 | 125.316 | 237.2166 | 162.953 | 55.4913 | 3079.2855 | 3 | 34.639 | 107.4571 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4669 | 45547.71 | 44270.9797 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.1 | 0:240:120 | 0:00 | 30.2841 | 7 | 28.3125 | 60.9145 | 89.227 | 69.2491 | 12.587 | 158.433 | 3 | 30.2841 | 78.935 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4672 | 45783.283 | 44270.9824 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.1 | 0:240:120 | 0:00 | 26.8427 | 7 | 3.7784 | 54.1669 | 57.9453 | 55.4291 | 1.8606 | 3.462 | 3 | 26.8427 | 62.1206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4675 | 45953.154 | 44270.9844 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.2 | 0:240:120 | 0:00 | 23.8064 | 7 | 4.7022 | 46.1399 | 50.8421 | 47.9718 | 2.1652 | 4.6881 | 3 | 23.8064 | 50.1343 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4678 | 46101.815 | 44270.9861 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.2 | 0:240:120 | 0:00 | 21.5465 | 7 | 6.4877 | 37.619 | 44.1067 | 40.2808 | 2.8883 | 8.3422 | 3 | 21.5465 | 42.526 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4681 | 46228.755 | 44270.9876 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.3 | 0:240:120 | 0:00 | 19.4733 | 7 | 4.9364 | 30.6753 | 35.6117 | 32.2736 | 2.3867 | 5.6961 | 3 | 19.4733 | 36.3408 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4684 | 46332.299 | 44270.9888 | Vista Speed | T | 20T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.4 | 0:240:120 | 0:00 | 17.7328 | 7 | 1.3624 | 28.2121 | 29.5745 | 28.7413 | 0.6271 | 0.3932 | 3 | 17.7328 | 31.6456 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4687 | 47091.397 | 44270.9975 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.312 | 0:240:120 | 0:00 | 66.5429 | 7 | 72.4624 | 623.0327 | 695.4951 | 649.2108 | 34.8283 | 1213.0073 | 3 | 66.5429 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4690 | 49054.925 | 44271.0203 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.4982 | 0:240:120 | 0:00 | 53.9778 | 7 | 87.0453 | 482.6323 | 569.6776 | 523.4933 | 35.3216 | 1247.6145 | 3 | 53.9778 | 709.4827 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4693 | 50640.872 | 44271.0386 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.7082 | 0:240:120 | 0:00 | 45.1148 | 7 | 118.8246 | 324.9142 | 443.7388 | 384.0612 | 46.9949 | 2208.5183 | 3 | 45.1148 | 229.4892 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4696 | 51848.137 | 44271.0526 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.9424 | 0:240:120 | 0:00 | 38.5323 | 7 | 123.4083 | 193.4048 | 316.8131 | 246.1025 | 54.599 | 2981.0476 | 3 | 38.5323 | 134.6868 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4699 | 52662.078 | 44271.062 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.2012 | 0:240:120 | 0:00 | 33.454 | 7 | 112.6893 | 66.5711 | 179.2604 | 107.1728 | 53.9119 | 2906.4922 | 3 | 33.454 | 94.2004 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4702 | 53087.395 | 44271.0669 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.4852 | 0:240:120 | 0:00 | 29.42 | 7 | 4.6115 | 59.5988 | 64.2103 | 61.1479 | 2.2586 | 5.1011 | 3 | 29.42 | 71.7585 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4705 | 53274.684 | 44271.0691 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.7949 | 0:240:120 | 0:00 | 26.1405 | 7 | 3.6051 | 52.5226 | 56.1277 | 53.7823 | 1.7571 | 3.0874 | 3 | 26.1405 | 57.5053 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4708 | 53438.994 | 44271.071 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.1308 | 0:240:120 | 0:00 | 23.4239 | 7 | 5.2925 | 43.8679 | 49.1604 | 46.1062 | 2.3406 | 5.4784 | 3 | 23.4239 | 47.6569 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4711 | 53582.36 | 44271.0727 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.4935 | 0:240:120 | 0:00 | 21.1384 | 7 | 6.5979 | 35.2468 | 41.8447 | 37.6276 | 3.1525 | 9.9383 | 3 | 21.1384 | 40.4496 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4714 | 53701.019 | 44271.074 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.8833 | 0:240:120 | 0:00 | 19.1904 | 7 | 1.2875 | 30.5803 | 31.8678 | 31.0205 | 0.6261 | 0.392 | 3 | 19.1904 | 34.9504 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4717 | 53797.386 | 44271.0752 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.301 | 0:240:120 | 0:00 | 17.5114 | 7 | 2.2761 | 27.1903 | 29.4664 | 28.1061 | 1.0406 | 1.0828 | 3 | 17.5114 | 30.6194 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4720 | 53885.694 | 44271.0762 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.747 | 0:240:120 | 0:00 | 16.0503 | 7 | 1.3586 | 24.8583 | 26.2169 | 25.3001 | 0.6599 | 0.4354 | 3 | 16.0503 | 27.1227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4723 | 53964.789 | 44271.0771 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.222 | 0:240:120 | 0:00 | 14.7684 | 7 | 2.1114 | 21.6033 | 23.7147 | 22.39 | 0.9959 | 0.9919 | 3 | 14.7684 | 24.2423 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4726 | 54035.65 | 44271.0779 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.7264 | 0:240:120 | 0:00 | 13.6354 | 7 | 0.7644 | 19.6856 | 20.45 | 19.9284 | 0.3616 | 0.1307 | 3 | 13.6354 | 21.8304 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4729 | 54098.531 | 44271.0786 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.2609 | 0:240:120 | 0:00 | 12.6274 | 7 | 1.1342 | 17.9796 | 19.1138 | 18.3661 | 0.5597 | 0.3133 | 3 | 12.6274 | 19.7826 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4732 | 54157.083 | 44271.0793 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.8261 | 0:240:120 | 0:00 | 11.7256 | 7 | 0.9342 | 16.4764 | 17.4106 | 16.9036 | 0.39 | 0.1521 | 3 | 11.7256 | 18.0236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4735 | 54210.881 | 44271.0799 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.4227 | 0:240:120 | 0:00 | 10.9147 | 7 | 0.6989 | 15.1165 | 15.8154 | 15.3515 | 0.3414 | 0.1166 | 3 | 10.9147 | 16.4975 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4738 | 54259.941 | 44271.0805 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.0511 | 0:240:120 | 0:00 | 10.182 | 7 | 0.6236 | 13.8849 | 14.5085 | 14.0896 | 0.3059 | 0.0936 | 3 | 10.182 | 15.1618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4741 | 54305.411 | 44271.081 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.7121 | 0:240:120 | 0:00 | 9.5174 | 7 | 0.6751 | 12.8728 | 13.5479 | 13.104 | 0.3324 | 0.1105 | 3 | 9.5174 | 13.9839 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4744 | 54348.024 | 44271.0815 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.4064 | 0:240:120 | 0:00 | 8.9121 | 7 | 0.6752 | 11.8606 | 12.5358 | 12.1053 | 0.3235 | 0.1046 | 3 | 8.9121 | 12.9381 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4747 | 54387.753 | 44271.082 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.1345 | 0:240:120 | 0:00 | 8.359 | 7 | 0.5598 | 10.9628 | 11.5226 | 11.1731 | 0.264 | 0.0697 | 3 | 8.359 | 12.0041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4750 | 54424.612 | 44271.0824 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.8972 | 0:240:120 | 0:00 | 7.852 | 7 | 0.4434 | 10.2963 | 10.7397 | 10.4676 | 0.2062 | 0.0425 | 3 | 7.852 | 11.1655 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4753 | 54459.025 | 44271.0828 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.6951 | 0:240:120 | 0:00 | 7.386 | 7 | 0.4451 | 9.6296 | 10.0747 | 9.7866 | 0.2158 | 0.0466 | 3 | 7.386 | 10.409 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4756 | 54491.696 | 44271.0832 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.529 | 0:240:120 | 0:00 | 6.9564 | 7 | 0.4459 | 8.9619 | 9.4078 | 9.112 | 0.2214 | 0.049 | 3 | 6.9564 | 9.7236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4759 | 54522.302 | 44271.0835 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.3996 | 0:240:120 | 0:00 | 6.5595 | 7 | 0.31 | 8.4906 | 8.8006 | 8.5943 | 0.1541 | 0.0237 | 3 | 6.5595 | 9.1001 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4762 | 54551.385 | 44271.0839 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.3076 | 0:240:120 | 0:00 | 6.1919 | 7 | 0.2915 | 7.9435 | 8.235 | 8.0708 | 0.1226 | 0.015 | 3 | 6.1919 | 8.531 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4765 | 54578.536 | 44271.0842 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.2538 | 0:240:120 | 0:00 | 5.8508 | 7 | 0.3123 | 7.3996 | 7.7119 | 7.5242 | 0.1429 | 0.0204 | 3 | 5.8508 | 8.0099 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4768 | 54604.353 | 44271.0845 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.2389 | 0:240:120 | 0:00 | 5.5336 | 7 | 0.2313 | 7.0504 | 7.2817 | 7.128 | 0.1149 | 0.0132 | 3 | 5.5336 | 7.5312 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4771 | 54628.649 | 44271.0848 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.2636 | 0:240:120 | 0:00 | 5.2382 | 7 | 0.2355 | 6.5963 | 6.8318 | 6.7071 | 0.0996 | 0.0099 | 3 | 5.2382 | 7.0904 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4774 | 54651.72 | 44271.085 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.3289 | 0:240:120 | 0:00 | 4.9626 | 7 | 0.2326 | 6.2408 | 6.4734 | 6.3186 | 0.1157 | 0.0134 | 3 | 4.9626 | 6.6834 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4777 | 54673.776 | 44271.0853 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.4355 | 0:240:120 | 0:00 | 4.705 | 7 | 0.1816 | 5.8883 | 6.0699 | 5.9718 | 0.0792 | 0.0063 | 3 | 4.705 | 6.3067 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4780 | 54694.575 | 44271.0855 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.5842 | 0:240:120 | 0:00 | 4.4639 | 7 | 0.2221 | 5.5696 | 5.7917 | 5.6626 | 0.0981 | 0.0096 | 3 | 4.4639 | 5.9574 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4783 | 54714.652 | 44271.0858 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.7759 | 0:240:120 | 0:00 | 4.238 | 7 | 0.1597 | 5.2861 | 5.4458 | 5.3401 | 0.079 | 0.0062 | 3 | 4.238 | 5.6328 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4786 | 54733.949 | 44271.086 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.0114 | 0:240:120 | 0:00 | 4.026 | 7 | 0.1423 | 5.0068 | 5.1491 | 5.0576 | 0.0686 | 0.0047 | 3 | 4.026 | 5.3307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4789 | 54752.04 | 44271.0862 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.2916 | 0:240:120 | 0:00 | 3.8269 | 7 | 0.1413 | 4.7314 | 4.8727 | 4.7891 | 0.0642 | 0.0041 | 3 | 3.8269 | 5.0489 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4792 | 54769.251 | 44271.0864 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.6174 | 0:240:120 | 0:00 | 3.6396 | 7 | 0.1129 | 4.4934 | 4.6063 | 4.5364 | 0.0527 | 0.0028 | 3 | 3.6396 | 4.7857 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4795 | 54786.095 | 44271.0866 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.9898 | 0:240:120 | 0:00 | 3.4632 | 7 | 0.1163 | 4.2682 | 4.3845 | 4.3114 | 0.0546 | 0.003 | 3 | 3.4632 | 4.5395 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4798 | 54802.45 | 44271.0868 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.4096 | 0:240:120 | 0:00 | 3.297 | 7 | 0.1002 | 4.0558 | 4.156 | 4.0907 | 0.049 | 0.0024 | 3 | 3.297 | 4.3088 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4801 | 54817.551 | 44271.087 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.8778 | 0:240:120 | 0:00 | 3.1402 | 7 | 0.0951 | 3.8689 | 3.964 | 3.9019 | 0.0461 | 0.0021 | 3 | 3.1402 | 4.0925 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4804 | 54832.254 | 44271.0871 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.3953 | 0:240:120 | 0:00 | 2.9922 | 7 | 0.1323 | 3.646 | 3.7783 | 3.705 | 0.0561 | 0.0031 | 3 | 2.9922 | 3.8894 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4807 | 54846.359 | 44271.0873 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.9632 | 0:240:120 | 0:00 | 2.8523 | 7 | 0.0812 | 3.4895 | 3.5707 | 3.5211 | 0.0376 | 0.0014 | 3 | 2.8523 | 3.6984 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4810 | 54859.992 | 44271.0875 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.5825 | 0:240:120 | 0:00 | 2.7199 | 7 | 0.1009 | 3.3119 | 3.4128 | 3.3542 | 0.0445 | 0.002 | 3 | 2.7199 | 3.5186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4813 | 54873.111 | 44271.0876 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.2542 | 0:240:120 | 0:00 | 2.5947 | 7 | 0.0698 | 3.1635 | 3.2333 | 3.1905 | 0.0321 | 0.001 | 3 | 2.5947 | 3.3492 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4816 | 54885.843 | 44271.0878 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.9792 | 0:240:120 | 0:00 | 2.4761 | 7 | 0.0955 | 3.0045 | 3.1 | 3.0457 | 0.0416 | 0.0017 | 3 | 2.4761 | 3.1895 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4819 | 54897.886 | 44271.0879 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.7588 | 0:240:120 | 0:00 | 2.3637 | 7 | 0.0731 | 2.8652 | 2.9383 | 2.8957 | 0.0327 | 0.0011 | 3 | 2.3637 | 3.0387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4822 | 54909.768 | 44271.088 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.594 | 0:240:120 | 0:00 | 2.2571 | 7 | 0.0601 | 2.7427 | 2.8028 | 2.7649 | 0.0278 | 0.0008 | 3 | 2.2571 | 2.8962 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4825 | 54921.029 | 44271.0882 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.4859 | 0:240:120 | 0:00 | 2.1559 | 7 | 0.0512 | 2.6159 | 2.6671 | 2.6341 | 0.024 | 0.0006 | 3 | 2.1559 | 2.7616 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4828 | 54932.076 | 44271.0883 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.4356 | 0:240:120 | 0:00 | 2.0599 | 7 | 0.0545 | 2.4944 | 2.5489 | 2.5174 | 0.0236 | 0.0006 | 3 | 2.0599 | 2.6341 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4831 | 54942.565 | 44271.0884 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.4443 | 0:240:120 | 0:00 | 1.9686 | 7 | 0.0576 | 2.3715 | 2.4291 | 2.3983 | 0.0234 | 0.0005 | 3 | 1.9686 | 2.5134 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4834 | 54952.56 | 44271.0885 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.5132 | 0:240:120 | 0:00 | 1.8819 | 7 | 0.0606 | 2.2654 | 2.326 | 2.2923 | 0.0263 | 0.0007 | 3 | 1.8819 | 2.3991 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4837 | 54962.467 | 44271.0886 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 159.6435 | 0:240:120 | 0:00 | 1.7994 | 7 | 0.0515 | 2.1713 | 2.2228 | 2.1937 | 0.0226 | 0.0005 | 3 | 1.7994 | 2.2906 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4840 | 54971.966 | 44271.0888 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 162.8363 | 0:240:120 | 0:00 | 1.7209 | 7 | 0.0501 | 2.0693 | 2.1194 | 2.0903 | 0.0213 | 0.0005 | 3 | 1.7209 | 2.1878 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4843 | 54981.159 | 44271.0889 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.0931 | 0:240:120 | 0:00 | 1.6462 | 7 | 0.047 | 1.9829 | 2.0299 | 2.0028 | 0.0207 | 0.0004 | 3 | 1.6462 | 2.0901 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4846 | 54990.205 | 44271.089 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.4149 | 0:240:120 | 0:00 | 1.5751 | 7 | 0.0472 | 1.8886 | 1.9358 | 1.909 | 0.0209 | 0.0004 | 3 | 1.5751 | 1.9973 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4849 | 54998.879 | 44271.0891 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 172.8032 | 0:240:120 | 0:00 | 1.5073 | 7 | 0.04 | 1.8107 | 1.8507 | 1.826 | 0.0177 | 0.0003 | 3 | 1.5073 | 1.9092 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4852 | 55007.179 | 44271.0892 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176.2593 | 0:240:120 | 0:00 | 1.4427 | 7 | 0.0353 | 1.7345 | 1.7698 | 1.747 | 0.0161 | 0.0003 | 3 | 1.4427 | 1.8254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4855 | 55015.405 | 44271.0893 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 179.7845 | 0:240:120 | 0:00 | 1.3812 | 7 | 0.0362 | 1.6549 | 1.6911 | 1.6704 | 0.0151 | 0.0002 | 3 | 1.3812 | 1.7456 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4858 | 55023.67 | 44271.0894 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.3802 | 0:240:120 | 0:00 | 1.3225 | 7 | 0.0312 | 1.5837 | 1.6149 | 1.5969 | 0.0136 | 0.0002 | 3 | 1.3225 | 1.6697 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4861 | 55031.355 | 44271.0894 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 187.0478 | 0:240:120 | 0:00 | 1.2665 | 7 | 0.0331 | 1.5142 | 1.5473 | 1.5287 | 0.0143 | 0.0002 | 3 | 1.2665 | 1.5975 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4864 | 55038.854 | 44271.0895 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 190.7887 | 0:240:120 | 0:00 | 1.213 | 7 | 0.0291 | 1.4551 | 1.4842 | 1.4667 | 0.0132 | 0.0002 | 3 | 1.213 | 1.5287 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4867 | 55046.193 | 44271.0896 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.6045 | 0:240:120 | 0:00 | 1.162 | 7 | 0.0262 | 1.3899 | 1.4161 | 1.4004 | 0.0115 | 0.0001 | 3 | 1.162 | 1.4631 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4870 | 55053.663 | 44271.0897 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 198.4966 | 0:240:120 | 0:00 | 1.1133 | 7 | 0.0251 | 1.3325 | 1.3576 | 1.3429 | 0.0111 | 0.0001 | 3 | 1.1133 | 1.4006 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4873 | 55060.729 | 44271.0898 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 202.4665 | 0:240:120 | 0:00 | 1.0668 | 7 | 0.0246 | 1.2763 | 1.3009 | 1.2868 | 0.0107 | 0.0001 | 3 | 1.0668 | 1.341 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4876 | 55067.593 | 44271.0899 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 206.5159 | 0:240:120 | 0:00 | 1.0223 | 7 | 0.0218 | 1.2221 | 1.2439 | 1.2309 | 0.0095 | 0.0001 | 3 | 1.0223 | 1.2841 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4879 | 55074.172 | 44271.0899 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 210.6462 | 0:240:120 | 0:00 | 0.9798 | 7 | 0.0228 | 1.1696 | 1.1924 | 1.1794 | 0.01 | 0.0001 | 3 | 0.9798 | 1.2299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4882 | 55080.567 | 44271.09 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 214.8591 | 0:240:120 | 0:00 | 0.9392 | 7 | 0.0188 | 1.1241 | 1.1429 | 1.1315 | 0.0085 | 0.0001 | 3 | 0.9392 | 1.1781 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4885 | 55086.861 | 44271.0901 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 219.1563 | 0:240:120 | 0:00 | 0.9004 | 7 | 0.0177 | 1.076 | 1.0937 | 1.0828 | 0.0075 | 0.0001 | 3 | 0.9004 | 1.1287 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4888 | 55093.166 | 44271.0902 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.5394 | 0:240:120 | 0:00 | 0.8633 | 7 | 0.0185 | 1.0304 | 1.0489 | 1.0379 | 0.008 | 0.0001 | 3 | 0.8633 | 1.0814 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4891 | 55099.227 | 44271.0902 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 228.0102 | 0:240:120 | 0:00 | 0.8278 | 7 | 0.0164 | 0.9875 | 1.0039 | 0.9937 | 0.0073 | 0.0001 | 3 | 0.8278 | 1.0363 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4894 | 55105.216 | 44271.0903 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 232.5704 | 0:240:120 | 0:00 | 0.7938 | 7 | 0.0145 | 0.9489 | 0.9634 | 0.9546 | 0.0063 | 0 | 3 | 0.7938 | 0.9932 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4897 | 55110.86 | 44271.0904 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.2218 | 0:240:120 | 0:00 | 0.7613 | 7 | 0.0143 | 0.9095 | 0.9238 | 0.9152 | 0.0063 | 0 | 3 | 0.7613 | 0.952 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4900 | 55116.712 | 44271.0904 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 241.9662 | 0:240:120 | 0:00 | 0.7302 | 7 | 0.0125 | 0.8719 | 0.8844 | 0.8771 | 0.0053 | 0 | 3 | 0.7302 | 0.9126 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4903 | 55122.335 | 44271.0905 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.8056 | 0:240:120 | 0:00 | 0.7004 | 7 | 0.0115 | 0.8353 | 0.8468 | 0.8399 | 0.005 | 0 | 3 | 0.7004 | 0.875 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4906 | 55127.83 | 44271.0906 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 251.7417 | 0:240:120 | 0:00 | 0.6719 | 7 | 0.0127 | 0.8004 | 0.8131 | 0.806 | 0.0054 | 0 | 3 | 0.6719 | 0.839 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4909 | 55133.052 | 44271.0906 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.7765 | 0:240:120 | 0:00 | 0.6446 | 7 | 0.0114 | 0.7677 | 0.7791 | 0.7725 | 0.0048 | 0 | 3 | 0.6446 | 0.8045 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4912 | 55138.548 | 44271.0907 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 261.912 | 0:240:120 | 0:00 | 0.6185 | 7 | 0.0096 | 0.7379 | 0.7475 | 0.7416 | 0.0041 | 0 | 3 | 0.6185 | 0.7716 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4915 | 55143.59 | 44271.0907 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 267.1503 | 0:240:120 | 0:00 | 0.5934 | 7 | 0.0094 | 0.7078 | 0.7172 | 0.7115 | 0.0039 | 0 | 3 | 0.5934 | 0.74 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4918 | 55148.808 | 44271.0908 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 272.4933 | 0:240:120 | 0:00 | 0.5695 | 7 | 0.0081 | 0.6786 | 0.6867 | 0.6818 | 0.0035 | 0 | 3 | 0.5695 | 0.7098 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4921 | 55153.886 | 44271.0909 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 277.9431 | 0:240:120 | 0:00 | 0.5465 | 7 | 0.0085 | 0.6508 | 0.6593 | 0.6545 | 0.0035 | 0 | 3 | 0.5465 | 0.6809 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4924 | 55158.638 | 44271.0909 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 283.502 | 0:240:120 | 0:00 | 0.5245 | 7 | 0.0092 | 0.6244 | 0.6336 | 0.628 | 0.0038 | 0 | 3 | 0.5245 | 0.6532 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4927 | 55163.363 | 44271.091 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 289.172 | 0:240:120 | 0:00 | 0.5034 | 7 | 0.0079 | 0.5986 | 0.6065 | 0.602 | 0.0034 | 0 | 3 | 0.5034 | 0.6267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4930 | 55168.116 | 44271.091 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.9555 | 0:240:120 | 0:00 | 0.4831 | 7 | 0.0079 | 0.5741 | 0.582 | 0.5778 | 0.003 | 0 | 3 | 0.4831 | 0.6013 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4933 | 55172.929 | 44271.0911 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 300.8546 | 0:240:120 | 0:00 | 0.4638 | 7 | 0.0056 | 0.5524 | 0.558 | 0.5547 | 0.0022 | 0 | 3 | 0.4638 | 0.577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4936 | 55177.698 | 44271.0911 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 306.8717 | 0:240:120 | 0:00 | 0.4452 | 7 | 0.0071 | 0.5304 | 0.5375 | 0.5328 | 0.0026 | 0 | 3 | 0.4452 | 0.5537 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4939 | 55182.19 | 44271.0912 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 313.0091 | 0:240:120 | 0:00 | 0.4274 | 7 | 0.0079 | 0.5074 | 0.5153 | 0.5108 | 0.0031 | 0 | 3 | 0.4274 | 0.5314 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4942 | 55186.749 | 44271.0912 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 319.2693 | 0:240:120 | 0:00 | 0.4103 | 7 | 0.0063 | 0.4879 | 0.4942 | 0.4905 | 0.0025 | 0 | 3 | 0.4103 | 0.51 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4945 | 55191.217 | 44271.0913 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 325.6547 | 0:240:120 | 0:00 | 0.3939 | 7 | 0.0052 | 0.4691 | 0.4743 | 0.4711 | 0.0021 | 0 | 3 | 0.3939 | 0.4895 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4948 | 55195.492 | 44271.0913 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 332.1678 | 0:240:120 | 0:00 | 0.3782 | 7 | 0.0063 | 0.4496 | 0.4559 | 0.452 | 0.0025 | 0 | 3 | 0.3782 | 0.4699 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4951 | 55199.737 | 44271.0914 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 338.8111 | 0:240:120 | 0:00 | 0.3631 | 7 | 0.0056 | 0.4317 | 0.4373 | 0.434 | 0.0022 | 0 | 3 | 0.3631 | 0.451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4954 | 55203.891 | 44271.0914 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 345.5874 | 0:240:120 | 0:00 | 0.3487 | 7 | 0.0078 | 0.4132 | 0.421 | 0.4166 | 0.0028 | 0 | 3 | 0.3487 | 0.433 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4957 | 55208.042 | 44271.0915 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 352.4991 | 0:240:120 | 0:00 | 0.3348 | 7 | 0.0058 | 0.3977 | 0.4035 | 0.4 | 0.0024 | 0 | 3 | 0.3348 | 0.4157 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4960 | 55212.17 | 44271.0915 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 359.5491 | 0:240:120 | 0:00 | 0.3215 | 7 | 0.0049 | 0.382 | 0.3869 | 0.384 | 0.0019 | 0 | 3 | 0.3215 | 0.3991 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4963 | 55216.281 | 44271.0916 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 366.7401 | 0:240:120 | 0:00 | 0.3087 | 7 | 0.0053 | 0.3666 | 0.3719 | 0.369 | 0.0019 | 0 | 3 | 0.3087 | 0.3831 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4966 | 55220.41 | 44271.0916 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 374.0749 | 0:240:120 | 0:00 | 0.2965 | 7 | 0.0041 | 0.3536 | 0.3577 | 0.3552 | 0.0016 | 0 | 3 | 0.2965 | 0.3679 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4969 | 55224.523 | 44271.0917 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 381.5564 | 0:240:120 | 0:00 | 0.2848 | 7 | 0.0058 | 0.3383 | 0.3441 | 0.3409 | 0.0023 | 0 | 3 | 0.2848 | 0.3532 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4972 | 55228.427 | 44271.0917 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 389.1875 | 0:240:120 | 0:00 | 0.2735 | 7 | 0.0057 | 0.3236 | 0.3293 | 0.3265 | 0.002 | 0 | 3 | 0.2735 | 0.3392 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4975 | 55232.301 | 44271.0918 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 396.9713 | 0:240:120 | 0:00 | 0.2627 | 7 | 0.0052 | 0.312 | 0.3172 | 0.3142 | 0.0022 | 0 | 3 | 0.2627 | 0.3257 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4978 | 55236.238 | 44271.0918 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 404.9107 | 0:240:120 | 0:00 | 0.2523 | 7 | 0.0042 | 0.3003 | 0.3045 | 0.3017 | 0.0017 | 0 | 3 | 0.2523 | 0.3128 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4981 | 55240.06 | 44271.0919 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 413.0089 | 0:240:120 | 0:00 | 0.2423 | 7 | 0.0042 | 0.288 | 0.2922 | 0.2895 | 0.0019 | 0 | 3 | 0.2423 | 0.3004 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4984 | 55243.7 | 44271.0919 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 421.2691 | 0:240:120 | 0:00 | 0.2327 | 7 | 0.0047 | 0.2762 | 0.2809 | 0.2784 | 0.0019 | 0 | 3 | 0.2327 | 0.2885 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4987 | 55247.665 | 44271.0919 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 429.6945 | 0:240:120 | 0:00 | 0.2236 | 7 | 0.0046 | 0.265 | 0.2696 | 0.2671 | 0.0018 | 0 | 3 | 0.2236 | 0.277 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4990 | 55251.558 | 44271.092 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 438.2883 | 0:240:120 | 0:00 | 0.2147 | 7 | 0.0043 | 0.2546 | 0.2589 | 0.2566 | 0.0015 | 0 | 3 | 0.2147 | 0.2661 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4993 | 55255.394 | 44271.092 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 447.0541 | 0:240:120 | 0:00 | 0.2063 | 7 | 0.0048 | 0.2445 | 0.2493 | 0.2463 | 0.002 | 0 | 3 | 0.2063 | 0.2556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4996 | 55259.221 | 44271.0921 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 455.9952 | 0:240:120 | 0:00 | 0.1982 | 7 | 0.0052 | 0.2354 | 0.2406 | 0.2375 | 0.0022 | 0 | 3 | 0.1982 | 0.2455 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4999 | 55263.298 | 44271.0921 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 465.1151 | 0:240:120 | 0:00 | 0.1904 | 7 | 0.005 | 0.2256 | 0.2306 | 0.2278 | 0.0019 | 0 | 3 | 0.1904 | 0.2358 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5002 | 55267.133 | 44271.0922 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 474.4174 | 0:240:120 | 0:00 | 0.1829 | 7 | 0.0042 | 0.2164 | 0.2206 | 0.2186 | 0.0014 | 0 | 3 | 0.1829 | 0.2265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5005 | 55270.852 | 44271.0922 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 483.9057 | 0:240:120 | 0:00 | 0.1757 | 7 | 0.0041 | 0.2085 | 0.2126 | 0.2101 | 0.0015 | 0 | 3 | 0.1757 | 0.2175 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5008 | 55274.361 | 44271.0923 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 493.5839 | 0:240:120 | 0:00 | 0.1688 | 7 | 0.0052 | 0.1993 | 0.2045 | 0.2015 | 0.0021 | 0 | 3 | 0.1688 | 0.209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5011 | 55277.965 | 44271.0923 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 503.4555 | 0:240:120 | 0:00 | 0.1621 | 7 | 0.0031 | 0.1928 | 0.1959 | 0.194 | 0.0013 | 0 | 3 | 0.1621 | 0.2007 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5014 | 55281.437 | 44271.0923 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 513.5246 | 0:240:120 | 0:00 | 0.1558 | 7 | 0.0029 | 0.1855 | 0.1884 | 0.1865 | 0.0011 | 0 | 3 | 0.1558 | 0.1928 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5017 | 55284.791 | 44271.0924 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 523.7951 | 0:240:120 | 0:00 | 0.1497 | 7 | 0.0036 | 0.1779 | 0.1815 | 0.1795 | 0.0013 | 0 | 3 | 0.1497 | 0.1852 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5020 | 55288.318 | 44271.0924 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 534.271 | 0:240:120 | 0:00 | 0.1438 | 7 | 0.0037 | 0.1707 | 0.1744 | 0.172 | 0.0014 | 0 | 3 | 0.1438 | 0.178 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5023 | 55291.82 | 44271.0925 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 544.9565 | 0:240:120 | 0:00 | 0.1382 | 7 | 0.0036 | 0.1638 | 0.1674 | 0.1652 | 0.0012 | 0 | 3 | 0.1382 | 0.171 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5026 | 55295.426 | 44271.0925 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 555.8556 | 0:240:120 | 0:00 | 0.1327 | 7 | 0.0038 | 0.1575 | 0.1613 | 0.1593 | 0.0014 | 0 | 3 | 0.1327 | 0.1642 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5029 | 55299.058 | 44271.0925 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 566.9727 | 0:240:120 | 0:00 | 0.1275 | 7 | 0.0041 | 0.1504 | 0.1545 | 0.1524 | 0.0014 | 0 | 3 | 0.1275 | 0.1578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5032 | 55302.32 | 44271.0926 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 578.3122 | 0:240:120 | 0:00 | 0.1225 | 7 | 0.0035 | 0.1447 | 0.1482 | 0.1463 | 0.0012 | 0 | 3 | 0.1225 | 0.1516 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5035 | 55305.714 | 44271.0926 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 589.8784 | 0:240:120 | 0:00 | 0.1177 | 7 | 0.0039 | 0.1387 | 0.1426 | 0.1407 | 0.0014 | 0 | 3 | 0.1177 | 0.1457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5038 | 55309.066 | 44271.0927 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 601.676 | 0:240:120 | 0:00 | 0.1131 | 7 | 0.0034 | 0.1343 | 0.1377 | 0.1358 | 0.0012 | 0 | 3 | 0.1131 | 0.1399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5041 | 55312.323 | 44271.0927 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 613.7095 | 0:240:120 | 0:00 | 0.1087 | 7 | 0.0022 | 0.1293 | 0.1315 | 0.1301 | 0.0008 | 0 | 3 | 0.1087 | 0.1345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5044 | 55315.612 | 44271.0927 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 625.9837 | 0:240:120 | 0:00 | 0.1045 | 7 | 0.0016 | 0.124 | 0.1256 | 0.1249 | 0.0007 | 0 | 3 | 0.1045 | 0.1292 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5047 | 55318.928 | 44271.0928 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 638.5033 | 0:240:120 | 0:00 | 0.1004 | 7 | 0.0028 | 0.119 | 0.1218 | 0.1204 | 0.001 | 0 | 3 | 0.1004 | 0.1241 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5050 | 55322.232 | 44271.0928 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 651.2734 | 0:240:120 | 0:00 | 0.0964 | 7 | 0.0025 | 0.1148 | 0.1173 | 0.1156 | 0.0009 | 0 | 3 | 0.0964 | 0.1193 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5053 | 55325.556 | 44271.0928 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 664.2989 | 0:240:120 | 0:00 | 0.0927 | 7 | 0.0026 | 0.1094 | 0.112 | 0.1105 | 0.0009 | 0 | 3 | 0.0927 | 0.1146 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5056 | 55328.853 | 44271.0929 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 677.5849 | 0:240:120 | 0:00 | 0.0891 | 7 | 0.0025 | 0.1051 | 0.1076 | 0.1067 | 0.001 | 0 | 3 | 0.0891 | 0.1101 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5059 | 55332.084 | 44271.0929 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 691.1366 | 0:240:120 | 0:00 | 0.0856 | 7 | 0.0029 | 0.1011 | 0.104 | 0.1025 | 0.0011 | 0 | 3 | 0.0856 | 0.1058 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5062 | 55335.548 | 44271.093 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 704.9593 | 0:240:120 | 0:00 | 0.0822 | 7 | 0.0024 | 0.0979 | 0.1003 | 0.099 | 0.0009 | 0 | 3 | 0.0822 | 0.1017 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5065 | 55338.837 | 44271.093 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 719.0585 | 0:240:120 | 0:00 | 0.079 | 7 | 0.0034 | 0.0938 | 0.0972 | 0.0952 | 0.0011 | 0 | 3 | 0.079 | 0.0977 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5068 | 55342.118 | 44271.093 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 733.4396 | 0:240:120 | 0:00 | 0.0759 | 7 | 0.0014 | 0.0904 | 0.0918 | 0.0912 | 0.0005 | 0 | 3 | 0.0759 | 0.0939 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5071 | 55345.389 | 44271.0931 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 748.1084 | 0:240:120 | 0:00 | 0.073 | 7 | 0.0042 | 0.0856 | 0.0898 | 0.0876 | 0.0015 | 0 | 3 | 0.073 | 0.0902 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5074 | 55348.627 | 44271.0931 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 763.0706 | 0:240:120 | 0:00 | 0.0701 | 7 | 0.0021 | 0.0834 | 0.0855 | 0.0845 | 0.0008 | 0 | 3 | 0.0701 | 0.0867 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5077 | 55351.892 | 44271.0932 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 778.332 | 0:240:120 | 0:00 | 0.0674 | 7 | 0.0028 | 0.0802 | 0.083 | 0.0813 | 0.0013 | 0 | 3 | 0.0674 | 0.0833 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5080 | 55355.15 | 44271.0932 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 793.8987 | 0:240:120 | 0:00 | 0.0648 | 7 | 0.0024 | 0.0768 | 0.0792 | 0.0781 | 0.0009 | 0 | 3 | 0.0648 | 0.08 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5083 | 55358.42 | 44271.0932 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 809.7766 | 0:240:120 | 0:00 | 0.0622 | 7 | 0.0027 | 0.0738 | 0.0765 | 0.0756 | 0.0009 | 0 | 3 | 0.0622 | 0.0769 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5086 | 55361.742 | 44271.0933 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 825.9722 | 0:240:120 | 0:00 | 0.0598 | 7 | 0.0032 | 0.0706 | 0.0738 | 0.0726 | 0.0013 | 0 | 3 | 0.0598 | 0.0739 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5089 | 55365.017 | 44271.0933 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 842.4916 | 0:240:120 | 0:00 | 0.0575 | 7 | 0.0041 | 0.0678 | 0.0719 | 0.0696 | 0.0013 | 0 | 3 | 0.0575 | 0.071 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5092 | 55368.366 | 44271.0933 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 859.3414 | 0:240:120 | 0:00 | 0.0552 | 7 | 0.0023 | 0.0654 | 0.0677 | 0.0667 | 0.0008 | 0 | 3 | 0.0552 | 0.0683 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5095 | 55371.586 | 44271.0934 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 876.5283 | 0:240:120 | 0:00 | 0.0531 | 7 | 0.0041 | 0.0618 | 0.0659 | 0.0641 | 0.0014 | 0 | 3 | 0.0531 | 0.0656 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5098 | 55374.843 | 44271.0934 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 894.0588 | 0:240:120 | 0:00 | 0.051 | 7 | 0.003 | 0.0608 | 0.0638 | 0.0623 | 0.0011 | 0 | 3 | 0.051 | 0.063 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5101 | 55378.141 | 44271.0935 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 911.94 | 0:240:120 | 0:00 | 0.049 | 7 | 0.003 | 0.0573 | 0.0603 | 0.0593 | 0.0013 | 0 | 3 | 0.049 | 0.0606 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5104 | 55381.408 | 44271.0935 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 930.1788 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0029 | 0.0553 | 0.0582 | 0.0569 | 0.0011 | 0 | 3 | 0.0471 | 0.0582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5107 | 55384.659 | 44271.0935 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 948.7824 | 0:240:120 | 0:00 | 0.0453 | 7 | 0.0024 | 0.054 | 0.0564 | 0.0552 | 0.0009 | 0 | 3 | 0.0453 | 0.0559 | P | NP | 0-1-0-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5110 | 55387.906 | 44271.0936 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 967.758 | 0:240:120 | 0:00 | 0.0435 | 7 | 0.0029 | 0.0509 | 0.0538 | 0.053 | 0.0013 | 0 | 3 | 0.0435 | 0.0538 | P | NP | 0-1-0-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5113 | 55391.054 | 44271.0936 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 987.1132 | 0:240:120 | 0:00 | 0.0418 | 7 | 0.0026 | 0.0495 | 0.0521 | 0.0509 | 0.001 | 0 | 3 | 0.0418 | 0.0518 | P | NP | 1-1-1-0-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5116 | 55394.445 | 44271.0936 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1006.8555 | 0:240:120 | 0:00 | 0.0402 | 7 | 0.003 | 0.0475 | 0.0505 | 0.0491 | 0.0011 | 0 | 3 | 0.0402 | 0.0502 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5119 | 55397.613 | 44271.0937 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1026.9926 | 0:240:120 | 0:00 | 0.0386 | 7 | 0.0037 | 0.045 | 0.0487 | 0.0471 | 0.0013 | 0 | 3 | 0.0386 | 0.0486 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5122 | 55400.667 | 44271.0937 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1047.5324 | 0:240:120 | 0:00 | 0.0371 | 7 | 0.0027 | 0.0439 | 0.0466 | 0.0457 | 0.0009 | 0 | 3 | 0.0371 | 0.0471 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5125 | 55403.716 | 44271.0938 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1068.4831 | 0:240:120 | 0:00 | 0.0357 | 7 | 0.0024 | 0.0428 | 0.0452 | 0.0438 | 0.0008 | 0 | 3 | 0.0357 | 0.0457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5128 | 55406.782 | 44271.0938 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1089.8527 | 0:240:120 | 0:00 | 0.0343 | 7 | 0.0022 | 0.0407 | 0.0429 | 0.0422 | 0.001 | 0 | 3 | 0.0343 | 0.0443 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5131 | 55410.044 | 44271.0938 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1111.6498 | 0:240:120 | 0:00 | 0.033 | 7 | 0.0032 | 0.0392 | 0.0424 | 0.0411 | 0.0012 | 0 | 3 | 0.033 | 0.043 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5134 | 55413.334 | 44271.0939 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1133.8828 | 0:240:120 | 0:00 | 0.0317 | 7 | 0.003 | 0.0368 | 0.0398 | 0.039 | 0.001 | 0 | 3 | 0.0317 | 0.0417 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5137 | 55416.407 | 44271.0939 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1156.5604 | 0:240:120 | 0:00 | 0.0304 | 7 | 0.0038 | 0.0356 | 0.0394 | 0.0378 | 0.0013 | 0 | 3 | 0.0304 | 0.0404 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5140 | 55419.589 | 44271.0939 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1179.6916 | 0:240:120 | 0:00 | 0.0293 | 7 | 0.0027 | 0.0347 | 0.0374 | 0.0364 | 0.0011 | 0 | 3 | 0.0293 | 0.0393 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5143 | 55422.546 | 44271.094 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1203.2855 | 0:240:120 | 0:00 | 0.0281 | 7 | 0.0021 | 0.0339 | 0.036 | 0.0349 | 0.0007 | 0 | 3 | 0.0281 | 0.0381 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5146 | 55425.677 | 44271.094 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1227.3512 | 0:240:120 | 0:00 | 0.027 | 7 | 0.0027 | 0.0321 | 0.0348 | 0.0339 | 0.001 | 0 | 3 | 0.027 | 0.037 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5149 | 55428.847 | 44271.094 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1251.8982 | 0:240:120 | 0:00 | 0.026 | 7 | 0.0031 | 0.0308 | 0.0339 | 0.0325 | 0.0011 | 0 | 3 | 0.026 | 0.036 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5152 | 55432.356 | 44271.0941 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1276.9362 | 0:240:120 | 0:00 | 0.025 | 7 | 0.0036 | 0.0291 | 0.0327 | 0.0314 | 0.0012 | 0 | 3 | 0.025 | 0.035 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5155 | 55435.412 | 44271.0941 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1302.4749 | 0:240:120 | 0:00 | 0.024 | 7 | 0.0035 | 0.0283 | 0.0318 | 0.0301 | 0.0011 | 0 | 3 | 0.024 | 0.034 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5158 | 55438.406 | 44271.0942 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1328.5244 | 0:240:120 | 0:00 | 0.0231 | 7 | 0.0022 | 0.0278 | 0.03 | 0.0291 | 0.0009 | 0 | 3 | 0.0231 | 0.0331 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5161 | 55441.692 | 44271.0942 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1355.0949 | 0:240:120 | 0:00 | 0.0222 | 7 | 0.0025 | 0.027 | 0.0295 | 0.0283 | 0.001 | 0 | 3 | 0.0222 | 0.0322 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5164 | 55444.842 | 44271.0942 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1382.1968 | 0:240:120 | 0:00 | 0.0213 | 7 | 0.0029 | 0.0257 | 0.0286 | 0.0273 | 0.0011 | 0 | 3 | 0.0213 | 0.0313 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5167 | 55447.997 | 44271.0943 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1409.8407 | 0:240:120 | 0:00 | 0.0205 | 7 | 0.0024 | 0.0251 | 0.0275 | 0.0264 | 0.0009 | 0 | 3 | 0.0205 | 0.0305 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5170 | 55451.047 | 44271.0943 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1438.0375 | 0:240:120 | 0:00 | 0.0197 | 7 | 0.0029 | 0.0237 | 0.0266 | 0.0256 | 0.0011 | 0 | 3 | 0.0197 | 0.0297 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5173 | 55453.987 | 44271.0943 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1466.7983 | 0:240:120 | 0:00 | 0.0189 | 7 | 0.0038 | 0.0228 | 0.0266 | 0.0249 | 0.0014 | 0 | 3 | 0.0189 | 0.0289 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5176 | 55457.034 | 44271.0944 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1496.1343 | 0:240:120 | 0:00 | 0.0182 | 7 | 0.0035 | 0.0225 | 0.026 | 0.0243 | 0.0012 | 0 | 3 | 0.0182 | 0.0282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5179 | 55460.256 | 44271.0944 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1526.0569 | 0:240:120 | 0:00 | 0.0175 | 7 | 0.0034 | 0.0216 | 0.025 | 0.0234 | 0.0011 | 0 | 3 | 0.0175 | 0.0275 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5182 | 55463.698 | 44271.0944 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1556.5781 | 0:240:120 | 0:00 | 0.0168 | 7 | 0.0029 | 0.0215 | 0.0244 | 0.0231 | 0.0012 | 0 | 3 | 0.0168 | 0.0268 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5185 | 55466.761 | 44271.0945 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1587.7096 | 0:240:120 | 0:00 | 0.0161 | 7 | 0.0033 | 0.0202 | 0.0235 | 0.0224 | 0.0012 | 0 | 3 | 0.0161 | 0.0261 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5188 | 55469.893 | 44271.0945 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1619.4638 | 0:240:120 | 0:00 | 0.0155 | 7 | 0.0029 | 0.0205 | 0.0234 | 0.022 | 0.001 | 0 | 3 | 0.0155 | 0.0255 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5191 | 55473.16 | 44271.0946 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1651.8531 | 0:240:120 | 0:00 | 0.0149 | 7 | 0.0042 | 0.0188 | 0.023 | 0.0214 | 0.0018 | 0 | 3 | 0.0149 | 0.0249 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5194 | 55476.144 | 44271.0946 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1684.8902 | 0:240:120 | 0:00 | 0.0143 | 7 | 0.003 | 0.0192 | 0.0222 | 0.021 | 0.0012 | 0 | 3 | 0.0143 | 0.0243 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5197 | 55479.176 | 44271.0946 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1718.588 | 0:240:120 | 0:00 | 0.0138 | 7 | 0.0037 | 0.0183 | 0.022 | 0.0204 | 0.0014 | 0 | 3 | 0.0138 | 0.0238 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5200 | 55482.163 | 44271.0947 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1752.9597 | 0:240:120 | 0:00 | 0.0132 | 7 | 0.0032 | 0.0181 | 0.0213 | 0.0199 | 0.0012 | 0 | 3 | 0.0132 | 0.0232 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5203 | 55485.195 | 44271.0947 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1788.0189 | 0:240:120 | 0:00 | 0.0127 | 7 | 0.0041 | 0.0175 | 0.0216 | 0.0194 | 0.0014 | 0 | 3 | 0.0127 | 0.0227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5206 | 55488.59 | 44271.0947 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1823.7793 | 0:240:120 | 0:00 | 0.0122 | 7 | 0.003 | 0.0178 | 0.0208 | 0.0191 | 0.0011 | 0 | 3 | 0.0122 | 0.0222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5209 | 55491.536 | 44271.0948 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1860.2549 | 0:240:120 | 0:00 | 0.0118 | 7 | 0.0029 | 0.0178 | 0.0207 | 0.0188 | 0.001 | 0 | 3 | 0.0118 | 0.0218 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5212 | 55494.52 | 44271.0948 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1897.46 | 0:240:120 | 0:00 | 0.0113 | 7 | 0.0025 | 0.0171 | 0.0196 | 0.0184 | 0.0008 | 0 | 3 | 0.0113 | 0.0213 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5215 | 55497.665 | 44271.0948 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1935.4092 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0022 | 0.0171 | 0.0193 | 0.0181 | 0.0008 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5218 | 55500.666 | 44271.0949 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1974.1174 | 0:240:120 | 0:00 | 0.0104 | 7 | 0.003 | 0.0166 | 0.0196 | 0.0178 | 0.001 | 0 | 3 | 0.0104 | 0.0204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5221 | 55503.739 | 44271.0949 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2013.5997 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0012 | 0.0166 | 0.0178 | 0.0172 | 0.0006 | 0 | 3 | 0.01 | 0.02 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5224 | 55506.779 | 44271.0949 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2016.3485 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0014 | 0.0171 | 0.0185 | 0.0178 | 0.0006 | 0 | 3 | 0.01 | 0.02 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5227 | 55509.747 | 44271.095 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2056.6754 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0013 | 0.0156 | 0.0169 | 0.0166 | 0.0006 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 1-0-0-1-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5230 | 55513.009 | 44271.095 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2097.809 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0022 | 0.0154 | 0.0176 | 0.0165 | 0.0007 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 1-0-0-1-1-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
5233 | 55515.999 | 44271.0951 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2139.7651 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0028 | 0.015 | 0.0178 | 0.0163 | 0.0009 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 1-0-0-0-1-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
5236 | 55519.095 | 44271.0951 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2182.5604 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0017 | 0.0149 | 0.0166 | 0.0156 | 0.0007 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-0-0-1-0-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5239 | 55522.456 | 44271.0951 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2226.2116 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.003 | 0.0142 | 0.0172 | 0.0157 | 0.001 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5242 | 55525.514 | 44271.0952 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2270.7359 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0041 | 0.0127 | 0.0168 | 0.015 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5245 | 55528.87 | 44271.0952 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2316.1506 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.005 | 0.0124 | 0.0174 | 0.0149 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5248 | 55532.06 | 44271.0952 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2362.4736 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0044 | 0.0119 | 0.0163 | 0.0143 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5251 | 55535.536 | 44271.0953 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2409.7231 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0038 | 0.0123 | 0.0161 | 0.0143 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5254 | 55538.584 | 44271.0953 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2457.9175 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0038 | 0.0123 | 0.0161 | 0.0139 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5257 | 55541.652 | 44271.0953 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2507.0759 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0051 | 0.0118 | 0.0169 | 0.0141 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5260 | 55544.846 | 44271.0954 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2557.2174 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0052 | 0.0115 | 0.0167 | 0.014 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5263 | 55548.032 | 44271.0954 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2608.3618 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0051 | 0.0112 | 0.0163 | 0.0138 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5266 | 55551.388 | 44271.0955 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2660.529 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0046 | 0.0114 | 0.016 | 0.0137 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5269 | 55554.438 | 44271.0955 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2713.7396 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0052 | 0.0111 | 0.0163 | 0.0137 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5272 | 55557.823 | 44271.0955 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2768.0144 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0058 | 0.011 | 0.0168 | 0.0136 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5275 | 55560.975 | 44271.0956 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2823.3747 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0051 | 0.0108 | 0.0159 | 0.0131 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5278 | 55564.043 | 44271.0956 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2879.8421 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0042 | 0.011 | 0.0152 | 0.0132 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5281 | 55567.216 | 44271.0956 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2937.439 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0041 | 0.0108 | 0.0149 | 0.0131 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5284 | 55570.508 | 44271.0957 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2996.1878 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0055 | 0.0103 | 0.0158 | 0.013 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5287 | 55573.579 | 44271.0957 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3056.1115 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.0047 | 0.0102 | 0.0149 | 0.0128 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5290 | 55576.66 | 44271.0958 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3117.2338 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0052 | 0.01 | 0.0152 | 0.0128 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5293 | 55579.826 | 44271.0958 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3179.5784 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0055 | 0.0099 | 0.0154 | 0.0126 | 0.0022 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5296 | 55582.78 | 44271.0958 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3243.17 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0051 | 0.0101 | 0.0152 | 0.0127 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5299 | 55585.742 | 44271.0959 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3308.0334 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0052 | 0.0104 | 0.0156 | 0.0128 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5302 | 55588.715 | 44271.0959 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3374.1941 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0041 | 0.01 | 0.0141 | 0.0118 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5305 | 55591.679 | 44271.0959 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3441.6779 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0049 | 0.0102 | 0.0151 | 0.012 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5308 | 55594.781 | 44271.096 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3510.5115 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0051 | 0.0099 | 0.015 | 0.0126 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5311 | 55597.868 | 44271.096 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3580.7217 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0029 | 0.01 | 0.0129 | 0.0113 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5314 | 55601.129 | 44271.096 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3652.3362 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0052 | 0.0098 | 0.015 | 0.012 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5317 | 55604.202 | 44271.0961 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3725.3829 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0038 | 0.0105 | 0.0143 | 0.0117 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5320 | 55607.264 | 44271.0961 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3799.8905 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0032 | 0.0098 | 0.013 | 0.011 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5323 | 55610.414 | 44271.0961 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3875.8884 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0052 | 0.0089 | 0.0141 | 0.0111 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5326 | 55613.549 | 44271.0962 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3953.4061 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0055 | 0.0095 | 0.015 | 0.0116 | 0.0022 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5329 | 55616.744 | 44271.0962 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4032.4743 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.003 | 0.0093 | 0.0123 | 0.0103 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5332 | 55619.79 | 44271.0963 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4032.697 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0053 | 0.0098 | 0.0151 | 0.012 | 0.002 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5335 | 55622.969 | 44271.0963 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4113.3509 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0044 | 0.0096 | 0.014 | 0.0111 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5338 | 55625.916 | 44271.0963 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4195.6179 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0033 | 0.0089 | 0.0122 | 0.0103 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5341 | 55628.985 | 44271.0964 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4279.5303 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0045 | 0.0097 | 0.0142 | 0.011 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5344 | 55632.035 | 44271.0964 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4365.1209 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0018 | 0.0099 | 0.0117 | 0.0107 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5347 | 55635.22 | 44271.0964 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4452.4233 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0043 | 0.0098 | 0.0141 | 0.0113 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5350 | 55638.305 | 44271.0965 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4541.4718 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0047 | 0.0093 | 0.014 | 0.011 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5353 | 55641.292 | 44271.0965 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4632.3012 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0059 | 0.0092 | 0.0151 | 0.0107 | 0.0019 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5356 | 55644.233 | 44271.0965 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4724.9472 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.005 | 0.0094 | 0.0144 | 0.0108 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5359 | 55647.285 | 44271.0966 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4819.4462 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0056 | 0.0092 | 0.0148 | 0.0109 | 0.0017 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5362 | 55650.378 | 44271.0966 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4915.8351 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0061 | 0.0089 | 0.015 | 0.0106 | 0.002 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5365 | 55653.287 | 44271.0966 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5014.1518 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.002 | 0.0094 | 0.0114 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5368 | 55656.522 | 44271.0967 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5114.4348 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0059 | 0.0091 | 0.015 | 0.0104 | 0.0019 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5371 | 55659.482 | 44271.0967 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5216.7235 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0053 | 0.0091 | 0.0144 | 0.0106 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5374 | 55662.548 | 44271.0967 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5321.058 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0021 | 0.0093 | 0.0114 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5377 | 55665.93 | 44271.0968 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5427.4791 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5380 | 55668.891 | 44271.0968 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5536.0287 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5383 | 55671.967 | 44271.0969 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5646.7493 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5386 | 55675.284 | 44271.0969 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5759.6843 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5389 | 55678.244 | 44271.0969 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5874.878 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0012 | 0.0093 | 0.0105 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5392 | 55681.437 | 44271.097 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5992.3755 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0016 | 0.0094 | 0.011 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5395 | 55684.497 | 44271.097 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6112.223 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0045 | 0.0095 | 0.014 | 0.0105 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5398 | 55687.902 | 44271.097 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6234.4675 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5401 | 55690.966 | 44271.0971 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6359.1569 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0055 | 0.0095 | 0.015 | 0.0106 | 0.0017 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5404 | 55694.118 | 44271.0971 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6486.34 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0005 | 0.0098 | 0.0103 | 0.0101 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5407 | 55697.077 | 44271.0971 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6616.0668 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0012 | 0.0093 | 0.0105 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5410 | 55700.169 | 44271.0972 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6748.3881 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5413 | 55703.115 | 44271.0972 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6883.3559 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0014 | 0.01 | 0.0114 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5416 | 55706.384 | 44271.0973 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7021.023 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5419 | 55709.741 | 44271.0973 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7161.4435 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0005 | 0.0098 | 0.0103 | 0.0101 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5422 | 55712.933 | 44271.0973 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7304.6723 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.002 | 0.0093 | 0.0113 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5425 | 55715.968 | 44271.0974 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7450.7658 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0023 | 0.009 | 0.0113 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5428 | 55719.034 | 44271.0974 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7599.7811 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.001 | 0.0095 | 0.0105 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5431 | 55722.019 | 44271.0974 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7751.7767 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5434 | 55725.095 | 44271.0975 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7906.8123 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.002 | 0.0092 | 0.0112 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5437 | 55728.17 | 44271.0975 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8064.9485 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0021 | 0.0093 | 0.0114 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5440 | 55731.117 | 44271.0975 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8226.2475 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5443 | 55734.263 | 44271.0976 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8390.7724 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0019 | 0.0094 | 0.0113 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5446 | 55737.238 | 44271.0976 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8558.5879 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0011 | 0.0097 | 0.0108 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5449 | 55740.31 | 44271.0976 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8729.7596 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5452 | 55743.786 | 44271.0977 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8904.3548 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0011 | 0.0091 | 0.0102 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5455 | 55746.959 | 44271.0977 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9082.4419 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5458 | 55750.059 | 44271.0978 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9264.0908 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5461 | 55753.182 | 44271.0978 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9449.3726 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0005 | 0.0096 | 0.0101 | 0.0099 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5464 | 55756.561 | 44271.0978 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9638.36 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.002 | 0.0094 | 0.0114 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5467 | 55759.839 | 44271.0979 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9831.1272 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0005 | 0.0095 | 0.01 | 0.0097 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5470 | 55762.823 | 44271.0979 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10027.7498 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5473 | 55765.884 | 44271.0979 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10228.3048 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5476 | 55768.936 | 44271.098 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10432.8708 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5479 | 55771.909 | 44271.098 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10641.5283 | 0:240:120 | 0:00 | 0.0004 | 7 | 0.0021 | 0.0089 | 0.011 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5482 | 55774.885 | 44271.098 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10854.3588 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0014 | 0.0091 | 0.0105 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5485 | 55778.204 | 44271.0981 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11071.446 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0014 | 0.0098 | 0.0112 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5488 | 55781.367 | 44271.0981 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11292.8749 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0012 | 0.0095 | 0.0107 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5491 | 55784.343 | 44271.0982 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11518.7324 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5494 | 55787.304 | 44271.0982 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11749.1071 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0002 | 0.0099 | 0.0101 | 0.01 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5497 | 55790.726 | 44271.0982 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11984.0892 | 0:240:120 | 0:00 | 0.0003 | 7 | 0.0006 | 0.0099 | 0.0105 | 0.0101 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5500 | 56159.78 | 44271.1025 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.3 | 0:240:120 | 0:00 | 41.7153 | 7 | 124.5797 | 256.0571 | 380.6368 | 309.1269 | 51.9727 | 2701.1642 | 3 | 41.7153 | 171.8022 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5503 | 57160.914 | 44271.1141 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.6 | 0:240:120 | 0:00 | 35.7136 | 7 | 112.0315 | 129.5835 | 241.615 | 171.2867 | 51.701 | 2672.9906 | 3 | 35.7136 | 110.0865 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5506 | 57751.514 | 44271.1209 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.8 | 0:240:120 | 0:00 | 31.4534 | 7 | 45.0065 | 63.0803 | 108.0868 | 77.8779 | 21.8636 | 478.0177 | 3 | 31.4534 | 82.266 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5509 | 58028.435 | 44271.1241 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.1 | 0:240:120 | 0:00 | 27.792 | 7 | 4.0085 | 56.1187 | 60.1272 | 57.4339 | 1.9674 | 3.8708 | 3 | 27.792 | 64.3152 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5512 | 58204.333 | 44271.1262 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.5 | 0:240:120 | 0:00 | 24.6394 | 7 | 4.7597 | 47.8814 | 52.6411 | 49.935 | 2.0644 | 4.2618 | 3 | 24.6394 | 51.874 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5515 | 58358.305 | 44271.1279 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.8 | 0:240:120 | 0:00 | 22.2486 | 7 | 6.9272 | 38.7434 | 45.6706 | 41.9208 | 2.9208 | 8.531 | 3 | 22.2486 | 43.8401 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5518 | 58488.482 | 44271.1295 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.2 | 0:240:120 | 0:00 | 20.1059 | 7 | 4.4345 | 31.7663 | 36.2008 | 33.2258 | 2.1787 | 4.7467 | 3 | 20.1059 | 37.4673 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5521 | 58594.319 | 44271.1307 | Vista Speed | T | 25T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.6 | 0:240:120 | 0:00 | 18.3073 | 7 | 1.7037 | 28.9159 | 30.6196 | 29.6661 | 0.7319 | 0.5357 | 3 | 18.3073 | 32.6287 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5524 | 59315.595 | 44271.139 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.44 | 0:240:120 | 0:00 | 62.7171 | 7 | 60.856 | 594.5292 | 655.3852 | 615.2047 | 30.137 | 908.2395 | 3 | 62.7171 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5527 | 61166.386 | 44271.1604 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.9888 | 0:240:120 | 0:00 | 50.8745 | 7 | 66.1077 | 470.6867 | 536.7944 | 495.7115 | 30.8741 | 953.2117 | 3 | 50.8745 | 668.6928 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5530 | 62661.154 | 44271.1777 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.5686 | 0:240:120 | 0:00 | 42.5211 | 7 | 69.8063 | 348.5294 | 418.3357 | 375.074 | 32.606 | 1063.1486 | 3 | 42.5211 | 216.2953 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5533 | 63800.48 | 44271.1909 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.1799 | 0:240:120 | 0:00 | 36.317 | 7 | 109.8803 | 189.7149 | 299.5952 | 240.6298 | 46.3203 | 2145.5726 | 3 | 36.317 | 126.9433 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5536 | 64577.113 | 44271.1999 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.8235 | 0:240:120 | 0:00 | 31.5306 | 7 | 112.7733 | 62.8916 | 175.6649 | 103.337 | 53.9486 | 2910.4558 | 3 | 31.5307 | 88.7846 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5539 | 64991.85 | 44271.2047 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.5 | 0:240:120 | 0:00 | 27.7286 | 7 | 4.777 | 56.1726 | 60.9496 | 57.7653 | 2.3625 | 5.5815 | 3 | 27.7286 | 67.633 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5542 | 65169.709 | 44271.2068 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.21 | 0:240:120 | 0:00 | 24.6376 | 7 | 3.3045 | 49.6116 | 52.9161 | 50.7131 | 1.6483 | 2.7168 | 3 | 24.6376 | 54.1992 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5545 | 65324.866 | 44271.2086 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.9542 | 0:240:120 | 0:00 | 22.0772 | 7 | 4.3398 | 41.9969 | 46.3367 | 43.8951 | 1.8606 | 3.462 | 3 | 22.0772 | 44.917 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5548 | 65460.41 | 44271.2101 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.7333 | 0:240:120 | 0:00 | 19.9231 | 7 | 6.5112 | 33.2244 | 39.7356 | 35.6223 | 3.0945 | 9.576 | 3 | 19.9231 | 38.124 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5551 | 65572.84 | 44271.2114 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.548 | 0:240:120 | 0:00 | 18.0871 | 7 | 1.2203 | 28.8535 | 30.0738 | 29.2509 | 0.5935 | 0.3522 | 3 | 18.0871 | 32.941 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5554 | 65663.916 | 44271.2125 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.3989 | 0:240:120 | 0:00 | 16.5046 | 7 | 1.9024 | 25.872 | 27.7744 | 26.8001 | 0.7663 | 0.5872 | 3 | 16.5046 | 28.859 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5557 | 65747.315 | 44271.2135 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.2869 | 0:240:120 | 0:00 | 15.1276 | 7 | 1.5669 | 23.4318 | 24.9987 | 23.9491 | 0.7745 | 0.5998 | 3 | 15.1276 | 25.5633 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5560 | 65822.566 | 44271.2143 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.2126 | 0:240:120 | 0:00 | 13.9193 | 7 | 1.9041 | 20.4472 | 22.3513 | 21.3651 | 0.7913 | 0.6261 | 3 | 13.9193 | 22.8486 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5563 | 65889.372 | 44271.2151 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.1769 | 0:240:120 | 0:00 | 12.8514 | 7 | 0.8915 | 18.5566 | 19.4481 | 18.8428 | 0.4283 | 0.1834 | 3 | 12.8514 | 20.5753 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5566 | 65949.308 | 44271.2158 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.1804 | 0:240:120 | 0:00 | 11.9014 | 7 | 1.0754 | 16.947 | 18.0224 | 17.368 | 0.4967 | 0.2467 | 3 | 11.9014 | 18.6453 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5569 | 66004.828 | 44271.2164 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.224 | 0:240:120 | 0:00 | 11.0515 | 7 | 0.7004 | 15.7114 | 16.4118 | 16.0158 | 0.3007 | 0.0904 | 3 | 11.0515 | 16.9874 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5572 | 66055.675 | 44271.217 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.3085 | 0:240:120 | 0:00 | 10.2872 | 7 | 0.8227 | 14.26 | 15.0827 | 14.533 | 0.4068 | 0.1655 | 3 | 10.2872 | 15.549 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5575 | 66102.609 | 44271.2176 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 108.4347 | 0:240:120 | 0:00 | 9.5966 | 7 | 0.635 | 13.0871 | 13.7221 | 13.3178 | 0.3043 | 0.0926 | 3 | 9.5966 | 14.2901 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5578 | 66145.782 | 44271.2181 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.6034 | 0:240:120 | 0:00 | 8.9702 | 7 | 0.6357 | 12.1341 | 12.7698 | 12.3941 | 0.2891 | 0.0836 | 3 | 8.9702 | 13.1799 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5581 | 66186.352 | 44271.2186 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.8155 | 0:240:120 | 0:00 | 8.3997 | 7 | 0.6164 | 11.1991 | 11.8155 | 11.4809 | 0.2694 | 0.0726 | 3 | 8.3997 | 12.1943 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5584 | 66223.73 | 44271.219 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 115.0718 | 0:240:120 | 0:00 | 7.8784 | 7 | 0.5106 | 10.3495 | 10.8601 | 10.5758 | 0.219 | 0.048 | 3 | 7.8784 | 11.314 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5587 | 66258.527 | 44271.2194 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.3732 | 0:240:120 | 0:00 | 7.4006 | 7 | 0.4057 | 9.7181 | 10.1238 | 9.9291 | 0.1579 | 0.0249 | 3 | 7.4006 | 10.5236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5590 | 66291.291 | 44271.2198 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.7207 | 0:240:120 | 0:00 | 6.9613 | 7 | 0.416 | 9.079 | 9.495 | 9.2483 | 0.1901 | 0.0362 | 3 | 6.9613 | 9.8106 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5593 | 66322.316 | 44271.2201 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 122.1151 | 0:240:120 | 0:00 | 6.5565 | 7 | 0.4196 | 8.4474 | 8.867 | 8.6006 | 0.2004 | 0.0401 | 3 | 6.5565 | 9.1645 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5596 | 66351.256 | 44271.2205 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.5574 | 0:240:120 | 0:00 | 6.1823 | 7 | 0.2956 | 8.0039 | 8.2995 | 8.1057 | 0.1449 | 0.021 | 3 | 6.1823 | 8.5769 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5599 | 66378.656 | 44271.2208 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 127.0485 | 0:240:120 | 0:00 | 5.8359 | 7 | 0.2642 | 7.5552 | 7.8194 | 7.6442 | 0.1266 | 0.016 | 3 | 5.8359 | 8.0405 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5602 | 66404.479 | 44271.2211 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 129.5895 | 0:240:120 | 0:00 | 5.5144 | 7 | 0.2907 | 6.9797 | 7.2704 | 7.1223 | 0.1189 | 0.0141 | 3 | 5.5144 | 7.5493 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5605 | 66428.874 | 44271.2214 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 132.1813 | 0:240:120 | 0:00 | 5.2155 | 7 | 0.219 | 6.6454 | 6.8644 | 6.7216 | 0.1071 | 0.0115 | 3 | 5.2155 | 7.0982 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5608 | 66451.953 | 44271.2216 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.8249 | 0:240:120 | 0:00 | 4.937 | 7 | 0.1894 | 6.288 | 6.4774 | 6.3589 | 0.08 | 0.0064 | 3 | 4.937 | 6.6827 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5611 | 66473.976 | 44271.2219 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.5214 | 0:240:120 | 0:00 | 4.6772 | 7 | 0.2179 | 5.8843 | 6.1022 | 5.9578 | 0.1075 | 0.0116 | 3 | 4.6772 | 6.2991 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5614 | 66494.828 | 44271.2221 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 140.2718 | 0:240:120 | 0:00 | 4.4345 | 7 | 0.1571 | 5.5788 | 5.7359 | 5.6472 | 0.0672 | 0.0045 | 3 | 4.4345 | 5.9441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5617 | 66514.9 | 44271.2224 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 143.0773 | 0:240:120 | 0:00 | 4.2073 | 7 | 0.1675 | 5.2981 | 5.4656 | 5.3547 | 0.0829 | 0.0069 | 3 | 4.2073 | 5.6149 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5620 | 66533.843 | 44271.2226 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 145.9388 | 0:240:120 | 0:00 | 3.9944 | 7 | 0.1487 | 4.9838 | 5.1325 | 5.0401 | 0.0698 | 0.0049 | 3 | 3.9944 | 5.309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5623 | 66551.846 | 44271.2228 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.8576 | 0:240:120 | 0:00 | 3.7946 | 7 | 0.1323 | 4.7212 | 4.8535 | 4.784 | 0.0571 | 0.0033 | 3 | 3.7946 | 5.0242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5626 | 66569.03 | 44271.223 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 151.8348 | 0:240:120 | 0:00 | 3.6069 | 7 | 0.1411 | 4.4628 | 4.6039 | 4.5283 | 0.0593 | 0.0035 | 3 | 3.6069 | 4.7586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5629 | 66585.751 | 44271.2232 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 154.8714 | 0:240:120 | 0:00 | 3.4303 | 7 | 0.1171 | 4.2395 | 4.3566 | 4.2935 | 0.05 | 0.0025 | 3 | 3.4303 | 4.5105 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5632 | 66601.882 | 44271.2234 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 157.9689 | 0:240:120 | 0:00 | 3.2641 | 7 | 0.1165 | 4.0236 | 4.1401 | 4.0791 | 0.0489 | 0.0024 | 3 | 3.2641 | 4.2785 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5635 | 66617.038 | 44271.2235 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 161.1283 | 0:240:120 | 0:00 | 3.1075 | 7 | 0.0984 | 3.8218 | 3.9202 | 3.8669 | 0.0422 | 0.0018 | 3 | 3.1075 | 4.0611 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5638 | 66631.619 | 44271.2237 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.3508 | 0:240:120 | 0:00 | 2.9597 | 7 | 0.0876 | 3.6482 | 3.7358 | 3.6825 | 0.0403 | 0.0016 | 3 | 2.9597 | 3.8572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5641 | 66645.766 | 44271.2239 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 167.6378 | 0:240:120 | 0:00 | 2.8201 | 7 | 0.0877 | 3.4746 | 3.5623 | 3.5046 | 0.0431 | 0.0019 | 3 | 2.8201 | 3.6658 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5644 | 66659.435 | 44271.224 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.9906 | 0:240:120 | 0:00 | 2.6883 | 7 | 0.0838 | 3.2905 | 3.3743 | 3.3282 | 0.0347 | 0.0012 | 3 | 2.6883 | 3.4857 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5647 | 66672.416 | 44271.2242 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 174.4104 | 0:240:120 | 0:00 | 2.5636 | 7 | 0.0739 | 3.143 | 3.2169 | 3.1694 | 0.0351 | 0.0012 | 3 | 2.5636 | 3.3163 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5650 | 66685.099 | 44271.2243 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 177.8986 | 0:240:120 | 0:00 | 2.4455 | 7 | 0.0723 | 2.9836 | 3.0559 | 3.0155 | 0.0302 | 0.0009 | 3 | 2.4455 | 3.1567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5653 | 66697.195 | 44271.2245 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 181.4566 | 0:240:120 | 0:00 | 2.3337 | 7 | 0.064 | 2.8573 | 2.9213 | 2.8793 | 0.0312 | 0.001 | 3 | 2.3337 | 3.0061 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5656 | 66708.682 | 44271.2246 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 185.0857 | 0:240:120 | 0:00 | 2.2278 | 7 | 0.0512 | 2.7179 | 2.7691 | 2.737 | 0.0238 | 0.0006 | 3 | 2.2278 | 2.864 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5659 | 66719.781 | 44271.2247 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 188.7874 | 0:240:120 | 0:00 | 2.1273 | 7 | 0.0505 | 2.5894 | 2.6399 | 2.6122 | 0.0219 | 0.0005 | 3 | 2.1273 | 2.7297 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5662 | 66730.81 | 44271.2249 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 192.5632 | 0:240:120 | 0:00 | 2.032 | 7 | 0.0456 | 2.4676 | 2.5132 | 2.4886 | 0.0189 | 0.0004 | 3 | 2.032 | 2.6028 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5665 | 66741.366 | 44271.225 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 196.4144 | 0:240:120 | 0:00 | 1.9414 | 7 | 0.0452 | 2.3553 | 2.4005 | 2.3771 | 0.0192 | 0.0004 | 3 | 1.9414 | 2.4827 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5668 | 66751.29 | 44271.2251 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 200.3427 | 0:240:120 | 0:00 | 1.8554 | 7 | 0.0383 | 2.2511 | 2.2894 | 2.2682 | 0.0166 | 0.0003 | 3 | 1.8554 | 2.3689 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5671 | 66761.034 | 44271.2252 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 204.3496 | 0:240:120 | 0:00 | 1.7737 | 7 | 0.041 | 2.1529 | 2.1939 | 2.1672 | 0.0194 | 0.0004 | 3 | 1.7737 | 2.2611 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5674 | 66770.496 | 44271.2253 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.4366 | 0:240:120 | 0:00 | 1.6959 | 7 | 0.0405 | 2.0559 | 2.0964 | 2.0713 | 0.0177 | 0.0003 | 3 | 1.6959 | 2.1589 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5677 | 66779.716 | 44271.2254 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 212.6053 | 0:240:120 | 0:00 | 1.622 | 7 | 0.034 | 1.9616 | 1.9956 | 1.9764 | 0.0147 | 0.0002 | 3 | 1.622 | 2.062 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5680 | 66788.681 | 44271.2255 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 216.8574 | 0:240:120 | 0:00 | 1.5516 | 7 | 0.0415 | 1.872 | 1.9135 | 1.8902 | 0.0175 | 0.0003 | 3 | 1.5516 | 1.9699 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5683 | 66797.362 | 44271.2256 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 221.1946 | 0:240:120 | 0:00 | 1.4845 | 7 | 0.0307 | 1.7934 | 1.8241 | 1.8038 | 0.015 | 0.0002 | 3 | 1.4845 | 1.8825 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5686 | 66805.566 | 44271.2257 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 225.6185 | 0:240:120 | 0:00 | 1.4207 | 7 | 0.0269 | 1.7137 | 1.7406 | 1.7258 | 0.0114 | 0.0001 | 3 | 1.4207 | 1.7994 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5689 | 66813.752 | 44271.2258 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 230.1308 | 0:240:120 | 0:00 | 1.3598 | 7 | 0.0263 | 1.6366 | 1.6629 | 1.6483 | 0.0114 | 0.0001 | 3 | 1.3598 | 1.7204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5692 | 66821.588 | 44271.2259 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.7334 | 0:240:120 | 0:00 | 1.3018 | 7 | 0.0249 | 1.5669 | 1.5918 | 1.5783 | 0.0104 | 0.0001 | 3 | 1.3018 | 1.6453 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5695 | 66829.171 | 44271.226 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 239.4281 | 0:240:120 | 0:00 | 1.2464 | 7 | 0.0208 | 1.501 | 1.5218 | 1.5102 | 0.0088 | 0.0001 | 3 | 1.2464 | 1.5737 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5698 | 66836.686 | 44271.2261 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 244.2167 | 0:240:120 | 0:00 | 1.1937 | 7 | 0.0215 | 1.4378 | 1.4593 | 1.446 | 0.0097 | 0.0001 | 3 | 1.1937 | 1.5057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5701 | 66843.925 | 44271.2262 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 249.101 | 0:240:120 | 0:00 | 1.1433 | 7 | 0.023 | 1.3762 | 1.3992 | 1.3847 | 0.0101 | 0.0001 | 3 | 1.1433 | 1.4408 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5704 | 66851.17 | 44271.2262 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 254.083 | 0:240:120 | 0:00 | 1.0952 | 7 | 0.0178 | 1.3168 | 1.3346 | 1.3244 | 0.0077 | 0.0001 | 3 | 1.0952 | 1.379 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5707 | 66858.102 | 44271.2263 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 259.1647 | 0:240:120 | 0:00 | 1.0493 | 7 | 0.0189 | 1.2573 | 1.2762 | 1.2658 | 0.0081 | 0.0001 | 3 | 1.0493 | 1.3201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5710 | 66864.9 | 44271.2264 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 264.348 | 0:240:120 | 0:00 | 1.0054 | 7 | 0.0178 | 1.2094 | 1.2272 | 1.2158 | 0.0081 | 0.0001 | 3 | 1.0054 | 1.2639 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5713 | 66871.55 | 44271.2265 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 269.6349 | 0:240:120 | 0:00 | 0.9635 | 7 | 0.0145 | 1.1582 | 1.1727 | 1.1634 | 0.0066 | 0 | 3 | 0.9635 | 1.2103 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5716 | 66877.887 | 44271.2266 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 275.0276 | 0:240:120 | 0:00 | 0.9235 | 7 | 0.0164 | 1.1085 | 1.1249 | 1.1144 | 0.0073 | 0.0001 | 3 | 0.9235 | 1.1592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5719 | 66884.382 | 44271.2266 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 280.5282 | 0:240:120 | 0:00 | 0.8852 | 7 | 0.0137 | 1.0614 | 1.0751 | 1.0669 | 0.006 | 0 | 3 | 0.8852 | 1.1104 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5722 | 66890.88 | 44271.2267 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 286.1388 | 0:240:120 | 0:00 | 0.8486 | 7 | 0.0139 | 1.017 | 1.0309 | 1.0225 | 0.0054 | 0 | 3 | 0.8486 | 1.0638 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5725 | 66897.045 | 44271.2268 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 291.8615 | 0:240:120 | 0:00 | 0.8136 | 7 | 0.0113 | 0.9761 | 0.9874 | 0.9808 | 0.0049 | 0 | 3 | 0.8136 | 1.0193 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5728 | 66902.897 | 44271.2268 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 297.6988 | 0:240:120 | 0:00 | 0.7802 | 7 | 0.0106 | 0.9343 | 0.9449 | 0.9389 | 0.0044 | 0 | 3 | 0.7802 | 0.9767 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5731 | 66908.921 | 44271.2269 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 303.6527 | 0:240:120 | 0:00 | 0.7482 | 7 | 0.013 | 0.8942 | 0.9072 | 0.8998 | 0.0055 | 0 | 3 | 0.7482 | 0.9361 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5734 | 66914.927 | 44271.227 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 309.7258 | 0:240:120 | 0:00 | 0.7175 | 7 | 0.0115 | 0.8577 | 0.8692 | 0.8625 | 0.0051 | 0 | 3 | 0.7175 | 0.8973 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5737 | 66920.573 | 44271.227 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 315.9203 | 0:240:120 | 0:00 | 0.6882 | 7 | 0.0114 | 0.8221 | 0.8335 | 0.8269 | 0.0048 | 0 | 3 | 0.6882 | 0.8602 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5740 | 66925.93 | 44271.2271 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 322.2387 | 0:240:120 | 0:00 | 0.6601 | 7 | 0.0105 | 0.7901 | 0.8006 | 0.7939 | 0.0044 | 0 | 3 | 0.6601 | 0.8247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5743 | 66931.549 | 44271.2272 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 328.6835 | 0:240:120 | 0:00 | 0.6333 | 7 | 0.0117 | 0.755 | 0.7667 | 0.7609 | 0.0047 | 0 | 3 | 0.6333 | 0.7907 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5746 | 66936.77 | 44271.2272 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 335.2572 | 0:240:120 | 0:00 | 0.6075 | 7 | 0.0098 | 0.7264 | 0.7362 | 0.73 | 0.0044 | 0 | 3 | 0.6075 | 0.7583 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5749 | 66941.909 | 44271.2273 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 341.9623 | 0:240:120 | 0:00 | 0.5829 | 7 | 0.0111 | 0.6947 | 0.7058 | 0.7003 | 0.0042 | 0 | 3 | 0.5829 | 0.7272 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5752 | 66947.125 | 44271.2274 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 348.8015 | 0:240:120 | 0:00 | 0.5593 | 7 | 0.0092 | 0.667 | 0.6762 | 0.6717 | 0.0039 | 0 | 3 | 0.5593 | 0.6975 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5755 | 66952.258 | 44271.2274 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 355.7776 | 0:240:120 | 0:00 | 0.5367 | 7 | 0.0083 | 0.6405 | 0.6488 | 0.6446 | 0.0035 | 0 | 3 | 0.5367 | 0.669 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5758 | 66957.352 | 44271.2275 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 362.8931 | 0:240:120 | 0:00 | 0.5151 | 7 | 0.0103 | 0.6125 | 0.6228 | 0.618 | 0.004 | 0 | 3 | 0.5151 | 0.6418 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5761 | 66962.066 | 44271.2275 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 370.151 | 0:240:120 | 0:00 | 0.4943 | 7 | 0.0087 | 0.5894 | 0.5981 | 0.593 | 0.0035 | 0 | 3 | 0.4943 | 0.6157 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5764 | 66966.654 | 44271.2276 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 377.554 | 0:240:120 | 0:00 | 0.4744 | 7 | 0.009 | 0.5645 | 0.5735 | 0.5688 | 0.0035 | 0 | 3 | 0.4744 | 0.5907 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5767 | 66971.269 | 44271.2276 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 385.1051 | 0:240:120 | 0:00 | 0.4554 | 7 | 0.008 | 0.5421 | 0.5501 | 0.5461 | 0.0031 | 0 | 3 | 0.4554 | 0.5668 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5770 | 66975.971 | 44271.2277 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 392.8072 | 0:240:120 | 0:00 | 0.4371 | 7 | 0.0077 | 0.5204 | 0.5281 | 0.5242 | 0.0031 | 0 | 3 | 0.4371 | 0.5439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5773 | 66980.608 | 44271.2277 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 400.6633 | 0:240:120 | 0:00 | 0.4196 | 7 | 0.0083 | 0.4991 | 0.5074 | 0.503 | 0.0032 | 0 | 3 | 0.4196 | 0.5219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5776 | 66985.249 | 44271.2278 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 408.6766 | 0:240:120 | 0:00 | 0.4028 | 7 | 0.0089 | 0.4778 | 0.4867 | 0.4827 | 0.0034 | 0 | 3 | 0.4028 | 0.5009 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5779 | 66989.63 | 44271.2278 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 416.8501 | 0:240:120 | 0:00 | 0.3867 | 7 | 0.0086 | 0.4596 | 0.4682 | 0.4638 | 0.0033 | 0 | 3 | 0.3867 | 0.4807 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5782 | 66993.917 | 44271.2279 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 425.1871 | 0:240:120 | 0:00 | 0.3712 | 7 | 0.0065 | 0.4419 | 0.4484 | 0.4451 | 0.0025 | 0 | 3 | 0.3712 | 0.4614 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5785 | 66998.17 | 44271.2279 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 433.6909 | 0:240:120 | 0:00 | 0.3564 | 7 | 0.0078 | 0.4236 | 0.4314 | 0.4275 | 0.0031 | 0 | 3 | 0.3564 | 0.4429 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5788 | 67002.459 | 44271.228 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 442.3647 | 0:240:120 | 0:00 | 0.3422 | 7 | 0.0065 | 0.4076 | 0.4141 | 0.4104 | 0.0028 | 0 | 3 | 0.3422 | 0.4251 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5791 | 67006.673 | 44271.228 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 451.212 | 0:240:120 | 0:00 | 0.3286 | 7 | 0.0075 | 0.3906 | 0.3981 | 0.3942 | 0.0028 | 0 | 3 | 0.3286 | 0.4081 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5794 | 67010.847 | 44271.2281 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 460.2362 | 0:240:120 | 0:00 | 0.3156 | 7 | 0.0075 | 0.3743 | 0.3818 | 0.3779 | 0.003 | 0 | 3 | 0.3156 | 0.3918 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5797 | 67015.114 | 44271.2281 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 469.441 | 0:240:120 | 0:00 | 0.303 | 7 | 0.0064 | 0.3603 | 0.3667 | 0.363 | 0.0027 | 0 | 3 | 0.303 | 0.3761 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5800 | 67019.35 | 44271.2282 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 478.8298 | 0:240:120 | 0:00 | 0.291 | 7 | 0.0085 | 0.3443 | 0.3528 | 0.3486 | 0.003 | 0 | 3 | 0.291 | 0.3611 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5803 | 67023.493 | 44271.2282 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 488.4064 | 0:240:120 | 0:00 | 0.2795 | 7 | 0.0069 | 0.3309 | 0.3378 | 0.3344 | 0.0026 | 0 | 3 | 0.2795 | 0.3467 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5806 | 67027.516 | 44271.2283 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 498.1745 | 0:240:120 | 0:00 | 0.2684 | 7 | 0.0078 | 0.3174 | 0.3252 | 0.3212 | 0.0033 | 0 | 3 | 0.2684 | 0.3329 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5809 | 67031.492 | 44271.2283 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 508.138 | 0:240:120 | 0:00 | 0.2578 | 7 | 0.0057 | 0.3054 | 0.3111 | 0.3084 | 0.0021 | 0 | 3 | 0.2578 | 0.3197 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5812 | 67035.461 | 44271.2284 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 518.3007 | 0:240:120 | 0:00 | 0.2476 | 7 | 0.0073 | 0.2931 | 0.3004 | 0.2966 | 0.0027 | 0 | 3 | 0.2476 | 0.307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5815 | 67039.668 | 44271.2284 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 528.6668 | 0:240:120 | 0:00 | 0.2378 | 7 | 0.0055 | 0.2823 | 0.2878 | 0.2848 | 0.0021 | 0 | 3 | 0.2378 | 0.2948 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5818 | 67043.856 | 44271.2285 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 539.2401 | 0:240:120 | 0:00 | 0.2284 | 7 | 0.0046 | 0.2713 | 0.2759 | 0.2733 | 0.0019 | 0 | 3 | 0.2284 | 0.2831 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5821 | 67047.806 | 44271.2285 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 550.0249 | 0:240:120 | 0:00 | 0.2194 | 7 | 0.0064 | 0.2604 | 0.2668 | 0.2632 | 0.0023 | 0 | 3 | 0.2194 | 0.2719 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5824 | 67051.788 | 44271.2286 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 561.0254 | 0:240:120 | 0:00 | 0.2107 | 7 | 0.0056 | 0.2502 | 0.2558 | 0.2524 | 0.0024 | 0 | 3 | 0.2107 | 0.2611 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5827 | 67055.671 | 44271.2286 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 572.2459 | 0:240:120 | 0:00 | 0.2024 | 7 | 0.0051 | 0.2395 | 0.2446 | 0.242 | 0.0021 | 0 | 3 | 0.2024 | 0.2508 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5830 | 67059.338 | 44271.2287 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 583.6908 | 0:240:120 | 0:00 | 0.1944 | 7 | 0.0046 | 0.2306 | 0.2352 | 0.2325 | 0.0018 | 0 | 3 | 0.1944 | 0.2409 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5833 | 67063.07 | 44271.2287 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 595.3646 | 0:240:120 | 0:00 | 0.1868 | 7 | 0.005 | 0.2208 | 0.2258 | 0.2231 | 0.0019 | 0 | 3 | 0.1868 | 0.2313 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5836 | 67066.717 | 44271.2287 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 607.2719 | 0:240:120 | 0:00 | 0.1794 | 7 | 0.0056 | 0.2118 | 0.2174 | 0.2142 | 0.0022 | 0 | 3 | 0.1794 | 0.2222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5839 | 67070.252 | 44271.2288 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 619.4174 | 0:240:120 | 0:00 | 0.1724 | 7 | 0.0042 | 0.2046 | 0.2088 | 0.2062 | 0.0016 | 0 | 3 | 0.1724 | 0.2134 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5842 | 67073.74 | 44271.2288 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 631.8057 | 0:240:120 | 0:00 | 0.1656 | 7 | 0.0038 | 0.1966 | 0.2004 | 0.1983 | 0.0015 | 0 | 3 | 0.1656 | 0.205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5845 | 67077.194 | 44271.2289 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 644.4418 | 0:240:120 | 0:00 | 0.1591 | 7 | 0.0041 | 0.1886 | 0.1927 | 0.1902 | 0.0016 | 0 | 3 | 0.1591 | 0.1969 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5848 | 67080.605 | 44271.2289 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 657.3307 | 0:240:120 | 0:00 | 0.1528 | 7 | 0.0041 | 0.1815 | 0.1856 | 0.1833 | 0.0017 | 0 | 3 | 0.1528 | 0.1892 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5851 | 67084.106 | 44271.2289 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 670.4773 | 0:240:120 | 0:00 | 0.1468 | 7 | 0.004 | 0.1742 | 0.1782 | 0.1754 | 0.0014 | 0 | 3 | 0.1468 | 0.1817 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5854 | 67087.76 | 44271.229 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 683.8868 | 0:240:120 | 0:00 | 0.1411 | 7 | 0.0028 | 0.1681 | 0.1709 | 0.1693 | 0.001 | 0 | 3 | 0.1411 | 0.1746 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5857 | 67091.136 | 44271.229 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 697.5646 | 0:240:120 | 0:00 | 0.1355 | 7 | 0.0042 | 0.161 | 0.1652 | 0.1624 | 0.0018 | 0 | 3 | 0.1355 | 0.1677 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5860 | 67094.752 | 44271.2291 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 711.5159 | 0:240:120 | 0:00 | 0.1302 | 7 | 0.0034 | 0.1548 | 0.1582 | 0.1563 | 0.0013 | 0 | 3 | 0.1302 | 0.1611 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5863 | 67098.554 | 44271.2291 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 725.7462 | 0:240:120 | 0:00 | 0.1251 | 7 | 0.0032 | 0.1489 | 0.1521 | 0.1503 | 0.0011 | 0 | 3 | 0.1251 | 0.1548 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5866 | 67101.959 | 44271.2291 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 740.2611 | 0:240:120 | 0:00 | 0.1202 | 7 | 0.0025 | 0.1426 | 0.1451 | 0.1436 | 0.0009 | 0 | 3 | 0.1202 | 0.1487 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5869 | 67105.384 | 44271.2292 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 755.0663 | 0:240:120 | 0:00 | 0.1155 | 7 | 0.0027 | 0.1376 | 0.1403 | 0.139 | 0.001 | 0 | 3 | 0.1155 | 0.1429 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5872 | 67108.832 | 44271.2292 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 770.1676 | 0:240:120 | 0:00 | 0.111 | 7 | 0.0035 | 0.1317 | 0.1352 | 0.1329 | 0.0014 | 0 | 3 | 0.111 | 0.1373 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5875 | 67112.136 | 44271.2293 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 785.571 | 0:240:120 | 0:00 | 0.1066 | 7 | 0.0028 | 0.1274 | 0.1302 | 0.1283 | 0.0011 | 0 | 3 | 0.1066 | 0.1319 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5878 | 67115.391 | 44271.2293 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 801.2824 | 0:240:120 | 0:00 | 0.1025 | 7 | 0.0035 | 0.1218 | 0.1253 | 0.1235 | 0.0012 | 0 | 3 | 0.1025 | 0.1267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5881 | 67118.817 | 44271.2293 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 817.3081 | 0:240:120 | 0:00 | 0.0984 | 7 | 0.0029 | 0.1169 | 0.1198 | 0.1179 | 0.001 | 0 | 3 | 0.0984 | 0.1218 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5884 | 67122.132 | 44271.2294 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 833.6542 | 0:240:120 | 0:00 | 0.0946 | 7 | 0.0022 | 0.1128 | 0.115 | 0.1139 | 0.0008 | 0 | 3 | 0.0946 | 0.117 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5887 | 67125.462 | 44271.2294 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 850.3273 | 0:240:120 | 0:00 | 0.0909 | 7 | 0.0022 | 0.1087 | 0.1109 | 0.1097 | 0.0008 | 0 | 3 | 0.0909 | 0.1124 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5890 | 67128.802 | 44271.2295 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 867.3339 | 0:240:120 | 0:00 | 0.0873 | 7 | 0.0026 | 0.1039 | 0.1065 | 0.1051 | 0.001 | 0 | 3 | 0.0873 | 0.108 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5893 | 67131.996 | 44271.2295 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 884.6805 | 0:240:120 | 0:00 | 0.0839 | 7 | 0.0035 | 0.0987 | 0.1022 | 0.1009 | 0.0012 | 0 | 3 | 0.0839 | 0.1038 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5896 | 67135.383 | 44271.2295 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 902.3741 | 0:240:120 | 0:00 | 0.0807 | 7 | 0.0024 | 0.096 | 0.0984 | 0.0967 | 0.001 | 0 | 3 | 0.0807 | 0.0997 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5899 | 67138.644 | 44271.2296 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 920.4216 | 0:240:120 | 0:00 | 0.0775 | 7 | 0.0022 | 0.0929 | 0.0951 | 0.094 | 0.0008 | 0 | 3 | 0.0775 | 0.0958 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5902 | 67141.963 | 44271.2296 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 938.8301 | 0:240:120 | 0:00 | 0.0745 | 7 | 0.0031 | 0.0879 | 0.091 | 0.0898 | 0.001 | 0 | 3 | 0.0745 | 0.0921 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5905 | 67145.293 | 44271.2296 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 957.6067 | 0:240:120 | 0:00 | 0.0716 | 7 | 0.0027 | 0.0849 | 0.0876 | 0.0863 | 0.0011 | 0 | 3 | 0.0716 | 0.0885 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5908 | 67148.593 | 44271.2297 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 976.7588 | 0:240:120 | 0:00 | 0.0688 | 7 | 0.0041 | 0.0809 | 0.085 | 0.0832 | 0.0013 | 0 | 3 | 0.0688 | 0.085 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5911 | 67151.862 | 44271.2297 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 996.294 | 0:240:120 | 0:00 | 0.0661 | 7 | 0.0033 | 0.078 | 0.0813 | 0.08 | 0.0012 | 0 | 3 | 0.0661 | 0.0817 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5914 | 67155.838 | 44271.2298 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1016.2198 | 0:240:120 | 0:00 | 0.0635 | 7 | 0.0035 | 0.075 | 0.0785 | 0.0768 | 0.0012 | 0 | 3 | 0.0635 | 0.0785 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5917 | 67159.398 | 44271.2298 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1036.5442 | 0:240:120 | 0:00 | 0.061 | 7 | 0.0025 | 0.073 | 0.0755 | 0.0742 | 0.0007 | 0 | 3 | 0.061 | 0.0754 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5920 | 67162.901 | 44271.2299 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1057.2751 | 0:240:120 | 0:00 | 0.0587 | 7 | 0.0013 | 0.0703 | 0.0716 | 0.0712 | 0.0006 | 0 | 3 | 0.0587 | 0.0725 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5923 | 67166.418 | 44271.2299 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1078.4206 | 0:240:120 | 0:00 | 0.0564 | 7 | 0.0033 | 0.0675 | 0.0708 | 0.0689 | 0.0012 | 0 | 3 | 0.0564 | 0.0697 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5926 | 67169.686 | 44271.2299 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1099.989 | 0:240:120 | 0:00 | 0.0542 | 7 | 0.0039 | 0.0637 | 0.0676 | 0.0657 | 0.0014 | 0 | 3 | 0.0542 | 0.0669 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5929 | 67173.398 | 44271.23 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1121.9888 | 0:240:120 | 0:00 | 0.0521 | 7 | 0.0031 | 0.0617 | 0.0648 | 0.0633 | 0.0011 | 0 | 3 | 0.0521 | 0.0643 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5932 | 67176.709 | 44271.23 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1144.4286 | 0:240:120 | 0:00 | 0.05 | 7 | 0.003 | 0.059 | 0.062 | 0.061 | 0.0012 | 0 | 3 | 0.05 | 0.0618 | P | NP | 0-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
5935 | 67179.926 | 44271.23 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1167.3172 | 0:240:120 | 0:00 | 0.0481 | 7 | 0.0022 | 0.0574 | 0.0596 | 0.0587 | 0.0007 | 0 | 3 | 0.0481 | 0.0594 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5938 | 67183.421 | 44271.2301 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1190.6635 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0023 | 0.0552 | 0.0575 | 0.0565 | 0.0009 | 0 | 3 | 0.0462 | 0.0571 | P | NP | 1-1-1-0-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5941 | 67186.832 | 44271.2301 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1214.4768 | 0:240:120 | 0:00 | 0.0444 | 7 | 0.0037 | 0.0519 | 0.0556 | 0.0541 | 0.0013 | 0 | 3 | 0.0444 | 0.0549 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5944 | 67190.061 | 44271.2302 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1238.7663 | 0:240:120 | 0:00 | 0.0427 | 7 | 0.0026 | 0.0508 | 0.0534 | 0.0522 | 0.0009 | 0 | 3 | 0.0427 | 0.0527 | P | NP | 0-1-0-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5947 | 67193.548 | 44271.2302 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1263.5417 | 0:240:120 | 0:00 | 0.041 | 7 | 0.0032 | 0.0485 | 0.0517 | 0.05 | 0.0011 | 0 | 3 | 0.041 | 0.051 | P | NP | 1-1-0-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5950 | 67196.841 | 44271.2302 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1288.8125 | 0:240:120 | 0:00 | 0.0394 | 7 | 0.0035 | 0.0457 | 0.0492 | 0.0478 | 0.0011 | 0 | 3 | 0.0394 | 0.0494 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5953 | 67200.12 | 44271.2303 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1314.5887 | 0:240:120 | 0:00 | 0.0379 | 7 | 0.0033 | 0.0443 | 0.0476 | 0.0463 | 0.0013 | 0 | 3 | 0.0379 | 0.0479 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5956 | 67203.264 | 44271.2303 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1340.8805 | 0:240:120 | 0:00 | 0.0364 | 7 | 0.0032 | 0.0433 | 0.0465 | 0.0447 | 0.0011 | 0 | 3 | 0.0364 | 0.0464 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5959 | 67206.54 | 44271.2304 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1367.6981 | 0:240:120 | 0:00 | 0.035 | 7 | 0.0032 | 0.0412 | 0.0444 | 0.043 | 0.0011 | 0 | 3 | 0.035 | 0.045 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5962 | 67209.82 | 44271.2304 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1395.0521 | 0:240:120 | 0:00 | 0.0336 | 7 | 0.0038 | 0.0388 | 0.0426 | 0.0408 | 0.0014 | 0 | 3 | 0.0336 | 0.0436 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5965 | 67213.081 | 44271.2304 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1422.9531 | 0:240:120 | 0:00 | 0.0323 | 7 | 0.0024 | 0.0383 | 0.0407 | 0.0398 | 0.001 | 0 | 3 | 0.0323 | 0.0423 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5968 | 67216.215 | 44271.2305 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1451.4122 | 0:240:120 | 0:00 | 0.0311 | 7 | 0.0033 | 0.0363 | 0.0396 | 0.0383 | 0.0012 | 0 | 3 | 0.0311 | 0.0411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5971 | 67219.409 | 44271.2305 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1480.4404 | 0:240:120 | 0:00 | 0.0299 | 7 | 0.0031 | 0.0355 | 0.0386 | 0.0368 | 0.001 | 0 | 3 | 0.0299 | 0.0399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5974 | 67222.566 | 44271.2305 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1510.0492 | 0:240:120 | 0:00 | 0.0287 | 7 | 0.0037 | 0.0332 | 0.0369 | 0.0354 | 0.0014 | 0 | 3 | 0.0287 | 0.0387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5977 | 67225.741 | 44271.2306 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1540.2502 | 0:240:120 | 0:00 | 0.0276 | 7 | 0.0027 | 0.0326 | 0.0353 | 0.0339 | 0.0008 | 0 | 3 | 0.0276 | 0.0376 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5980 | 67229.035 | 44271.2306 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1571.0552 | 0:240:120 | 0:00 | 0.0265 | 7 | 0.0024 | 0.0317 | 0.0341 | 0.0332 | 0.0008 | 0 | 3 | 0.0265 | 0.0365 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5983 | 67232.189 | 44271.2307 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1602.4763 | 0:240:120 | 0:00 | 0.0255 | 7 | 0.0031 | 0.0304 | 0.0335 | 0.0321 | 0.0014 | 0 | 3 | 0.0255 | 0.0355 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5986 | 67235.403 | 44271.2307 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1634.5259 | 0:240:120 | 0:00 | 0.0245 | 7 | 0.0031 | 0.0287 | 0.0318 | 0.0303 | 0.0011 | 0 | 3 | 0.0245 | 0.0345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5989 | 67238.457 | 44271.2307 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1667.2164 | 0:240:120 | 0:00 | 0.0235 | 7 | 0.0033 | 0.028 | 0.0313 | 0.0297 | 0.0012 | 0 | 3 | 0.0235 | 0.0335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5992 | 67241.704 | 44271.2308 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1700.5607 | 0:240:120 | 0:00 | 0.0226 | 7 | 0.0028 | 0.027 | 0.0298 | 0.0287 | 0.001 | 0 | 3 | 0.0226 | 0.0326 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5995 | 67244.725 | 44271.2308 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1734.5719 | 0:240:120 | 0:00 | 0.0217 | 7 | 0.0029 | 0.0268 | 0.0297 | 0.0281 | 0.0009 | 0 | 3 | 0.0217 | 0.0317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5998 | 67248.099 | 44271.2308 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1769.2634 | 0:240:120 | 0:00 | 0.0209 | 7 | 0.0041 | 0.0245 | 0.0286 | 0.0268 | 0.0014 | 0 | 3 | 0.0209 | 0.0309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6001 | 67251.306 | 44271.2309 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1804.6486 | 0:240:120 | 0:00 | 0.0201 | 7 | 0.0024 | 0.0247 | 0.0271 | 0.0258 | 0.0009 | 0 | 3 | 0.0201 | 0.0301 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6004 | 67254.328 | 44271.2309 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1840.7416 | 0:240:120 | 0:00 | 0.0193 | 7 | 0.0032 | 0.0231 | 0.0263 | 0.0252 | 0.0011 | 0 | 3 | 0.0193 | 0.0293 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6007 | 67257.639 | 44271.2309 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1877.5564 | 0:240:120 | 0:00 | 0.0185 | 7 | 0.0037 | 0.0225 | 0.0262 | 0.0245 | 0.0012 | 0 | 3 | 0.0185 | 0.0285 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6010 | 67260.842 | 44271.231 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1915.1076 | 0:240:120 | 0:00 | 0.0178 | 7 | 0.0027 | 0.0223 | 0.025 | 0.0236 | 0.0009 | 0 | 3 | 0.0178 | 0.0278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6013 | 67264.31 | 44271.231 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1953.4097 | 0:240:120 | 0:00 | 0.0171 | 7 | 0.0036 | 0.0208 | 0.0244 | 0.023 | 0.0012 | 0 | 3 | 0.0171 | 0.0271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6016 | 67267.387 | 44271.2311 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1992.4779 | 0:240:120 | 0:00 | 0.0165 | 7 | 0.0029 | 0.0209 | 0.0238 | 0.0228 | 0.0012 | 0 | 3 | 0.0165 | 0.0265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6019 | 67270.458 | 44271.2311 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2032.3275 | 0:240:120 | 0:00 | 0.0158 | 7 | 0.0043 | 0.02 | 0.0243 | 0.0224 | 0.0016 | 0 | 3 | 0.0158 | 0.0258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6022 | 67273.549 | 44271.2311 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2072.974 | 0:240:120 | 0:00 | 0.0152 | 7 | 0.0041 | 0.0191 | 0.0232 | 0.0215 | 0.0014 | 0 | 3 | 0.0152 | 0.0252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6025 | 67276.972 | 44271.2312 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2114.4335 | 0:240:120 | 0:00 | 0.0146 | 7 | 0.0042 | 0.0185 | 0.0227 | 0.0212 | 0.0014 | 0 | 3 | 0.0146 | 0.0246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6028 | 67280.044 | 44271.2312 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2156.7222 | 0:240:120 | 0:00 | 0.014 | 7 | 0.0036 | 0.0184 | 0.022 | 0.0206 | 0.0014 | 0 | 3 | 0.014 | 0.024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6031 | 67283.084 | 44271.2312 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2199.8566 | 0:240:120 | 0:00 | 0.0135 | 7 | 0.0034 | 0.0185 | 0.0219 | 0.0204 | 0.0012 | 0 | 3 | 0.0135 | 0.0235 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6034 | 67286.269 | 44271.2313 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2243.8537 | 0:240:120 | 0:00 | 0.013 | 7 | 0.0033 | 0.0179 | 0.0212 | 0.0198 | 0.0013 | 0 | 3 | 0.013 | 0.023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6037 | 67289.368 | 44271.2313 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2288.7308 | 0:240:120 | 0:00 | 0.0125 | 7 | 0.0032 | 0.0179 | 0.0211 | 0.0193 | 0.001 | 0 | 3 | 0.0125 | 0.0225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6040 | 67292.63 | 44271.2314 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2334.5054 | 0:240:120 | 0:00 | 0.012 | 7 | 0.0032 | 0.0178 | 0.021 | 0.0192 | 0.0012 | 0 | 3 | 0.012 | 0.022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6043 | 67295.702 | 44271.2314 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2381.1955 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0022 | 0.0174 | 0.0196 | 0.0186 | 0.0007 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6046 | 67298.654 | 44271.2314 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2428.8194 | 0:240:120 | 0:00 | 0.0111 | 7 | 0.0018 | 0.0175 | 0.0193 | 0.0181 | 0.0007 | 0 | 3 | 0.0111 | 0.0211 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6049 | 67301.723 | 44271.2315 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2477.3958 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0018 | 0.0172 | 0.019 | 0.0179 | 0.0008 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6052 | 67304.876 | 44271.2315 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2526.9437 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.0013 | 0.0173 | 0.0186 | 0.0178 | 0.0004 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6055 | 67307.957 | 44271.2315 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2555.8788 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0016 | 0.0164 | 0.018 | 0.0171 | 0.0004 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6058 | 67311.009 | 44271.2316 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2606.9963 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0021 | 0.0156 | 0.0177 | 0.0168 | 0.0007 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-1-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
6061 | 67313.99 | 44271.2316 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2659.1363 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0011 | 0.0159 | 0.017 | 0.0164 | 0.0004 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 0-0-0-1-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6064 | 67317.07 | 44271.2316 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2712.319 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0022 | 0.0147 | 0.0169 | 0.0161 | 0.0007 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6067 | 67320.135 | 44271.2317 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2766.5654 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0018 | 0.0149 | 0.0167 | 0.0158 | 0.0006 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-1-0-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6070 | 67323.193 | 44271.2317 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2821.8967 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.003 | 0.0141 | 0.0171 | 0.0154 | 0.001 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6073 | 67326.365 | 44271.2317 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2878.3346 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0027 | 0.0137 | 0.0164 | 0.0153 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6076 | 67329.528 | 44271.2318 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2935.9013 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0035 | 0.0129 | 0.0164 | 0.0147 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6079 | 67332.912 | 44271.2318 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2994.6193 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0044 | 0.0126 | 0.017 | 0.0147 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6082 | 67335.981 | 44271.2319 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3054.5117 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0043 | 0.0123 | 0.0166 | 0.0144 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6085 | 67339.091 | 44271.2319 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3115.602 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0037 | 0.0119 | 0.0156 | 0.014 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6088 | 67342.447 | 44271.2319 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3177.914 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0053 | 0.0112 | 0.0165 | 0.0138 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6091 | 67345.432 | 44271.232 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3241.4723 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.005 | 0.011 | 0.016 | 0.0137 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6094 | 67348.593 | 44271.232 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3306.3017 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0052 | 0.0109 | 0.0161 | 0.0135 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6097 | 67351.638 | 44271.232 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3372.4277 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0054 | 0.0109 | 0.0163 | 0.0136 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6100 | 67354.6 | 44271.2321 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3439.8763 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0042 | 0.0114 | 0.0156 | 0.0135 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6103 | 67357.767 | 44271.2321 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3508.6738 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0055 | 0.0111 | 0.0166 | 0.0138 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6106 | 67361.176 | 44271.2321 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3578.8473 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0042 | 0.0108 | 0.015 | 0.0132 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6109 | 67364.13 | 44271.2322 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3650.4243 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0046 | 0.0108 | 0.0154 | 0.0134 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6112 | 67367.235 | 44271.2322 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3723.4327 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0048 | 0.0106 | 0.0154 | 0.013 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6115 | 67370.62 | 44271.2323 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3797.9014 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0046 | 0.011 | 0.0156 | 0.0131 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6118 | 67373.706 | 44271.2323 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3873.8594 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.0033 | 0.011 | 0.0143 | 0.0129 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6121 | 67376.879 | 44271.2323 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3951.3366 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0052 | 0.0103 | 0.0155 | 0.0127 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6124 | 67379.958 | 44271.2324 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4030.3633 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0055 | 0.0103 | 0.0158 | 0.0129 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6127 | 67383.218 | 44271.2324 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4110.9706 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0043 | 0.0107 | 0.015 | 0.0129 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6130 | 67386.464 | 44271.2324 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4193.19 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0054 | 0.0105 | 0.0159 | 0.013 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6133 | 67389.383 | 44271.2325 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4277.0538 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0051 | 0.0105 | 0.0156 | 0.0129 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6136 | 67392.474 | 44271.2325 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4362.5949 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0042 | 0.0107 | 0.0149 | 0.0127 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6139 | 67395.973 | 44271.2326 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4449.8468 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0052 | 0.0099 | 0.0151 | 0.0123 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6142 | 67399.046 | 44271.2326 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4538.8437 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0047 | 0.0101 | 0.0148 | 0.012 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6145 | 67402.124 | 44271.2326 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4629.6206 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0034 | 0.0102 | 0.0136 | 0.0118 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6148 | 67405.1 | 44271.2327 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4722.213 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0037 | 0.0101 | 0.0138 | 0.0113 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6151 | 67408.163 | 44271.2327 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4816.6573 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0022 | 0.0105 | 0.0127 | 0.0113 | 0.0008 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6154 | 67411.331 | 44271.2327 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4912.9904 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.005 | 0.0092 | 0.0142 | 0.0112 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6157 | 67414.404 | 44271.2328 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5011.2502 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0028 | 0.0093 | 0.0121 | 0.0108 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6160 | 67417.572 | 44271.2328 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5111.4752 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0044 | 0.0099 | 0.0143 | 0.0114 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6163 | 67420.719 | 44271.2328 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5111.7575 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0048 | 0.0091 | 0.0139 | 0.011 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6166 | 67423.891 | 44271.2329 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5213.9927 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0035 | 0.0093 | 0.0128 | 0.0106 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6169 | 67426.973 | 44271.2329 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5318.2725 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0046 | 0.0098 | 0.0144 | 0.0113 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6172 | 67430.056 | 44271.2329 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5424.638 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0044 | 0.0096 | 0.014 | 0.0112 | 0.0017 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6175 | 67433.236 | 44271.233 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5533.1307 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0039 | 0.0102 | 0.0141 | 0.0112 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6178 | 67436.278 | 44271.233 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5643.7934 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0045 | 0.0095 | 0.014 | 0.011 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6181 | 67439.338 | 44271.2331 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5756.6692 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0028 | 0.0096 | 0.0124 | 0.0106 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6184 | 67442.431 | 44271.2331 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5871.8026 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0045 | 0.0098 | 0.0143 | 0.0111 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6187 | 67445.49 | 44271.2331 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5989.2387 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0052 | 0.0097 | 0.0149 | 0.0115 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6190 | 67448.468 | 44271.2332 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6109.0234 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6193 | 67451.438 | 44271.2332 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6231.2039 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0014 | 0.0101 | 0.0115 | 0.0106 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6196 | 67454.463 | 44271.2332 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6355.828 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0038 | 0.0101 | 0.0139 | 0.0108 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6199 | 67457.453 | 44271.2333 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6482.9445 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0051 | 0.0098 | 0.0149 | 0.0115 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6202 | 67460.531 | 44271.2333 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6612.6034 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0009 | 0.0097 | 0.0106 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6205 | 67463.725 | 44271.2333 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6744.8555 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6208 | 67466.778 | 44271.2334 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6879.7526 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0047 | 0.0102 | 0.0149 | 0.011 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6211 | 67469.724 | 44271.2334 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7017.3477 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6214 | 67472.684 | 44271.2334 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7157.6946 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0053 | 0.0097 | 0.015 | 0.0103 | 0.0017 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6217 | 67475.672 | 44271.2335 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7300.8485 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0015 | 0.0089 | 0.0104 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6220 | 67478.813 | 44271.2335 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7446.8655 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6223 | 67481.91 | 44271.2335 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7595.8028 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.001 | 0.0096 | 0.0106 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6226 | 67485.194 | 44271.2336 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7747.7188 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6229 | 67488.27 | 44271.2336 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7902.6732 | 0:240:120 | 0:00 | 0.001 | 7 | 0.006 | 0.009 | 0.015 | 0.0103 | 0.0019 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6232 | 67491.267 | 44271.2337 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8060.7267 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0003 | 0.0106 | 0.0109 | 0.0108 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6235 | 67494.371 | 44271.2337 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8221.9412 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0015 | 0.0098 | 0.0113 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6238 | 67497.438 | 44271.2337 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8386.38 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0012 | 0.0095 | 0.0107 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6241 | 67500.645 | 44271.2338 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8554.1076 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6244 | 67503.662 | 44271.2338 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8725.1898 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.001 | 0.0103 | 0.0113 | 0.0106 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6247 | 67506.838 | 44271.2338 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8899.6936 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0016 | 0.0094 | 0.011 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6250 | 67509.803 | 44271.2339 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9077.6875 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6253 | 67513.123 | 44271.2339 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9259.2412 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6256 | 67516.176 | 44271.2339 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9444.426 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0019 | 0.0094 | 0.0113 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6259 | 67519.104 | 44271.234 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9633.3146 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0015 | 0.0096 | 0.0111 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6262 | 67522.096 | 44271.234 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9825.9808 | 0:240:120 | 0:00 | 0.0007 | 7 | 0.0024 | 0.0089 | 0.0113 | 0.0101 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6265 | 67525.269 | 44271.234 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10022.5005 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0008 | 0.0094 | 0.0102 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6268 | 67528.327 | 44271.2341 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10222.9505 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.002 | 0.0089 | 0.0109 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6271 | 67531.392 | 44271.2341 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10427.4095 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0018 | 0.0094 | 0.0112 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6274 | 67534.432 | 44271.2342 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10635.9577 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0013 | 0.0098 | 0.0111 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6277 | 67537.43 | 44271.2342 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10848.6768 | 0:240:120 | 0:00 | 0.0006 | 7 | 0.0018 | 0.009 | 0.0108 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6280 | 67540.719 | 44271.2342 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11065.6504 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6283 | 67544.106 | 44271.2343 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11286.9634 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.0103 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6286 | 67547.09 | 44271.2343 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11512.7026 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0011 | 0.0097 | 0.0108 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6289 | 67550.163 | 44271.2343 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11742.9567 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6292 | 67553.224 | 44271.2344 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11977.8158 | 0:240:120 | 0:00 | 0.0005 | 7 | 0.0007 | 0.0102 | 0.0109 | 0.0106 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6295 | 67906.568 | 44271.2385 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.4 | 0:240:120 | 0:00 | 39.0919 | 7 | 117.6562 | 241.3467 | 359.0029 | 293.5888 | 48.8727 | 2388.5454 | 3 | 39.0919 | 158.8726 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6298 | 68867.515 | 44271.2496 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83 | 0:240:120 | 0:00 | 33.7719 | 7 | 115.219 | 124.8731 | 240.0921 | 172.5102 | 51.7411 | 2677.137 | 3 | 33.7719 | 104.6201 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6301 | 69450.093 | 44271.2563 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.7 | 0:240:120 | 0:00 | 29.4309 | 7 | 41.3196 | 59.4542 | 100.7738 | 73.0797 | 20.2504 | 410.0793 | 3 | 29.4309 | 76.3589 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6304 | 69710.017 | 44271.2593 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.4 | 0:240:120 | 0:00 | 26.0187 | 7 | 3.5191 | 52.8929 | 56.412 | 54.0442 | 1.7261 | 2.9793 | 3 | 26.0187 | 59.8607 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6307 | 69875.482 | 44271.2612 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.1 | 0:240:120 | 0:00 | 23.2674 | 7 | 3.2974 | 46.3178 | 49.6152 | 47.4242 | 1.6429 | 2.6993 | 3 | 23.2674 | 49.052 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6310 | 70020.678 | 44271.2629 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.8 | 0:240:120 | 0:00 | 21.0033 | 7 | 4.8871 | 38.17 | 43.0571 | 40.3914 | 2.0706 | 4.2875 | 3 | 21.0033 | 41.4261 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6313 | 70145.929 | 44271.2644 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.6 | 0:240:120 | 0:00 | 19.0064 | 7 | 6.2438 | 29.9412 | 36.185 | 32.0546 | 3.0792 | 9.4813 | 3 | 19.0064 | 35.4721 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6316 | 70250.319 | 44271.2656 | Vista Speed | T | 30T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.5 | 0:240:120 | 0:00 | 17.2409 | 7 | 1.101 | 27.7585 | 28.8595 | 28.1284 | 0.5471 | 0.2993 | 3 | 17.2409 | 30.717 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6319 | 70984.719 | 44271.2741 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.12 | 0:240:120 | 0:00 | 64.3114 | 7 | 60.6402 | 611.3538 | 671.994 | 631.5677 | 30.3181 | 919.1882 | 3 | 64.3114 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6322 | 72882.211 | 44271.296 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.0824 | 0:240:120 | 0:00 | 52.1678 | 7 | 60.8914 | 489.6627 | 550.5541 | 509.9625 | 30.439 | 926.5328 | 3 | 52.1678 | 685.6911 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6325 | 74415.228 | 44271.3138 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.084 | 0:240:120 | 0:00 | 43.602 | 7 | 60.8308 | 368.1146 | 428.9454 | 388.3986 | 30.4089 | 924.6997 | 3 | 43.602 | 221.7936 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6328 | 75583.35 | 44271.3273 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.1257 | 0:240:120 | 0:00 | 37.2402 | 7 | 65.4059 | 241.9908 | 307.3967 | 265.4987 | 31.4666 | 990.15 | 3 | 37.2402 | 130.1703 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6331 | 76387.094 | 44271.3366 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.2082 | 0:240:120 | 0:00 | 32.3322 | 7 | 117.3691 | 68.4193 | 185.7884 | 124.3393 | 50.1985 | 2519.89 | 3 | 32.3322 | 91.0415 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6334 | 76825.287 | 44271.3417 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 108.3324 | 0:240:120 | 0:00 | 28.4334 | 7 | 6.1611 | 57.5972 | 63.7583 | 59.9281 | 2.857 | 8.1625 | 3 | 28.4334 | 69.3522 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6337 | 77010.167 | 44271.3438 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.4991 | 0:240:120 | 0:00 | 25.2639 | 7 | 3.4665 | 50.875 | 54.3415 | 52.0305 | 1.7264 | 2.9805 | 3 | 25.2639 | 55.5769 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6340 | 77169.399 | 44271.3457 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.709 | 0:240:120 | 0:00 | 22.6384 | 7 | 3.3664 | 44.1483 | 47.5147 | 45.2716 | 1.6818 | 2.8283 | 3 | 22.6384 | 46.0588 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6343 | 77308.225 | 44271.3473 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.9632 | 0:240:120 | 0:00 | 20.4296 | 7 | 6.6206 | 34.1684 | 40.789 | 37.3325 | 2.8055 | 7.8709 | 3 | 20.4296 | 39.0931 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6346 | 77423.983 | 44271.3486 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.2625 | 0:240:120 | 0:00 | 18.5468 | 7 | 1.559 | 29.5884 | 31.1474 | 30.0773 | 0.7324 | 0.5364 | 3 | 18.5468 | 33.7783 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6349 | 77517.711 | 44271.3497 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.6077 | 0:240:120 | 0:00 | 16.9241 | 7 | 1.2786 | 27.2021 | 28.4807 | 27.7083 | 0.5803 | 0.3368 | 3 | 16.9241 | 29.5926 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6352 | 77603.809 | 44271.3507 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.9999 | 0:240:120 | 0:00 | 15.5121 | 7 | 1.9804 | 24.0294 | 26.0098 | 24.7349 | 0.9459 | 0.8947 | 3 | 15.5121 | 26.2132 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6355 | 77681.725 | 44271.3516 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.4399 | 0:240:120 | 0:00 | 14.2732 | 7 | 1.1562 | 21.7637 | 22.9199 | 22.1656 | 0.5646 | 0.3188 | 3 | 14.2732 | 23.4294 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6358 | 77750.906 | 44271.3524 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.9287 | 0:240:120 | 0:00 | 13.1781 | 7 | 1.1107 | 19.029 | 20.1397 | 19.4031 | 0.5457 | 0.2978 | 3 | 13.1781 | 21.0983 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6361 | 77812.584 | 44271.3531 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 129.4673 | 0:240:120 | 0:00 | 12.204 | 7 | 0.9674 | 17.5121 | 18.4795 | 17.9667 | 0.4155 | 0.1726 | 3 | 12.204 | 19.1192 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6364 | 77869.414 | 44271.3538 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 132.0566 | 0:240:120 | 0:00 | 11.3324 | 7 | 0.5552 | 16.2734 | 16.8286 | 16.4593 | 0.2764 | 0.0764 | 3 | 11.3324 | 17.4192 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6367 | 77921.682 | 44271.3544 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.6977 | 0:240:120 | 0:00 | 10.5487 | 7 | 0.9688 | 14.6243 | 15.5931 | 14.9464 | 0.4727 | 0.2235 | 3 | 10.5487 | 15.9443 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6370 | 77969.965 | 44271.3549 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.3917 | 0:240:120 | 0:00 | 9.8406 | 7 | 0.6516 | 13.4205 | 14.0721 | 13.7027 | 0.2917 | 0.0851 | 3 | 9.8406 | 14.6534 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6373 | 78014.067 | 44271.3554 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 140.1395 | 0:240:120 | 0:00 | 9.1982 | 7 | 0.6131 | 12.4974 | 13.1105 | 12.7875 | 0.2571 | 0.0661 | 3 | 9.1982 | 13.5149 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6376 | 78055.383 | 44271.3559 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.9423 | 0:240:120 | 0:00 | 8.6132 | 7 | 0.4614 | 11.6549 | 12.1163 | 11.8656 | 0.193 | 0.0372 | 3 | 8.6132 | 12.5042 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6379 | 78093.791 | 44271.3564 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 145.8012 | 0:240:120 | 0:00 | 8.0787 | 7 | 0.3419 | 10.794 | 11.1359 | 10.9143 | 0.1657 | 0.0274 | 3 | 8.0787 | 11.6016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6382 | 78129.269 | 44271.3568 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.7172 | 0:240:120 | 0:00 | 7.5887 | 7 | 0.2431 | 10.1374 | 10.3805 | 10.2297 | 0.1126 | 0.0127 | 3 | 7.5887 | 10.7911 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6385 | 78162.584 | 44271.3572 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 151.6915 | 0:240:120 | 0:00 | 7.1383 | 7 | 0.3081 | 9.4285 | 9.7366 | 9.5702 | 0.1281 | 0.0164 | 3 | 7.1383 | 10.06 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6388 | 78194.169 | 44271.3575 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 154.7254 | 0:240:120 | 0:00 | 6.7231 | 7 | 0.426 | 8.6652 | 9.0912 | 8.8791 | 0.1813 | 0.0329 | 3 | 6.7231 | 9.3975 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6391 | 78223.711 | 44271.3579 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 157.8199 | 0:240:120 | 0:00 | 6.3395 | 7 | 0.3018 | 8.2074 | 8.5092 | 8.3445 | 0.132 | 0.0174 | 3 | 6.3395 | 8.7949 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6394 | 78251.833 | 44271.3582 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.9763 | 0:240:120 | 0:00 | 5.9843 | 7 | 0.2963 | 7.7543 | 8.0506 | 7.8529 | 0.1466 | 0.0215 | 3 | 5.9843 | 8.2449 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6397 | 78278.416 | 44271.3585 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.1958 | 0:240:120 | 0:00 | 5.6546 | 7 | 0.1902 | 7.2654 | 7.4556 | 7.3474 | 0.0807 | 0.0065 | 3 | 5.6546 | 7.7413 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6400 | 78303.357 | 44271.3588 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 167.4797 | 0:240:120 | 0:00 | 5.3481 | 7 | 0.2225 | 6.8157 | 7.0382 | 6.9222 | 0.096 | 0.0092 | 3 | 5.3481 | 7.2786 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6403 | 78327.15 | 44271.3591 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.8293 | 0:240:120 | 0:00 | 5.0625 | 7 | 0.1885 | 6.4764 | 6.6649 | 6.5383 | 0.0889 | 0.0079 | 3 | 5.0625 | 6.8526 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6406 | 78349.769 | 44271.3593 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 174.2459 | 0:240:120 | 0:00 | 4.7961 | 7 | 0.2233 | 6.0334 | 6.2567 | 6.1406 | 0.0966 | 0.0093 | 3 | 4.7961 | 6.4592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6409 | 78370.966 | 44271.3596 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 177.7308 | 0:240:120 | 0:00 | 4.5472 | 7 | 0.1064 | 5.7737 | 5.8801 | 5.8086 | 0.0497 | 0.0025 | 3 | 4.5472 | 6.0952 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6412 | 78391.223 | 44271.3598 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 181.2854 | 0:240:120 | 0:00 | 4.3142 | 7 | 0.1719 | 5.4338 | 5.6057 | 5.5006 | 0.0796 | 0.0063 | 3 | 4.3142 | 5.7576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6415 | 78410.707 | 44271.36 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 184.9111 | 0:240:120 | 0:00 | 4.0959 | 7 | 0.1552 | 5.1097 | 5.2649 | 5.1831 | 0.0664 | 0.0044 | 3 | 4.0959 | 5.4439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6418 | 78429.155 | 44271.3602 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 188.6093 | 0:240:120 | 0:00 | 3.891 | 7 | 0.1144 | 4.8618 | 4.9762 | 4.9183 | 0.0462 | 0.0021 | 3 | 3.891 | 5.1519 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6421 | 78446.921 | 44271.3605 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 192.3815 | 0:240:120 | 0:00 | 3.6985 | 7 | 0.0748 | 4.6366 | 4.7114 | 4.6618 | 0.0354 | 0.0013 | 3 | 3.6985 | 4.8796 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6424 | 78463.777 | 44271.3606 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 196.2292 | 0:240:120 | 0:00 | 3.5175 | 7 | 0.0638 | 4.3949 | 4.4587 | 4.4158 | 0.0304 | 0.0009 | 3 | 3.5175 | 4.6252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6427 | 78479.796 | 44271.3608 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 200.1537 | 0:240:120 | 0:00 | 3.3471 | 7 | 0.0597 | 4.1783 | 4.238 | 4.1985 | 0.0284 | 0.0008 | 3 | 3.3471 | 4.3872 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6430 | 78495.271 | 44271.361 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 204.1568 | 0:240:120 | 0:00 | 3.1864 | 7 | 0.0795 | 3.9402 | 4.0197 | 3.9762 | 0.0328 | 0.0011 | 3 | 3.1864 | 4.1644 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6433 | 78510.165 | 44271.3612 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.24 | 0:240:120 | 0:00 | 3.0349 | 7 | 0.0888 | 3.7421 | 3.8309 | 3.7855 | 0.038 | 0.0014 | 3 | 3.0349 | 3.9553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6436 | 78524.471 | 44271.3614 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 212.4048 | 0:240:120 | 0:00 | 2.8918 | 7 | 0.0888 | 3.5651 | 3.6539 | 3.5981 | 0.0416 | 0.0017 | 3 | 2.8918 | 3.7589 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6439 | 78538.179 | 44271.3615 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 216.6529 | 0:240:120 | 0:00 | 2.7566 | 7 | 0.048 | 3.4064 | 3.4544 | 3.422 | 0.0207 | 0.0004 | 3 | 2.7566 | 3.5744 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6442 | 78551.344 | 44271.3617 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 220.9859 | 0:240:120 | 0:00 | 2.6287 | 7 | 0.0744 | 3.224 | 3.2984 | 3.26 | 0.0321 | 0.001 | 3 | 2.6287 | 3.4006 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6445 | 78563.846 | 44271.3618 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 225.4056 | 0:240:120 | 0:00 | 2.5077 | 7 | 0.0358 | 3.0866 | 3.1224 | 3.0992 | 0.0169 | 0.0003 | 3 | 2.5077 | 3.2369 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6448 | 78576.056 | 44271.3619 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 229.9137 | 0:240:120 | 0:00 | 2.3931 | 7 | 0.0615 | 2.9339 | 2.9954 | 2.9597 | 0.0273 | 0.0007 | 3 | 2.3931 | 3.0825 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6451 | 78587.917 | 44271.3621 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.512 | 0:240:120 | 0:00 | 2.2844 | 7 | 0.0542 | 2.7855 | 2.8397 | 2.8125 | 0.0226 | 0.0005 | 3 | 2.2844 | 2.9368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6454 | 78599.257 | 44271.3622 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 239.2023 | 0:240:120 | 0:00 | 2.1814 | 7 | 0.0375 | 2.6708 | 2.7083 | 2.6866 | 0.0162 | 0.0003 | 3 | 2.1814 | 2.7991 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6457 | 78610.218 | 44271.3623 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 243.9863 | 0:240:120 | 0:00 | 2.0836 | 7 | 0.0324 | 2.5422 | 2.5746 | 2.5572 | 0.0131 | 0.0002 | 3 | 2.0836 | 2.669 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6460 | 78620.84 | 44271.3625 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 248.866 | 0:240:120 | 0:00 | 1.9908 | 7 | 0.0364 | 2.4261 | 2.4625 | 2.4426 | 0.0144 | 0.0002 | 3 | 1.9908 | 2.5458 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6463 | 78630.992 | 44271.3626 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 253.8433 | 0:240:120 | 0:00 | 1.9026 | 7 | 0.0378 | 2.3093 | 2.3471 | 2.3279 | 0.0154 | 0.0002 | 3 | 1.9026 | 2.4291 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6466 | 78641.368 | 44271.3627 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 258.9202 | 0:240:120 | 0:00 | 1.8188 | 7 | 0.0393 | 2.2091 | 2.2484 | 2.2276 | 0.0169 | 0.0003 | 3 | 1.8188 | 2.3186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6469 | 78651.297 | 44271.3628 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 264.0986 | 0:240:120 | 0:00 | 1.739 | 7 | 0.0296 | 2.1149 | 2.1445 | 2.1251 | 0.0138 | 0.0002 | 3 | 1.739 | 2.2138 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6472 | 78660.612 | 44271.3629 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 269.3806 | 0:240:120 | 0:00 | 1.6632 | 7 | 0.032 | 2.0139 | 2.0459 | 2.029 | 0.0134 | 0.0002 | 3 | 1.6632 | 2.1144 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6475 | 78669.561 | 44271.363 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 274.7682 | 0:240:120 | 0:00 | 1.591 | 7 | 0.0277 | 1.9313 | 1.959 | 1.9416 | 0.0115 | 0.0001 | 3 | 1.591 | 2.02 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6478 | 78678.307 | 44271.3631 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 280.2636 | 0:240:120 | 0:00 | 1.5223 | 7 | 0.0296 | 1.8409 | 1.8705 | 1.8552 | 0.0126 | 0.0002 | 3 | 1.5223 | 1.9304 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6481 | 78686.668 | 44271.3632 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 285.8688 | 0:240:120 | 0:00 | 1.4568 | 7 | 0.0234 | 1.762 | 1.7854 | 1.7726 | 0.0096 | 0.0001 | 3 | 1.4568 | 1.8452 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6484 | 78694.822 | 44271.3633 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 291.5862 | 0:240:120 | 0:00 | 1.3944 | 7 | 0.0196 | 1.6847 | 1.7043 | 1.6928 | 0.0082 | 0.0001 | 3 | 1.3944 | 1.7642 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6487 | 78702.839 | 44271.3634 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 297.4179 | 0:240:120 | 0:00 | 1.3349 | 7 | 0.0167 | 1.6143 | 1.631 | 1.6211 | 0.0073 | 0.0001 | 3 | 1.3349 | 1.6871 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6490 | 78710.687 | 44271.3635 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 303.3663 | 0:240:120 | 0:00 | 1.2781 | 7 | 0.0209 | 1.5396 | 1.5605 | 1.5495 | 0.0087 | 0.0001 | 3 | 1.2781 | 1.6138 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6493 | 78718.271 | 44271.3636 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 309.4336 | 0:240:120 | 0:00 | 1.224 | 7 | 0.0216 | 1.4751 | 1.4967 | 1.4853 | 0.0092 | 0.0001 | 3 | 1.224 | 1.5439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6496 | 78725.624 | 44271.3637 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 315.6223 | 0:240:120 | 0:00 | 1.1723 | 7 | 0.02 | 1.4159 | 1.4359 | 1.4247 | 0.0084 | 0.0001 | 3 | 1.1723 | 1.4774 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6499 | 78732.739 | 44271.3638 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 321.9347 | 0:240:120 | 0:00 | 1.123 | 7 | 0.0174 | 1.3503 | 1.3677 | 1.3588 | 0.0071 | 0.0001 | 3 | 1.123 | 1.414 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6502 | 78739.75 | 44271.3638 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 328.3734 | 0:240:120 | 0:00 | 1.0759 | 7 | 0.0199 | 1.2956 | 1.3155 | 1.3054 | 0.0079 | 0.0001 | 3 | 1.0759 | 1.3536 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6505 | 78746.942 | 44271.3639 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 334.9409 | 0:240:120 | 0:00 | 1.031 | 7 | 0.0168 | 1.2407 | 1.2575 | 1.249 | 0.0068 | 0 | 3 | 1.031 | 1.296 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6508 | 78753.562 | 44271.364 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 341.6397 | 0:240:120 | 0:00 | 0.988 | 7 | 0.0138 | 1.1878 | 1.2016 | 1.1943 | 0.0056 | 0 | 3 | 0.988 | 1.2411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6511 | 78760.045 | 44271.3641 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 348.4725 | 0:240:120 | 0:00 | 0.947 | 7 | 0.0154 | 1.138 | 1.1534 | 1.1447 | 0.0061 | 0 | 3 | 0.947 | 1.1886 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6514 | 78766.42 | 44271.3642 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 355.442 | 0:240:120 | 0:00 | 0.9077 | 7 | 0.0176 | 1.0873 | 1.1049 | 1.0963 | 0.0074 | 0.0001 | 3 | 0.9077 | 1.1386 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6517 | 78772.61 | 44271.3642 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 362.5508 | 0:240:120 | 0:00 | 0.8702 | 7 | 0.0187 | 1.0423 | 1.061 | 1.0519 | 0.0076 | 0.0001 | 3 | 0.8702 | 1.0908 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6520 | 78778.811 | 44271.3643 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 369.8018 | 0:240:120 | 0:00 | 0.8343 | 7 | 0.0138 | 0.9994 | 1.0132 | 1.0059 | 0.0057 | 0 | 3 | 0.8343 | 1.0452 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6523 | 78784.755 | 44271.3644 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 377.1979 | 0:240:120 | 0:00 | 0.8 | 7 | 0.016 | 0.9577 | 0.9737 | 0.9658 | 0.0067 | 0 | 3 | 0.8 | 1.0016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6526 | 78790.841 | 44271.3644 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 384.7418 | 0:240:120 | 0:00 | 0.7672 | 7 | 0.0139 | 0.9178 | 0.9317 | 0.9249 | 0.0059 | 0 | 3 | 0.7672 | 0.9599 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6529 | 78796.75 | 44271.3645 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 392.4367 | 0:240:120 | 0:00 | 0.7358 | 7 | 0.0142 | 0.8786 | 0.8928 | 0.8859 | 0.006 | 0 | 3 | 0.7358 | 0.9201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6532 | 78802.578 | 44271.3646 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 400.2854 | 0:240:120 | 0:00 | 0.7057 | 7 | 0.0127 | 0.8429 | 0.8556 | 0.8494 | 0.0051 | 0 | 3 | 0.7057 | 0.882 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6535 | 78808.084 | 44271.3646 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 408.2911 | 0:240:120 | 0:00 | 0.6769 | 7 | 0.0131 | 0.809 | 0.8221 | 0.8158 | 0.0054 | 0 | 3 | 0.6769 | 0.8456 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6538 | 78813.754 | 44271.3647 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 416.4569 | 0:240:120 | 0:00 | 0.6494 | 7 | 0.0155 | 0.7737 | 0.7892 | 0.7817 | 0.0066 | 0 | 3 | 0.6494 | 0.8108 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6541 | 78819.127 | 44271.3648 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 424.7861 | 0:240:120 | 0:00 | 0.623 | 7 | 0.0108 | 0.7448 | 0.7556 | 0.7504 | 0.0042 | 0 | 3 | 0.623 | 0.7775 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6544 | 78824.426 | 44271.3648 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 433.2818 | 0:240:120 | 0:00 | 0.5977 | 7 | 0.0126 | 0.7138 | 0.7264 | 0.7193 | 0.0053 | 0 | 3 | 0.5977 | 0.7457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6547 | 78829.494 | 44271.3649 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 441.9474 | 0:240:120 | 0:00 | 0.5735 | 7 | 0.0131 | 0.6845 | 0.6976 | 0.6906 | 0.0052 | 0 | 3 | 0.5735 | 0.7152 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6550 | 78834.555 | 44271.3649 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 450.7864 | 0:240:120 | 0:00 | 0.5504 | 7 | 0.0122 | 0.6561 | 0.6683 | 0.6618 | 0.005 | 0 | 3 | 0.5504 | 0.686 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6553 | 78839.764 | 44271.365 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 459.8021 | 0:240:120 | 0:00 | 0.5281 | 7 | 0.0125 | 0.6278 | 0.6403 | 0.6343 | 0.0051 | 0 | 3 | 0.5281 | 0.6581 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6556 | 78844.837 | 44271.3651 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 468.9981 | 0:240:120 | 0:00 | 0.5069 | 7 | 0.0098 | 0.6044 | 0.6142 | 0.6097 | 0.004 | 0 | 3 | 0.5069 | 0.6313 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6559 | 78849.742 | 44271.3651 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 478.3781 | 0:240:120 | 0:00 | 0.4865 | 7 | 0.0115 | 0.5796 | 0.5911 | 0.5846 | 0.0044 | 0 | 3 | 0.4865 | 0.6057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6562 | 78854.765 | 44271.3652 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 487.9457 | 0:240:120 | 0:00 | 0.4669 | 7 | 0.0141 | 0.5546 | 0.5687 | 0.5614 | 0.0051 | 0 | 3 | 0.4669 | 0.5812 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6565 | 78859.623 | 44271.3652 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 497.7046 | 0:240:120 | 0:00 | 0.4482 | 7 | 0.0108 | 0.5332 | 0.544 | 0.5383 | 0.0045 | 0 | 3 | 0.4482 | 0.5577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6568 | 78864.236 | 44271.3653 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 507.6587 | 0:240:120 | 0:00 | 0.4302 | 7 | 0.0115 | 0.5119 | 0.5234 | 0.5171 | 0.0049 | 0 | 3 | 0.4302 | 0.5352 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6571 | 78868.785 | 44271.3653 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 517.8118 | 0:240:120 | 0:00 | 0.413 | 7 | 0.0092 | 0.4909 | 0.5001 | 0.4962 | 0.0037 | 0 | 3 | 0.413 | 0.5136 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6574 | 78873.29 | 44271.3654 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 528.1681 | 0:240:120 | 0:00 | 0.3965 | 7 | 0.0109 | 0.4708 | 0.4817 | 0.4765 | 0.0041 | 0 | 3 | 0.3965 | 0.4929 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6577 | 78878.467 | 44271.3654 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 538.7314 | 0:240:120 | 0:00 | 0.3807 | 7 | 0.0098 | 0.4522 | 0.462 | 0.4569 | 0.004 | 0 | 3 | 0.3807 | 0.4731 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6580 | 78883.119 | 44271.3655 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 549.5061 | 0:240:120 | 0:00 | 0.3655 | 7 | 0.0092 | 0.4342 | 0.4434 | 0.4388 | 0.0035 | 0 | 3 | 0.3655 | 0.4541 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6583 | 78887.388 | 44271.3656 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 560.4962 | 0:240:120 | 0:00 | 0.3509 | 7 | 0.0087 | 0.4173 | 0.426 | 0.4215 | 0.0036 | 0 | 3 | 0.3509 | 0.4359 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6586 | 78891.635 | 44271.3656 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 571.7061 | 0:240:120 | 0:00 | 0.337 | 7 | 0.008 | 0.3998 | 0.4078 | 0.4037 | 0.0033 | 0 | 3 | 0.337 | 0.4185 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6589 | 78895.7 | 44271.3656 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 583.1402 | 0:240:120 | 0:00 | 0.3236 | 7 | 0.0078 | 0.3841 | 0.3919 | 0.3882 | 0.0029 | 0 | 3 | 0.3236 | 0.4017 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6592 | 78899.989 | 44271.3657 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 594.803 | 0:240:120 | 0:00 | 0.3107 | 7 | 0.009 | 0.3679 | 0.3769 | 0.3725 | 0.0035 | 0 | 3 | 0.3107 | 0.3857 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6595 | 78904.139 | 44271.3657 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 606.6991 | 0:240:120 | 0:00 | 0.2984 | 7 | 0.0076 | 0.3542 | 0.3618 | 0.358 | 0.0026 | 0 | 3 | 0.2984 | 0.3703 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6598 | 78908.165 | 44271.3658 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 618.8331 | 0:240:120 | 0:00 | 0.2866 | 7 | 0.0074 | 0.3398 | 0.3472 | 0.3435 | 0.0029 | 0 | 3 | 0.2866 | 0.3555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6601 | 78912.193 | 44271.3658 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 631.2097 | 0:240:120 | 0:00 | 0.2752 | 7 | 0.008 | 0.3255 | 0.3335 | 0.3296 | 0.0031 | 0 | 3 | 0.2752 | 0.3414 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6604 | 78916.196 | 44271.3659 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 643.8339 | 0:240:120 | 0:00 | 0.2643 | 7 | 0.0052 | 0.3144 | 0.3196 | 0.3166 | 0.002 | 0 | 3 | 0.2643 | 0.3278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6607 | 78920.353 | 44271.3659 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 656.7106 | 0:240:120 | 0:00 | 0.2538 | 7 | 0.006 | 0.3018 | 0.3078 | 0.3047 | 0.0022 | 0 | 3 | 0.2538 | 0.3148 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6610 | 78924.296 | 44271.366 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 669.8448 | 0:240:120 | 0:00 | 0.2438 | 7 | 0.0063 | 0.2904 | 0.2967 | 0.2928 | 0.0027 | 0 | 3 | 0.2438 | 0.3023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6613 | 78928.259 | 44271.366 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 683.2417 | 0:240:120 | 0:00 | 0.2342 | 7 | 0.0047 | 0.278 | 0.2827 | 0.2803 | 0.0017 | 0 | 3 | 0.2342 | 0.2903 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6616 | 78932.12 | 44271.3661 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 696.9065 | 0:240:120 | 0:00 | 0.2249 | 7 | 0.0042 | 0.2675 | 0.2717 | 0.2694 | 0.0017 | 0 | 3 | 0.2249 | 0.2788 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6619 | 78936.306 | 44271.3661 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 710.8447 | 0:240:120 | 0:00 | 0.2161 | 7 | 0.0052 | 0.2564 | 0.2616 | 0.2584 | 0.0024 | 0 | 3 | 0.2161 | 0.2677 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6622 | 78940.232 | 44271.3662 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 725.0616 | 0:240:120 | 0:00 | 0.2075 | 7 | 0.0049 | 0.2461 | 0.251 | 0.2482 | 0.002 | 0 | 3 | 0.2075 | 0.2572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6625 | 78944.031 | 44271.3662 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 739.5628 | 0:240:120 | 0:00 | 0.1994 | 7 | 0.0037 | 0.2372 | 0.2409 | 0.2389 | 0.0014 | 0 | 3 | 0.1994 | 0.247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6628 | 78947.689 | 44271.3663 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 754.3541 | 0:240:120 | 0:00 | 0.1915 | 7 | 0.0037 | 0.2286 | 0.2323 | 0.23 | 0.0015 | 0 | 3 | 0.1915 | 0.2372 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6631 | 78951.338 | 44271.3663 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 769.4411 | 0:240:120 | 0:00 | 0.184 | 7 | 0.005 | 0.2184 | 0.2234 | 0.2203 | 0.0021 | 0 | 3 | 0.184 | 0.2279 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6634 | 78954.976 | 44271.3663 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 784.83 | 0:240:120 | 0:00 | 0.1767 | 7 | 0.0044 | 0.2099 | 0.2143 | 0.2114 | 0.0018 | 0 | 3 | 0.1767 | 0.2189 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6637 | 78958.626 | 44271.3664 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 800.5266 | 0:240:120 | 0:00 | 0.1698 | 7 | 0.0041 | 0.2018 | 0.2059 | 0.2034 | 0.0017 | 0 | 3 | 0.1698 | 0.2102 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6640 | 78962.3 | 44271.3664 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 816.5371 | 0:240:120 | 0:00 | 0.1631 | 7 | 0.0044 | 0.1936 | 0.198 | 0.1958 | 0.0016 | 0 | 3 | 0.1631 | 0.202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6643 | 78965.804 | 44271.3665 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 832.8678 | 0:240:120 | 0:00 | 0.1567 | 7 | 0.0042 | 0.1859 | 0.1901 | 0.188 | 0.0016 | 0 | 3 | 0.1567 | 0.194 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6646 | 78969.504 | 44271.3665 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 849.5252 | 0:240:120 | 0:00 | 0.1506 | 7 | 0.0033 | 0.1796 | 0.1829 | 0.1813 | 0.0011 | 0 | 3 | 0.1506 | 0.1864 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6649 | 78972.897 | 44271.3665 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 866.5157 | 0:240:120 | 0:00 | 0.1446 | 7 | 0.0051 | 0.1718 | 0.1769 | 0.1741 | 0.0018 | 0 | 3 | 0.1446 | 0.179 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6652 | 78976.589 | 44271.3666 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 883.846 | 0:240:120 | 0:00 | 0.139 | 7 | 0.0036 | 0.1653 | 0.1689 | 0.167 | 0.0014 | 0 | 3 | 0.139 | 0.172 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6655 | 78979.996 | 44271.3666 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 901.5229 | 0:240:120 | 0:00 | 0.1335 | 7 | 0.0038 | 0.1584 | 0.1622 | 0.1601 | 0.0014 | 0 | 3 | 0.1335 | 0.1652 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6658 | 78983.698 | 44271.3667 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 919.5534 | 0:240:120 | 0:00 | 0.1283 | 7 | 0.0036 | 0.1525 | 0.1561 | 0.1539 | 0.0013 | 0 | 3 | 0.1283 | 0.1587 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6661 | 78987.064 | 44271.3667 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 937.9445 | 0:240:120 | 0:00 | 0.1233 | 7 | 0.0035 | 0.1467 | 0.1502 | 0.1481 | 0.0011 | 0 | 3 | 0.1233 | 0.1525 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6664 | 78990.728 | 44271.3667 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 956.7033 | 0:240:120 | 0:00 | 0.1184 | 7 | 0.0041 | 0.1406 | 0.1447 | 0.1423 | 0.0016 | 0 | 3 | 0.1184 | 0.1465 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6667 | 78994.401 | 44271.3668 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 975.8374 | 0:240:120 | 0:00 | 0.1138 | 7 | 0.0021 | 0.1353 | 0.1374 | 0.1363 | 0.0007 | 0 | 3 | 0.1138 | 0.1408 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6670 | 78997.714 | 44271.3668 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 995.3542 | 0:240:120 | 0:00 | 0.1093 | 7 | 0.003 | 0.1301 | 0.1331 | 0.1316 | 0.0011 | 0 | 3 | 0.1093 | 0.1352 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6673 | 79001.027 | 44271.3669 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1015.2612 | 0:240:120 | 0:00 | 0.1051 | 7 | 0.003 | 0.1252 | 0.1282 | 0.1268 | 0.001 | 0 | 3 | 0.1051 | 0.1299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6676 | 79004.344 | 44271.3669 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1035.5665 | 0:240:120 | 0:00 | 0.101 | 7 | 0.0027 | 0.1199 | 0.1226 | 0.1211 | 0.0012 | 0 | 3 | 0.101 | 0.1249 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6679 | 79007.672 | 44271.3669 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1056.2778 | 0:240:120 | 0:00 | 0.097 | 7 | 0.0031 | 0.1153 | 0.1184 | 0.1168 | 0.001 | 0 | 3 | 0.097 | 0.12 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6682 | 79010.951 | 44271.367 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1077.4034 | 0:240:120 | 0:00 | 0.0932 | 7 | 0.003 | 0.1109 | 0.1139 | 0.1125 | 0.0011 | 0 | 3 | 0.0932 | 0.1153 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6685 | 79014.214 | 44271.367 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1098.9514 | 0:240:120 | 0:00 | 0.0896 | 7 | 0.0025 | 0.1073 | 0.1098 | 0.1083 | 0.0011 | 0 | 3 | 0.0896 | 0.1107 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6688 | 79017.511 | 44271.3671 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1120.9304 | 0:240:120 | 0:00 | 0.0861 | 7 | 0.0026 | 0.1025 | 0.1051 | 0.1036 | 0.001 | 0 | 3 | 0.0861 | 0.1064 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6691 | 79020.83 | 44271.3671 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1143.3491 | 0:240:120 | 0:00 | 0.0827 | 7 | 0.0035 | 0.0981 | 0.1016 | 0.0996 | 0.0011 | 0 | 3 | 0.0827 | 0.1023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6694 | 79024.265 | 44271.3671 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1166.216 | 0:240:120 | 0:00 | 0.0795 | 7 | 0.0036 | 0.0938 | 0.0974 | 0.0956 | 0.0013 | 0 | 3 | 0.0795 | 0.0983 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6697 | 79027.747 | 44271.3672 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1189.5404 | 0:240:120 | 0:00 | 0.0764 | 7 | 0.0029 | 0.0907 | 0.0936 | 0.0919 | 0.0011 | 0 | 3 | 0.0764 | 0.0944 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6700 | 79031.199 | 44271.3672 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1213.3312 | 0:240:120 | 0:00 | 0.0734 | 7 | 0.003 | 0.0866 | 0.0896 | 0.0881 | 0.001 | 0 | 3 | 0.0734 | 0.0907 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6703 | 79034.475 | 44271.3673 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1237.5978 | 0:240:120 | 0:00 | 0.0705 | 7 | 0.003 | 0.0834 | 0.0864 | 0.0849 | 0.0011 | 0 | 3 | 0.0705 | 0.0872 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6706 | 79037.771 | 44271.3673 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1262.3497 | 0:240:120 | 0:00 | 0.0678 | 7 | 0.0038 | 0.0803 | 0.0841 | 0.0818 | 0.0012 | 0 | 3 | 0.0678 | 0.0838 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6709 | 79041.05 | 44271.3673 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1287.5967 | 0:240:120 | 0:00 | 0.0651 | 7 | 0.0039 | 0.0764 | 0.0803 | 0.0783 | 0.0014 | 0 | 3 | 0.0651 | 0.0805 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6712 | 79044.346 | 44271.3674 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1313.3487 | 0:240:120 | 0:00 | 0.0626 | 7 | 0.0041 | 0.0735 | 0.0776 | 0.0755 | 0.0015 | 0 | 3 | 0.0626 | 0.0774 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6715 | 79047.653 | 44271.3674 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1339.6156 | 0:240:120 | 0:00 | 0.0601 | 7 | 0.0025 | 0.0711 | 0.0736 | 0.0724 | 0.0009 | 0 | 3 | 0.0601 | 0.0743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6718 | 79051.162 | 44271.3674 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1366.408 | 0:240:120 | 0:00 | 0.0578 | 7 | 0.0041 | 0.0678 | 0.0719 | 0.0698 | 0.0013 | 0 | 3 | 0.0578 | 0.0714 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6721 | 79054.348 | 44271.3675 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1393.7361 | 0:240:120 | 0:00 | 0.0555 | 7 | 0.0035 | 0.0653 | 0.0688 | 0.067 | 0.0012 | 0 | 3 | 0.0555 | 0.0686 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6724 | 79057.499 | 44271.3675 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1421.6108 | 0:240:120 | 0:00 | 0.0534 | 7 | 0.0029 | 0.0636 | 0.0665 | 0.0651 | 0.0011 | 0 | 3 | 0.0534 | 0.066 | P | NP | 1-1-1-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6727 | 79060.77 | 44271.3676 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1450.0431 | 0:240:120 | 0:00 | 0.0513 | 7 | 0.0033 | 0.0603 | 0.0636 | 0.0618 | 0.0014 | 0 | 3 | 0.0513 | 0.0634 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6730 | 79064.284 | 44271.3676 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1479.0439 | 0:240:120 | 0:00 | 0.0493 | 7 | 0.0033 | 0.0575 | 0.0608 | 0.0595 | 0.0012 | 0 | 3 | 0.0493 | 0.0609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6733 | 79067.654 | 44271.3676 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1508.6248 | 0:240:120 | 0:00 | 0.0474 | 7 | 0.004 | 0.0549 | 0.0589 | 0.0573 | 0.0012 | 0 | 3 | 0.0474 | 0.0585 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6736 | 79071.122 | 44271.3677 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1538.7973 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0029 | 0.0532 | 0.0561 | 0.0549 | 0.0012 | 0 | 3 | 0.0455 | 0.0563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6739 | 79075.049 | 44271.3677 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1569.5732 | 0:240:120 | 0:00 | 0.0438 | 7 | 0.0029 | 0.0514 | 0.0543 | 0.0531 | 0.001 | 0 | 3 | 0.0438 | 0.0541 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6742 | 79078.122 | 44271.3678 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1600.9647 | 0:240:120 | 0:00 | 0.0421 | 7 | 0.0045 | 0.0486 | 0.0531 | 0.051 | 0.0017 | 0 | 3 | 0.0421 | 0.0521 | P | NP | 1-1-0-0-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
6745 | 79081.295 | 44271.3678 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1632.984 | 0:240:120 | 0:00 | 0.0404 | 7 | 0.0024 | 0.0478 | 0.0502 | 0.0493 | 0.0011 | 0 | 3 | 0.0404 | 0.0504 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6748 | 79084.263 | 44271.3678 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1665.6437 | 0:240:120 | 0:00 | 0.0388 | 7 | 0.003 | 0.0448 | 0.0478 | 0.0467 | 0.0013 | 0 | 3 | 0.0388 | 0.0488 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6751 | 79087.541 | 44271.3679 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1698.9566 | 0:240:120 | 0:00 | 0.0373 | 7 | 0.003 | 0.0436 | 0.0466 | 0.0453 | 0.001 | 0 | 3 | 0.0373 | 0.0473 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6754 | 79090.703 | 44271.3679 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1732.9357 | 0:240:120 | 0:00 | 0.0359 | 7 | 0.0022 | 0.0427 | 0.0449 | 0.0437 | 0.0007 | 0 | 3 | 0.0359 | 0.0459 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6757 | 79093.817 | 44271.3679 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1767.5944 | 0:240:120 | 0:00 | 0.0345 | 7 | 0.0036 | 0.0403 | 0.0439 | 0.0426 | 0.0013 | 0 | 3 | 0.0345 | 0.0445 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6760 | 79097.157 | 44271.368 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1802.9463 | 0:240:120 | 0:00 | 0.0331 | 7 | 0.0021 | 0.0393 | 0.0414 | 0.0406 | 0.0007 | 0 | 3 | 0.0331 | 0.0431 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6763 | 79100.435 | 44271.368 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1839.0052 | 0:240:120 | 0:00 | 0.0318 | 7 | 0.003 | 0.0374 | 0.0404 | 0.0389 | 0.001 | 0 | 3 | 0.0318 | 0.0418 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6766 | 79103.593 | 44271.3681 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1875.7853 | 0:240:120 | 0:00 | 0.0306 | 7 | 0.0033 | 0.036 | 0.0393 | 0.0377 | 0.0011 | 0 | 3 | 0.0306 | 0.0406 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6769 | 79106.706 | 44271.3681 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1913.301 | 0:240:120 | 0:00 | 0.0294 | 7 | 0.0037 | 0.0348 | 0.0385 | 0.0366 | 0.0013 | 0 | 3 | 0.0294 | 0.0394 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6772 | 79109.85 | 44271.3681 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1951.567 | 0:240:120 | 0:00 | 0.0283 | 7 | 0.0031 | 0.0338 | 0.0369 | 0.0352 | 0.0012 | 0 | 3 | 0.0283 | 0.0383 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6775 | 79113.363 | 44271.3682 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1990.5984 | 0:240:120 | 0:00 | 0.0272 | 7 | 0.0042 | 0.0311 | 0.0353 | 0.0339 | 0.0015 | 0 | 3 | 0.0272 | 0.0372 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6778 | 79116.405 | 44271.3682 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2030.4104 | 0:240:120 | 0:00 | 0.0261 | 7 | 0.003 | 0.0311 | 0.0341 | 0.0328 | 0.0012 | 0 | 3 | 0.0261 | 0.0361 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6781 | 79119.416 | 44271.3682 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2071.0186 | 0:240:120 | 0:00 | 0.0251 | 7 | 0.0029 | 0.03 | 0.0329 | 0.0315 | 0.0012 | 0 | 3 | 0.0251 | 0.0351 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6784 | 79122.904 | 44271.3683 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2112.4389 | 0:240:120 | 0:00 | 0.0241 | 7 | 0.0036 | 0.028 | 0.0316 | 0.0301 | 0.0012 | 0 | 3 | 0.0241 | 0.0341 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6787 | 79126.259 | 44271.3683 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2154.6877 | 0:240:120 | 0:00 | 0.0232 | 7 | 0.0029 | 0.0275 | 0.0304 | 0.0291 | 0.0012 | 0 | 3 | 0.0232 | 0.0332 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6790 | 79129.404 | 44271.3684 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2197.7815 | 0:240:120 | 0:00 | 0.0223 | 7 | 0.0027 | 0.0267 | 0.0294 | 0.028 | 0.001 | 0 | 3 | 0.0223 | 0.0323 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6793 | 79132.561 | 44271.3684 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2241.7371 | 0:240:120 | 0:00 | 0.0214 | 7 | 0.0025 | 0.0259 | 0.0284 | 0.0275 | 0.0009 | 0 | 3 | 0.0214 | 0.0314 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6796 | 79135.748 | 44271.3684 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2286.5718 | 0:240:120 | 0:00 | 0.0206 | 7 | 0.0025 | 0.025 | 0.0275 | 0.0265 | 0.001 | 0 | 3 | 0.0206 | 0.0306 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6799 | 79138.82 | 44271.3685 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2332.3033 | 0:240:120 | 0:00 | 0.0198 | 7 | 0.0037 | 0.0234 | 0.0271 | 0.0256 | 0.0014 | 0 | 3 | 0.0198 | 0.0298 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6802 | 79141.969 | 44271.3685 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2378.9493 | 0:240:120 | 0:00 | 0.019 | 7 | 0.0029 | 0.0233 | 0.0262 | 0.025 | 0.0009 | 0 | 3 | 0.019 | 0.029 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6805 | 79145.058 | 44271.3685 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2426.5283 | 0:240:120 | 0:00 | 0.0183 | 7 | 0.0028 | 0.0229 | 0.0257 | 0.0244 | 0.0011 | 0 | 3 | 0.0183 | 0.0283 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6808 | 79148.129 | 44271.3686 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2475.0589 | 0:240:120 | 0:00 | 0.0176 | 7 | 0.0025 | 0.0226 | 0.0251 | 0.0239 | 0.001 | 0 | 3 | 0.0176 | 0.0276 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6811 | 79151.206 | 44271.3686 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2524.5601 | 0:240:120 | 0:00 | 0.0169 | 7 | 0.0037 | 0.0215 | 0.0252 | 0.0234 | 0.0013 | 0 | 3 | 0.0169 | 0.0269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6814 | 79154.374 | 44271.3686 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2575.0513 | 0:240:120 | 0:00 | 0.0162 | 7 | 0.0032 | 0.0208 | 0.024 | 0.0228 | 0.0012 | 0 | 3 | 0.0162 | 0.0262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6817 | 79157.535 | 44271.3687 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2626.5523 | 0:240:120 | 0:00 | 0.0156 | 7 | 0.003 | 0.0203 | 0.0233 | 0.0221 | 0.0011 | 0 | 3 | 0.0156 | 0.0256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6820 | 79160.568 | 44271.3687 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2679.0833 | 0:240:120 | 0:00 | 0.015 | 7 | 0.0044 | 0.0193 | 0.0237 | 0.0216 | 0.0016 | 0 | 3 | 0.015 | 0.025 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6823 | 79163.743 | 44271.3688 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2732.665 | 0:240:120 | 0:00 | 0.0144 | 7 | 0.0042 | 0.019 | 0.0232 | 0.0213 | 0.0015 | 0 | 3 | 0.0144 | 0.0244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6826 | 79166.896 | 44271.3688 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2787.3183 | 0:240:120 | 0:00 | 0.0138 | 7 | 0.0044 | 0.0183 | 0.0227 | 0.0208 | 0.0014 | 0 | 3 | 0.0138 | 0.0238 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6829 | 79170.031 | 44271.3688 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2843.0647 | 0:240:120 | 0:00 | 0.0133 | 7 | 0.0032 | 0.0185 | 0.0217 | 0.0205 | 0.0012 | 0 | 3 | 0.0133 | 0.0233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6832 | 79172.934 | 44271.3689 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2899.926 | 0:240:120 | 0:00 | 0.0128 | 7 | 0.0027 | 0.0185 | 0.0212 | 0.02 | 0.001 | 0 | 3 | 0.0128 | 0.0228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6835 | 79176.217 | 44271.3689 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2957.9245 | 0:240:120 | 0:00 | 0.0123 | 7 | 0.0035 | 0.0175 | 0.021 | 0.0194 | 0.0013 | 0 | 3 | 0.0123 | 0.0223 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6838 | 79179.409 | 44271.3689 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3017.083 | 0:240:120 | 0:00 | 0.0118 | 7 | 0.0033 | 0.0177 | 0.021 | 0.0194 | 0.001 | 0 | 3 | 0.0118 | 0.0218 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6841 | 79182.486 | 44271.369 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3077.4246 | 0:240:120 | 0:00 | 0.0114 | 7 | 0.0028 | 0.0175 | 0.0203 | 0.0187 | 0.0009 | 0 | 3 | 0.0114 | 0.0214 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6844 | 79185.437 | 44271.369 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3138.9731 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0023 | 0.0177 | 0.02 | 0.0187 | 0.0008 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6847 | 79188.522 | 44271.369 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3201.7526 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0014 | 0.0178 | 0.0192 | 0.0182 | 0.0005 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6850 | 79191.488 | 44271.3691 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3265.7876 | 0:240:120 | 0:00 | 0.0101 | 7 | 0.0013 | 0.0172 | 0.0185 | 0.0179 | 0.0005 | 0 | 3 | 0.0101 | 0.0201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6853 | 79194.563 | 44271.3691 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3279.2861 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0011 | 0.0172 | 0.0183 | 0.0178 | 0.0004 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6856 | 79197.943 | 44271.3691 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3344.8718 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0015 | 0.0164 | 0.0179 | 0.0171 | 0.0007 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6859 | 79201.155 | 44271.3692 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3411.7692 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0016 | 0.016 | 0.0176 | 0.0168 | 0.0006 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 0-0-0-0-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
6862 | 79204.239 | 44271.3692 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3480.0046 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0016 | 0.0155 | 0.0171 | 0.0162 | 0.0007 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6865 | 79207.297 | 44271.3693 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3549.6047 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0024 | 0.0148 | 0.0172 | 0.0163 | 0.0009 | 0 | 3 | 0.0085 | 0.016 | NP | NP | 1-0-0-0-1-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
6868 | 79210.536 | 44271.3693 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3620.5968 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0029 | 0.0147 | 0.0176 | 0.0158 | 0.0009 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6871 | 79213.504 | 44271.3693 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3693.0088 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0042 | 0.0131 | 0.0173 | 0.0149 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6874 | 79216.89 | 44271.3694 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3766.8689 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0043 | 0.0125 | 0.0168 | 0.0148 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6877 | 79220.279 | 44271.3694 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3842.2063 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0041 | 0.0125 | 0.0166 | 0.0146 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6880 | 79223.329 | 44271.3694 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3919.0504 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0046 | 0.012 | 0.0166 | 0.0143 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6883 | 79226.603 | 44271.3695 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3997.4314 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0041 | 0.0121 | 0.0162 | 0.0142 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6886 | 79229.96 | 44271.3695 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4077.3801 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0042 | 0.0121 | 0.0163 | 0.0141 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6889 | 79233.028 | 44271.3696 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4158.9277 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0051 | 0.0113 | 0.0164 | 0.0139 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6892 | 79236.346 | 44271.3696 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4242.1062 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0052 | 0.011 | 0.0162 | 0.0138 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6895 | 79239.425 | 44271.3696 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4326.9483 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0052 | 0.011 | 0.0162 | 0.0136 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
6898 | 79242.42 | 44271.3697 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4413.4873 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0043 | 0.0114 | 0.0157 | 0.0135 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6901 | 79245.363 | 44271.3697 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4501.7571 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0052 | 0.011 | 0.0162 | 0.0135 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6904 | 79248.443 | 44271.3697 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4591.7922 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0051 | 0.0109 | 0.016 | 0.0134 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6907 | 79251.578 | 44271.3698 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4683.628 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0057 | 0.0108 | 0.0165 | 0.0134 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6910 | 79254.664 | 44271.3698 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4777.3006 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0052 | 0.0104 | 0.0156 | 0.0132 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6913 | 79257.854 | 44271.3698 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4872.8466 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0042 | 0.011 | 0.0152 | 0.0132 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6916 | 79260.807 | 44271.3699 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4970.3036 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.0051 | 0.0103 | 0.0154 | 0.0128 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6919 | 79263.865 | 44271.3699 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5069.7096 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0054 | 0.0102 | 0.0156 | 0.0127 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6922 | 79267.104 | 44271.3699 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5171.1038 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0055 | 0.0099 | 0.0154 | 0.0128 | 0.0022 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6925 | 79270.174 | 44271.37 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5274.5259 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0056 | 0.0103 | 0.0159 | 0.0129 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6928 | 79273.253 | 44271.37 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5380.0164 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0053 | 0.0099 | 0.0152 | 0.0128 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6931 | 79276.34 | 44271.3701 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5487.6167 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0045 | 0.01 | 0.0145 | 0.0122 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6934 | 79279.305 | 44271.3701 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5597.3691 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0047 | 0.0103 | 0.015 | 0.0127 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6937 | 79282.333 | 44271.3701 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5709.3165 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0043 | 0.0103 | 0.0146 | 0.0124 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6940 | 79285.403 | 44271.3702 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5823.5028 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0045 | 0.0104 | 0.0149 | 0.0125 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6943 | 79288.466 | 44271.3702 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5939.9728 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0042 | 0.0108 | 0.015 | 0.0126 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6946 | 79292.17 | 44271.3702 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6058.7723 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0054 | 0.0098 | 0.0152 | 0.0121 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6949 | 79295.265 | 44271.3703 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6179.9477 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0031 | 0.01 | 0.0131 | 0.0111 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6952 | 79298.54 | 44271.3703 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6303.5467 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0043 | 0.009 | 0.0133 | 0.0109 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6955 | 79301.614 | 44271.3703 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6429.6176 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0051 | 0.0089 | 0.014 | 0.0112 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6958 | 79304.695 | 44271.3704 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6558.21 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0055 | 0.0096 | 0.0151 | 0.0123 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6961 | 79307.863 | 44271.3704 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6558.5722 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0034 | 0.0092 | 0.0126 | 0.0103 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6964 | 79311.252 | 44271.3705 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6689.7436 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0041 | 0.009 | 0.0131 | 0.0107 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6967 | 79314.211 | 44271.3705 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6823.5385 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0039 | 0.01 | 0.0139 | 0.0113 | 0.0013 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6970 | 79317.482 | 44271.3705 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6960.0093 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0044 | 0.0095 | 0.0139 | 0.011 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6973 | 79320.553 | 44271.3706 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7099.2094 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0037 | 0.0104 | 0.0141 | 0.0113 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6976 | 79323.547 | 44271.3706 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7241.1936 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0052 | 0.0098 | 0.015 | 0.0112 | 0.0019 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6979 | 79326.589 | 44271.3706 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7386.0175 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0032 | 0.0095 | 0.0127 | 0.0107 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6982 | 79329.569 | 44271.3707 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7533.7379 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0029 | 0.0096 | 0.0125 | 0.0105 | 0.0011 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6985 | 79332.527 | 44271.3707 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7684.4126 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0013 | 0.0101 | 0.0114 | 0.0106 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6988 | 79335.49 | 44271.3707 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7838.1009 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0014 | 0.0097 | 0.0111 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6991 | 79338.641 | 44271.3708 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7994.8629 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.002 | 0.0098 | 0.0118 | 0.0107 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6994 | 79341.748 | 44271.3708 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8154.7601 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0013 | 0.01 | 0.0113 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6997 | 79344.934 | 44271.3708 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8317.8553 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.002 | 0.0091 | 0.0111 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7000 | 79348.037 | 44271.3709 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8484.2124 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7003 | 79351.211 | 44271.3709 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8653.8967 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.001 | 0.0102 | 0.0112 | 0.0107 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7006 | 79354.185 | 44271.371 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8826.9746 | 0:240:120 | 0:00 | 0.0014 | 7 | 0 | 0.01 | 0.01 | 0.01 | 0 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7009 | 79357.196 | 44271.371 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9003.5141 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0016 | 0.009 | 0.0106 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7012 | 79360.404 | 44271.371 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9183.5844 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7015 | 79363.513 | 44271.3711 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9367.2561 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0011 | 0.01 | 0.0111 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7018 | 79366.498 | 44271.3711 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9554.6012 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0019 | 0.0095 | 0.0114 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7021 | 79369.771 | 44271.3711 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9745.6932 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0023 | 0.0091 | 0.0114 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7024 | 79372.973 | 44271.3712 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9940.6071 | 0:240:120 | 0:00 | 0.0011 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7027 | 79376.352 | 44271.3712 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10139.4192 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0004 | 0.0104 | 0.0108 | 0.0106 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7030 | 79379.227 | 44271.3712 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10342.2076 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0001 | 0.0101 | 0.0102 | 0.0101 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7033 | 79382.483 | 44271.3713 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10549.0518 | 0:240:120 | 0:00 | 0.001 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7036 | 79385.549 | 44271.3713 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10760.0328 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0014 | 0.0093 | 0.0107 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7039 | 79388.606 | 44271.3714 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10975.2335 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0016 | 0.0097 | 0.0113 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7042 | 79391.683 | 44271.3714 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11194.7381 | 0:240:120 | 0:00 | 0.0009 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7045 | 79394.773 | 44271.3714 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11418.6329 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0014 | 0.0098 | 0.0112 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7048 | 79397.817 | 44271.3715 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11647.0056 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0003 | 0.0095 | 0.0098 | 0.0096 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7051 | 79400.916 | 44271.3715 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11879.9457 | 0:240:120 | 0:00 | 0.0008 | 7 | 0.0015 | 0.0093 | 0.0108 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7054 | 79769.23 | 44271.3758 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.1 | 0:240:120 | 0:00 | 40.2016 | 7 | 108.1546 | 259.9905 | 368.1451 | 319.4315 | 38.6573 | 1494.3896 | 3 | 40.2016 | 164.4732 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7057 | 80755.093 | 44271.3872 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.2 | 0:240:120 | 0:00 | 34.5478 | 7 | 106.08 | 140.4712 | 246.5512 | 191.0661 | 44.9601 | 2021.4133 | 3 | 34.5478 | 106.6405 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7060 | 81364.523 | 44271.3942 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.3 | 0:240:120 | 0:00 | 30.2132 | 7 | 54.3767 | 60.9863 | 115.363 | 79.4327 | 26.1226 | 682.3883 | 3 | 30.2132 | 78.4863 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7063 | 81655.639 | 44271.3976 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.4 | 0:240:120 | 0:00 | 26.7859 | 7 | 4.5188 | 54.2365 | 58.7553 | 55.8555 | 2.1578 | 4.656 | 3 | 26.7859 | 61.8379 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7066 | 81826.839 | 44271.3996 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.6 | 0:240:120 | 0:00 | 23.8905 | 7 | 3.3682 | 47.5092 | 50.8774 | 48.6332 | 1.6823 | 2.8302 | 3 | 23.8905 | 50.4128 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7069 | 81975.798 | 44271.4013 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.8 | 0:240:120 | 0:00 | 21.5182 | 7 | 3.6543 | 40.499 | 44.1533 | 41.8516 | 1.7278 | 2.9853 | 3 | 21.5182 | 42.4194 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7072 | 82103.96 | 44271.4028 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.1 | 0:240:120 | 0:00 | 19.4579 | 7 | 6.3989 | 30.7053 | 37.1042 | 33.1915 | 2.9562 | 8.7389 | 3 | 19.4579 | 36.2846 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7075 | 82210.694 | 44271.404 | Vista Speed | T | 40T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.4 | 0:240:120 | 0:00 | 17.7267 | 7 | 1.1217 | 28.4735 | 29.5952 | 28.8488 | 0.5573 | 0.3106 | 3 | 17.7267 | 31.6201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7078 | 82936.933 | 44271.4124 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.63 | 0:240:120 | 0:00 | 63.381 | 7 | 59.8235 | 602.4318 | 662.2553 | 622.3734 | 29.9067 | 894.4082 | 3 | 63.381 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7081 | 84806.885 | 44271.4341 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 127.1226 | 0:240:120 | 0:00 | 51.413 | 7 | 59.8581 | 482.627 | 542.4851 | 502.5809 | 29.9273 | 895.6423 | 3 | 51.413 | 675.7704 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7084 | 86317.776 | 44271.4516 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 129.6651 | 0:240:120 | 0:00 | 42.9711 | 7 | 59.9313 | 362.8499 | 422.7812 | 382.8294 | 29.9632 | 897.7904 | 3 | 42.9711 | 218.5846 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7087 | 87469.482 | 44271.4649 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 132.2584 | 0:240:120 | 0:00 | 36.7014 | 7 | 59.9405 | 243.0336 | 302.9741 | 263.0158 | 29.9676 | 898.0571 | 3 | 36.7014 | 128.2869 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7090 | 88261.917 | 44271.4741 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.9035 | 0:240:120 | 0:00 | 31.8644 | 7 | 83.2104 | 99.9407 | 183.1511 | 135.6299 | 36.835 | 1356.8196 | 3 | 31.8644 | 89.7243 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7093 | 88694.308 | 44271.4791 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.6016 | 0:240:120 | 0:00 | 28.022 | 7 | 6.0281 | 56.7964 | 62.8245 | 59.4382 | 2.6311 | 6.9224 | 3 | 28.022 | 68.3488 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7096 | 88876.433 | 44271.4812 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 140.3536 | 0:240:120 | 0:00 | 24.8984 | 7 | 3.329 | 50.1389 | 53.4679 | 51.3017 | 1.6223 | 2.6319 | 3 | 24.8984 | 54.7728 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7099 | 89033.656 | 44271.483 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 143.1607 | 0:240:120 | 0:00 | 22.3109 | 7 | 3.3182 | 43.509 | 46.8272 | 44.6168 | 1.6573 | 2.7465 | 3 | 22.3109 | 45.3924 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7102 | 89170.737 | 44271.4846 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 146.0239 | 0:240:120 | 0:00 | 20.134 | 7 | 5.0923 | 35.109 | 40.2013 | 37.5923 | 2.0373 | 4.1506 | 3 | 20.134 | 38.5275 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7105 | 89285.094 | 44271.4859 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.9444 | 0:240:120 | 0:00 | 18.2785 | 7 | 1.3176 | 29.1629 | 30.4805 | 29.6169 | 0.6204 | 0.3849 | 3 | 18.2785 | 33.2896 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7108 | 89377.235 | 44271.487 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 151.9233 | 0:240:120 | 0:00 | 16.6793 | 7 | 1.099 | 26.9675 | 28.0665 | 27.3347 | 0.5485 | 0.3008 | 3 | 16.6793 | 29.1645 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7111 | 89462.638 | 44271.488 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 154.9617 | 0:240:120 | 0:00 | 15.2877 | 7 | 2.0672 | 23.6807 | 25.7479 | 24.5921 | 0.8839 | 0.7813 | 3 | 15.2877 | 25.8339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7114 | 89540.133 | 44271.4888 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 158.061 | 0:240:120 | 0:00 | 14.0667 | 7 | 1.0989 | 21.4863 | 22.5852 | 21.8531 | 0.5482 | 0.3006 | 3 | 14.0667 | 23.0904 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7117 | 89608.645 | 44271.4896 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 161.2222 | 0:240:120 | 0:00 | 12.9874 | 7 | 1.1576 | 18.7542 | 19.9118 | 19.1622 | 0.5272 | 0.2779 | 3 | 12.9874 | 20.7931 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7120 | 89669.887 | 44271.4904 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.4466 | 0:240:120 | 0:00 | 12.0274 | 7 | 0.5943 | 17.6181 | 18.2124 | 17.8373 | 0.2814 | 0.0792 | 3 | 12.0274 | 18.8426 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7123 | 89726.211 | 44271.491 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 167.7356 | 0:240:120 | 0:00 | 11.1685 | 7 | 0.545 | 16.0393 | 16.5843 | 16.2215 | 0.272 | 0.074 | 3 | 11.1685 | 17.1672 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7126 | 89777.994 | 44271.4916 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 171.0903 | 0:240:120 | 0:00 | 10.396 | 7 | 0.9187 | 14.413 | 15.3317 | 14.7824 | 0.3985 | 0.1588 | 3 | 10.396 | 15.7136 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7129 | 89825.722 | 44271.4922 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 174.5121 | 0:240:120 | 0:00 | 9.6982 | 7 | 0.6449 | 13.2401 | 13.885 | 13.5594 | 0.2737 | 0.0749 | 3 | 9.6982 | 14.4414 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7132 | 89869.765 | 44271.4927 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 178.0023 | 0:240:120 | 0:00 | 9.0651 | 7 | 0.3763 | 12.5288 | 12.9051 | 12.6793 | 0.1698 | 0.0288 | 3 | 9.0651 | 13.3194 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7135 | 89910.554 | 44271.4931 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 181.5624 | 0:240:120 | 0:00 | 8.4886 | 7 | 0.3231 | 11.6169 | 11.94 | 11.7255 | 0.1606 | 0.0258 | 3 | 8.4886 | 12.3233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7138 | 89948.457 | 44271.4936 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 185.1936 | 0:240:120 | 0:00 | 7.9618 | 7 | 0.3252 | 10.6504 | 10.9756 | 10.7601 | 0.1612 | 0.026 | 3 | 7.9618 | 11.4337 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7141 | 89983.59 | 44271.494 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 188.8975 | 0:240:120 | 0:00 | 7.4789 | 7 | 0.2139 | 10.016 | 10.2299 | 10.0882 | 0.1055 | 0.0111 | 3 | 7.4789 | 10.635 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7144 | 90016.69 | 44271.4944 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 192.6754 | 0:240:120 | 0:00 | 7.035 | 7 | 0.214 | 9.3815 | 9.5955 | 9.454 | 0.1059 | 0.0112 | 3 | 7.035 | 9.9144 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7147 | 90048.069 | 44271.4947 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 196.529 | 0:240:120 | 0:00 | 6.6258 | 7 | 0.2341 | 8.7258 | 8.9599 | 8.8136 | 0.1097 | 0.012 | 3 | 6.6258 | 9.2615 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7150 | 90077.394 | 44271.4951 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 200.4595 | 0:240:120 | 0:00 | 6.2478 | 7 | 0.2941 | 8.0927 | 8.3868 | 8.2423 | 0.1223 | 0.015 | 3 | 6.2478 | 8.6677 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7153 | 90104.858 | 44271.4954 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 204.4687 | 0:240:120 | 0:00 | 5.8977 | 7 | 0.2268 | 7.6419 | 7.8687 | 7.7258 | 0.0975 | 0.0095 | 3 | 5.8977 | 8.1256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7156 | 90131.015 | 44271.4957 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.5581 | 0:240:120 | 0:00 | 5.5728 | 7 | 0.1525 | 7.1918 | 7.3443 | 7.2437 | 0.0747 | 0.0056 | 3 | 5.5728 | 7.6292 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7159 | 90155.875 | 44271.496 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 212.7293 | 0:240:120 | 0:00 | 5.2707 | 7 | 0.2164 | 6.7203 | 6.9367 | 6.8372 | 0.081 | 0.0066 | 3 | 5.2707 | 7.1733 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7162 | 90179.46 | 44271.4962 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 216.9838 | 0:240:120 | 0:00 | 4.9893 | 7 | 0.111 | 6.3865 | 6.4975 | 6.4234 | 0.0546 | 0.003 | 3 | 4.9893 | 6.7534 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7165 | 90201.629 | 44271.4965 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 221.3235 | 0:240:120 | 0:00 | 4.7268 | 7 | 0.1862 | 5.9796 | 6.1658 | 6.0689 | 0.0777 | 0.006 | 3 | 4.7268 | 6.3658 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7168 | 90223.051 | 44271.4968 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 225.75 | 0:240:120 | 0:00 | 4.4814 | 7 | 0.0874 | 5.691 | 5.7784 | 5.7208 | 0.0422 | 0.0018 | 3 | 4.4814 | 6.007 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7171 | 90243.998 | 44271.497 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 230.265 | 0:240:120 | 0:00 | 4.2518 | 7 | 0.1667 | 5.3561 | 5.5228 | 5.4376 | 0.0709 | 0.005 | 3 | 4.2518 | 5.6743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7174 | 90263.592 | 44271.4972 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.8703 | 0:240:120 | 0:00 | 4.0366 | 7 | 0.1204 | 5.0676 | 5.188 | 5.1208 | 0.0519 | 0.0027 | 3 | 4.0366 | 5.3652 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7177 | 90282.341 | 44271.4974 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 239.5677 | 0:240:120 | 0:00 | 3.8347 | 7 | 0.0688 | 4.8351 | 4.9039 | 4.8594 | 0.0334 | 0.0011 | 3 | 3.8347 | 5.0774 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7180 | 90299.963 | 44271.4976 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 244.3591 | 0:240:120 | 0:00 | 3.645 | 7 | 0.0689 | 4.5707 | 4.6396 | 4.5947 | 0.0331 | 0.0011 | 3 | 3.645 | 4.809 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7183 | 90316.522 | 44271.4978 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 249.2462 | 0:240:120 | 0:00 | 3.4666 | 7 | 0.0566 | 4.3316 | 4.3882 | 4.352 | 0.0265 | 0.0007 | 3 | 3.4666 | 4.5583 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7186 | 90332.479 | 44271.498 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 254.2312 | 0:240:120 | 0:00 | 3.2987 | 7 | 0.0565 | 4.1168 | 4.1733 | 4.1369 | 0.027 | 0.0007 | 3 | 3.2987 | 4.3238 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7189 | 90347.975 | 44271.4982 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 259.3158 | 0:240:120 | 0:00 | 3.1403 | 7 | 0.0572 | 3.9035 | 3.9607 | 3.9235 | 0.0275 | 0.0008 | 3 | 3.1403 | 4.1041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7192 | 90362.788 | 44271.4984 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 264.5021 | 0:240:120 | 0:00 | 2.991 | 7 | 0.0626 | 3.7117 | 3.7743 | 3.7397 | 0.0265 | 0.0007 | 3 | 2.991 | 3.8981 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7195 | 90376.925 | 44271.4985 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 269.7921 | 0:240:120 | 0:00 | 2.85 | 7 | 0.0826 | 3.5137 | 3.5963 | 3.553 | 0.0336 | 0.0011 | 3 | 2.85 | 3.7046 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7198 | 90390.48 | 44271.4987 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 275.188 | 0:240:120 | 0:00 | 2.7167 | 7 | 0.0392 | 3.3576 | 3.3968 | 3.372 | 0.0183 | 0.0003 | 3 | 2.7167 | 3.5226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7201 | 90403.511 | 44271.4988 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 280.6917 | 0:240:120 | 0:00 | 2.5907 | 7 | 0.0685 | 3.1836 | 3.2521 | 3.2159 | 0.0292 | 0.0009 | 3 | 2.5907 | 3.3514 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7204 | 90416.606 | 44271.499 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 286.3056 | 0:240:120 | 0:00 | 2.4714 | 7 | 0.0325 | 3.0427 | 3.0752 | 3.0547 | 0.0151 | 0.0002 | 3 | 2.4714 | 3.1901 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7207 | 90428.942 | 44271.4991 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 292.0317 | 0:240:120 | 0:00 | 2.3584 | 7 | 0.0517 | 2.892 | 2.9437 | 2.9182 | 0.0218 | 0.0005 | 3 | 2.3584 | 3.0379 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7210 | 90440.718 | 44271.4993 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 297.8723 | 0:240:120 | 0:00 | 2.2514 | 7 | 0.0488 | 2.7496 | 2.7984 | 2.775 | 0.0185 | 0.0003 | 3 | 2.2514 | 2.8943 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7213 | 90452.275 | 44271.4994 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 303.8298 | 0:240:120 | 0:00 | 2.1498 | 7 | 0.0288 | 2.6405 | 2.6693 | 2.6504 | 0.0138 | 0.0002 | 3 | 2.1498 | 2.7586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7216 | 90463.677 | 44271.4995 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 309.9064 | 0:240:120 | 0:00 | 2.0535 | 7 | 0.025 | 2.5124 | 2.5374 | 2.5222 | 0.0113 | 0.0001 | 3 | 2.0535 | 2.6303 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7219 | 90474.787 | 44271.4997 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 316.1045 | 0:240:120 | 0:00 | 1.962 | 7 | 0.0232 | 2.4022 | 2.4254 | 2.4107 | 0.0108 | 0.0001 | 3 | 1.962 | 2.5089 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7222 | 90484.97 | 44271.4998 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 322.4266 | 0:240:120 | 0:00 | 1.8751 | 7 | 0.0301 | 2.2835 | 2.3136 | 2.2971 | 0.0123 | 0.0002 | 3 | 1.8751 | 2.394 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7225 | 90494.917 | 44271.4999 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 328.8751 | 0:240:120 | 0:00 | 1.7924 | 7 | 0.0388 | 2.1771 | 2.2159 | 2.1958 | 0.0166 | 0.0003 | 3 | 1.7924 | 2.2851 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7228 | 90504.676 | 44271.5 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 335.4526 | 0:240:120 | 0:00 | 1.7139 | 7 | 0.0336 | 2.0843 | 2.1179 | 2.1006 | 0.0139 | 0.0002 | 3 | 1.7139 | 2.1818 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7231 | 90514.316 | 44271.5001 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 342.1617 | 0:240:120 | 0:00 | 1.6391 | 7 | 0.0329 | 1.9832 | 2.0161 | 2.0009 | 0.0138 | 0.0002 | 3 | 1.6391 | 2.0838 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7234 | 90523.353 | 44271.5002 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 349.0049 | 0:240:120 | 0:00 | 1.568 | 7 | 0.0294 | 1.9035 | 1.9329 | 1.9174 | 0.0124 | 0.0002 | 3 | 1.568 | 1.9908 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7237 | 90531.948 | 44271.5003 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 355.985 | 0:240:120 | 0:00 | 1.5002 | 7 | 0.0304 | 1.8129 | 1.8433 | 1.828 | 0.0129 | 0.0002 | 3 | 1.5002 | 1.9024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7240 | 90540.522 | 44271.5004 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 363.1047 | 0:240:120 | 0:00 | 1.4357 | 7 | 0.0293 | 1.7313 | 1.7606 | 1.7493 | 0.0131 | 0.0002 | 3 | 1.4357 | 1.8185 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7243 | 90548.757 | 44271.5005 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 370.3668 | 0:240:120 | 0:00 | 1.3742 | 7 | 0.0345 | 1.655 | 1.6895 | 1.6742 | 0.0148 | 0.0002 | 3 | 1.3742 | 1.7386 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7246 | 90556.876 | 44271.5006 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 377.7741 | 0:240:120 | 0:00 | 1.3156 | 7 | 0.0329 | 1.5858 | 1.6187 | 1.6034 | 0.0136 | 0.0002 | 3 | 1.3156 | 1.6627 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7249 | 90564.554 | 44271.5007 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 385.3296 | 0:240:120 | 0:00 | 1.2596 | 7 | 0.0292 | 1.5165 | 1.5457 | 1.5322 | 0.012 | 0.0001 | 3 | 1.2596 | 1.5904 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7252 | 90572.414 | 44271.5008 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 393.0362 | 0:240:120 | 0:00 | 1.2063 | 7 | 0.0246 | 1.4522 | 1.4768 | 1.4639 | 0.0095 | 0.0001 | 3 | 1.2063 | 1.5216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7255 | 90579.809 | 44271.5009 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 400.8969 | 0:240:120 | 0:00 | 1.1554 | 7 | 0.0267 | 1.3874 | 1.4141 | 1.4019 | 0.0107 | 0.0001 | 3 | 1.1554 | 1.456 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7258 | 90586.972 | 44271.501 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 408.9149 | 0:240:120 | 0:00 | 1.1068 | 7 | 0.026 | 1.3306 | 1.3566 | 1.3441 | 0.0105 | 0.0001 | 3 | 1.1068 | 1.3936 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7261 | 90593.986 | 44271.501 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 417.0932 | 0:240:120 | 0:00 | 1.0604 | 7 | 0.0261 | 1.2712 | 1.2973 | 1.2848 | 0.011 | 0.0001 | 3 | 1.0604 | 1.334 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7264 | 90601.114 | 44271.5011 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 425.435 | 0:240:120 | 0:00 | 1.0161 | 7 | 0.0208 | 1.2183 | 1.2391 | 1.2294 | 0.0085 | 0.0001 | 3 | 1.0161 | 1.2773 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7267 | 90607.946 | 44271.5012 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 433.9437 | 0:240:120 | 0:00 | 0.9737 | 7 | 0.0207 | 1.1678 | 1.1885 | 1.1777 | 0.0082 | 0.0001 | 3 | 0.9737 | 1.2231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7270 | 90614.661 | 44271.5013 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 442.6226 | 0:240:120 | 0:00 | 0.9333 | 7 | 0.0234 | 1.1155 | 1.1389 | 1.1279 | 0.0095 | 0.0001 | 3 | 0.9333 | 1.1714 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7273 | 90621.206 | 44271.5014 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 451.4751 | 0:240:120 | 0:00 | 0.8946 | 7 | 0.0189 | 1.0708 | 1.0897 | 1.0803 | 0.0081 | 0.0001 | 3 | 0.8946 | 1.1221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7276 | 90627.324 | 44271.5014 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 460.5046 | 0:240:120 | 0:00 | 0.8576 | 7 | 0.0178 | 1.0274 | 1.0452 | 1.0369 | 0.0075 | 0.0001 | 3 | 0.8576 | 1.075 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7279 | 90633.444 | 44271.5015 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 469.7146 | 0:240:120 | 0:00 | 0.8222 | 7 | 0.0211 | 0.9823 | 1.0034 | 0.9937 | 0.0087 | 0.0001 | 3 | 0.8222 | 1.03 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7282 | 90639.543 | 44271.5016 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 479.1089 | 0:240:120 | 0:00 | 0.7884 | 7 | 0.017 | 0.943 | 0.96 | 0.952 | 0.007 | 0 | 3 | 0.7884 | 0.9871 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7285 | 90645.378 | 44271.5016 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 488.6911 | 0:240:120 | 0:00 | 0.7561 | 7 | 0.0188 | 0.903 | 0.9218 | 0.9122 | 0.0078 | 0.0001 | 3 | 0.7561 | 0.946 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7288 | 90651.255 | 44271.5017 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 498.4649 | 0:240:120 | 0:00 | 0.7251 | 7 | 0.0181 | 0.8663 | 0.8844 | 0.8754 | 0.0076 | 0.0001 | 3 | 0.7251 | 0.9068 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7291 | 90657.151 | 44271.5018 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 508.4342 | 0:240:120 | 0:00 | 0.6955 | 7 | 0.0179 | 0.8314 | 0.8493 | 0.8394 | 0.007 | 0 | 3 | 0.6955 | 0.8693 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7294 | 90662.668 | 44271.5018 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 518.6029 | 0:240:120 | 0:00 | 0.6671 | 7 | 0.0184 | 0.7943 | 0.8127 | 0.8038 | 0.0073 | 0.0001 | 3 | 0.6671 | 0.8334 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7297 | 90668.07 | 44271.5019 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 528.975 | 0:240:120 | 0:00 | 0.64 | 7 | 0.0167 | 0.7616 | 0.7783 | 0.7708 | 0.0068 | 0 | 3 | 0.64 | 0.7991 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7300 | 90673.236 | 44271.502 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 539.5545 | 0:240:120 | 0:00 | 0.614 | 7 | 0.0177 | 0.7303 | 0.748 | 0.7393 | 0.0068 | 0 | 3 | 0.614 | 0.7663 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7303 | 90678.613 | 44271.502 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 550.3456 | 0:240:120 | 0:00 | 0.5891 | 7 | 0.0165 | 0.7002 | 0.7167 | 0.7089 | 0.0068 | 0 | 3 | 0.5891 | 0.7349 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7306 | 90683.861 | 44271.5021 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 561.3525 | 0:240:120 | 0:00 | 0.5652 | 7 | 0.0149 | 0.6714 | 0.6863 | 0.6799 | 0.0059 | 0 | 3 | 0.5652 | 0.7048 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7309 | 90688.983 | 44271.5021 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 572.5795 | 0:240:120 | 0:00 | 0.5424 | 7 | 0.0147 | 0.6449 | 0.6596 | 0.6527 | 0.0062 | 0 | 3 | 0.5424 | 0.6761 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7312 | 90693.937 | 44271.5022 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 584.0311 | 0:240:120 | 0:00 | 0.5205 | 7 | 0.0126 | 0.619 | 0.6316 | 0.6255 | 0.005 | 0 | 3 | 0.5205 | 0.6485 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7315 | 90698.951 | 44271.5023 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 595.7117 | 0:240:120 | 0:00 | 0.4995 | 7 | 0.0119 | 0.5937 | 0.6056 | 0.6004 | 0.005 | 0 | 3 | 0.4995 | 0.6222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7318 | 90703.953 | 44271.5023 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 607.626 | 0:240:120 | 0:00 | 0.4794 | 7 | 0.0125 | 0.5697 | 0.5822 | 0.5758 | 0.0051 | 0 | 3 | 0.4794 | 0.5969 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7321 | 90708.907 | 44271.5024 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 619.7785 | 0:240:120 | 0:00 | 0.4602 | 7 | 0.0125 | 0.5472 | 0.5597 | 0.5533 | 0.0049 | 0 | 3 | 0.4602 | 0.5728 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7324 | 90713.521 | 44271.5024 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 632.1741 | 0:240:120 | 0:00 | 0.4417 | 7 | 0.0115 | 0.5248 | 0.5363 | 0.5304 | 0.0046 | 0 | 3 | 0.4417 | 0.5496 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7327 | 90718.629 | 44271.5025 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 644.8176 | 0:240:120 | 0:00 | 0.424 | 7 | 0.0125 | 0.5027 | 0.5152 | 0.509 | 0.0047 | 0 | 3 | 0.424 | 0.5274 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7330 | 90723.66 | 44271.5025 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 657.7139 | 0:240:120 | 0:00 | 0.407 | 7 | 0.0093 | 0.4839 | 0.4932 | 0.4885 | 0.0037 | 0 | 3 | 0.407 | 0.5062 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7333 | 90728.231 | 44271.5026 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 670.8682 | 0:240:120 | 0:00 | 0.3908 | 7 | 0.0102 | 0.4637 | 0.4739 | 0.4692 | 0.004 | 0 | 3 | 0.3908 | 0.4858 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7336 | 90732.92 | 44271.5027 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 684.2855 | 0:240:120 | 0:00 | 0.3752 | 7 | 0.0096 | 0.4455 | 0.4551 | 0.4501 | 0.0037 | 0 | 3 | 0.3752 | 0.4663 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7339 | 90737.309 | 44271.5027 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 697.9713 | 0:240:120 | 0:00 | 0.3602 | 7 | 0.0087 | 0.4277 | 0.4364 | 0.4318 | 0.0034 | 0 | 3 | 0.3602 | 0.4475 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7342 | 90741.817 | 44271.5028 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 711.9307 | 0:240:120 | 0:00 | 0.3459 | 7 | 0.0086 | 0.4115 | 0.4201 | 0.4154 | 0.0034 | 0 | 3 | 0.3459 | 0.4296 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7345 | 90746.181 | 44271.5028 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 726.1693 | 0:240:120 | 0:00 | 0.3321 | 7 | 0.0079 | 0.3949 | 0.4028 | 0.3987 | 0.003 | 0 | 3 | 0.3321 | 0.4124 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7348 | 90751.095 | 44271.5029 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 740.6927 | 0:240:120 | 0:00 | 0.3189 | 7 | 0.0066 | 0.3795 | 0.3861 | 0.3824 | 0.0028 | 0 | 3 | 0.3189 | 0.3959 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7351 | 90755.91 | 44271.5029 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 755.5065 | 0:240:120 | 0:00 | 0.3062 | 7 | 0.007 | 0.3647 | 0.3717 | 0.3677 | 0.0029 | 0 | 3 | 0.3062 | 0.3801 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7354 | 90760.764 | 44271.503 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 770.6167 | 0:240:120 | 0:00 | 0.2941 | 7 | 0.0075 | 0.3493 | 0.3568 | 0.3527 | 0.0028 | 0 | 3 | 0.2941 | 0.3649 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7357 | 90765.664 | 44271.503 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 786.029 | 0:240:120 | 0:00 | 0.2824 | 7 | 0.0067 | 0.3356 | 0.3423 | 0.3388 | 0.0026 | 0 | 3 | 0.2824 | 0.3504 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7360 | 90770.101 | 44271.5031 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 801.7496 | 0:240:120 | 0:00 | 0.2712 | 7 | 0.0062 | 0.3217 | 0.3279 | 0.3246 | 0.0024 | 0 | 3 | 0.2712 | 0.3364 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7363 | 90774.6 | 44271.5031 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 817.7846 | 0:240:120 | 0:00 | 0.2605 | 7 | 0.0073 | 0.3092 | 0.3165 | 0.3124 | 0.0027 | 0 | 3 | 0.2605 | 0.3231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7366 | 90779.168 | 44271.5032 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 834.1403 | 0:240:120 | 0:00 | 0.2502 | 7 | 0.0065 | 0.2969 | 0.3034 | 0.3 | 0.0025 | 0 | 3 | 0.2502 | 0.3102 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7369 | 90783.414 | 44271.5032 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 850.8231 | 0:240:120 | 0:00 | 0.2403 | 7 | 0.0055 | 0.2858 | 0.2913 | 0.2881 | 0.0024 | 0 | 3 | 0.2403 | 0.2979 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7372 | 90787.492 | 44271.5033 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 867.8395 | 0:240:120 | 0:00 | 0.2308 | 7 | 0.0054 | 0.274 | 0.2794 | 0.2766 | 0.0021 | 0 | 3 | 0.2308 | 0.2861 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7375 | 90792.001 | 44271.5033 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 885.1963 | 0:240:120 | 0:00 | 0.2217 | 7 | 0.0054 | 0.263 | 0.2684 | 0.2653 | 0.0021 | 0 | 3 | 0.2217 | 0.2748 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7378 | 90796.436 | 44271.5034 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 902.9002 | 0:240:120 | 0:00 | 0.2129 | 7 | 0.0053 | 0.2536 | 0.2589 | 0.2557 | 0.0023 | 0 | 3 | 0.2129 | 0.2639 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7381 | 90800.9 | 44271.5034 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 920.9583 | 0:240:120 | 0:00 | 0.2045 | 7 | 0.0051 | 0.2432 | 0.2483 | 0.2458 | 0.0019 | 0 | 3 | 0.2045 | 0.2534 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7384 | 90804.876 | 44271.5035 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 939.3774 | 0:240:120 | 0:00 | 0.1965 | 7 | 0.0051 | 0.2335 | 0.2386 | 0.2354 | 0.0019 | 0 | 3 | 0.1965 | 0.2434 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7387 | 90808.725 | 44271.5035 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 958.165 | 0:240:120 | 0:00 | 0.1887 | 7 | 0.0051 | 0.2235 | 0.2286 | 0.2258 | 0.002 | 0 | 3 | 0.1887 | 0.2338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7390 | 90812.683 | 44271.5036 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 977.3283 | 0:240:120 | 0:00 | 0.1813 | 7 | 0.0039 | 0.2159 | 0.2198 | 0.2175 | 0.0016 | 0 | 3 | 0.1813 | 0.2246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7393 | 90816.349 | 44271.5036 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 996.8748 | 0:240:120 | 0:00 | 0.1742 | 7 | 0.003 | 0.208 | 0.211 | 0.2088 | 0.0012 | 0 | 3 | 0.1742 | 0.2157 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7396 | 90820.37 | 44271.5037 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1016.8123 | 0:240:120 | 0:00 | 0.1673 | 7 | 0.0042 | 0.1991 | 0.2033 | 0.2006 | 0.0019 | 0 | 3 | 0.1673 | 0.2072 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7399 | 90823.907 | 44271.5037 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1037.1486 | 0:240:120 | 0:00 | 0.1608 | 7 | 0.0041 | 0.191 | 0.1951 | 0.1924 | 0.0018 | 0 | 3 | 0.1608 | 0.199 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7402 | 90827.473 | 44271.5037 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1057.8915 | 0:240:120 | 0:00 | 0.1544 | 7 | 0.0037 | 0.1838 | 0.1875 | 0.1851 | 0.0015 | 0 | 3 | 0.1544 | 0.1912 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7405 | 90830.97 | 44271.5038 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1079.0494 | 0:240:120 | 0:00 | 0.1484 | 7 | 0.0033 | 0.177 | 0.1803 | 0.1782 | 0.0014 | 0 | 3 | 0.1484 | 0.1837 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7408 | 90834.777 | 44271.5038 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1100.6304 | 0:240:120 | 0:00 | 0.1426 | 7 | 0.0038 | 0.1694 | 0.1732 | 0.1708 | 0.0015 | 0 | 3 | 0.1426 | 0.1764 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7411 | 90838.185 | 44271.5039 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1122.643 | 0:240:120 | 0:00 | 0.137 | 7 | 0.0035 | 0.1626 | 0.1661 | 0.1642 | 0.0014 | 0 | 3 | 0.137 | 0.1695 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7414 | 90841.656 | 44271.5039 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1145.0958 | 0:240:120 | 0:00 | 0.1316 | 7 | 0.0038 | 0.1566 | 0.1604 | 0.1582 | 0.0014 | 0 | 3 | 0.1316 | 0.1628 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7417 | 90845.289 | 44271.504 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1167.9977 | 0:240:120 | 0:00 | 0.1264 | 7 | 0.0024 | 0.1506 | 0.153 | 0.1519 | 0.0008 | 0 | 3 | 0.1264 | 0.1564 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7420 | 90848.66 | 44271.504 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1191.3577 | 0:240:120 | 0:00 | 0.1215 | 7 | 0.0042 | 0.1444 | 0.1486 | 0.1461 | 0.0015 | 0 | 3 | 0.1215 | 0.1503 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7423 | 90852.056 | 44271.504 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1215.1849 | 0:240:120 | 0:00 | 0.1167 | 7 | 0.0034 | 0.1388 | 0.1422 | 0.1403 | 0.0011 | 0 | 3 | 0.1167 | 0.1444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7426 | 90855.603 | 44271.5041 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1239.4886 | 0:240:120 | 0:00 | 0.1121 | 7 | 0.005 | 0.1314 | 0.1364 | 0.1339 | 0.0018 | 0 | 3 | 0.1121 | 0.1387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7429 | 90859.003 | 44271.5041 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1264.2783 | 0:240:120 | 0:00 | 0.1078 | 7 | 0.004 | 0.1271 | 0.1311 | 0.1291 | 0.0014 | 0 | 3 | 0.1078 | 0.1333 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7432 | 90862.375 | 44271.5042 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1289.5639 | 0:240:120 | 0:00 | 0.1035 | 7 | 0.0054 | 0.1224 | 0.1278 | 0.1242 | 0.0018 | 0 | 3 | 0.1035 | 0.1281 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7435 | 90866.394 | 44271.5042 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1315.3552 | 0:240:120 | 0:00 | 0.0995 | 7 | 0.0045 | 0.1175 | 0.122 | 0.1196 | 0.0017 | 0 | 3 | 0.0995 | 0.123 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7438 | 90869.73 | 44271.5042 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1341.6623 | 0:240:120 | 0:00 | 0.0956 | 7 | 0.0044 | 0.1125 | 0.1169 | 0.1145 | 0.0014 | 0 | 3 | 0.0956 | 0.1182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7441 | 90873.047 | 44271.5043 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1368.4955 | 0:240:120 | 0:00 | 0.0919 | 7 | 0.0029 | 0.1091 | 0.112 | 0.1102 | 0.001 | 0 | 3 | 0.0919 | 0.1136 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7444 | 90876.359 | 44271.5043 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1395.8654 | 0:240:120 | 0:00 | 0.0883 | 7 | 0.0035 | 0.1037 | 0.1072 | 0.1058 | 0.001 | 0 | 3 | 0.0883 | 0.1091 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7447 | 90879.863 | 44271.5044 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1423.7827 | 0:240:120 | 0:00 | 0.0848 | 7 | 0.0041 | 0.0996 | 0.1037 | 0.1018 | 0.0016 | 0 | 3 | 0.0848 | 0.1049 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7450 | 90883.6 | 44271.5044 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1452.2584 | 0:240:120 | 0:00 | 0.0815 | 7 | 0.0043 | 0.0958 | 0.1001 | 0.0979 | 0.0013 | 0 | 3 | 0.0815 | 0.1008 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7453 | 90886.925 | 44271.5044 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1481.3036 | 0:240:120 | 0:00 | 0.0783 | 7 | 0.0044 | 0.0927 | 0.0971 | 0.0943 | 0.0013 | 0 | 3 | 0.0783 | 0.0968 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7456 | 90890.259 | 44271.5045 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1510.9296 | 0:240:120 | 0:00 | 0.0753 | 7 | 0.004 | 0.0885 | 0.0925 | 0.0904 | 0.0013 | 0 | 3 | 0.0753 | 0.093 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7459 | 90893.595 | 44271.5045 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1541.1482 | 0:240:120 | 0:00 | 0.0723 | 7 | 0.0045 | 0.0851 | 0.0896 | 0.087 | 0.0015 | 0 | 3 | 0.0723 | 0.0894 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7462 | 90896.949 | 44271.5046 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1571.9712 | 0:240:120 | 0:00 | 0.0695 | 7 | 0.0038 | 0.0813 | 0.0851 | 0.0833 | 0.0012 | 0 | 3 | 0.0695 | 0.0859 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7465 | 90900.28 | 44271.5046 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1603.4106 | 0:240:120 | 0:00 | 0.0668 | 7 | 0.0028 | 0.0789 | 0.0817 | 0.0802 | 0.001 | 0 | 3 | 0.0668 | 0.0826 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7468 | 90903.66 | 44271.5046 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1635.4788 | 0:240:120 | 0:00 | 0.0642 | 7 | 0.0039 | 0.0753 | 0.0792 | 0.0777 | 0.0012 | 0 | 3 | 0.0642 | 0.0793 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7471 | 90907.054 | 44271.5047 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1668.1884 | 0:240:120 | 0:00 | 0.0617 | 7 | 0.0039 | 0.0723 | 0.0762 | 0.0739 | 0.0014 | 0 | 3 | 0.0617 | 0.0762 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7474 | 90910.258 | 44271.5047 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1701.5522 | 0:240:120 | 0:00 | 0.0593 | 7 | 0.0025 | 0.0698 | 0.0723 | 0.0713 | 0.0008 | 0 | 3 | 0.0593 | 0.0733 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7477 | 90913.685 | 44271.5047 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1735.5832 | 0:240:120 | 0:00 | 0.057 | 7 | 0.0033 | 0.0674 | 0.0707 | 0.0685 | 0.0011 | 0 | 3 | 0.057 | 0.0704 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7480 | 90917.034 | 44271.5048 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1770.2949 | 0:240:120 | 0:00 | 0.0547 | 7 | 0.0027 | 0.0644 | 0.0671 | 0.0658 | 0.0008 | 0 | 3 | 0.0547 | 0.0676 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7483 | 90920.232 | 44271.5048 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1805.7008 | 0:240:120 | 0:00 | 0.0526 | 7 | 0.003 | 0.0625 | 0.0655 | 0.0637 | 0.0012 | 0 | 3 | 0.0526 | 0.065 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7486 | 90923.553 | 44271.5049 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1841.8148 | 0:240:120 | 0:00 | 0.0506 | 7 | 0.0034 | 0.0593 | 0.0627 | 0.0609 | 0.0013 | 0 | 3 | 0.0506 | 0.0625 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7489 | 90926.921 | 44271.5049 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1878.6511 | 0:240:120 | 0:00 | 0.0486 | 7 | 0.0027 | 0.0579 | 0.0606 | 0.0589 | 0.0011 | 0 | 3 | 0.0486 | 0.06 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7492 | 90930.208 | 44271.5049 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1916.2241 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0028 | 0.0554 | 0.0582 | 0.0567 | 0.0009 | 0 | 3 | 0.0467 | 0.0577 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7495 | 90933.528 | 44271.505 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1954.5486 | 0:240:120 | 0:00 | 0.0449 | 7 | 0.003 | 0.0531 | 0.0561 | 0.0547 | 0.0009 | 0 | 3 | 0.0449 | 0.0554 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7498 | 90937.078 | 44271.505 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1993.6396 | 0:240:120 | 0:00 | 0.0431 | 7 | 0.0025 | 0.0514 | 0.0539 | 0.0525 | 0.0009 | 0 | 3 | 0.0431 | 0.0533 | P | NP | 0-1-1-0-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7501 | 90940.424 | 44271.5051 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2033.5123 | 0:240:120 | 0:00 | 0.0414 | 7 | 0.0023 | 0.0491 | 0.0514 | 0.0504 | 0.0008 | 0 | 3 | 0.0414 | 0.0514 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7504 | 90943.612 | 44271.5051 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2074.1826 | 0:240:120 | 0:00 | 0.0398 | 7 | 0.0029 | 0.0471 | 0.05 | 0.0485 | 0.001 | 0 | 3 | 0.0398 | 0.0498 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7507 | 90947.08 | 44271.5051 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2115.6662 | 0:240:120 | 0:00 | 0.0383 | 7 | 0.0016 | 0.0458 | 0.0474 | 0.0467 | 0.0006 | 0 | 3 | 0.0383 | 0.0483 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7510 | 90950.534 | 44271.5052 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2157.9796 | 0:240:120 | 0:00 | 0.0368 | 7 | 0.0023 | 0.0439 | 0.0462 | 0.0451 | 0.001 | 0 | 3 | 0.0368 | 0.0468 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7513 | 90953.601 | 44271.5052 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2201.1392 | 0:240:120 | 0:00 | 0.0354 | 7 | 0.0036 | 0.0413 | 0.0449 | 0.0429 | 0.0012 | 0 | 3 | 0.0354 | 0.0454 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7516 | 90956.81 | 44271.5052 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2245.1619 | 0:240:120 | 0:00 | 0.034 | 7 | 0.0029 | 0.0397 | 0.0426 | 0.0415 | 0.0012 | 0 | 3 | 0.034 | 0.044 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7519 | 90959.829 | 44271.5053 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2290.0652 | 0:240:120 | 0:00 | 0.0327 | 7 | 0.0029 | 0.0385 | 0.0414 | 0.0399 | 0.0009 | 0 | 3 | 0.0327 | 0.0427 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7522 | 90963.157 | 44271.5053 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2335.8665 | 0:240:120 | 0:00 | 0.0314 | 7 | 0.0042 | 0.036 | 0.0402 | 0.0384 | 0.0014 | 0 | 3 | 0.0314 | 0.0414 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7525 | 90966.379 | 44271.5054 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2382.5838 | 0:240:120 | 0:00 | 0.0302 | 7 | 0.0026 | 0.0355 | 0.0381 | 0.0368 | 0.0009 | 0 | 3 | 0.0302 | 0.0402 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7528 | 90969.803 | 44271.5054 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2430.2355 | 0:240:120 | 0:00 | 0.029 | 7 | 0.0028 | 0.0344 | 0.0372 | 0.0358 | 0.0009 | 0 | 3 | 0.029 | 0.039 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7531 | 90973.313 | 44271.5054 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2478.8402 | 0:240:120 | 0:00 | 0.0279 | 7 | 0.0032 | 0.0326 | 0.0358 | 0.0345 | 0.0012 | 0 | 3 | 0.0279 | 0.0379 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7534 | 90976.981 | 44271.5055 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2528.417 | 0:240:120 | 0:00 | 0.0268 | 7 | 0.0031 | 0.031 | 0.0341 | 0.0331 | 0.0011 | 0 | 3 | 0.0268 | 0.0368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7537 | 90980.224 | 44271.5055 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2578.9853 | 0:240:120 | 0:00 | 0.0257 | 7 | 0.003 | 0.03 | 0.033 | 0.032 | 0.0012 | 0 | 3 | 0.0257 | 0.0357 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7540 | 90983.228 | 44271.5056 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2630.5651 | 0:240:120 | 0:00 | 0.0247 | 7 | 0.0027 | 0.029 | 0.0317 | 0.0311 | 0.0009 | 0 | 3 | 0.0247 | 0.0347 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7543 | 90986.423 | 44271.5056 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2683.1764 | 0:240:120 | 0:00 | 0.0238 | 7 | 0.0029 | 0.0282 | 0.0311 | 0.0301 | 0.0009 | 0 | 3 | 0.0238 | 0.0338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7546 | 90989.635 | 44271.5056 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2736.8399 | 0:240:120 | 0:00 | 0.0228 | 7 | 0.0037 | 0.0268 | 0.0305 | 0.0289 | 0.0013 | 0 | 3 | 0.0228 | 0.0328 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7549 | 90992.896 | 44271.5057 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2791.5767 | 0:240:120 | 0:00 | 0.022 | 7 | 0.003 | 0.0258 | 0.0288 | 0.0277 | 0.0012 | 0 | 3 | 0.022 | 0.032 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7552 | 90995.997 | 44271.5057 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2847.4082 | 0:240:120 | 0:00 | 0.0211 | 7 | 0.0035 | 0.0246 | 0.0281 | 0.0266 | 0.0011 | 0 | 3 | 0.0211 | 0.0311 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7555 | 90999.245 | 44271.5057 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2904.3564 | 0:240:120 | 0:00 | 0.0203 | 7 | 0.0036 | 0.0241 | 0.0277 | 0.0262 | 0.0013 | 0 | 3 | 0.0203 | 0.0303 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7558 | 91002.598 | 44271.5058 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2962.4435 | 0:240:120 | 0:00 | 0.0195 | 7 | 0.0037 | 0.0235 | 0.0272 | 0.0253 | 0.0012 | 0 | 3 | 0.0195 | 0.0295 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7561 | 91005.726 | 44271.5058 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3021.6924 | 0:240:120 | 0:00 | 0.0187 | 7 | 0.0026 | 0.0231 | 0.0257 | 0.0248 | 0.001 | 0 | 3 | 0.0187 | 0.0287 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7564 | 91008.861 | 44271.5058 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3082.1262 | 0:240:120 | 0:00 | 0.018 | 7 | 0.003 | 0.0219 | 0.0249 | 0.0237 | 0.0013 | 0 | 3 | 0.018 | 0.028 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7567 | 91012.12 | 44271.5059 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3143.7687 | 0:240:120 | 0:00 | 0.0173 | 7 | 0.0028 | 0.0219 | 0.0247 | 0.0235 | 0.0012 | 0 | 3 | 0.0173 | 0.0273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7570 | 91015.507 | 44271.5059 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3206.6441 | 0:240:120 | 0:00 | 0.0166 | 7 | 0.0041 | 0.0205 | 0.0246 | 0.0226 | 0.0013 | 0 | 3 | 0.0166 | 0.0266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7573 | 91018.652 | 44271.506 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3270.777 | 0:240:120 | 0:00 | 0.016 | 7 | 0.0045 | 0.0198 | 0.0243 | 0.0221 | 0.0016 | 0 | 3 | 0.016 | 0.026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7576 | 91022.085 | 44271.506 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3336.1925 | 0:240:120 | 0:00 | 0.0154 | 7 | 0.003 | 0.0197 | 0.0227 | 0.0215 | 0.0011 | 0 | 3 | 0.0154 | 0.0254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7579 | 91025.099 | 44271.506 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3402.9164 | 0:240:120 | 0:00 | 0.0148 | 7 | 0.0031 | 0.0192 | 0.0223 | 0.0212 | 0.0012 | 0 | 3 | 0.0148 | 0.0248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7582 | 91028.209 | 44271.5061 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3470.9747 | 0:240:120 | 0:00 | 0.0142 | 7 | 0.0032 | 0.0185 | 0.0217 | 0.0206 | 0.0013 | 0 | 3 | 0.0142 | 0.0242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7585 | 91031.913 | 44271.5061 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3540.3942 | 0:240:120 | 0:00 | 0.0136 | 7 | 0.0042 | 0.018 | 0.0222 | 0.0203 | 0.0015 | 0 | 3 | 0.0136 | 0.0236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7588 | 91035.065 | 44271.5062 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3611.2021 | 0:240:120 | 0:00 | 0.0131 | 7 | 0.0041 | 0.018 | 0.0221 | 0.02 | 0.0014 | 0 | 3 | 0.0131 | 0.0231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7591 | 91038.646 | 44271.5062 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3683.4261 | 0:240:120 | 0:00 | 0.0126 | 7 | 0.0031 | 0.0183 | 0.0214 | 0.0197 | 0.0011 | 0 | 3 | 0.0126 | 0.0226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7594 | 91041.782 | 44271.5062 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3757.0947 | 0:240:120 | 0:00 | 0.0121 | 7 | 0.0038 | 0.0173 | 0.0211 | 0.0188 | 0.0014 | 0 | 3 | 0.0121 | 0.0221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7597 | 91044.925 | 44271.5063 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3832.2366 | 0:240:120 | 0:00 | 0.0116 | 7 | 0.0036 | 0.0171 | 0.0207 | 0.0184 | 0.0012 | 0 | 3 | 0.0116 | 0.0216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7600 | 91048.055 | 44271.5063 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3908.8813 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.003 | 0.0171 | 0.0201 | 0.0182 | 0.001 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7603 | 91051.094 | 44271.5063 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3987.0589 | 0:240:120 | 0:00 | 0.0108 | 7 | 0.0014 | 0.0176 | 0.019 | 0.0183 | 0.0005 | 0 | 3 | 0.0108 | 0.0208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7606 | 91054.236 | 44271.5064 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4066.8001 | 0:240:120 | 0:00 | 0.0103 | 7 | 0.0022 | 0.0164 | 0.0186 | 0.0175 | 0.0007 | 0 | 3 | 0.0103 | 0.0203 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7609 | 91057.472 | 44271.5064 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4135.062 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0021 | 0.0163 | 0.0184 | 0.0173 | 0.0005 | 0 | 3 | 0.01 | 0.02 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7612 | 91060.714 | 44271.5064 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4217.7632 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0016 | 0.0163 | 0.0179 | 0.0169 | 0.0006 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7615 | 91063.787 | 44271.5065 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4302.1185 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0013 | 0.0153 | 0.0166 | 0.0163 | 0.0004 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 0-0-0-0-0-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
7618 | 91067.497 | 44271.5065 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4388.1608 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.003 | 0.0143 | 0.0173 | 0.016 | 0.0009 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
7621 | 91070.681 | 44271.5066 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4475.9241 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0019 | 0.0149 | 0.0168 | 0.0158 | 0.0006 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
7624 | 91073.692 | 44271.5066 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4565.4425 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0035 | 0.0136 | 0.0171 | 0.0155 | 0.0013 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
7627 | 91076.829 | 44271.5066 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4656.7514 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0042 | 0.0132 | 0.0174 | 0.0149 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
7630 | 91079.974 | 44271.5067 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4749.8864 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0046 | 0.0122 | 0.0168 | 0.0146 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7633 | 91083.201 | 44271.5067 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4844.8841 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0047 | 0.0123 | 0.017 | 0.0144 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7636 | 91086.331 | 44271.5067 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4941.7818 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0051 | 0.0118 | 0.0169 | 0.0142 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
7639 | 91089.823 | 44271.5068 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5040.6175 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0043 | 0.012 | 0.0163 | 0.0141 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
7642 | 91092.745 | 44271.5068 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5141.4298 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0051 | 0.0115 | 0.0166 | 0.0139 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7645 | 91095.884 | 44271.5069 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5244.2584 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.004 | 0.0118 | 0.0158 | 0.0139 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7648 | 91099.198 | 44271.5069 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5349.1436 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0051 | 0.011 | 0.0161 | 0.0136 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7651 | 91102.499 | 44271.5069 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5456.1265 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0038 | 0.0119 | 0.0157 | 0.0135 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7654 | 91105.644 | 44271.507 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5565.249 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0052 | 0.011 | 0.0162 | 0.0134 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
7657 | 91108.746 | 44271.507 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5676.554 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0042 | 0.0114 | 0.0156 | 0.0137 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7660 | 91111.893 | 44271.507 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5790.085 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0052 | 0.0107 | 0.0159 | 0.0134 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7663 | 91115.349 | 44271.5071 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5905.8867 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0051 | 0.0111 | 0.0162 | 0.0134 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7666 | 91118.479 | 44271.5071 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6024.0045 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0059 | 0.0103 | 0.0162 | 0.0132 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7669 | 91121.717 | 44271.5072 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6144.4846 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0053 | 0.0107 | 0.016 | 0.013 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7672 | 91124.852 | 44271.5072 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6267.3743 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.0041 | 0.0106 | 0.0147 | 0.0129 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7675 | 91128.045 | 44271.5072 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6392.7217 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0045 | 0.0102 | 0.0147 | 0.0127 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7678 | 91131.371 | 44271.5073 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6520.5762 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0047 | 0.0102 | 0.0149 | 0.0128 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7681 | 91134.524 | 44271.5073 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6650.9877 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0056 | 0.0099 | 0.0155 | 0.0128 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7684 | 91137.643 | 44271.5073 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6784.0075 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0045 | 0.0102 | 0.0147 | 0.0124 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7687 | 91140.688 | 44271.5074 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6919.6876 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0051 | 0.01 | 0.0151 | 0.0123 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7690 | 91143.888 | 44271.5074 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7058.0814 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0035 | 0.0105 | 0.014 | 0.0122 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7693 | 91147.229 | 44271.5074 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7199.243 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0051 | 0.0099 | 0.015 | 0.0118 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7696 | 91150.293 | 44271.5075 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7343.2278 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0044 | 0.0101 | 0.0145 | 0.0119 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7699 | 91153.511 | 44271.5075 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7490.0924 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0041 | 0.01 | 0.0141 | 0.0113 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7702 | 91156.63 | 44271.5076 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7639.8942 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0034 | 0.0101 | 0.0135 | 0.0114 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7705 | 91159.651 | 44271.5076 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7792.6921 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0032 | 0.0092 | 0.0124 | 0.0108 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7708 | 91162.767 | 44271.5076 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7948.546 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0026 | 0.0095 | 0.0121 | 0.0108 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7711 | 91165.785 | 44271.5077 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8107.5169 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0053 | 0.0095 | 0.0148 | 0.0115 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7714 | 91169.015 | 44271.5077 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8269.6672 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.002 | 0.0101 | 0.0121 | 0.0108 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7717 | 91172.026 | 44271.5077 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8270.1239 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0058 | 0.0091 | 0.0149 | 0.011 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7720 | 91174.951 | 44271.5078 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8435.5264 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.0029 | 0.0101 | 0.013 | 0.0109 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7723 | 91178.414 | 44271.5078 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8604.2369 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.0052 | 0.0092 | 0.0144 | 0.0111 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7726 | 91181.623 | 44271.5078 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8776.3217 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0029 | 0.0098 | 0.0127 | 0.0109 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7729 | 91184.766 | 44271.5079 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8951.8481 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0046 | 0.0098 | 0.0144 | 0.0118 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7732 | 91187.776 | 44271.5079 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9130.8851 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0029 | 0.0093 | 0.0122 | 0.0105 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7735 | 91191.146 | 44271.508 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9313.5028 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0029 | 0.0095 | 0.0124 | 0.0108 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7738 | 91194.303 | 44271.508 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9499.7728 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0021 | 0.01 | 0.0121 | 0.0107 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7741 | 91197.415 | 44271.508 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9689.7683 | 0:240:120 | 0:00 | 0.0018 | 7 | 0.0028 | 0.009 | 0.0118 | 0.0104 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7744 | 91200.635 | 44271.5081 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9883.5637 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0016 | 0.0099 | 0.0115 | 0.0107 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7747 | 91203.785 | 44271.5081 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10081.2349 | 0:240:120 | 0:00 | 0.0017 | 7 | 0.0038 | 0.0104 | 0.0142 | 0.0112 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
7750 | 91206.987 | 44271.5081 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10282.8596 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0026 | 0.009 | 0.0116 | 0.01 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7753 | 91209.969 | 44271.5082 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10488.5168 | 0:240:120 | 0:00 | 0.0016 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7756 | 91213.027 | 44271.5082 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10698.2872 | 0:240:120 | 0:00 | 0.0015 | 7 | 0.0011 | 0.0101 | 0.0112 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7759 | 91216.119 | 44271.5082 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10912.2529 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0021 | 0.009 | 0.0111 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7762 | 91219.425 | 44271.5083 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11130.498 | 0:240:120 | 0:00 | 0.0014 | 7 | 0.0016 | 0.0098 | 0.0114 | 0.0107 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7765 | 91222.514 | 44271.5083 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11353.1079 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7768 | 91225.655 | 44271.5084 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11580.1701 | 0:240:120 | 0:00 | 0.0013 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7771 | 91228.953 | 44271.5084 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11811.7735 | 0:240:120 | 0:00 | 0.0012 | 7 | 0.0011 | 0.0103 | 0.0114 | 0.0107 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7774 | 91589.002 | 44271.5126 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131 | 0:240:120 | 0:00 | 39.5131 | 7 | 97.0916 | 265.7663 | 362.8579 | 317.0688 | 34.9308 | 1220.1632 | 3 | 39.5131 | 160.6542 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7777 | 92560.64 | 44271.5238 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.6 | 0:240:120 | 0:00 | 34.0895 | 7 | 67.7684 | 175.2725 | 243.0409 | 201.382 | 31.3404 | 982.2235 | 3 | 34.0895 | 105.4186 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7780 | 93163.095 | 44271.5308 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.3 | 0:240:120 | 0:00 | 29.7622 | 7 | 55.7161 | 60.211 | 115.9271 | 79.3871 | 26.5632 | 705.6031 | 3 | 29.7622 | 77.2754 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7783 | 93453.969 | 44271.5341 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 139 | 0:240:120 | 0:00 | 26.3504 | 7 | 3.599 | 53.454 | 57.053 | 54.7516 | 1.7192 | 2.9556 | 3 | 26.3504 | 60.7365 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7786 | 93621.097 | 44271.5361 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.8 | 0:240:120 | 0:00 | 23.5008 | 7 | 3.3202 | 46.8205 | 50.1407 | 47.9294 | 1.6569 | 2.7453 | 3 | 23.5008 | 49.5247 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7789 | 93767.942 | 44271.5378 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.6 | 0:240:120 | 0:00 | 21.1662 | 7 | 3.3183 | 40.1951 | 43.5134 | 41.3021 | 1.6581 | 2.7493 | 3 | 21.1662 | 41.6777 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7792 | 93894.544 | 44271.5392 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.5 | 0:240:120 | 0:00 | 19.156 | 7 | 6.1952 | 30.2687 | 36.4639 | 33.1791 | 2.6888 | 7.2297 | 3 | 19.156 | 35.7022 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7795 | 93999.434 | 44271.5405 | Vista Speed | T | 50T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.4 | 0:240:120 | 0:00 | 17.4644 | 7 | 1.0994 | 28.0627 | 29.1621 | 28.4302 | 0.5485 | 0.3008 | 3 | 17.4644 | 31.1477 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7798 | 94725.274 | 44271.5489 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.97 | 0:240:120 | 0:00 | 63.4229 | 7 | 60.0905 | 602.7726 | 662.8631 | 622.8035 | 30.0442 | 902.655 | 3 | 63.4229 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7801 | 96596.953 | 44271.5705 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.1094 | 0:240:120 | 0:00 | 51.447 | 7 | 59.9408 | 482.9548 | 542.8956 | 502.9365 | 29.969 | 898.143 | 3 | 51.447 | 676.2171 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7804 | 98109.161 | 44271.588 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 163.3116 | 0:240:120 | 0:00 | 42.9995 | 7 | 59.9359 | 363.0956 | 423.0315 | 383.0757 | 29.9651 | 897.9057 | 3 | 42.9995 | 218.7291 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7807 | 99261.355 | 44271.6014 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.5778 | 0:240:120 | 0:00 | 36.7257 | 7 | 59.9401 | 243.2043 | 303.1444 | 263.1873 | 29.9668 | 898.0091 | 3 | 36.7257 | 128.3718 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7810 | 100053.605 | 44271.6105 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.9094 | 0:240:120 | 0:00 | 31.8854 | 7 | 60.2062 | 123.0877 | 183.2939 | 143.279 | 30.0109 | 900.6532 | 3 | 31.8854 | 89.7836 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
7813 | 100485.506 | 44271.6155 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 173.3076 | 0:240:120 | 0:00 | 28.0406 | 7 | 4.9317 | 57.7457 | 62.6774 | 60.1399 | 2.0795 | 4.3242 | 3 | 28.0406 | 68.394 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7816 | 100667.213 | 44271.6176 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176.7737 | 0:240:120 | 0:00 | 24.9149 | 7 | 3.3176 | 50.1719 | 53.4895 | 51.5748 | 1.4874 | 2.2124 | 3 | 24.9149 | 54.809 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7819 | 100824.135 | 44271.6195 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 180.3092 | 0:240:120 | 0:00 | 22.3257 | 7 | 3.3193 | 43.5375 | 46.8568 | 44.6449 | 1.6582 | 2.7495 | 3 | 22.3257 | 45.4224 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7822 | 100961.247 | 44271.621 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.9154 | 0:240:120 | 0:00 | 20.1473 | 7 | 3.33 | 36.8969 | 40.2269 | 38.0118 | 1.6601 | 2.7559 | 3 | 20.1473 | 38.553 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
7825 | 101074.937 | 44271.6224 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 187.5937 | 0:240:120 | 0:00 | 18.2906 | 7 | 1.098 | 29.1822 | 30.2802 | 29.7345 | 0.4754 | 0.226 | 3 | 18.2906 | 33.3116 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7828 | 101166.643 | 44271.6234 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 191.3456 | 0:240:120 | 0:00 | 16.6903 | 7 | 1.1026 | 26.984 | 28.0866 | 27.3533 | 0.5491 | 0.3015 | 3 | 16.6903 | 29.1838 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7831 | 101251.143 | 44271.6244 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 195.1725 | 0:240:120 | 0:00 | 15.2978 | 7 | 1.312 | 23.7465 | 25.0585 | 24.5231 | 0.5703 | 0.3253 | 3 | 15.2978 | 25.851 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7834 | 101326.781 | 44271.6253 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 199.0759 | 0:240:120 | 0:00 | 14.076 | 7 | 1.1012 | 21.5013 | 22.6025 | 21.8697 | 0.5491 | 0.3015 | 3 | 14.076 | 23.1057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7837 | 101394.442 | 44271.6261 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 203.0574 | 0:240:120 | 0:00 | 12.996 | 7 | 0.5688 | 18.7665 | 19.3353 | 19.1136 | 0.2621 | 0.0687 | 3 | 12.996 | 20.8068 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7840 | 101454.187 | 44271.6267 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 207.1186 | 0:240:120 | 0:00 | 12.0354 | 7 | 0.5474 | 17.6788 | 18.2262 | 17.8622 | 0.2719 | 0.0739 | 3 | 12.0354 | 18.8551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7843 | 101510.338 | 44271.6274 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 211.261 | 0:240:120 | 0:00 | 11.1759 | 7 | 0.5473 | 16.0497 | 16.597 | 16.2328 | 0.272 | 0.074 | 3 | 11.1759 | 17.1786 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7846 | 101561.711 | 44271.628 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 215.4862 | 0:240:120 | 0:00 | 10.4029 | 7 | 0.5614 | 14.4214 | 14.9828 | 14.7718 | 0.263 | 0.0692 | 3 | 10.4029 | 15.724 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7849 | 101608.562 | 44271.6285 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 219.7959 | 0:240:120 | 0:00 | 9.7046 | 7 | 0.3504 | 13.5276 | 13.878 | 13.6585 | 0.1645 | 0.027 | 3 | 9.7046 | 14.4509 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7852 | 101652.275 | 44271.629 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 224.1918 | 0:240:120 | 0:00 | 9.0711 | 7 | 0.3252 | 12.5903 | 12.9155 | 12.6987 | 0.1614 | 0.026 | 3 | 9.0711 | 13.3282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7855 | 101692.871 | 44271.6295 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 228.6756 | 0:240:120 | 0:00 | 8.4942 | 7 | 0.3259 | 11.6228 | 11.9487 | 11.7326 | 0.1615 | 0.0261 | 3 | 8.4942 | 12.3315 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7858 | 101730.717 | 44271.6299 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 233.2492 | 0:240:120 | 0:00 | 7.9671 | 7 | 0.3246 | 10.6575 | 10.9821 | 10.7669 | 0.1611 | 0.026 | 3 | 7.9671 | 11.4413 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7861 | 101766.03 | 44271.6304 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.9141 | 0:240:120 | 0:00 | 7.4839 | 7 | 0.2145 | 10.0226 | 10.2371 | 10.0945 | 0.1062 | 0.0113 | 3 | 7.4839 | 10.642 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7864 | 101798.997 | 44271.6307 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 242.6724 | 0:240:120 | 0:00 | 7.0397 | 7 | 0.2153 | 9.3866 | 9.6019 | 9.4595 | 0.1061 | 0.0112 | 3 | 7.0397 | 9.921 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7867 | 101830.177 | 44271.6311 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 247.5259 | 0:240:120 | 0:00 | 6.6302 | 7 | 0.2148 | 8.7525 | 8.9673 | 8.8245 | 0.1063 | 0.0113 | 3 | 6.6302 | 9.2677 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7870 | 101859.636 | 44271.6314 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 252.4764 | 0:240:120 | 0:00 | 6.2519 | 7 | 0.1847 | 8.2062 | 8.3909 | 8.286 | 0.0783 | 0.0061 | 3 | 6.2519 | 8.6734 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7873 | 101887.39 | 44271.6318 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 257.5259 | 0:240:120 | 0:00 | 5.9016 | 7 | 0.1499 | 7.6469 | 7.7968 | 7.7442 | 0.0729 | 0.0053 | 3 | 5.9016 | 8.131 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7876 | 101913.253 | 44271.6321 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 262.6764 | 0:240:120 | 0:00 | 5.5765 | 7 | 0.1505 | 7.199 | 7.3495 | 7.2506 | 0.0739 | 0.0055 | 3 | 5.5765 | 7.6343 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7879 | 101938.06 | 44271.6323 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 267.93 | 0:240:120 | 0:00 | 5.2742 | 7 | 0.1125 | 6.8283 | 6.9408 | 6.8662 | 0.0558 | 0.0031 | 3 | 5.2742 | 7.1781 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7882 | 101961.54 | 44271.6326 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 273.2886 | 0:240:120 | 0:00 | 4.9926 | 7 | 0.1106 | 6.3906 | 6.5012 | 6.452 | 0.0491 | 0.0024 | 3 | 4.9926 | 6.7579 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7885 | 101983.655 | 44271.6329 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 278.7543 | 0:240:120 | 0:00 | 4.7299 | 7 | 0.113 | 6.0576 | 6.1706 | 6.0967 | 0.0551 | 0.003 | 3 | 4.7299 | 6.37 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7888 | 102004.76 | 44271.6331 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 284.3294 | 0:240:120 | 0:00 | 4.4844 | 7 | 0.0831 | 5.6979 | 5.781 | 5.7333 | 0.0375 | 0.0014 | 3 | 4.4844 | 6.011 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7891 | 102024.751 | 44271.6333 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 290.016 | 0:240:120 | 0:00 | 4.2546 | 7 | 0.1189 | 5.3634 | 5.4823 | 5.4282 | 0.0475 | 0.0023 | 3 | 4.2546 | 5.6781 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7894 | 102043.986 | 44271.6336 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 295.8163 | 0:240:120 | 0:00 | 4.0393 | 7 | 0.0881 | 5.104 | 5.1921 | 5.134 | 0.043 | 0.0019 | 3 | 4.0393 | 5.3687 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7897 | 102062.313 | 44271.6338 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 301.7327 | 0:240:120 | 0:00 | 3.8373 | 7 | 0.0693 | 4.8385 | 4.9078 | 4.8628 | 0.0335 | 0.0011 | 3 | 3.8373 | 5.0807 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7900 | 102079.794 | 44271.634 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 307.7673 | 0:240:120 | 0:00 | 3.6474 | 7 | 0.0667 | 4.5759 | 4.6426 | 4.6027 | 0.0307 | 0.0009 | 3 | 3.6474 | 4.8121 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7903 | 102096.359 | 44271.6342 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 313.9227 | 0:240:120 | 0:00 | 3.4689 | 7 | 0.0529 | 4.3367 | 4.3896 | 4.3632 | 0.0226 | 0.0005 | 3 | 3.4689 | 4.5613 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7906 | 102112.44 | 44271.6344 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 320.2011 | 0:240:120 | 0:00 | 3.3008 | 7 | 0.0541 | 4.1223 | 4.1764 | 4.152 | 0.0232 | 0.0005 | 3 | 3.3008 | 4.3266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7909 | 102128.023 | 44271.6345 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 326.6051 | 0:240:120 | 0:00 | 3.1424 | 7 | 0.0545 | 3.909 | 3.9635 | 3.9313 | 0.025 | 0.0006 | 3 | 3.1424 | 4.1068 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7912 | 102142.983 | 44271.6347 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 333.1372 | 0:240:120 | 0:00 | 2.993 | 7 | 0.0658 | 3.712 | 3.7778 | 3.7431 | 0.0267 | 0.0007 | 3 | 2.993 | 3.9006 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7915 | 102157.203 | 44271.6349 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 339.8 | 0:240:120 | 0:00 | 2.8519 | 7 | 0.0891 | 3.5142 | 3.6033 | 3.5582 | 0.0379 | 0.0014 | 3 | 2.8519 | 3.707 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7918 | 102170.863 | 44271.635 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 346.596 | 0:240:120 | 0:00 | 2.7185 | 7 | 0.0384 | 3.3621 | 3.4005 | 3.3864 | 0.0178 | 0.0003 | 3 | 2.7185 | 3.525 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7921 | 102183.881 | 44271.6352 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 353.5279 | 0:240:120 | 0:00 | 2.5924 | 7 | 0.0725 | 3.1811 | 3.2536 | 3.2166 | 0.031 | 0.001 | 3 | 2.5924 | 3.3536 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7924 | 102196.53 | 44271.6353 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 360.5985 | 0:240:120 | 0:00 | 2.4731 | 7 | 0.0366 | 3.0468 | 3.0834 | 3.0675 | 0.0155 | 0.0002 | 3 | 2.4731 | 3.1922 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7927 | 102208.764 | 44271.6355 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 367.8104 | 0:240:120 | 0:00 | 2.36 | 7 | 0.0618 | 2.8932 | 2.955 | 2.9234 | 0.0261 | 0.0007 | 3 | 2.36 | 3.0399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7930 | 102220.507 | 44271.6356 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 375.1666 | 0:240:120 | 0:00 | 2.2529 | 7 | 0.0515 | 2.7485 | 2.8 | 2.7761 | 0.0226 | 0.0005 | 3 | 2.2529 | 2.8962 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7933 | 102231.811 | 44271.6357 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 382.67 | 0:240:120 | 0:00 | 2.1513 | 7 | 0.0527 | 2.6182 | 2.6709 | 2.6515 | 0.0237 | 0.0006 | 3 | 2.1513 | 2.7605 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7936 | 102242.626 | 44271.6359 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 390.3234 | 0:240:120 | 0:00 | 2.0548 | 7 | 0.0544 | 2.4976 | 2.552 | 2.5281 | 0.0199 | 0.0004 | 3 | 2.0548 | 2.6321 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7939 | 102253.351 | 44271.636 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 398.1298 | 0:240:120 | 0:00 | 1.9633 | 7 | 0.0478 | 2.3832 | 2.431 | 2.413 | 0.0218 | 0.0005 | 3 | 1.9633 | 2.5106 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7942 | 102263.737 | 44271.6361 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 406.0924 | 0:240:120 | 0:00 | 1.8763 | 7 | 0.0454 | 2.2746 | 2.32 | 2.3001 | 0.0187 | 0.0003 | 3 | 1.8763 | 2.3956 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7945 | 102273.634 | 44271.6362 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 414.2143 | 0:240:120 | 0:00 | 1.7936 | 7 | 0.0384 | 2.1788 | 2.2172 | 2.199 | 0.0163 | 0.0003 | 3 | 1.7936 | 2.2866 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7948 | 102283.219 | 44271.6363 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 422.4986 | 0:240:120 | 0:00 | 1.715 | 7 | 0.0344 | 2.0847 | 2.1191 | 2.1015 | 0.0146 | 0.0002 | 3 | 1.715 | 2.1832 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7951 | 102292.415 | 44271.6364 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 430.9485 | 0:240:120 | 0:00 | 1.6402 | 7 | 0.0438 | 1.9832 | 2.027 | 2.0082 | 0.0191 | 0.0004 | 3 | 1.6402 | 2.0852 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7954 | 102301.331 | 44271.6365 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 439.5675 | 0:240:120 | 0:00 | 1.569 | 7 | 0.0366 | 1.8974 | 1.934 | 1.9172 | 0.0145 | 0.0002 | 3 | 1.569 | 1.9921 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7957 | 102310.236 | 44271.6367 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 448.3589 | 0:240:120 | 0:00 | 1.5012 | 7 | 0.0303 | 1.8143 | 1.8446 | 1.8316 | 0.0131 | 0.0002 | 3 | 1.5012 | 1.9037 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7960 | 102318.588 | 44271.6367 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 457.326 | 0:240:120 | 0:00 | 1.4366 | 7 | 0.0394 | 1.733 | 1.7724 | 1.7544 | 0.017 | 0.0003 | 3 | 1.4366 | 1.8197 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7963 | 102327.89 | 44271.6369 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 466.4726 | 0:240:120 | 0:00 | 1.3751 | 7 | 0.0387 | 1.6556 | 1.6943 | 1.6761 | 0.0163 | 0.0003 | 3 | 1.3751 | 1.7398 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7966 | 102336.006 | 44271.6369 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 475.802 | 0:240:120 | 0:00 | 1.3164 | 7 | 0.0354 | 1.5848 | 1.6202 | 1.6038 | 0.0152 | 0.0002 | 3 | 1.3164 | 1.6638 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7969 | 102343.902 | 44271.637 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 485.3181 | 0:240:120 | 0:00 | 1.2605 | 7 | 0.0304 | 1.5185 | 1.5489 | 1.5347 | 0.0129 | 0.0002 | 3 | 1.2605 | 1.5915 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7972 | 102351.282 | 44271.6371 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 495.0244 | 0:240:120 | 0:00 | 1.2071 | 7 | 0.0353 | 1.4503 | 1.4856 | 1.4696 | 0.0146 | 0.0002 | 3 | 1.2071 | 1.5226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7975 | 102358.535 | 44271.6372 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 504.9249 | 0:240:120 | 0:00 | 1.1561 | 7 | 0.0288 | 1.3869 | 1.4157 | 1.4024 | 0.0121 | 0.0001 | 3 | 1.1561 | 1.457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7978 | 102365.944 | 44271.6373 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 515.0234 | 0:240:120 | 0:00 | 1.1075 | 7 | 0.0274 | 1.3315 | 1.3589 | 1.3459 | 0.0116 | 0.0001 | 3 | 1.1075 | 1.3945 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7981 | 102372.912 | 44271.6374 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 525.3239 | 0:240:120 | 0:00 | 1.0611 | 7 | 0.0274 | 1.2719 | 1.2993 | 1.286 | 0.0113 | 0.0001 | 3 | 1.0611 | 1.3349 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7984 | 102379.77 | 44271.6375 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 535.8303 | 0:240:120 | 0:00 | 1.0167 | 7 | 0.0304 | 1.2166 | 1.247 | 1.2324 | 0.0123 | 0.0002 | 3 | 1.0167 | 1.2781 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7987 | 102386.662 | 44271.6375 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 546.547 | 0:240:120 | 0:00 | 0.9744 | 7 | 0.029 | 1.1647 | 1.1937 | 1.1806 | 0.0124 | 0.0002 | 3 | 0.9744 | 1.2239 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7990 | 102393.368 | 44271.6376 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 557.4779 | 0:240:120 | 0:00 | 0.9339 | 7 | 0.0275 | 1.116 | 1.1435 | 1.131 | 0.0117 | 0.0001 | 3 | 0.9339 | 1.1722 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7993 | 102399.589 | 44271.6377 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 568.6275 | 0:240:120 | 0:00 | 0.8952 | 7 | 0.0234 | 1.0718 | 1.0952 | 1.0837 | 0.0099 | 0.0001 | 3 | 0.8952 | 1.1229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7996 | 102405.58 | 44271.6378 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 580 | 0:240:120 | 0:00 | 0.8582 | 7 | 0.0209 | 1.0258 | 1.0467 | 1.0373 | 0.0086 | 0.0001 | 3 | 0.8582 | 1.0757 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7999 | 102411.659 | 44271.6378 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 591.6 | 0:240:120 | 0:00 | 0.8228 | 7 | 0.023 | 0.9818 | 1.0048 | 0.9945 | 0.0097 | 0.0001 | 3 | 0.8228 | 1.0307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8002 | 102417.48 | 44271.6379 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 603.432 | 0:240:120 | 0:00 | 0.7889 | 7 | 0.0217 | 0.9391 | 0.9608 | 0.9514 | 0.0094 | 0.0001 | 3 | 0.7889 | 0.9877 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8005 | 102423.271 | 44271.638 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 615.5006 | 0:240:120 | 0:00 | 0.7566 | 7 | 0.0198 | 0.9042 | 0.924 | 0.9137 | 0.0081 | 0.0001 | 3 | 0.7566 | 0.9467 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8008 | 102428.923 | 44271.638 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 627.8107 | 0:240:120 | 0:00 | 0.7256 | 7 | 0.0198 | 0.8658 | 0.8856 | 0.8758 | 0.0083 | 0.0001 | 3 | 0.7256 | 0.9074 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8011 | 102434.799 | 44271.6381 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 640.3669 | 0:240:120 | 0:00 | 0.6959 | 7 | 0.0185 | 0.8293 | 0.8478 | 0.8385 | 0.0074 | 0.0001 | 3 | 0.6959 | 0.8699 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8014 | 102440.461 | 44271.6382 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 653.1742 | 0:240:120 | 0:00 | 0.6676 | 7 | 0.0193 | 0.794 | 0.8133 | 0.8042 | 0.0075 | 0.0001 | 3 | 0.6676 | 0.834 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8017 | 102445.724 | 44271.6382 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 666.2377 | 0:240:120 | 0:00 | 0.6404 | 7 | 0.0163 | 0.7631 | 0.7794 | 0.7719 | 0.007 | 0 | 3 | 0.6404 | 0.7996 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8020 | 102450.902 | 44271.6383 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 679.5624 | 0:240:120 | 0:00 | 0.6144 | 7 | 0.0193 | 0.7301 | 0.7494 | 0.74 | 0.0073 | 0.0001 | 3 | 0.6144 | 0.7668 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8023 | 102456.091 | 44271.6383 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 693.1537 | 0:240:120 | 0:00 | 0.5895 | 7 | 0.0163 | 0.7013 | 0.7176 | 0.7093 | 0.0067 | 0 | 3 | 0.5895 | 0.7354 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8026 | 102461.189 | 44271.6384 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 707.0168 | 0:240:120 | 0:00 | 0.5656 | 7 | 0.0137 | 0.6735 | 0.6872 | 0.6802 | 0.0056 | 0 | 3 | 0.5656 | 0.7053 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8029 | 102466.209 | 44271.6385 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 721.1571 | 0:240:120 | 0:00 | 0.5428 | 7 | 0.0135 | 0.646 | 0.6595 | 0.653 | 0.0056 | 0 | 3 | 0.5428 | 0.6765 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8032 | 102471.074 | 44271.6385 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 735.5802 | 0:240:120 | 0:00 | 0.5209 | 7 | 0.0141 | 0.619 | 0.6331 | 0.6263 | 0.0057 | 0 | 3 | 0.5209 | 0.649 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8035 | 102476.118 | 44271.6386 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 750.2918 | 0:240:120 | 0:00 | 0.4999 | 7 | 0.01 | 0.5953 | 0.6053 | 0.6004 | 0.0041 | 0 | 3 | 0.4999 | 0.6226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8038 | 102480.797 | 44271.6386 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 765.2977 | 0:240:120 | 0:00 | 0.4798 | 7 | 0.0117 | 0.5716 | 0.5833 | 0.5772 | 0.0048 | 0 | 3 | 0.4798 | 0.5973 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8041 | 102485.454 | 44271.6387 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 780.6036 | 0:240:120 | 0:00 | 0.4605 | 7 | 0.0111 | 0.5483 | 0.5594 | 0.5534 | 0.0044 | 0 | 3 | 0.4605 | 0.5731 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8044 | 102490.273 | 44271.6387 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 796.2157 | 0:240:120 | 0:00 | 0.442 | 7 | 0.0103 | 0.5265 | 0.5368 | 0.5311 | 0.0044 | 0 | 3 | 0.442 | 0.55 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8047 | 102495.068 | 44271.6388 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 812.14 | 0:240:120 | 0:00 | 0.4243 | 7 | 0.0114 | 0.5045 | 0.5159 | 0.5101 | 0.0042 | 0 | 3 | 0.4243 | 0.5278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8050 | 102499.697 | 44271.6388 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 828.3828 | 0:240:120 | 0:00 | 0.4073 | 7 | 0.01 | 0.484 | 0.494 | 0.4892 | 0.004 | 0 | 3 | 0.4073 | 0.5065 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8053 | 102504.05 | 44271.6389 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 844.9505 | 0:240:120 | 0:00 | 0.391 | 7 | 0.009 | 0.4651 | 0.4741 | 0.4696 | 0.0036 | 0 | 3 | 0.391 | 0.4861 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8056 | 102508.676 | 44271.6389 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 861.8495 | 0:240:120 | 0:00 | 0.3754 | 7 | 0.0086 | 0.4466 | 0.4552 | 0.4506 | 0.0034 | 0 | 3 | 0.3754 | 0.4666 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8059 | 102512.952 | 44271.639 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 879.0865 | 0:240:120 | 0:00 | 0.3605 | 7 | 0.0087 | 0.4284 | 0.4371 | 0.4328 | 0.0035 | 0 | 3 | 0.3605 | 0.4478 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8062 | 102517.183 | 44271.639 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 896.6682 | 0:240:120 | 0:00 | 0.3461 | 7 | 0.0098 | 0.411 | 0.4208 | 0.4157 | 0.0037 | 0 | 3 | 0.3461 | 0.4299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8065 | 102521.252 | 44271.6391 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 914.6016 | 0:240:120 | 0:00 | 0.3323 | 7 | 0.008 | 0.3948 | 0.4028 | 0.3986 | 0.0031 | 0 | 3 | 0.3323 | 0.4127 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8068 | 102525.565 | 44271.6391 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 932.8936 | 0:240:120 | 0:00 | 0.3191 | 7 | 0.0082 | 0.3795 | 0.3877 | 0.3838 | 0.003 | 0 | 3 | 0.3191 | 0.3962 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8071 | 102529.596 | 44271.6392 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 951.5515 | 0:240:120 | 0:00 | 0.3064 | 7 | 0.0077 | 0.365 | 0.3727 | 0.3684 | 0.0031 | 0 | 3 | 0.3064 | 0.3804 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8074 | 102533.668 | 44271.6392 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 970.5825 | 0:240:120 | 0:00 | 0.2943 | 7 | 0.0074 | 0.3501 | 0.3575 | 0.3533 | 0.0028 | 0 | 3 | 0.2943 | 0.3652 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8077 | 102537.628 | 44271.6393 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 989.9942 | 0:240:120 | 0:00 | 0.2826 | 7 | 0.0055 | 0.337 | 0.3425 | 0.3391 | 0.0021 | 0 | 3 | 0.2826 | 0.3506 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8080 | 102541.709 | 44271.6393 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1009.794 | 0:240:120 | 0:00 | 0.2714 | 7 | 0.0062 | 0.3222 | 0.3284 | 0.325 | 0.0024 | 0 | 3 | 0.2714 | 0.3367 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8083 | 102545.626 | 44271.6394 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1029.9899 | 0:240:120 | 0:00 | 0.2607 | 7 | 0.0069 | 0.3091 | 0.316 | 0.3121 | 0.0027 | 0 | 3 | 0.2607 | 0.3233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8086 | 102549.388 | 44271.6394 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1050.5897 | 0:240:120 | 0:00 | 0.2503 | 7 | 0.0068 | 0.2973 | 0.3041 | 0.3002 | 0.0027 | 0 | 3 | 0.2503 | 0.3104 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8089 | 102553.359 | 44271.6395 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1071.6015 | 0:240:120 | 0:00 | 0.2404 | 7 | 0.005 | 0.286 | 0.291 | 0.2886 | 0.0018 | 0 | 3 | 0.2404 | 0.2981 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8092 | 102557.085 | 44271.6395 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1093.0335 | 0:240:120 | 0:00 | 0.2309 | 7 | 0.005 | 0.2744 | 0.2794 | 0.2767 | 0.0018 | 0 | 3 | 0.2309 | 0.2863 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8095 | 102560.901 | 44271.6396 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1114.8942 | 0:240:120 | 0:00 | 0.2218 | 7 | 0.0062 | 0.2635 | 0.2697 | 0.2661 | 0.0025 | 0 | 3 | 0.2218 | 0.2749 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8098 | 102564.631 | 44271.6396 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1137.1921 | 0:240:120 | 0:00 | 0.2131 | 7 | 0.0044 | 0.2544 | 0.2588 | 0.2559 | 0.0021 | 0 | 3 | 0.2131 | 0.264 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8101 | 102568.679 | 44271.6396 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1159.9359 | 0:240:120 | 0:00 | 0.2047 | 7 | 0.0063 | 0.2428 | 0.2491 | 0.2458 | 0.0024 | 0 | 3 | 0.2047 | 0.2536 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8104 | 102572.534 | 44271.6397 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1183.1347 | 0:240:120 | 0:00 | 0.1966 | 7 | 0.0059 | 0.2339 | 0.2398 | 0.2362 | 0.0022 | 0 | 3 | 0.1966 | 0.2436 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8107 | 102576.467 | 44271.6397 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1206.7974 | 0:240:120 | 0:00 | 0.1889 | 7 | 0.0041 | 0.225 | 0.2291 | 0.2264 | 0.0015 | 0 | 3 | 0.1889 | 0.2339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8110 | 102580.122 | 44271.6398 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1230.9333 | 0:240:120 | 0:00 | 0.1814 | 7 | 0.0079 | 0.2123 | 0.2202 | 0.2167 | 0.0028 | 0 | 3 | 0.1814 | 0.2247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8113 | 102583.753 | 44271.6398 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1255.552 | 0:240:120 | 0:00 | 0.1743 | 7 | 0.0048 | 0.2074 | 0.2122 | 0.2095 | 0.0017 | 0 | 3 | 0.1743 | 0.2158 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8116 | 102587.436 | 44271.6399 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1280.663 | 0:240:120 | 0:00 | 0.1674 | 7 | 0.0056 | 0.1968 | 0.2024 | 0.1997 | 0.0022 | 0 | 3 | 0.1674 | 0.2073 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8119 | 102590.81 | 44271.6399 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1306.2763 | 0:240:120 | 0:00 | 0.1609 | 7 | 0.0062 | 0.188 | 0.1942 | 0.1913 | 0.002 | 0 | 3 | 0.1609 | 0.1992 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8122 | 102594.325 | 44271.6399 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1332.4018 | 0:240:120 | 0:00 | 0.1545 | 7 | 0.0038 | 0.1843 | 0.1881 | 0.1855 | 0.0015 | 0 | 3 | 0.1545 | 0.1913 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8125 | 102597.761 | 44271.64 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1359.0498 | 0:240:120 | 0:00 | 0.1485 | 7 | 0.0041 | 0.1754 | 0.1795 | 0.177 | 0.0014 | 0 | 3 | 0.1485 | 0.1838 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8128 | 102601.266 | 44271.64 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1386.2308 | 0:240:120 | 0:00 | 0.1426 | 7 | 0.0057 | 0.1679 | 0.1736 | 0.1699 | 0.0018 | 0 | 3 | 0.1426 | 0.1766 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8131 | 102604.891 | 44271.6401 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1413.9554 | 0:240:120 | 0:00 | 0.1371 | 7 | 0.0042 | 0.1617 | 0.1659 | 0.1637 | 0.0015 | 0 | 3 | 0.1371 | 0.1696 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8134 | 102608.32 | 44271.6401 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1442.2346 | 0:240:120 | 0:00 | 0.1317 | 7 | 0.0062 | 0.1541 | 0.1603 | 0.1576 | 0.0018 | 0 | 3 | 0.1317 | 0.1629 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8137 | 102611.598 | 44271.6401 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1471.0792 | 0:240:120 | 0:00 | 0.1265 | 7 | 0.0055 | 0.1493 | 0.1548 | 0.1513 | 0.0018 | 0 | 3 | 0.1265 | 0.1565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8140 | 102615.216 | 44271.6402 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1500.5008 | 0:240:120 | 0:00 | 0.1216 | 7 | 0.0042 | 0.1433 | 0.1475 | 0.145 | 0.0017 | 0 | 3 | 0.1216 | 0.1504 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8143 | 102618.636 | 44271.6402 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1530.5108 | 0:240:120 | 0:00 | 0.1168 | 7 | 0.0037 | 0.1378 | 0.1415 | 0.1393 | 0.0015 | 0 | 3 | 0.1168 | 0.1445 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8146 | 102622.048 | 44271.6403 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1561.1211 | 0:240:120 | 0:00 | 0.1122 | 7 | 0.0029 | 0.1338 | 0.1367 | 0.1349 | 0.0013 | 0 | 3 | 0.1122 | 0.1388 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8149 | 102625.365 | 44271.6403 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1592.3435 | 0:240:120 | 0:00 | 0.1078 | 7 | 0.0038 | 0.1269 | 0.1307 | 0.1289 | 0.0016 | 0 | 3 | 0.1078 | 0.1334 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8152 | 102628.642 | 44271.6403 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1624.1904 | 0:240:120 | 0:00 | 0.1036 | 7 | 0.0035 | 0.1225 | 0.126 | 0.1236 | 0.0014 | 0 | 3 | 0.1036 | 0.1281 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8155 | 102631.931 | 44271.6404 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1656.6742 | 0:240:120 | 0:00 | 0.0996 | 7 | 0.0051 | 0.1164 | 0.1215 | 0.1191 | 0.0014 | 0 | 3 | 0.0996 | 0.1231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8158 | 102635.366 | 44271.6404 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1689.8076 | 0:240:120 | 0:00 | 0.0957 | 7 | 0.0035 | 0.1134 | 0.1169 | 0.1148 | 0.0013 | 0 | 3 | 0.0957 | 0.1183 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8161 | 102638.608 | 44271.6405 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1723.6038 | 0:240:120 | 0:00 | 0.0919 | 7 | 0.004 | 0.1081 | 0.1121 | 0.1103 | 0.0013 | 0 | 3 | 0.0919 | 0.1137 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8164 | 102641.925 | 44271.6405 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1758.0759 | 0:240:120 | 0:00 | 0.0883 | 7 | 0.003 | 0.1042 | 0.1072 | 0.1058 | 0.0011 | 0 | 3 | 0.0883 | 0.1092 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8167 | 102645.246 | 44271.6405 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1793.2374 | 0:240:120 | 0:00 | 0.0849 | 7 | 0.0036 | 0.0999 | 0.1035 | 0.1018 | 0.0012 | 0 | 3 | 0.0849 | 0.1049 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8170 | 102648.54 | 44271.6406 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1829.1021 | 0:240:120 | 0:00 | 0.0816 | 7 | 0.0023 | 0.0969 | 0.0992 | 0.0979 | 0.0009 | 0 | 3 | 0.0816 | 0.1008 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8173 | 102651.833 | 44271.6406 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1865.6842 | 0:240:120 | 0:00 | 0.0784 | 7 | 0.0027 | 0.0933 | 0.096 | 0.0945 | 0.001 | 0 | 3 | 0.0784 | 0.0969 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8176 | 102655.354 | 44271.6406 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1902.9979 | 0:240:120 | 0:00 | 0.0753 | 7 | 0.004 | 0.0882 | 0.0922 | 0.0904 | 0.0015 | 0 | 3 | 0.0753 | 0.0931 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8179 | 102658.677 | 44271.6407 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1941.0578 | 0:240:120 | 0:00 | 0.0724 | 7 | 0.0041 | 0.0851 | 0.0892 | 0.0869 | 0.0014 | 0 | 3 | 0.0724 | 0.0895 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8182 | 102662.239 | 44271.6407 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1979.879 | 0:240:120 | 0:00 | 0.0696 | 7 | 0.0038 | 0.0816 | 0.0854 | 0.084 | 0.0012 | 0 | 3 | 0.0696 | 0.086 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8185 | 102665.702 | 44271.6408 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2019.4766 | 0:240:120 | 0:00 | 0.0668 | 7 | 0.0045 | 0.0786 | 0.0831 | 0.0807 | 0.0016 | 0 | 3 | 0.0668 | 0.0826 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
8188 | 102669.228 | 44271.6408 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2059.8661 | 0:240:120 | 0:00 | 0.0642 | 7 | 0.0037 | 0.0756 | 0.0793 | 0.0775 | 0.0012 | 0 | 3 | 0.0642 | 0.0794 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8191 | 102672.562 | 44271.6408 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2101.0634 | 0:240:120 | 0:00 | 0.0617 | 7 | 0.0037 | 0.0722 | 0.0759 | 0.0738 | 0.0012 | 0 | 3 | 0.0617 | 0.0763 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8194 | 102675.761 | 44271.6409 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2143.0847 | 0:240:120 | 0:00 | 0.0593 | 7 | 0.0033 | 0.0689 | 0.0722 | 0.071 | 0.0009 | 0 | 3 | 0.0593 | 0.0733 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8197 | 102679.08 | 44271.6409 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2185.9464 | 0:240:120 | 0:00 | 0.057 | 7 | 0.0022 | 0.0669 | 0.0691 | 0.068 | 0.0009 | 0 | 3 | 0.057 | 0.0704 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8200 | 102682.326 | 44271.641 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2229.6653 | 0:240:120 | 0:00 | 0.0548 | 7 | 0.0038 | 0.0641 | 0.0679 | 0.0661 | 0.0013 | 0 | 3 | 0.0548 | 0.0677 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
8203 | 102685.648 | 44271.641 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2274.2586 | 0:240:120 | 0:00 | 0.0526 | 7 | 0.0029 | 0.0619 | 0.0648 | 0.0635 | 0.0013 | 0 | 3 | 0.0526 | 0.0651 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8206 | 102688.91 | 44271.641 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2319.7438 | 0:240:120 | 0:00 | 0.0506 | 7 | 0.0035 | 0.0592 | 0.0627 | 0.0607 | 0.0012 | 0 | 3 | 0.0506 | 0.0625 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
8209 | 102692.154 | 44271.6411 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2366.1386 | 0:240:120 | 0:00 | 0.0486 | 7 | 0.0016 | 0.058 | 0.0596 | 0.0592 | 0.0007 | 0 | 3 | 0.0486 | 0.0601 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8212 | 102695.355 | 44271.6411 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2413.4614 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0024 | 0.0551 | 0.0575 | 0.0565 | 0.001 | 0 | 3 | 0.0467 | 0.0577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8215 | 102698.84 | 44271.6411 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2461.7307 | 0:240:120 | 0:00 | 0.0449 | 7 | 0.0021 | 0.0529 | 0.055 | 0.0542 | 0.0007 | 0 | 3 | 0.0449 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8218 | 102702.26 | 44271.6412 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2510.9653 | 0:240:120 | 0:00 | 0.0432 | 7 | 0.0024 | 0.0513 | 0.0537 | 0.0526 | 0.0009 | 0 | 3 | 0.0432 | 0.0533 | P | NP | 0-1-0-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
8221 | 102705.663 | 44271.6412 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2561.1846 | 0:240:120 | 0:00 | 0.0415 | 7 | 0.0026 | 0.0488 | 0.0514 | 0.0503 | 0.0009 | 0 | 3 | 0.0415 | 0.0515 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8224 | 102708.825 | 44271.6413 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2612.4083 | 0:240:120 | 0:00 | 0.0399 | 7 | 0.0029 | 0.0468 | 0.0497 | 0.0483 | 0.0012 | 0 | 3 | 0.0399 | 0.0499 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8227 | 102712.679 | 44271.6413 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2664.6564 | 0:240:120 | 0:00 | 0.0383 | 7 | 0.0026 | 0.0449 | 0.0475 | 0.0466 | 0.001 | 0 | 3 | 0.0383 | 0.0483 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8230 | 102715.814 | 44271.6413 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2717.9496 | 0:240:120 | 0:00 | 0.0368 | 7 | 0.0041 | 0.0424 | 0.0465 | 0.0449 | 0.0012 | 0 | 3 | 0.0368 | 0.0468 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8233 | 102718.995 | 44271.6414 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2772.3085 | 0:240:120 | 0:00 | 0.0354 | 7 | 0.0034 | 0.0415 | 0.0449 | 0.0432 | 0.0011 | 0 | 3 | 0.0354 | 0.0454 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8236 | 102722.169 | 44271.6414 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2827.7547 | 0:240:120 | 0:00 | 0.034 | 7 | 0.0029 | 0.0397 | 0.0426 | 0.0418 | 0.001 | 0 | 3 | 0.034 | 0.044 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8239 | 102725.692 | 44271.6415 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2884.3098 | 0:240:120 | 0:00 | 0.0327 | 7 | 0.0026 | 0.0385 | 0.0411 | 0.04 | 0.0008 | 0 | 3 | 0.0327 | 0.0427 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8242 | 102728.839 | 44271.6415 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2941.996 | 0:240:120 | 0:00 | 0.0314 | 7 | 0.0041 | 0.0361 | 0.0402 | 0.0384 | 0.0018 | 0 | 3 | 0.0314 | 0.0414 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8245 | 102732.032 | 44271.6415 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3000.8359 | 0:240:120 | 0:00 | 0.0302 | 7 | 0.0032 | 0.0353 | 0.0385 | 0.037 | 0.0011 | 0 | 3 | 0.0302 | 0.0402 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8248 | 102735.018 | 44271.6416 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3060.8526 | 0:240:120 | 0:00 | 0.029 | 7 | 0.0036 | 0.0337 | 0.0373 | 0.0356 | 0.0011 | 0 | 3 | 0.029 | 0.039 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8251 | 102738.162 | 44271.6416 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3122.0697 | 0:240:120 | 0:00 | 0.0279 | 7 | 0.0028 | 0.0329 | 0.0357 | 0.0344 | 0.0011 | 0 | 3 | 0.0279 | 0.0379 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8254 | 102741.359 | 44271.6416 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3184.5111 | 0:240:120 | 0:00 | 0.0268 | 7 | 0.0037 | 0.031 | 0.0347 | 0.0332 | 0.0013 | 0 | 3 | 0.0268 | 0.0368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8257 | 102744.495 | 44271.6417 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3248.2013 | 0:240:120 | 0:00 | 0.0258 | 7 | 0.0033 | 0.0303 | 0.0336 | 0.0322 | 0.001 | 0 | 3 | 0.0258 | 0.0358 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8260 | 102747.764 | 44271.6417 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3313.1653 | 0:240:120 | 0:00 | 0.0248 | 7 | 0.0034 | 0.0287 | 0.0321 | 0.0305 | 0.0014 | 0 | 3 | 0.0248 | 0.0348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8263 | 102751.378 | 44271.6418 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3379.4286 | 0:240:120 | 0:00 | 0.0238 | 7 | 0.0038 | 0.0277 | 0.0315 | 0.0301 | 0.0015 | 0 | 3 | 0.0238 | 0.0338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8266 | 102754.416 | 44271.6418 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3447.0172 | 0:240:120 | 0:00 | 0.0229 | 7 | 0.003 | 0.0272 | 0.0302 | 0.029 | 0.0009 | 0 | 3 | 0.0229 | 0.0329 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8269 | 102757.534 | 44271.6418 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3515.9576 | 0:240:120 | 0:00 | 0.022 | 7 | 0.0027 | 0.0266 | 0.0293 | 0.0278 | 0.001 | 0 | 3 | 0.022 | 0.032 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8272 | 102760.571 | 44271.6419 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3586.2767 | 0:240:120 | 0:00 | 0.0211 | 7 | 0.0035 | 0.025 | 0.0285 | 0.0268 | 0.0013 | 0 | 3 | 0.0211 | 0.0311 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8275 | 102763.97 | 44271.6419 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3658.0023 | 0:240:120 | 0:00 | 0.0203 | 7 | 0.004 | 0.0237 | 0.0277 | 0.026 | 0.0015 | 0 | 3 | 0.0203 | 0.0303 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8278 | 102767.369 | 44271.6419 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3731.1623 | 0:240:120 | 0:00 | 0.0195 | 7 | 0.0025 | 0.0239 | 0.0264 | 0.0256 | 0.001 | 0 | 3 | 0.0195 | 0.0295 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8281 | 102770.686 | 44271.642 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3805.7855 | 0:240:120 | 0:00 | 0.0188 | 7 | 0.0042 | 0.0221 | 0.0263 | 0.0247 | 0.0014 | 0 | 3 | 0.0188 | 0.0288 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8284 | 102773.643 | 44271.642 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3881.9013 | 0:240:120 | 0:00 | 0.018 | 7 | 0.0034 | 0.0218 | 0.0252 | 0.0238 | 0.0013 | 0 | 3 | 0.018 | 0.028 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8287 | 102776.943 | 44271.6421 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3959.5393 | 0:240:120 | 0:00 | 0.0173 | 7 | 0.0036 | 0.0208 | 0.0244 | 0.0231 | 0.0013 | 0 | 3 | 0.0173 | 0.0273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8290 | 102780.051 | 44271.6421 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4038.7301 | 0:240:120 | 0:00 | 0.0166 | 7 | 0.003 | 0.0208 | 0.0238 | 0.0226 | 0.0011 | 0 | 3 | 0.0166 | 0.0266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8293 | 102783.173 | 44271.6421 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4119.5047 | 0:240:120 | 0:00 | 0.016 | 7 | 0.0041 | 0.0194 | 0.0235 | 0.0221 | 0.0014 | 0 | 3 | 0.016 | 0.026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8296 | 102786.255 | 44271.6422 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4201.8948 | 0:240:120 | 0:00 | 0.0154 | 7 | 0.0042 | 0.0198 | 0.024 | 0.0217 | 0.0015 | 0 | 3 | 0.0154 | 0.0254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8299 | 102789.421 | 44271.6422 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4285.9327 | 0:240:120 | 0:00 | 0.0148 | 7 | 0.0039 | 0.0188 | 0.0227 | 0.0212 | 0.0013 | 0 | 3 | 0.0148 | 0.0248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8302 | 102792.52 | 44271.6422 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4371.6513 | 0:240:120 | 0:00 | 0.0142 | 7 | 0.003 | 0.0192 | 0.0222 | 0.0208 | 0.0011 | 0 | 3 | 0.0142 | 0.0242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8305 | 102795.803 | 44271.6423 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4459.0843 | 0:240:120 | 0:00 | 0.0137 | 7 | 0.0034 | 0.0181 | 0.0215 | 0.0202 | 0.0013 | 0 | 3 | 0.0137 | 0.0237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8308 | 102798.894 | 44271.6423 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4548.266 | 0:240:120 | 0:00 | 0.0131 | 7 | 0.0016 | 0.0189 | 0.0205 | 0.0199 | 0.0007 | 0 | 3 | 0.0131 | 0.0231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8311 | 102802.083 | 44271.6423 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4639.2313 | 0:240:120 | 0:00 | 0.0126 | 7 | 0.0035 | 0.0178 | 0.0213 | 0.0195 | 0.0014 | 0 | 3 | 0.0126 | 0.0226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8314 | 102805.051 | 44271.6424 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4732.016 | 0:240:120 | 0:00 | 0.0121 | 7 | 0.0032 | 0.0177 | 0.0209 | 0.0192 | 0.001 | 0 | 3 | 0.0121 | 0.0221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8317 | 102808.256 | 44271.6424 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4826.6563 | 0:240:120 | 0:00 | 0.0117 | 7 | 0.0025 | 0.0174 | 0.0199 | 0.0188 | 0.001 | 0 | 3 | 0.0117 | 0.0217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8320 | 102811.203 | 44271.6424 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4923.1894 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.0023 | 0.0173 | 0.0196 | 0.0181 | 0.0008 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8323 | 102814.314 | 44271.6425 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5021.6532 | 0:240:120 | 0:00 | 0.0108 | 7 | 0.0018 | 0.0173 | 0.0191 | 0.018 | 0.0005 | 0 | 3 | 0.0108 | 0.0208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8326 | 102817.383 | 44271.6425 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5122.0863 | 0:240:120 | 0:00 | 0.0103 | 7 | 0.001 | 0.0172 | 0.0182 | 0.0177 | 0.0004 | 0 | 3 | 0.0103 | 0.0203 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8329 | 102820.374 | 44271.6426 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5209.7814 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0014 | 0.0167 | 0.0181 | 0.017 | 0.0004 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
8332 | 102823.451 | 44271.6426 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5313.977 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.002 | 0.0159 | 0.0179 | 0.0168 | 0.0007 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 1-1-0-1-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
8335 | 102826.451 | 44271.6426 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5420.2565 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0025 | 0.0153 | 0.0178 | 0.0166 | 0.0007 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 1-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
8338 | 102829.405 | 44271.6427 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5528.6617 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0025 | 0.0147 | 0.0172 | 0.0163 | 0.0011 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 1-1-0-1-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
8341 | 102832.402 | 44271.6427 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5639.2349 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0031 | 0.0141 | 0.0172 | 0.0157 | 0.0011 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
8344 | 102835.531 | 44271.6427 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5752.0196 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0031 | 0.0138 | 0.0169 | 0.0152 | 0.0012 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
8347 | 102838.504 | 44271.6428 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5867.06 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0052 | 0.0123 | 0.0175 | 0.0152 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
8350 | 102841.485 | 44271.6428 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5984.4012 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0033 | 0.0131 | 0.0164 | 0.0149 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
8353 | 102844.882 | 44271.6428 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6104.0892 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0048 | 0.012 | 0.0168 | 0.0145 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
8356 | 102847.953 | 44271.6429 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6226.171 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0042 | 0.012 | 0.0162 | 0.0142 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
8359 | 102851.113 | 44271.6429 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6350.6944 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0033 | 0.0124 | 0.0157 | 0.0142 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8362 | 102854.395 | 44271.6429 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6477.7083 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0038 | 0.0119 | 0.0157 | 0.014 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8365 | 102857.464 | 44271.643 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6607.2625 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0049 | 0.011 | 0.0159 | 0.0135 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8368 | 102860.613 | 44271.643 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6739.4077 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0041 | 0.0119 | 0.016 | 0.0139 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8371 | 102863.771 | 44271.6431 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6874.1959 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0046 | 0.0113 | 0.0159 | 0.0138 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8374 | 102866.842 | 44271.6431 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7011.6798 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0054 | 0.0114 | 0.0168 | 0.0139 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
8377 | 102869.917 | 44271.6431 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7151.9134 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0052 | 0.0116 | 0.0168 | 0.0135 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
8380 | 102873.013 | 44271.6432 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7294.9517 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0042 | 0.0112 | 0.0154 | 0.0133 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8383 | 102876.002 | 44271.6432 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7440.8507 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0043 | 0.0108 | 0.0151 | 0.0132 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8386 | 102879.157 | 44271.6432 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7589.6677 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0045 | 0.0105 | 0.015 | 0.013 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8389 | 102882.13 | 44271.6433 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7741.4611 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0044 | 0.0102 | 0.0146 | 0.0129 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8392 | 102885.391 | 44271.6433 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7896.2903 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.0052 | 0.0108 | 0.016 | 0.0131 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8395 | 102888.431 | 44271.6433 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8054.2161 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0047 | 0.0102 | 0.0149 | 0.0126 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8398 | 102891.431 | 44271.6434 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8215.3004 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0045 | 0.0104 | 0.0149 | 0.0127 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8401 | 102894.815 | 44271.6434 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8379.6064 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0055 | 0.0103 | 0.0158 | 0.0127 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8404 | 102897.666 | 44271.6434 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8547.1986 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0043 | 0.0106 | 0.0149 | 0.013 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8407 | 102900.75 | 44271.6435 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8718.1425 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0046 | 0.0102 | 0.0148 | 0.0125 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8410 | 102903.851 | 44271.6435 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8892.5054 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0023 | 0.0101 | 0.0124 | 0.0113 | 0.0009 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8413 | 102906.924 | 44271.6436 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9070.3555 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.004 | 0.0102 | 0.0142 | 0.012 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8416 | 102910.435 | 44271.6436 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9251.7626 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0041 | 0.0102 | 0.0143 | 0.0116 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8419 | 102913.506 | 44271.6436 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9436.7978 | 0:240:120 | 0:00 | 0.003 | 7 | 0.0053 | 0.0096 | 0.0149 | 0.0118 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8422 | 102916.586 | 44271.6437 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9625.5338 | 0:240:120 | 0:00 | 0.0029 | 7 | 0.0036 | 0.0097 | 0.0133 | 0.0112 | 0.0013 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8425 | 102919.653 | 44271.6437 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9818.0445 | 0:240:120 | 0:00 | 0.0028 | 7 | 0.0052 | 0.0097 | 0.0149 | 0.0115 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8428 | 102922.61 | 44271.6437 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10014.4054 | 0:240:120 | 0:00 | 0.0027 | 7 | 0.0052 | 0.0097 | 0.0149 | 0.0115 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8431 | 102925.667 | 44271.6438 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10214.6935 | 0:240:120 | 0:00 | 0.0026 | 7 | 0.0038 | 0.01 | 0.0138 | 0.0113 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8434 | 102928.721 | 44271.6438 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10418.9873 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0037 | 0.0092 | 0.0129 | 0.0106 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8437 | 102931.78 | 44271.6438 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10419.5627 | 0:240:120 | 0:00 | 0.0025 | 7 | 0.0057 | 0.0093 | 0.015 | 0.0113 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
8440 | 102935.304 | 44271.6439 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10627.954 | 0:240:120 | 0:00 | 0.0024 | 7 | 0.003 | 0.0093 | 0.0123 | 0.0108 | 0.0012 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8443 | 102938.693 | 44271.6439 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10840.5131 | 0:240:120 | 0:00 | 0.0023 | 7 | 0.003 | 0.0095 | 0.0125 | 0.0108 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8446 | 102941.733 | 44271.644 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11057.3234 | 0:240:120 | 0:00 | 0.0022 | 7 | 0.0049 | 0.0091 | 0.014 | 0.0111 | 0.0016 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8449 | 102944.706 | 44271.644 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11278.4698 | 0:240:120 | 0:00 | 0.0021 | 7 | 0.0028 | 0.0096 | 0.0124 | 0.0104 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8452 | 102947.663 | 44271.644 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11504.0392 | 0:240:120 | 0:00 | 0.002 | 7 | 0.003 | 0.0093 | 0.0123 | 0.0105 | 0.001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8455 | 102950.943 | 44271.6441 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11734.12 | 0:240:120 | 0:00 | 0.002 | 7 | 0.0027 | 0.0096 | 0.0123 | 0.0108 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8458 | 102954.033 | 44271.6441 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11968.8024 | 0:240:120 | 0:00 | 0.0019 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.0106 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8461 | 103316.534 | 44271.6483 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.9 | 0:240:120 | 0:00 | 39.7168 | 7 | 69.8798 | 293.2257 | 363.1055 | 321.4339 | 30.4872 | 929.4721 | 3 | 39.7168 | 163.1623 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
8464 | 104288.844 | 44271.6596 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 168.2 | 0:240:120 | 0:00 | 34.2099 | 7 | 59.926 | 183.2881 | 243.2141 | 203.2662 | 29.9589 | 897.5382 | 3 | 34.2099 | 106.2497 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
8467 | 104897.963 | 44271.6666 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 171.6 | 0:240:120 | 0:00 | 29.8587 | 7 | 58.6905 | 62.7166 | 121.4071 | 82.3215 | 28.8389 | 831.6825 | 3 | 29.8587 | 77.747 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
8470 | 105200.968 | 44271.6701 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175 | 0:240:120 | 0:00 | 26.4298 | 7 | 3.7342 | 53.4952 | 57.2294 | 55.7383 | 1.7015 | 2.895 | 3 | 26.4298 | 61.0437 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8473 | 105368.4 | 44271.672 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 178.5 | 0:240:120 | 0:00 | 23.586 | 7 | 3.3188 | 46.8547 | 50.1735 | 47.9655 | 1.6558 | 2.7415 | 3 | 23.586 | 49.8086 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
8476 | 105515.154 | 44271.6737 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 182.1 | 0:240:120 | 0:00 | 21.1934 | 7 | 3.322 | 40.2217 | 43.5437 | 41.3306 | 1.6585 | 2.7505 | 3 | 21.1934 | 41.7469 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
8479 | 105639.655 | 44271.6752 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 185.8 | 0:240:120 | 0:00 | 19.1558 | 7 | 4.1572 | 30.5435 | 34.7007 | 32.9042 | 1.814 | 3.2907 | 3 | 19.1558 | 35.6897 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8482 | 105741.331 | 44271.6764 | Vista Speed | T | 65T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 189.5 | 0:240:120 | 0:00 | 17.4449 | 7 | 1.1029 | 28.082 | 29.1849 | 28.4506 | 0.5495 | 0.302 | 3 | 17.4449 | 31.0883 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8485 | 106486.175 | 44271.685 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.04 | 0:240:120 | 0:00 | 65.2662 | 7 | 61.6617 | 620.3593 | 682.021 | 640.9146 | 30.8286 | 950.4031 | 3 | 65.2662 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8488 | 108412.031 | 44271.7073 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 197.9208 | 0:240:120 | 0:00 | 52.9422 | 7 | 61.6781 | 497.037 | 558.7151 | 517.5976 | 30.8372 | 950.9309 | 3 | 52.9422 | 695.8708 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8491 | 109967.881 | 44271.7253 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 201.8792 | 0:240:120 | 0:00 | 44.2493 | 7 | 61.6503 | 373.6414 | 435.2917 | 394.194 | 30.8207 | 949.9181 | 3 | 44.2493 | 225.0863 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
8494 | 111153.388 | 44271.739 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 205.9168 | 0:240:120 | 0:00 | 37.7931 | 7 | 61.6584 | 250.291 | 311.9494 | 270.8458 | 30.8259 | 950.2356 | 3 | 37.7931 | 132.1028 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
8497 | 111968.893 | 44271.7484 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 210.0351 | 0:240:120 | 0:00 | 32.8122 | 7 | 61.5755 | 126.9387 | 188.5142 | 147.4584 | 30.7697 | 946.7768 | 3 | 32.8122 | 92.3931 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
8500 | 112411 | 44271.7536 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 214.2358 | 0:240:120 | 0:00 | 28.8555 | 7 | 0.533 | 61.6227 | 62.1557 | 61.9064 | 0.176 | 0.031 | 3 | 28.8555 | 70.3818 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8503 | 112593.225 | 44271.7557 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 218.5206 | 0:240:120 | 0:00 | 25.639 | 7 | 3.4134 | 51.6297 | 55.0431 | 53.7447 | 1.6003 | 2.5611 | 3 | 25.639 | 56.402 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8506 | 112754.55 | 44271.7575 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 222.891 | 0:240:120 | 0:00 | 22.9745 | 7 | 3.4173 | 44.8012 | 48.2185 | 45.9426 | 1.7056 | 2.9089 | 3 | 22.9745 | 46.7425 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
8509 | 112895.212 | 44271.7592 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 227.3488 | 0:240:120 | 0:00 | 20.7329 | 7 | 3.4102 | 37.9793 | 41.3895 | 39.1168 | 1.7013 | 2.8943 | 3 | 20.7329 | 39.6735 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
8512 | 113012.039 | 44271.7605 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 231.8958 | 0:240:120 | 0:00 | 18.8222 | 7 | 1.1272 | 30.0313 | 31.1585 | 30.7795 | 0.558 | 0.3114 | 3 | 18.8222 | 34.2798 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8515 | 113106.264 | 44271.7616 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 236.5337 | 0:240:120 | 0:00 | 17.1754 | 7 | 1.1343 | 27.7692 | 28.9035 | 28.1482 | 0.565 | 0.3192 | 3 | 17.1754 | 30.032 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8518 | 113192.529 | 44271.7626 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 241.2644 | 0:240:120 | 0:00 | 15.7424 | 7 | 0.7068 | 24.8207 | 25.5275 | 25.3982 | 0.2316 | 0.0536 | 3 | 15.7424 | 26.6023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8521 | 113270.175 | 44271.7635 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.0896 | 0:240:120 | 0:00 | 14.4851 | 7 | 1.1322 | 22.1257 | 23.2579 | 22.5039 | 0.5646 | 0.3187 | 3 | 14.4851 | 23.7772 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8524 | 113339.477 | 44271.7643 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 251.0114 | 0:240:120 | 0:00 | 13.3738 | 7 | 0.4678 | 19.4044 | 19.8722 | 19.7249 | 0.2178 | 0.0474 | 3 | 13.3738 | 21.4116 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8527 | 113400.975 | 44271.765 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.0317 | 0:240:120 | 0:00 | 12.3852 | 7 | 0.5629 | 18.1911 | 18.754 | 18.3796 | 0.28 | 0.0784 | 3 | 12.3852 | 19.4031 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8530 | 113458.609 | 44271.7657 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 261.1523 | 0:240:120 | 0:00 | 11.5007 | 7 | 0.5605 | 16.5169 | 17.0774 | 16.7333 | 0.2614 | 0.0683 | 3 | 11.5007 | 17.6778 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8533 | 113511.146 | 44271.7663 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 266.3753 | 0:240:120 | 0:00 | 10.7053 | 7 | 0.5569 | 14.8453 | 15.4022 | 15.2286 | 0.2583 | 0.0667 | 3 | 10.7053 | 16.181 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8536 | 113559.065 | 44271.7668 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 271.7028 | 0:240:120 | 0:00 | 9.9867 | 7 | 0.2083 | 13.9492 | 14.1575 | 14.0134 | 0.0949 | 0.009 | 3 | 9.9867 | 14.8709 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8539 | 113603.606 | 44271.7674 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 277.1369 | 0:240:120 | 0:00 | 9.3348 | 7 | 0.335 | 12.9556 | 13.2906 | 13.0683 | 0.1659 | 0.0275 | 3 | 9.3348 | 13.7156 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8542 | 113645.434 | 44271.7678 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 282.6796 | 0:240:120 | 0:00 | 8.7411 | 7 | 0.3343 | 11.9611 | 12.2954 | 12.0736 | 0.166 | 0.0276 | 3 | 8.7411 | 12.6899 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8545 | 113684.248 | 44271.7683 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 288.3332 | 0:240:120 | 0:00 | 8.1986 | 7 | 0.3342 | 10.9684 | 11.3026 | 11.0812 | 0.1657 | 0.0275 | 3 | 8.1986 | 11.7738 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8548 | 113720.447 | 44271.7687 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.0999 | 0:240:120 | 0:00 | 7.7014 | 7 | 0.2201 | 10.3144 | 10.5345 | 10.3889 | 0.1085 | 0.0118 | 3 | 7.7014 | 10.9513 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8551 | 113754.416 | 44271.7691 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 299.9819 | 0:240:120 | 0:00 | 7.2443 | 7 | 0.2204 | 9.6606 | 9.881 | 9.7351 | 0.109 | 0.0119 | 3 | 7.2443 | 10.2093 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8554 | 113786.406 | 44271.7695 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 305.9815 | 0:240:120 | 0:00 | 6.8229 | 7 | 0.2202 | 9.0057 | 9.2259 | 9.0803 | 0.1089 | 0.0119 | 3 | 6.8229 | 9.537 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8557 | 113816.546 | 44271.7698 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 312.1012 | 0:240:120 | 0:00 | 6.4336 | 7 | 0.1425 | 8.4825 | 8.625 | 8.5291 | 0.0688 | 0.0047 | 3 | 6.4336 | 8.9255 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8560 | 113844.964 | 44271.7702 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 318.3432 | 0:240:120 | 0:00 | 6.0731 | 7 | 0.1592 | 7.8692 | 8.0284 | 7.9717 | 0.0763 | 0.0058 | 3 | 6.0731 | 8.3673 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8563 | 113871.627 | 44271.7705 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 324.7101 | 0:240:120 | 0:00 | 5.7385 | 7 | 0.1541 | 7.4104 | 7.5645 | 7.4969 | 0.0684 | 0.0047 | 3 | 5.7385 | 7.8562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8566 | 113896.711 | 44271.7708 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 331.2043 | 0:240:120 | 0:00 | 5.4275 | 7 | 0.1155 | 7.0271 | 7.1426 | 7.0663 | 0.0569 | 0.0032 | 3 | 5.4275 | 7.3867 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8569 | 113920.592 | 44271.771 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 337.8283 | 0:240:120 | 0:00 | 5.1377 | 7 | 0.1138 | 6.5759 | 6.6897 | 6.6514 | 0.0562 | 0.0032 | 3 | 5.1377 | 6.9543 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8572 | 113943.403 | 44271.7713 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 344.5849 | 0:240:120 | 0:00 | 4.8673 | 7 | 0.1194 | 6.231 | 6.3504 | 6.2726 | 0.0579 | 0.0034 | 3 | 4.8673 | 6.5551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8575 | 113965.009 | 44271.7715 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 351.4766 | 0:240:120 | 0:00 | 4.6147 | 7 | 0.087 | 5.8621 | 5.9491 | 5.9197 | 0.0427 | 0.0018 | 3 | 4.6147 | 6.1857 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8578 | 113985.507 | 44271.7718 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 358.5061 | 0:240:120 | 0:00 | 4.3783 | 7 | 0.1725 | 5.5151 | 5.6876 | 5.6011 | 0.0742 | 0.0055 | 3 | 4.3783 | 5.8431 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8581 | 114005.037 | 44271.772 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 365.6763 | 0:240:120 | 0:00 | 4.1567 | 7 | 0.1109 | 5.2302 | 5.3411 | 5.2789 | 0.0473 | 0.0022 | 3 | 4.1567 | 5.5247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8584 | 114024.047 | 44271.7722 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 372.9898 | 0:240:120 | 0:00 | 3.9488 | 7 | 0.0691 | 4.9818 | 5.0509 | 5.025 | 0.0323 | 0.001 | 3 | 3.9488 | 5.2284 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8587 | 114041.954 | 44271.7724 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 380.4496 | 0:240:120 | 0:00 | 3.7535 | 7 | 0.0682 | 4.7093 | 4.7775 | 4.7536 | 0.0331 | 0.0011 | 3 | 3.7535 | 4.952 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8590 | 114059.188 | 44271.7726 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 388.0586 | 0:240:120 | 0:00 | 3.5697 | 7 | 0.0551 | 4.4619 | 4.517 | 4.4978 | 0.0267 | 0.0007 | 3 | 3.5697 | 4.6939 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8593 | 114075.764 | 44271.7728 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 395.8197 | 0:240:120 | 0:00 | 3.3968 | 7 | 0.0564 | 4.2414 | 4.2978 | 4.2784 | 0.0272 | 0.0007 | 3 | 3.3968 | 4.4524 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8596 | 114091.363 | 44271.773 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 403.7361 | 0:240:120 | 0:00 | 3.2337 | 7 | 0.0582 | 4.0183 | 4.0765 | 4.057 | 0.0279 | 0.0008 | 3 | 3.2337 | 4.2262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8599 | 114106.533 | 44271.7732 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 411.8109 | 0:240:120 | 0:00 | 3.08 | 7 | 0.0901 | 3.7966 | 3.8867 | 3.848 | 0.0386 | 0.0015 | 3 | 3.08 | 4.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8602 | 114120.908 | 44271.7733 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 420.0471 | 0:240:120 | 0:00 | 2.9348 | 7 | 0.0892 | 3.6169 | 3.7061 | 3.6609 | 0.0383 | 0.0015 | 3 | 2.9348 | 3.8148 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8605 | 114134.775 | 44271.7735 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 428.448 | 0:240:120 | 0:00 | 2.7975 | 7 | 0.0625 | 3.4597 | 3.5222 | 3.492 | 0.0258 | 0.0007 | 3 | 2.7975 | 3.6274 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8608 | 114148.103 | 44271.7737 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 437.017 | 0:240:120 | 0:00 | 2.6678 | 7 | 0.0756 | 3.2723 | 3.3479 | 3.3096 | 0.0323 | 0.001 | 3 | 2.6678 | 3.4511 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8611 | 114160.975 | 44271.7738 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 445.7573 | 0:240:120 | 0:00 | 2.5449 | 7 | 0.0673 | 3.1277 | 3.195 | 3.1628 | 0.0266 | 0.0007 | 3 | 2.5449 | 3.285 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8614 | 114173.382 | 44271.774 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 454.6725 | 0:240:120 | 0:00 | 2.4286 | 7 | 0.0634 | 2.9763 | 3.0397 | 3.0078 | 0.0269 | 0.0007 | 3 | 2.4286 | 3.1283 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8617 | 114185.207 | 44271.7741 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 463.7659 | 0:240:120 | 0:00 | 2.3183 | 7 | 0.0528 | 2.8283 | 2.8811 | 2.8596 | 0.0238 | 0.0006 | 3 | 2.3183 | 2.9804 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8620 | 114196.865 | 44271.7742 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 473.0412 | 0:240:120 | 0:00 | 2.2138 | 7 | 0.0665 | 2.6941 | 2.7606 | 2.7325 | 0.0288 | 0.0008 | 3 | 2.2138 | 2.8407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8623 | 114207.948 | 44271.7744 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 482.5021 | 0:240:120 | 0:00 | 2.1145 | 7 | 0.0699 | 2.5683 | 2.6382 | 2.6058 | 0.0304 | 0.0009 | 3 | 2.1145 | 2.7086 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8626 | 114219.199 | 44271.7745 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 492.1521 | 0:240:120 | 0:00 | 2.0203 | 7 | 0.0709 | 2.451 | 2.5219 | 2.4892 | 0.0304 | 0.0009 | 3 | 2.0203 | 2.5836 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8629 | 114229.76 | 44271.7746 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 501.9951 | 0:240:120 | 0:00 | 1.9308 | 7 | 0.0612 | 2.3411 | 2.4023 | 2.3741 | 0.0261 | 0.0007 | 3 | 1.9308 | 2.4652 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8632 | 114240.328 | 44271.7747 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 512.035 | 0:240:120 | 0:00 | 1.8458 | 7 | 0.0407 | 2.2417 | 2.2824 | 2.2659 | 0.0182 | 0.0003 | 3 | 1.8458 | 2.353 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8635 | 114250.285 | 44271.7748 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 522.2757 | 0:240:120 | 0:00 | 1.7649 | 7 | 0.0533 | 2.1299 | 2.1832 | 2.1586 | 0.0217 | 0.0005 | 3 | 1.7649 | 2.2467 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8638 | 114259.778 | 44271.775 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 532.7213 | 0:240:120 | 0:00 | 1.6879 | 7 | 0.0536 | 2.0404 | 2.094 | 2.0697 | 0.0229 | 0.0005 | 3 | 1.6879 | 2.1458 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8641 | 114268.931 | 44271.7751 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 543.3757 | 0:240:120 | 0:00 | 1.6146 | 7 | 0.0476 | 1.9448 | 1.9924 | 1.9707 | 0.0194 | 0.0004 | 3 | 1.6146 | 2.05 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8644 | 114277.76 | 44271.7752 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 554.2432 | 0:240:120 | 0:00 | 1.5449 | 7 | 0.0433 | 1.8665 | 1.9098 | 1.8906 | 0.0184 | 0.0003 | 3 | 1.5449 | 1.959 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8647 | 114286.575 | 44271.7753 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 565.3281 | 0:240:120 | 0:00 | 1.4784 | 7 | 0.0416 | 1.7839 | 1.8255 | 1.806 | 0.0179 | 0.0003 | 3 | 1.4784 | 1.8726 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8650 | 114295.223 | 44271.7754 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 576.6346 | 0:240:120 | 0:00 | 1.4151 | 7 | 0.0406 | 1.7036 | 1.7442 | 1.7248 | 0.0173 | 0.0003 | 3 | 1.4151 | 1.7903 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8653 | 114303.457 | 44271.7755 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 588.1673 | 0:240:120 | 0:00 | 1.3547 | 7 | 0.0365 | 1.6304 | 1.6669 | 1.6501 | 0.0156 | 0.0002 | 3 | 1.3547 | 1.7121 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8656 | 114311.177 | 44271.7756 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 599.9307 | 0:240:120 | 0:00 | 1.2971 | 7 | 0.0329 | 1.5615 | 1.5944 | 1.5794 | 0.0139 | 0.0002 | 3 | 1.2971 | 1.6377 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8659 | 114318.899 | 44271.7756 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 611.9293 | 0:240:120 | 0:00 | 1.2422 | 7 | 0.0441 | 1.4853 | 1.5294 | 1.5109 | 0.0182 | 0.0003 | 3 | 1.2422 | 1.5668 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8662 | 114326.397 | 44271.7757 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 624.1679 | 0:240:120 | 0:00 | 1.1897 | 7 | 0.0292 | 1.4269 | 1.4561 | 1.4427 | 0.0126 | 0.0002 | 3 | 1.1897 | 1.4993 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8665 | 114333.53 | 44271.7758 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 636.6512 | 0:240:120 | 0:00 | 1.1397 | 7 | 0.0292 | 1.3685 | 1.3977 | 1.3843 | 0.0123 | 0.0002 | 3 | 1.1397 | 1.435 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8668 | 114340.603 | 44271.7759 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 649.3842 | 0:240:120 | 0:00 | 1.0919 | 7 | 0.0286 | 1.3095 | 1.3381 | 1.3234 | 0.0115 | 0.0001 | 3 | 1.0919 | 1.3737 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8671 | 114347.309 | 44271.776 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 662.3719 | 0:240:120 | 0:00 | 1.0463 | 7 | 0.0314 | 1.2517 | 1.2831 | 1.2666 | 0.0128 | 0.0002 | 3 | 1.0463 | 1.3153 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8674 | 114354.33 | 44271.776 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 675.6194 | 0:240:120 | 0:00 | 1.0027 | 7 | 0.0293 | 1.1988 | 1.2281 | 1.2138 | 0.0124 | 0.0002 | 3 | 1.0027 | 1.2595 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8677 | 114360.822 | 44271.7761 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 689.1317 | 0:240:120 | 0:00 | 0.961 | 7 | 0.0285 | 1.1477 | 1.1762 | 1.1625 | 0.0121 | 0.0001 | 3 | 0.961 | 1.2063 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8680 | 114367.291 | 44271.7762 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 702.9144 | 0:240:120 | 0:00 | 0.9212 | 7 | 0.025 | 1.1013 | 1.1263 | 1.1137 | 0.0105 | 0.0001 | 3 | 0.9212 | 1.1555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8683 | 114373.645 | 44271.7763 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 716.9727 | 0:240:120 | 0:00 | 0.8831 | 7 | 0.019 | 1.0564 | 1.0754 | 1.0669 | 0.0079 | 0.0001 | 3 | 0.8831 | 1.107 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8686 | 114379.958 | 44271.7763 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 731.3121 | 0:240:120 | 0:00 | 0.8467 | 7 | 0.0229 | 1.0105 | 1.0334 | 1.022 | 0.0098 | 0.0001 | 3 | 0.8467 | 1.0607 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8689 | 114386.197 | 44271.7764 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 745.9384 | 0:240:120 | 0:00 | 0.8119 | 7 | 0.0202 | 0.9698 | 0.99 | 0.9806 | 0.0077 | 0.0001 | 3 | 0.8119 | 1.0164 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8692 | 114392.06 | 44271.7765 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 760.8571 | 0:240:120 | 0:00 | 0.7786 | 7 | 0.0195 | 0.9318 | 0.9513 | 0.9407 | 0.0078 | 0.0001 | 3 | 0.7786 | 0.9742 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8695 | 114397.887 | 44271.7766 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 776.0743 | 0:240:120 | 0:00 | 0.7467 | 7 | 0.0193 | 0.8924 | 0.9117 | 0.9013 | 0.0082 | 0.0001 | 3 | 0.7467 | 0.9338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8698 | 114403.617 | 44271.7766 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 791.5958 | 0:240:120 | 0:00 | 0.7162 | 7 | 0.0188 | 0.8546 | 0.8734 | 0.8637 | 0.0073 | 0.0001 | 3 | 0.7162 | 0.8951 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8701 | 114409.116 | 44271.7767 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 807.4277 | 0:240:120 | 0:00 | 0.687 | 7 | 0.0182 | 0.8177 | 0.8359 | 0.8275 | 0.0075 | 0.0001 | 3 | 0.687 | 0.8582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8704 | 114414.539 | 44271.7767 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 823.5762 | 0:240:120 | 0:00 | 0.659 | 7 | 0.0166 | 0.7852 | 0.8018 | 0.7937 | 0.0066 | 0 | 3 | 0.659 | 0.8229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8707 | 114419.877 | 44271.7768 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 840.0478 | 0:240:120 | 0:00 | 0.6322 | 7 | 0.0182 | 0.7526 | 0.7708 | 0.7616 | 0.0077 | 0.0001 | 3 | 0.6322 | 0.7891 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8710 | 114425.088 | 44271.7769 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 856.8487 | 0:240:120 | 0:00 | 0.6066 | 7 | 0.0164 | 0.7224 | 0.7388 | 0.7308 | 0.0064 | 0 | 3 | 0.6066 | 0.7567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8713 | 114430.219 | 44271.7769 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 873.9857 | 0:240:120 | 0:00 | 0.582 | 7 | 0.0141 | 0.6931 | 0.7072 | 0.7001 | 0.0057 | 0 | 3 | 0.582 | 0.7258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8716 | 114435.365 | 44271.777 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 891.4654 | 0:240:120 | 0:00 | 0.5585 | 7 | 0.0142 | 0.6646 | 0.6788 | 0.6716 | 0.0054 | 0 | 3 | 0.5585 | 0.6962 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8719 | 114440.182 | 44271.777 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 909.2947 | 0:240:120 | 0:00 | 0.536 | 7 | 0.0141 | 0.6369 | 0.651 | 0.6445 | 0.0057 | 0 | 3 | 0.536 | 0.6678 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8722 | 114445.045 | 44271.7771 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 927.4806 | 0:240:120 | 0:00 | 0.5144 | 7 | 0.0098 | 0.6138 | 0.6236 | 0.619 | 0.0041 | 0 | 3 | 0.5144 | 0.6407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8725 | 114449.926 | 44271.7772 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 946.0302 | 0:240:120 | 0:00 | 0.4937 | 7 | 0.0139 | 0.5867 | 0.6006 | 0.5935 | 0.0057 | 0 | 3 | 0.4937 | 0.6147 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8728 | 114454.552 | 44271.7772 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 964.9508 | 0:240:120 | 0:00 | 0.4739 | 7 | 0.0122 | 0.5633 | 0.5755 | 0.5691 | 0.005 | 0 | 3 | 0.4739 | 0.5898 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8731 | 114459.235 | 44271.7773 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 984.2498 | 0:240:120 | 0:00 | 0.4549 | 7 | 0.0102 | 0.5412 | 0.5514 | 0.5462 | 0.0042 | 0 | 3 | 0.4549 | 0.566 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8734 | 114463.832 | 44271.7773 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1003.9348 | 0:240:120 | 0:00 | 0.4366 | 7 | 0.0117 | 0.5194 | 0.5311 | 0.5248 | 0.0043 | 0 | 3 | 0.4366 | 0.5431 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8737 | 114468.629 | 44271.7774 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1024.0135 | 0:240:120 | 0:00 | 0.4192 | 7 | 0.0103 | 0.4982 | 0.5085 | 0.5036 | 0.004 | 0 | 3 | 0.4192 | 0.5212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8740 | 114472.863 | 44271.7774 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1044.4938 | 0:240:120 | 0:00 | 0.4024 | 7 | 0.0089 | 0.4793 | 0.4882 | 0.4836 | 0.0036 | 0 | 3 | 0.4024 | 0.5002 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8743 | 114477.421 | 44271.7775 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1065.3837 | 0:240:120 | 0:00 | 0.3863 | 7 | 0.0092 | 0.46 | 0.4692 | 0.4642 | 0.0037 | 0 | 3 | 0.3863 | 0.4801 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8746 | 114481.796 | 44271.7775 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1086.6913 | 0:240:120 | 0:00 | 0.3709 | 7 | 0.0077 | 0.4414 | 0.4491 | 0.4451 | 0.0031 | 0 | 3 | 0.3709 | 0.4609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8749 | 114486.179 | 44271.7776 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1108.4252 | 0:240:120 | 0:00 | 0.3562 | 7 | 0.0092 | 0.423 | 0.4322 | 0.4276 | 0.0038 | 0 | 3 | 0.3562 | 0.4424 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8752 | 114490.519 | 44271.7776 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1130.5937 | 0:240:120 | 0:00 | 0.342 | 7 | 0.0097 | 0.4054 | 0.4151 | 0.4102 | 0.0039 | 0 | 3 | 0.342 | 0.4247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8755 | 114494.888 | 44271.7777 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1153.2056 | 0:240:120 | 0:00 | 0.3284 | 7 | 0.0088 | 0.3908 | 0.3996 | 0.3949 | 0.0035 | 0 | 3 | 0.3284 | 0.4077 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8758 | 114499.435 | 44271.7777 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1176.2697 | 0:240:120 | 0:00 | 0.3153 | 7 | 0.0091 | 0.3746 | 0.3837 | 0.3789 | 0.0036 | 0 | 3 | 0.3153 | 0.3914 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8761 | 114503.461 | 44271.7778 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1199.7951 | 0:240:120 | 0:00 | 0.3028 | 7 | 0.0075 | 0.3592 | 0.3667 | 0.3632 | 0.0031 | 0 | 3 | 0.3028 | 0.3758 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8764 | 114507.593 | 44271.7778 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1223.791 | 0:240:120 | 0:00 | 0.2908 | 7 | 0.0104 | 0.3417 | 0.3521 | 0.3479 | 0.0034 | 0 | 3 | 0.2908 | 0.3608 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8767 | 114511.633 | 44271.7779 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1248.2668 | 0:240:120 | 0:00 | 0.2793 | 7 | 0.0085 | 0.3314 | 0.3399 | 0.3349 | 0.003 | 0 | 3 | 0.2793 | 0.3465 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8770 | 114515.764 | 44271.7779 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1273.2321 | 0:240:120 | 0:00 | 0.2682 | 7 | 0.0085 | 0.3159 | 0.3244 | 0.32 | 0.0029 | 0 | 3 | 0.2682 | 0.3327 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8773 | 114519.77 | 44271.778 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1298.6968 | 0:240:120 | 0:00 | 0.2576 | 7 | 0.0076 | 0.3043 | 0.3119 | 0.3078 | 0.0026 | 0 | 3 | 0.2576 | 0.3195 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8776 | 114523.674 | 44271.778 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1324.6707 | 0:240:120 | 0:00 | 0.2474 | 7 | 0.0056 | 0.2917 | 0.2973 | 0.2949 | 0.0018 | 0 | 3 | 0.2474 | 0.3068 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8779 | 114527.629 | 44271.7781 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1351.1641 | 0:240:120 | 0:00 | 0.2377 | 7 | 0.0115 | 0.2789 | 0.2904 | 0.2852 | 0.0038 | 0 | 3 | 0.2377 | 0.2946 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8782 | 114531.439 | 44271.7781 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1378.1874 | 0:240:120 | 0:00 | 0.2283 | 7 | 0.0103 | 0.2674 | 0.2777 | 0.2726 | 0.0031 | 0 | 3 | 0.2283 | 0.2829 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8785 | 114535.51 | 44271.7781 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1405.7511 | 0:240:120 | 0:00 | 0.2193 | 7 | 0.0083 | 0.2579 | 0.2662 | 0.2611 | 0.0027 | 0 | 3 | 0.2193 | 0.2717 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8788 | 114539.343 | 44271.7782 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1433.8662 | 0:240:120 | 0:00 | 0.2106 | 7 | 0.0089 | 0.2463 | 0.2552 | 0.2511 | 0.0031 | 0 | 3 | 0.2106 | 0.261 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8791 | 114543.063 | 44271.7782 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1462.5435 | 0:240:120 | 0:00 | 0.2023 | 7 | 0.0064 | 0.2381 | 0.2445 | 0.2416 | 0.0019 | 0 | 3 | 0.2023 | 0.2507 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8794 | 114546.913 | 44271.7783 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1491.7943 | 0:240:120 | 0:00 | 0.1944 | 7 | 0.0065 | 0.2289 | 0.2354 | 0.2318 | 0.0018 | 0 | 3 | 0.1944 | 0.2407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8797 | 114550.598 | 44271.7783 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1521.6302 | 0:240:120 | 0:00 | 0.1867 | 7 | 0.0063 | 0.2192 | 0.2255 | 0.2224 | 0.0021 | 0 | 3 | 0.1867 | 0.2312 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8800 | 114554.323 | 44271.7784 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1552.0628 | 0:240:120 | 0:00 | 0.1794 | 7 | 0.0062 | 0.2111 | 0.2173 | 0.2142 | 0.0019 | 0 | 3 | 0.1794 | 0.2221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8803 | 114557.973 | 44271.7784 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1583.1041 | 0:240:120 | 0:00 | 0.1723 | 7 | 0.0055 | 0.2029 | 0.2084 | 0.2057 | 0.0022 | 0 | 3 | 0.1723 | 0.2134 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8806 | 114561.622 | 44271.7784 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1614.7662 | 0:240:120 | 0:00 | 0.1655 | 7 | 0.0044 | 0.1959 | 0.2003 | 0.1977 | 0.0018 | 0 | 3 | 0.1655 | 0.2049 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8809 | 114565.006 | 44271.7785 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1647.0615 | 0:240:120 | 0:00 | 0.159 | 7 | 0.0038 | 0.1885 | 0.1923 | 0.1896 | 0.0014 | 0 | 3 | 0.159 | 0.1969 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8812 | 114568.544 | 44271.7785 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1680.0027 | 0:240:120 | 0:00 | 0.1528 | 7 | 0.0063 | 0.1809 | 0.1872 | 0.1832 | 0.0021 | 0 | 3 | 0.1528 | 0.1891 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8815 | 114571.975 | 44271.7786 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1713.6028 | 0:240:120 | 0:00 | 0.1468 | 7 | 0.0054 | 0.173 | 0.1784 | 0.1755 | 0.0022 | 0 | 3 | 0.1468 | 0.1817 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8818 | 114575.751 | 44271.7786 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1747.8748 | 0:240:120 | 0:00 | 0.141 | 7 | 0.0037 | 0.1673 | 0.171 | 0.169 | 0.0011 | 0 | 3 | 0.141 | 0.1745 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8821 | 114579.344 | 44271.7787 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1782.8323 | 0:240:120 | 0:00 | 0.1355 | 7 | 0.0038 | 0.1601 | 0.1639 | 0.1618 | 0.0013 | 0 | 3 | 0.1355 | 0.1677 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8824 | 114582.634 | 44271.7787 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1818.489 | 0:240:120 | 0:00 | 0.1302 | 7 | 0.0062 | 0.1529 | 0.1591 | 0.1558 | 0.002 | 0 | 3 | 0.1302 | 0.1611 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8827 | 114586.053 | 44271.7787 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1854.8588 | 0:240:120 | 0:00 | 0.1251 | 7 | 0.0053 | 0.1473 | 0.1526 | 0.1493 | 0.0017 | 0 | 3 | 0.1251 | 0.1548 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8830 | 114589.445 | 44271.7788 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1891.9559 | 0:240:120 | 0:00 | 0.1202 | 7 | 0.0037 | 0.1424 | 0.1461 | 0.1437 | 0.0015 | 0 | 3 | 0.1202 | 0.1487 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8833 | 114593.214 | 44271.7788 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1929.7951 | 0:240:120 | 0:00 | 0.1155 | 7 | 0.0038 | 0.136 | 0.1398 | 0.1383 | 0.0012 | 0 | 3 | 0.1155 | 0.1429 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8836 | 114596.597 | 44271.7789 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1968.391 | 0:240:120 | 0:00 | 0.111 | 7 | 0.004 | 0.1308 | 0.1348 | 0.1327 | 0.0014 | 0 | 3 | 0.111 | 0.1373 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8839 | 114599.896 | 44271.7789 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2007.7588 | 0:240:120 | 0:00 | 0.1066 | 7 | 0.004 | 0.1246 | 0.1286 | 0.1273 | 0.0012 | 0 | 3 | 0.1066 | 0.1319 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8842 | 114603.25 | 44271.7789 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2047.914 | 0:240:120 | 0:00 | 0.1025 | 7 | 0.0029 | 0.1217 | 0.1246 | 0.1227 | 0.0011 | 0 | 3 | 0.1025 | 0.1267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8845 | 114606.776 | 44271.779 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2088.8722 | 0:240:120 | 0:00 | 0.0984 | 7 | 0.0048 | 0.1163 | 0.1211 | 0.1184 | 0.0016 | 0 | 3 | 0.0984 | 0.1217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8848 | 114610.092 | 44271.779 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2130.6497 | 0:240:120 | 0:00 | 0.0946 | 7 | 0.0037 | 0.1118 | 0.1155 | 0.1132 | 0.0014 | 0 | 3 | 0.0946 | 0.117 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8851 | 114613.393 | 44271.779 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2173.2627 | 0:240:120 | 0:00 | 0.0909 | 7 | 0.0029 | 0.107 | 0.1099 | 0.1085 | 0.001 | 0 | 3 | 0.0909 | 0.1124 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8854 | 114616.721 | 44271.7791 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2216.7279 | 0:240:120 | 0:00 | 0.0873 | 7 | 0.0028 | 0.1031 | 0.1059 | 0.1045 | 0.0011 | 0 | 3 | 0.0873 | 0.108 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8857 | 114620.046 | 44271.7791 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2261.0625 | 0:240:120 | 0:00 | 0.0839 | 7 | 0.0039 | 0.099 | 0.1029 | 0.1005 | 0.0015 | 0 | 3 | 0.0839 | 0.1038 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8860 | 114623.664 | 44271.7792 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2306.2837 | 0:240:120 | 0:00 | 0.0807 | 7 | 0.0013 | 0.0961 | 0.0974 | 0.0968 | 0.0006 | 0 | 3 | 0.0807 | 0.0997 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8863 | 114626.977 | 44271.7792 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2352.4094 | 0:240:120 | 0:00 | 0.0775 | 7 | 0.0027 | 0.0911 | 0.0938 | 0.0927 | 0.0011 | 0 | 3 | 0.0775 | 0.0958 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8866 | 114630.229 | 44271.7792 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2399.4576 | 0:240:120 | 0:00 | 0.0745 | 7 | 0.0031 | 0.0878 | 0.0909 | 0.0893 | 0.001 | 0 | 3 | 0.0745 | 0.0921 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8869 | 114633.634 | 44271.7793 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2447.4468 | 0:240:120 | 0:00 | 0.0716 | 7 | 0.0041 | 0.0844 | 0.0885 | 0.0862 | 0.0014 | 0 | 3 | 0.0716 | 0.0885 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
8872 | 114636.917 | 44271.7793 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2496.3957 | 0:240:120 | 0:00 | 0.0688 | 7 | 0.0025 | 0.0813 | 0.0838 | 0.0827 | 0.0009 | 0 | 3 | 0.0688 | 0.085 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8875 | 114640.226 | 44271.7794 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2546.3236 | 0:240:120 | 0:00 | 0.0661 | 7 | 0.0042 | 0.0771 | 0.0813 | 0.0793 | 0.0013 | 0 | 3 | 0.0661 | 0.0817 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8878 | 114643.502 | 44271.7794 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2597.2501 | 0:240:120 | 0:00 | 0.0635 | 7 | 0.0028 | 0.0749 | 0.0777 | 0.0766 | 0.0009 | 0 | 3 | 0.0635 | 0.0785 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8881 | 114646.829 | 44271.7794 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2649.1951 | 0:240:120 | 0:00 | 0.061 | 7 | 0.0025 | 0.0719 | 0.0744 | 0.0732 | 0.0009 | 0 | 3 | 0.061 | 0.0754 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8884 | 114650.263 | 44271.7795 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2702.179 | 0:240:120 | 0:00 | 0.0587 | 7 | 0.0032 | 0.0689 | 0.0721 | 0.0704 | 0.0013 | 0 | 3 | 0.0587 | 0.0725 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8887 | 114653.414 | 44271.7795 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2756.2226 | 0:240:120 | 0:00 | 0.0564 | 7 | 0.0034 | 0.0659 | 0.0693 | 0.0676 | 0.0012 | 0 | 3 | 0.0564 | 0.0697 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8890 | 114656.958 | 44271.7796 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2811.347 | 0:240:120 | 0:00 | 0.0542 | 7 | 0.0034 | 0.0638 | 0.0672 | 0.0656 | 0.0012 | 0 | 3 | 0.0542 | 0.0669 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
8893 | 114660.253 | 44271.7796 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2867.5739 | 0:240:120 | 0:00 | 0.0521 | 7 | 0.0022 | 0.0621 | 0.0643 | 0.0632 | 0.0008 | 0 | 3 | 0.0521 | 0.0643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8896 | 114663.487 | 44271.7796 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2924.9254 | 0:240:120 | 0:00 | 0.05 | 7 | 0.0026 | 0.0589 | 0.0615 | 0.0604 | 0.001 | 0 | 3 | 0.05 | 0.0618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8899 | 114666.755 | 44271.7797 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2983.4239 | 0:240:120 | 0:00 | 0.0481 | 7 | 0.0031 | 0.0562 | 0.0593 | 0.058 | 0.0011 | 0 | 3 | 0.0481 | 0.0594 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8902 | 114669.868 | 44271.7797 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3043.0924 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0028 | 0.0541 | 0.0569 | 0.0559 | 0.0009 | 0 | 3 | 0.0462 | 0.0571 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8905 | 114673.382 | 44271.7797 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3103.9543 | 0:240:120 | 0:00 | 0.0444 | 7 | 0.0033 | 0.0517 | 0.055 | 0.0535 | 0.0011 | 0 | 3 | 0.0444 | 0.0549 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
8908 | 114676.57 | 44271.7798 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3166.0333 | 0:240:120 | 0:00 | 0.0427 | 7 | 0.0037 | 0.0498 | 0.0535 | 0.0519 | 0.0012 | 0 | 3 | 0.0427 | 0.0527 | P | NP | 1-1-0-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
8911 | 114679.734 | 44271.7798 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3229.354 | 0:240:120 | 0:00 | 0.041 | 7 | 0.003 | 0.0477 | 0.0507 | 0.0493 | 0.0012 | 0 | 3 | 0.041 | 0.051 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8914 | 114683.343 | 44271.7799 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3293.9411 | 0:240:120 | 0:00 | 0.0394 | 7 | 0.0028 | 0.0463 | 0.0491 | 0.048 | 0.001 | 0 | 3 | 0.0394 | 0.0494 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8917 | 114686.756 | 44271.7799 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3359.8199 | 0:240:120 | 0:00 | 0.0379 | 7 | 0.003 | 0.0442 | 0.0472 | 0.0459 | 0.001 | 0 | 3 | 0.0379 | 0.0479 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8920 | 114690.025 | 44271.7799 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3427.0163 | 0:240:120 | 0:00 | 0.0364 | 7 | 0.0031 | 0.0422 | 0.0453 | 0.0437 | 0.0012 | 0 | 3 | 0.0364 | 0.0464 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8923 | 114693.529 | 44271.78 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3495.5566 | 0:240:120 | 0:00 | 0.035 | 7 | 0.0031 | 0.0411 | 0.0442 | 0.0426 | 0.0011 | 0 | 3 | 0.035 | 0.045 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8926 | 114696.621 | 44271.78 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3565.4678 | 0:240:120 | 0:00 | 0.0336 | 7 | 0.0038 | 0.0385 | 0.0423 | 0.0411 | 0.0013 | 0 | 3 | 0.0336 | 0.0436 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8929 | 114699.785 | 44271.78 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3636.7771 | 0:240:120 | 0:00 | 0.0323 | 7 | 0.003 | 0.0382 | 0.0412 | 0.0397 | 0.0011 | 0 | 3 | 0.0323 | 0.0423 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8932 | 114703.062 | 44271.7801 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3709.5127 | 0:240:120 | 0:00 | 0.0311 | 7 | 0.0032 | 0.0364 | 0.0396 | 0.0381 | 0.001 | 0 | 3 | 0.0311 | 0.0411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8935 | 114706.214 | 44271.7801 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3783.7029 | 0:240:120 | 0:00 | 0.0299 | 7 | 0.0027 | 0.0352 | 0.0379 | 0.0365 | 0.0009 | 0 | 3 | 0.0299 | 0.0399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8938 | 114709.429 | 44271.7802 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3859.377 | 0:240:120 | 0:00 | 0.0287 | 7 | 0.003 | 0.0339 | 0.0369 | 0.0354 | 0.0009 | 0 | 3 | 0.0287 | 0.0387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8941 | 114712.535 | 44271.7802 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3936.5645 | 0:240:120 | 0:00 | 0.0276 | 7 | 0.0025 | 0.0329 | 0.0354 | 0.034 | 0.0008 | 0 | 3 | 0.0276 | 0.0376 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8944 | 114716.066 | 44271.7802 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4015.2958 | 0:240:120 | 0:00 | 0.0265 | 7 | 0.0013 | 0.0317 | 0.033 | 0.0326 | 0.0005 | 0 | 3 | 0.0265 | 0.0365 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8947 | 114719.247 | 44271.7803 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4095.6017 | 0:240:120 | 0:00 | 0.0255 | 7 | 0.0025 | 0.0301 | 0.0326 | 0.0317 | 0.0011 | 0 | 3 | 0.0255 | 0.0355 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8950 | 114722.631 | 44271.7803 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4177.5138 | 0:240:120 | 0:00 | 0.0245 | 7 | 0.0038 | 0.0287 | 0.0325 | 0.0308 | 0.0014 | 0 | 3 | 0.0245 | 0.0345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8953 | 114725.689 | 44271.7803 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4261.064 | 0:240:120 | 0:00 | 0.0235 | 7 | 0.0028 | 0.0279 | 0.0307 | 0.0296 | 0.001 | 0 | 3 | 0.0235 | 0.0335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8956 | 114729.036 | 44271.7804 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4346.2853 | 0:240:120 | 0:00 | 0.0226 | 7 | 0.0035 | 0.0266 | 0.0301 | 0.0285 | 0.0013 | 0 | 3 | 0.0226 | 0.0326 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8959 | 114732.281 | 44271.7804 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4433.211 | 0:240:120 | 0:00 | 0.0217 | 7 | 0.0029 | 0.0257 | 0.0286 | 0.0276 | 0.001 | 0 | 3 | 0.0217 | 0.0317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8962 | 114735.578 | 44271.7805 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4521.8752 | 0:240:120 | 0:00 | 0.0209 | 7 | 0.004 | 0.025 | 0.029 | 0.0271 | 0.0012 | 0 | 3 | 0.0209 | 0.0309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8965 | 114738.816 | 44271.7805 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4612.3127 | 0:240:120 | 0:00 | 0.0201 | 7 | 0.0043 | 0.0234 | 0.0277 | 0.026 | 0.0013 | 0 | 3 | 0.0201 | 0.0301 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8968 | 114741.831 | 44271.7805 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4704.559 | 0:240:120 | 0:00 | 0.0193 | 7 | 0.0025 | 0.0237 | 0.0262 | 0.0251 | 0.001 | 0 | 3 | 0.0193 | 0.0293 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8971 | 114744.833 | 44271.7806 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4798.6502 | 0:240:120 | 0:00 | 0.0185 | 7 | 0.0024 | 0.0229 | 0.0253 | 0.0243 | 0.001 | 0 | 3 | 0.0185 | 0.0285 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8974 | 114748.127 | 44271.7806 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4894.6232 | 0:240:120 | 0:00 | 0.0178 | 7 | 0.0034 | 0.0221 | 0.0255 | 0.024 | 0.0012 | 0 | 3 | 0.0178 | 0.0278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8977 | 114751.207 | 44271.7806 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4992.5157 | 0:240:120 | 0:00 | 0.0171 | 7 | 0.0028 | 0.0209 | 0.0237 | 0.0229 | 0.0011 | 0 | 3 | 0.0171 | 0.0271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8980 | 114754.399 | 44271.7807 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5092.366 | 0:240:120 | 0:00 | 0.0165 | 7 | 0.0031 | 0.0211 | 0.0242 | 0.0229 | 0.0012 | 0 | 3 | 0.0165 | 0.0265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8983 | 114757.47 | 44271.7807 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5194.2133 | 0:240:120 | 0:00 | 0.0158 | 7 | 0.0026 | 0.0207 | 0.0233 | 0.0223 | 0.001 | 0 | 3 | 0.0158 | 0.0258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8986 | 114760.516 | 44271.7808 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5298.0975 | 0:240:120 | 0:00 | 0.0152 | 7 | 0.0041 | 0.0197 | 0.0238 | 0.022 | 0.0016 | 0 | 3 | 0.0152 | 0.0252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8989 | 114763.715 | 44271.7808 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5404.0595 | 0:240:120 | 0:00 | 0.0146 | 7 | 0.0041 | 0.019 | 0.0231 | 0.0212 | 0.0013 | 0 | 3 | 0.0146 | 0.0246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8992 | 114766.571 | 44271.7808 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5512.1407 | 0:240:120 | 0:00 | 0.0141 | 7 | 0.0037 | 0.0186 | 0.0223 | 0.0209 | 0.0012 | 0 | 3 | 0.0141 | 0.0241 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8995 | 114769.82 | 44271.7809 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5622.3835 | 0:240:120 | 0:00 | 0.0135 | 7 | 0.0024 | 0.019 | 0.0214 | 0.0203 | 0.001 | 0 | 3 | 0.0135 | 0.0235 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
8998 | 114772.886 | 44271.7809 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5734.8312 | 0:240:120 | 0:00 | 0.013 | 7 | 0.0032 | 0.0181 | 0.0213 | 0.0201 | 0.0012 | 0 | 3 | 0.013 | 0.023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9001 | 114776.029 | 44271.7809 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5849.5278 | 0:240:120 | 0:00 | 0.0125 | 7 | 0.0029 | 0.0184 | 0.0213 | 0.0195 | 0.001 | 0 | 3 | 0.0125 | 0.0225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9004 | 114779.211 | 44271.781 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5966.5184 | 0:240:120 | 0:00 | 0.012 | 7 | 0.0037 | 0.0175 | 0.0212 | 0.0193 | 0.0013 | 0 | 3 | 0.012 | 0.022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9007 | 114782.188 | 44271.781 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6085.8487 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0027 | 0.0175 | 0.0202 | 0.0186 | 0.0012 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9010 | 114785.378 | 44271.781 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6207.5657 | 0:240:120 | 0:00 | 0.0111 | 7 | 0.0031 | 0.0171 | 0.0202 | 0.0181 | 0.0012 | 0 | 3 | 0.0111 | 0.0211 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9013 | 114788.758 | 44271.7811 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6331.717 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0016 | 0.0178 | 0.0194 | 0.0183 | 0.0007 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9016 | 114791.963 | 44271.7811 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6458.3513 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.0018 | 0.0168 | 0.0186 | 0.0177 | 0.0006 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9019 | 114794.942 | 44271.7811 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6532.9711 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0019 | 0.0164 | 0.0183 | 0.0173 | 0.0007 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9022 | 114797.936 | 44271.7812 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6663.6305 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0006 | 0.0164 | 0.017 | 0.0167 | 0.0002 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9025 | 114801.249 | 44271.7812 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6796.9031 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0016 | 0.0158 | 0.0174 | 0.0167 | 0.0005 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 1-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9028 | 114804.434 | 44271.7813 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6932.8412 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0019 | 0.0152 | 0.0171 | 0.016 | 0.0006 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 1-0-0-1-1-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9031 | 114807.431 | 44271.7813 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7071.498 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0017 | 0.0151 | 0.0168 | 0.0157 | 0.0006 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
9034 | 114810.422 | 44271.7813 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7212.928 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0039 | 0.0136 | 0.0175 | 0.0153 | 0.0014 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
9037 | 114813.532 | 44271.7814 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7357.1865 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0029 | 0.014 | 0.0169 | 0.0153 | 0.0011 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
9040 | 114816.601 | 44271.7814 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7504.3302 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0044 | 0.013 | 0.0174 | 0.0147 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
9043 | 114819.552 | 44271.7814 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7654.4169 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0046 | 0.0124 | 0.017 | 0.0146 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
9046 | 114822.589 | 44271.7815 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7807.5052 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0042 | 0.012 | 0.0162 | 0.0141 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
9049 | 114826.023 | 44271.7815 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7963.6553 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0044 | 0.0119 | 0.0163 | 0.0144 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
9052 | 114829.216 | 44271.7815 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8122.9284 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0055 | 0.0112 | 0.0167 | 0.0139 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
9055 | 114832.481 | 44271.7816 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8285.387 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0038 | 0.0121 | 0.0159 | 0.0141 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9058 | 114835.88 | 44271.7816 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8451.0947 | 0:240:120 | 0:00 | 0.006 | 7 | 0.0054 | 0.0113 | 0.0167 | 0.0138 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
9061 | 114839.37 | 44271.7817 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8620.1166 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.0049 | 0.0112 | 0.0161 | 0.0139 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
9064 | 114842.345 | 44271.7817 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8792.5189 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.0041 | 0.0113 | 0.0154 | 0.0135 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9067 | 114845.458 | 44271.7817 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8968.3693 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0057 | 0.0109 | 0.0166 | 0.0136 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
9070 | 114848.504 | 44271.7818 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9147.7367 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0056 | 0.0107 | 0.0163 | 0.0133 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
9073 | 114851.599 | 44271.7818 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9330.6914 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0042 | 0.0108 | 0.015 | 0.0132 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9076 | 114854.765 | 44271.7818 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9517.3053 | 0:240:120 | 0:00 | 0.0047 | 7 | 0.0048 | 0.0107 | 0.0155 | 0.0131 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9079 | 114857.712 | 44271.7819 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9707.6514 | 0:240:120 | 0:00 | 0.0045 | 7 | 0.0052 | 0.0105 | 0.0157 | 0.0131 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9082 | 114860.79 | 44271.7819 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9901.8044 | 0:240:120 | 0:00 | 0.0044 | 7 | 0.0052 | 0.0104 | 0.0156 | 0.0129 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9085 | 114863.873 | 44271.7819 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10099.8405 | 0:240:120 | 0:00 | 0.0042 | 7 | 0.0041 | 0.0108 | 0.0149 | 0.0129 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9088 | 114866.931 | 44271.782 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10301.8373 | 0:240:120 | 0:00 | 0.004 | 7 | 0.0045 | 0.0103 | 0.0148 | 0.0128 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9091 | 114870.015 | 44271.782 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10507.874 | 0:240:120 | 0:00 | 0.0039 | 7 | 0.0055 | 0.0104 | 0.0159 | 0.0128 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9094 | 114873.097 | 44271.7821 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10718.0315 | 0:240:120 | 0:00 | 0.0037 | 7 | 0.0047 | 0.0105 | 0.0152 | 0.0126 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9097 | 114876.158 | 44271.7821 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10932.3921 | 0:240:120 | 0:00 | 0.0036 | 7 | 0.0043 | 0.01 | 0.0143 | 0.0123 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9100 | 114879.217 | 44271.7821 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11151.04 | 0:240:120 | 0:00 | 0.0034 | 7 | 0.0052 | 0.0098 | 0.015 | 0.0123 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9103 | 114882.524 | 44271.7822 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11374.0608 | 0:240:120 | 0:00 | 0.0033 | 7 | 0.0022 | 0.0103 | 0.0125 | 0.0115 | 0.0008 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9106 | 114885.609 | 44271.7822 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11601.542 | 0:240:120 | 0:00 | 0.0032 | 7 | 0.0037 | 0.0102 | 0.0139 | 0.0113 | 0.0012 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9109 | 114888.715 | 44271.7822 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11833.5729 | 0:240:120 | 0:00 | 0.003 | 7 | 0.002 | 0.0103 | 0.0123 | 0.0113 | 0.0009 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9112 | 115250.879 | 44271.7864 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 203.9 | 0:240:120 | 0:00 | 40.7799 | 7 | 64.0205 | 309.6261 | 373.6466 | 330.6142 | 29.0008 | 841.0464 | 3 | 40.7799 | 166.6638 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9115 | 116251.441 | 44271.798 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208 | 0:240:120 | 0:00 | 35.1103 | 7 | 61.6847 | 188.6136 | 250.2983 | 209.1785 | 30.8378 | 950.9684 | 3 | 35.1103 | 108.6068 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9118 | 116855.726 | 44271.805 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 212.1 | 0:240:120 | 0:00 | 30.75 | 7 | 35.4293 | 65.2739 | 100.7032 | 76.4059 | 16.7177 | 279.4805 | 3 | 30.75 | 80.1359 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
9121 | 117112.28 | 44271.808 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 216.4 | 0:240:120 | 0:00 | 27.144 | 7 | 3.0749 | 55.3812 | 58.4561 | 57.4515 | 1.5029 | 2.2587 | 3 | 27.144 | 62.5851 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9124 | 117283.938 | 44271.81 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 220.7 | 0:240:120 | 0:00 | 24.2438 | 7 | 3.4117 | 48.2187 | 51.6304 | 49.4204 | 1.6609 | 2.7587 | 3 | 24.2438 | 51.1563 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
9127 | 117435.138 | 44271.8117 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 225.1 | 0:240:120 | 0:00 | 21.8117 | 7 | 3.4172 | 41.3898 | 44.807 | 42.5315 | 1.7061 | 2.9106 | 3 | 21.8117 | 42.9676 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
9130 | 117562.651 | 44271.8132 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 229.6 | 0:240:120 | 0:00 | 19.7455 | 7 | 0.7154 | 34.1692 | 34.8846 | 34.5205 | 0.2645 | 0.07 | 3 | 19.7455 | 36.8196 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9133 | 117665.155 | 44271.8144 | Vista Speed | T | 80T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.2 | 0:240:120 | 0:00 | 17.9704 | 7 | 1.1329 | 28.8986 | 30.0315 | 29.2838 | 0.5602 | 0.3138 | 3 | 17.9704 | 32.0395 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9136 | 118478.65 | 44271.8238 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 236.28 | 0:240:120 | 0:00 | 71.6638 | 7 | 67.6958 | 681.1491 | 748.8449 | 703.7925 | 33.7868 | 1141.5503 | 3 | 71.6638 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9139 | 120592.651 | 44271.8483 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 241.0056 | 0:240:120 | 0:00 | 58.1318 | 7 | 67.8042 | 545.6541 | 613.4583 | 568.2777 | 33.88 | 1147.8522 | 3 | 58.1318 | 764.0825 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9142 | 122300.62 | 44271.868 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 245.8257 | 0:240:120 | 0:00 | 48.5867 | 7 | 67.7521 | 410.2619 | 478.014 | 432.8477 | 33.8741 | 1147.4575 | 3 | 48.5867 | 247.15 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9145 | 123602.078 | 44271.8831 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 250.7422 | 0:240:120 | 0:00 | 41.4977 | 7 | 67.7245 | 274.8214 | 342.5459 | 297.3984 | 33.8587 | 1146.4099 | 3 | 41.4977 | 145.052 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9148 | 124453.837 | 44271.8929 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 255.7571 | 0:240:120 | 0:00 | 36.0285 | 7 | 24.4116 | 139.3894 | 163.801 | 147.1359 | 11.6218 | 135.0671 | 3 | 36.0285 | 101.4498 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9151 | 124848.79 | 44271.8975 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 260.8722 | 0:240:120 | 0:00 | 31.6841 | 7 | 0.0164 | 67.9149 | 67.9313 | 67.9266 | 0.0048 | 0 | 3 | 31.6841 | 77.2809 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9154 | 125048.38 | 44271.8998 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 266.0897 | 0:240:120 | 0:00 | 28.1522 | 7 | 3.7478 | 56.6905 | 60.4383 | 59.1832 | 1.8687 | 3.4919 | 3 | 28.1522 | 61.9307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9157 | 125225.226 | 44271.9019 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 271.4115 | 0:240:120 | 0:00 | 25.2266 | 7 | 3.7517 | 49.195 | 52.9467 | 50.4477 | 1.8737 | 3.5106 | 3 | 25.2266 | 51.3244 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
9160 | 125376.537 | 44271.9036 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 276.8397 | 0:240:120 | 0:00 | 22.7652 | 7 | 1.2799 | 41.702 | 42.9819 | 41.9618 | 0.4438 | 0.197 | 3 | 22.7652 | 43.5624 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9163 | 125498.913 | 44271.905 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 282.3765 | 0:240:120 | 0:00 | 20.6672 | 7 | 1.2407 | 32.971 | 34.2117 | 33.8088 | 0.6029 | 0.3635 | 3 | 20.6672 | 37.64 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9166 | 125602.095 | 44271.9062 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 288.024 | 0:240:120 | 0:00 | 18.859 | 7 | 1.2421 | 30.4917 | 31.7338 | 30.9063 | 0.62 | 0.3844 | 3 | 18.859 | 32.9758 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9169 | 125696.659 | 44271.9073 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 293.7845 | 0:240:120 | 0:00 | 17.2855 | 7 | 0.7432 | 27.2725 | 28.0157 | 27.8823 | 0.2507 | 0.0629 | 3 | 17.2855 | 29.21 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9172 | 125781.063 | 44271.9083 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 299.6602 | 0:240:120 | 0:00 | 15.9049 | 7 | 1.2438 | 24.2936 | 25.5374 | 24.7093 | 0.6204 | 0.3849 | 3 | 15.9049 | 26.108 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9175 | 125857.106 | 44271.9092 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 305.6534 | 0:240:120 | 0:00 | 14.6847 | 7 | 0.5976 | 21.2215 | 21.8191 | 21.624 | 0.2904 | 0.0843 | 3 | 14.6847 | 23.5104 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9178 | 125924.649 | 44271.91 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 311.7664 | 0:240:120 | 0:00 | 13.5992 | 7 | 0.6156 | 19.9749 | 20.5905 | 20.1807 | 0.3057 | 0.0935 | 3 | 13.5992 | 21.305 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9181 | 125987.742 | 44271.9107 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 318.0018 | 0:240:120 | 0:00 | 12.628 | 7 | 0.6138 | 18.1371 | 18.7509 | 18.4985 | 0.2802 | 0.0785 | 3 | 12.628 | 19.4107 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9184 | 126045.103 | 44271.9114 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 324.3618 | 0:240:120 | 0:00 | 11.7546 | 7 | 0.6148 | 16.2953 | 16.9101 | 16.7045 | 0.3059 | 0.0936 | 3 | 11.7546 | 17.7671 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9187 | 126097.532 | 44271.912 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 330.849 | 0:240:120 | 0:00 | 10.9656 | 7 | 0.1669 | 15.3169 | 15.4838 | 15.3624 | 0.0687 | 0.0047 | 3 | 10.9656 | 16.3286 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9190 | 126146.159 | 44271.9125 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 337.466 | 0:240:120 | 0:00 | 10.2498 | 7 | 0.3666 | 14.2251 | 14.5917 | 14.3477 | 0.1823 | 0.0332 | 3 | 10.2498 | 15.06 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9193 | 126191.951 | 44271.9131 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 344.2153 | 0:240:120 | 0:00 | 9.5979 | 7 | 0.3634 | 13.1363 | 13.4997 | 13.2616 | 0.1785 | 0.0319 | 3 | 9.5979 | 13.9338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9196 | 126234.321 | 44271.9135 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 351.0997 | 0:240:120 | 0:00 | 9.0023 | 7 | 0.3648 | 12.0447 | 12.4095 | 12.1773 | 0.174 | 0.0303 | 3 | 9.0023 | 12.9279 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9199 | 126273.635 | 44271.914 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 358.1216 | 0:240:120 | 0:00 | 8.4563 | 7 | 0.2391 | 11.3272 | 11.5663 | 11.4492 | 0.1051 | 0.011 | 3 | 8.4563 | 12.0248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9202 | 126310.483 | 44271.9144 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 365.2841 | 0:240:120 | 0:00 | 7.9544 | 7 | 0.2414 | 10.607 | 10.8484 | 10.6986 | 0.1137 | 0.0129 | 3 | 7.9544 | 11.2101 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9205 | 126345.323 | 44271.9148 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 372.5898 | 0:240:120 | 0:00 | 7.4917 | 7 | 0.2417 | 9.8896 | 10.1313 | 9.9707 | 0.1198 | 0.0143 | 3 | 7.4917 | 10.4719 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9208 | 126378.04 | 44271.9152 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 380.0416 | 0:240:120 | 0:00 | 7.0643 | 7 | 0.3364 | 9.1462 | 9.4826 | 9.3141 | 0.1453 | 0.0211 | 3 | 7.0643 | 9.8004 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9211 | 126408.991 | 44271.9156 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 387.6424 | 0:240:120 | 0:00 | 6.6684 | 7 | 0.2086 | 8.6405 | 8.8491 | 8.7599 | 0.09 | 0.0081 | 3 | 6.6684 | 9.1875 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9214 | 126438.126 | 44271.9159 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 395.3952 | 0:240:120 | 0:00 | 6.301 | 7 | 0.1686 | 8.1354 | 8.304 | 8.2472 | 0.0831 | 0.0069 | 3 | 6.301 | 8.6263 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9217 | 126465.695 | 44271.9162 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 403.3031 | 0:240:120 | 0:00 | 5.9595 | 7 | 0.2502 | 7.5927 | 7.8429 | 7.7175 | 0.1078 | 0.0116 | 3 | 5.9595 | 8.1108 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9220 | 126491.934 | 44271.9165 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 411.3692 | 0:240:120 | 0:00 | 5.6413 | 7 | 0.1254 | 7.2197 | 7.3451 | 7.3026 | 0.0615 | 0.0038 | 3 | 5.6413 | 7.636 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9223 | 126516.689 | 44271.9168 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 419.5966 | 0:240:120 | 0:00 | 5.3445 | 7 | 0.2491 | 6.7218 | 6.9709 | 6.8496 | 0.104 | 0.0108 | 3 | 5.3445 | 7.1977 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9226 | 126540.186 | 44271.9171 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 427.9885 | 0:240:120 | 0:00 | 5.0671 | 7 | 0.0951 | 6.4365 | 6.5316 | 6.4995 | 0.0468 | 0.0022 | 3 | 5.0671 | 6.792 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9229 | 126562.872 | 44271.9174 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 436.5483 | 0:240:120 | 0:00 | 4.8074 | 7 | 0.1913 | 6.0557 | 6.247 | 6.1501 | 0.082 | 0.0067 | 3 | 4.8074 | 6.4159 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9232 | 126584.505 | 44271.9176 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 445.2793 | 0:240:120 | 0:00 | 4.5641 | 7 | 0.1711 | 5.6942 | 5.8653 | 5.7755 | 0.074 | 0.0055 | 3 | 4.5641 | 6.0663 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9235 | 126604.79 | 44271.9178 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 454.1848 | 0:240:120 | 0:00 | 4.3359 | 7 | 0.1398 | 5.4039 | 5.5437 | 5.4991 | 0.0629 | 0.004 | 3 | 4.3359 | 5.7409 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9238 | 126624.497 | 44271.9181 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 463.2685 | 0:240:120 | 0:00 | 4.1214 | 7 | 0.0919 | 5.1535 | 5.2454 | 5.2162 | 0.0413 | 0.0017 | 3 | 4.1214 | 5.4374 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9241 | 126642.831 | 44271.9183 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 472.5339 | 0:240:120 | 0:00 | 3.9197 | 7 | 0.0824 | 4.8774 | 4.9598 | 4.9353 | 0.0345 | 0.0012 | 3 | 3.9197 | 5.154 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9244 | 126660.57 | 44271.9185 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 481.9846 | 0:240:120 | 0:00 | 3.7297 | 7 | 0.1208 | 4.6058 | 4.7266 | 4.687 | 0.048 | 0.0023 | 3 | 3.7297 | 4.8888 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9247 | 126677.617 | 44271.9187 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 491.6243 | 0:240:120 | 0:00 | 3.5507 | 7 | 0.1106 | 4.3674 | 4.478 | 4.4401 | 0.0535 | 0.0029 | 3 | 3.5507 | 4.6404 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9250 | 126693.635 | 44271.9189 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 501.4568 | 0:240:120 | 0:00 | 3.3819 | 7 | 0.1002 | 4.1689 | 4.2691 | 4.2224 | 0.0435 | 0.0019 | 3 | 3.3819 | 4.4075 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9253 | 126709.14 | 44271.919 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 511.4859 | 0:240:120 | 0:00 | 3.2224 | 7 | 0.099 | 3.9718 | 4.0708 | 4.0205 | 0.0422 | 0.0018 | 3 | 3.2224 | 4.1887 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9256 | 126724.648 | 44271.9192 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 521.7156 | 0:240:120 | 0:00 | 3.0718 | 7 | 0.1146 | 3.7576 | 3.8722 | 3.8215 | 0.0491 | 0.0024 | 3 | 3.0718 | 3.983 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9259 | 126739.04 | 44271.9194 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 532.1499 | 0:240:120 | 0:00 | 2.9293 | 7 | 0.0826 | 3.5932 | 3.6758 | 3.634 | 0.0352 | 0.0012 | 3 | 2.9293 | 3.7894 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9262 | 126752.84 | 44271.9196 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 542.7929 | 0:240:120 | 0:00 | 2.7944 | 7 | 0.1031 | 3.4069 | 3.51 | 3.4628 | 0.0431 | 0.0019 | 3 | 2.7944 | 3.607 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9265 | 126766.559 | 44271.9197 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 553.6488 | 0:240:120 | 0:00 | 2.6667 | 7 | 0.0745 | 3.2634 | 3.3379 | 3.3017 | 0.0305 | 0.0009 | 3 | 2.6667 | 3.4349 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9268 | 126779.398 | 44271.9199 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 564.7218 | 0:240:120 | 0:00 | 2.5456 | 7 | 0.0591 | 3.106 | 3.1651 | 3.1398 | 0.0257 | 0.0007 | 3 | 2.5456 | 3.2725 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9271 | 126791.771 | 44271.92 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 576.0162 | 0:240:120 | 0:00 | 2.4308 | 7 | 0.059 | 2.9584 | 3.0174 | 2.9967 | 0.0285 | 0.0008 | 3 | 2.4308 | 3.1191 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9274 | 126803.652 | 44271.9201 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 587.5365 | 0:240:120 | 0:00 | 2.3218 | 7 | 0.0679 | 2.8194 | 2.8873 | 2.8579 | 0.0295 | 0.0009 | 3 | 2.3218 | 2.9741 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9277 | 126815.2 | 44271.9203 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 599.2872 | 0:240:120 | 0:00 | 2.2184 | 7 | 0.0615 | 2.6915 | 2.753 | 2.7281 | 0.0278 | 0.0008 | 3 | 2.2184 | 2.8368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9280 | 126826.633 | 44271.9204 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 611.273 | 0:240:120 | 0:00 | 2.1201 | 7 | 0.0524 | 2.5717 | 2.6241 | 2.6006 | 0.0218 | 0.0005 | 3 | 2.1201 | 2.7069 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9283 | 126837.449 | 44271.9205 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 623.4985 | 0:240:120 | 0:00 | 2.0267 | 7 | 0.0535 | 2.4518 | 2.5053 | 2.4812 | 0.0216 | 0.0005 | 3 | 2.0267 | 2.5837 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9286 | 126847.785 | 44271.9207 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 635.9684 | 0:240:120 | 0:00 | 1.9379 | 7 | 0.0575 | 2.3379 | 2.3954 | 2.369 | 0.0247 | 0.0006 | 3 | 1.9379 | 2.4669 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9289 | 126857.777 | 44271.9208 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 648.6878 | 0:240:120 | 0:00 | 1.8533 | 7 | 0.0502 | 2.2408 | 2.291 | 2.2683 | 0.0211 | 0.0004 | 3 | 1.8533 | 2.3561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9292 | 126867.652 | 44271.9209 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 661.6615 | 0:240:120 | 0:00 | 1.7729 | 7 | 0.0511 | 2.135 | 2.1861 | 2.1627 | 0.022 | 0.0005 | 3 | 1.7729 | 2.251 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9295 | 126877.059 | 44271.921 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 674.8948 | 0:240:120 | 0:00 | 1.6963 | 7 | 0.0412 | 2.0428 | 2.084 | 2.0639 | 0.0175 | 0.0003 | 3 | 1.6963 | 2.1511 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9298 | 126886.446 | 44271.9211 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 688.3927 | 0:240:120 | 0:00 | 1.6233 | 7 | 0.0457 | 1.958 | 2.0037 | 1.9815 | 0.0189 | 0.0004 | 3 | 1.6233 | 2.0561 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9301 | 126895.611 | 44271.9212 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 702.1605 | 0:240:120 | 0:00 | 1.5538 | 7 | 0.0446 | 1.8693 | 1.9139 | 1.8933 | 0.0186 | 0.0003 | 3 | 1.5538 | 1.9658 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9304 | 126904.268 | 44271.9213 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 716.2037 | 0:240:120 | 0:00 | 1.4875 | 7 | 0.0405 | 1.7898 | 1.8303 | 1.8116 | 0.0175 | 0.0003 | 3 | 1.4875 | 1.88 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9307 | 126912.607 | 44271.9214 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 730.5278 | 0:240:120 | 0:00 | 1.4242 | 7 | 0.0366 | 1.7131 | 1.7497 | 1.7324 | 0.0154 | 0.0002 | 3 | 1.4242 | 1.7982 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9310 | 126920.956 | 44271.9215 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 745.1384 | 0:240:120 | 0:00 | 1.3639 | 7 | 0.0374 | 1.6315 | 1.6689 | 1.6512 | 0.0154 | 0.0002 | 3 | 1.3639 | 1.7204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9313 | 126928.759 | 44271.9216 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 760.0411 | 0:240:120 | 0:00 | 1.3064 | 7 | 0.0314 | 1.5671 | 1.5985 | 1.5843 | 0.0135 | 0.0002 | 3 | 1.3064 | 1.6463 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9316 | 126936.411 | 44271.9217 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 775.242 | 0:240:120 | 0:00 | 1.2514 | 7 | 0.0389 | 1.4959 | 1.5348 | 1.5161 | 0.0161 | 0.0003 | 3 | 1.2514 | 1.5757 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9319 | 126943.926 | 44271.9218 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 790.7468 | 0:240:120 | 0:00 | 1.199 | 7 | 0.0289 | 1.4373 | 1.4662 | 1.4525 | 0.0122 | 0.0001 | 3 | 1.199 | 1.5084 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9322 | 126951.21 | 44271.9218 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 806.5617 | 0:240:120 | 0:00 | 1.1488 | 7 | 0.0288 | 1.3748 | 1.4036 | 1.3898 | 0.0116 | 0.0001 | 3 | 1.1488 | 1.4442 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9325 | 126958.349 | 44271.9219 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 822.693 | 0:240:120 | 0:00 | 1.101 | 7 | 0.0293 | 1.3155 | 1.3448 | 1.33 | 0.0123 | 0.0002 | 3 | 1.101 | 1.383 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9328 | 126965.335 | 44271.922 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 839.1468 | 0:240:120 | 0:00 | 1.0552 | 7 | 0.0291 | 1.2594 | 1.2885 | 1.274 | 0.0123 | 0.0002 | 3 | 1.0552 | 1.3245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9331 | 126972.037 | 44271.9221 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 855.9298 | 0:240:120 | 0:00 | 1.0115 | 7 | 0.0238 | 1.2096 | 1.2334 | 1.2216 | 0.0099 | 0.0001 | 3 | 1.0115 | 1.2688 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9334 | 126978.789 | 44271.9222 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 873.0484 | 0:240:120 | 0:00 | 0.9697 | 7 | 0.0228 | 1.1582 | 1.181 | 1.1706 | 0.0098 | 0.0001 | 3 | 0.9697 | 1.2155 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9337 | 126985.043 | 44271.9222 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 890.5093 | 0:240:120 | 0:00 | 0.9297 | 7 | 0.0262 | 1.1098 | 1.136 | 1.1219 | 0.0106 | 0.0001 | 3 | 0.9297 | 1.1647 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9340 | 126991.528 | 44271.9223 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 908.3195 | 0:240:120 | 0:00 | 0.8915 | 7 | 0.0248 | 1.0611 | 1.0859 | 1.0749 | 0.0105 | 0.0001 | 3 | 0.8915 | 1.1161 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9343 | 126997.742 | 44271.9224 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 926.4859 | 0:240:120 | 0:00 | 0.8549 | 7 | 0.0187 | 1.0208 | 1.0395 | 1.0301 | 0.0077 | 0.0001 | 3 | 0.8549 | 1.0697 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9346 | 127003.742 | 44271.9225 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 945.0156 | 0:240:120 | 0:00 | 0.8199 | 7 | 0.0188 | 0.9782 | 0.997 | 0.9875 | 0.0072 | 0.0001 | 3 | 0.8199 | 1.0253 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9349 | 127009.498 | 44271.9225 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 963.9159 | 0:240:120 | 0:00 | 0.7864 | 7 | 0.0187 | 0.9371 | 0.9558 | 0.9464 | 0.0072 | 0.0001 | 3 | 0.7864 | 0.9829 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9352 | 127015.373 | 44271.9226 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 983.1942 | 0:240:120 | 0:00 | 0.7543 | 7 | 0.0194 | 0.8973 | 0.9167 | 0.9075 | 0.0078 | 0.0001 | 3 | 0.7543 | 0.9423 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9355 | 127021.253 | 44271.9227 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1002.8581 | 0:240:120 | 0:00 | 0.7236 | 7 | 0.0187 | 0.861 | 0.8797 | 0.8704 | 0.0077 | 0.0001 | 3 | 0.7236 | 0.9035 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9358 | 127027.419 | 44271.9227 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1022.9153 | 0:240:120 | 0:00 | 0.6942 | 7 | 0.0162 | 0.8257 | 0.8419 | 0.8344 | 0.0068 | 0 | 3 | 0.6942 | 0.8664 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9361 | 127032.815 | 44271.9228 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1043.3736 | 0:240:120 | 0:00 | 0.6661 | 7 | 0.018 | 0.7921 | 0.8101 | 0.8011 | 0.0072 | 0.0001 | 3 | 0.6661 | 0.8309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9364 | 127038.333 | 44271.9229 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1064.2411 | 0:240:120 | 0:00 | 0.6391 | 7 | 0.0166 | 0.7602 | 0.7768 | 0.768 | 0.0069 | 0 | 3 | 0.6391 | 0.797 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9367 | 127043.574 | 44271.9229 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1085.5259 | 0:240:120 | 0:00 | 0.6133 | 7 | 0.0166 | 0.7284 | 0.745 | 0.7366 | 0.0068 | 0 | 3 | 0.6133 | 0.7644 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9370 | 127048.968 | 44271.923 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1107.2364 | 0:240:120 | 0:00 | 0.5885 | 7 | 0.0138 | 0.6997 | 0.7135 | 0.7068 | 0.0056 | 0 | 3 | 0.5885 | 0.7333 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9373 | 127054.073 | 44271.923 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1129.3811 | 0:240:120 | 0:00 | 0.5648 | 7 | 0.0142 | 0.6705 | 0.6847 | 0.6785 | 0.0055 | 0 | 3 | 0.5648 | 0.7035 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9376 | 127059.107 | 44271.9231 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1151.9688 | 0:240:120 | 0:00 | 0.5421 | 7 | 0.0126 | 0.6449 | 0.6575 | 0.6514 | 0.0051 | 0 | 3 | 0.5421 | 0.675 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9379 | 127064.339 | 44271.9232 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1175.0081 | 0:240:120 | 0:00 | 0.5203 | 7 | 0.0139 | 0.6186 | 0.6325 | 0.6252 | 0.0054 | 0 | 3 | 0.5203 | 0.6476 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9382 | 127069.306 | 44271.9232 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1198.5083 | 0:240:120 | 0:00 | 0.4994 | 7 | 0.0128 | 0.5937 | 0.6065 | 0.5999 | 0.0053 | 0 | 3 | 0.4994 | 0.6214 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9385 | 127074.275 | 44271.9233 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1222.4785 | 0:240:120 | 0:00 | 0.4794 | 7 | 0.0125 | 0.568 | 0.5805 | 0.5751 | 0.0052 | 0 | 3 | 0.4794 | 0.5963 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9388 | 127079.255 | 44271.9233 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1246.928 | 0:240:120 | 0:00 | 0.4602 | 7 | 0.0104 | 0.5494 | 0.5598 | 0.553 | 0.0034 | 0 | 3 | 0.4602 | 0.5723 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9391 | 127083.878 | 44271.9234 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1271.8666 | 0:240:120 | 0:00 | 0.4418 | 7 | 0.0198 | 0.5175 | 0.5373 | 0.5284 | 0.0068 | 0 | 3 | 0.4418 | 0.5493 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9394 | 127088.418 | 44271.9234 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1297.3039 | 0:240:120 | 0:00 | 0.4242 | 7 | 0.0169 | 0.4976 | 0.5145 | 0.507 | 0.0066 | 0 | 3 | 0.4242 | 0.5272 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9397 | 127092.971 | 44271.9235 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1323.25 | 0:240:120 | 0:00 | 0.4073 | 7 | 0.0146 | 0.4775 | 0.4921 | 0.486 | 0.0048 | 0 | 3 | 0.4073 | 0.506 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9400 | 127097.398 | 44271.9235 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1349.715 | 0:240:120 | 0:00 | 0.3911 | 7 | 0.0187 | 0.4586 | 0.4773 | 0.4676 | 0.0059 | 0 | 3 | 0.3911 | 0.4858 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9403 | 127101.807 | 44271.9236 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1376.7093 | 0:240:120 | 0:00 | 0.3755 | 7 | 0.0064 | 0.4472 | 0.4536 | 0.4498 | 0.0023 | 0 | 3 | 0.3755 | 0.4663 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9406 | 127106.3 | 44271.9236 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1404.2435 | 0:240:120 | 0:00 | 0.3606 | 7 | 0.0109 | 0.4254 | 0.4363 | 0.4299 | 0.0035 | 0 | 3 | 0.3606 | 0.4477 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9409 | 127110.396 | 44271.9237 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1432.3284 | 0:240:120 | 0:00 | 0.3462 | 7 | 0.0136 | 0.4052 | 0.4188 | 0.4129 | 0.0043 | 0 | 3 | 0.3462 | 0.4298 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9412 | 127114.487 | 44271.9237 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1460.9749 | 0:240:120 | 0:00 | 0.3325 | 7 | 0.0117 | 0.3918 | 0.4035 | 0.397 | 0.0041 | 0 | 3 | 0.3325 | 0.4126 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9415 | 127118.563 | 44271.9238 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1490.1944 | 0:240:120 | 0:00 | 0.3193 | 7 | 0.0085 | 0.3773 | 0.3858 | 0.3807 | 0.0025 | 0 | 3 | 0.3193 | 0.3962 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9418 | 127122.813 | 44271.9238 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1519.9983 | 0:240:120 | 0:00 | 0.3067 | 7 | 0.0122 | 0.3605 | 0.3727 | 0.366 | 0.0041 | 0 | 3 | 0.3067 | 0.3804 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9421 | 127126.957 | 44271.9239 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1550.3983 | 0:240:120 | 0:00 | 0.2945 | 7 | 0.0131 | 0.3425 | 0.3556 | 0.3512 | 0.0039 | 0 | 3 | 0.2945 | 0.3653 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9424 | 127131.088 | 44271.9239 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1581.4063 | 0:240:120 | 0:00 | 0.2829 | 7 | 0.0072 | 0.3345 | 0.3417 | 0.3376 | 0.0026 | 0 | 3 | 0.2829 | 0.3508 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9427 | 127135.301 | 44271.924 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1613.0344 | 0:240:120 | 0:00 | 0.2717 | 7 | 0.009 | 0.3192 | 0.3282 | 0.3237 | 0.0028 | 0 | 3 | 0.2717 | 0.3368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9430 | 127139.332 | 44271.924 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1645.2951 | 0:240:120 | 0:00 | 0.261 | 7 | 0.0093 | 0.3074 | 0.3167 | 0.3114 | 0.0035 | 0 | 3 | 0.261 | 0.3235 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9433 | 127143.319 | 44271.9241 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1678.201 | 0:240:120 | 0:00 | 0.2507 | 7 | 0.0089 | 0.2934 | 0.3023 | 0.2988 | 0.0027 | 0 | 3 | 0.2507 | 0.3107 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9436 | 127147.237 | 44271.9241 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1711.765 | 0:240:120 | 0:00 | 0.2408 | 7 | 0.0078 | 0.2821 | 0.2899 | 0.2869 | 0.0027 | 0 | 3 | 0.2408 | 0.2984 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9439 | 127151.088 | 44271.9242 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1746.0003 | 0:240:120 | 0:00 | 0.2313 | 7 | 0.0081 | 0.2708 | 0.2789 | 0.2747 | 0.0031 | 0 | 3 | 0.2313 | 0.2866 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9442 | 127154.947 | 44271.9242 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1780.9203 | 0:240:120 | 0:00 | 0.2222 | 7 | 0.0086 | 0.261 | 0.2696 | 0.2647 | 0.0028 | 0 | 3 | 0.2222 | 0.2752 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9445 | 127158.866 | 44271.9243 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1816.5387 | 0:240:120 | 0:00 | 0.2134 | 7 | 0.0072 | 0.2507 | 0.2579 | 0.2543 | 0.0023 | 0 | 3 | 0.2134 | 0.2643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9448 | 127162.635 | 44271.9243 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1852.8695 | 0:240:120 | 0:00 | 0.205 | 7 | 0.0074 | 0.2414 | 0.2488 | 0.2443 | 0.0025 | 0 | 3 | 0.205 | 0.2539 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9451 | 127166.353 | 44271.9243 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1889.9269 | 0:240:120 | 0:00 | 0.1969 | 7 | 0.0079 | 0.2321 | 0.24 | 0.235 | 0.0026 | 0 | 3 | 0.1969 | 0.2439 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9454 | 127170.145 | 44271.9244 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1927.7254 | 0:240:120 | 0:00 | 0.1892 | 7 | 0.0052 | 0.224 | 0.2292 | 0.2261 | 0.0016 | 0 | 3 | 0.1892 | 0.2343 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9457 | 127174.105 | 44271.9244 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1966.2799 | 0:240:120 | 0:00 | 0.1818 | 7 | 0.0051 | 0.2144 | 0.2195 | 0.2166 | 0.0019 | 0 | 3 | 0.1818 | 0.225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9460 | 127177.831 | 44271.9245 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2005.6055 | 0:240:120 | 0:00 | 0.1746 | 7 | 0.0065 | 0.2041 | 0.2106 | 0.2074 | 0.0022 | 0 | 3 | 0.1746 | 0.2162 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9463 | 127181.361 | 44271.9245 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2045.7176 | 0:240:120 | 0:00 | 0.1678 | 7 | 0.0051 | 0.1974 | 0.2025 | 0.1997 | 0.0018 | 0 | 3 | 0.1678 | 0.2077 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9466 | 127184.9 | 44271.9246 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2086.632 | 0:240:120 | 0:00 | 0.1612 | 7 | 0.0053 | 0.1898 | 0.1951 | 0.1922 | 0.0018 | 0 | 3 | 0.1612 | 0.1995 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9469 | 127188.558 | 44271.9246 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2128.3646 | 0:240:120 | 0:00 | 0.1549 | 7 | 0.005 | 0.1826 | 0.1876 | 0.1849 | 0.0021 | 0 | 3 | 0.1549 | 0.1916 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9472 | 127192.211 | 44271.9246 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2170.9319 | 0:240:120 | 0:00 | 0.1488 | 7 | 0.005 | 0.1752 | 0.1802 | 0.1773 | 0.0017 | 0 | 3 | 0.1488 | 0.1841 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9475 | 127195.622 | 44271.9247 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2214.3505 | 0:240:120 | 0:00 | 0.143 | 7 | 0.0043 | 0.1689 | 0.1732 | 0.1709 | 0.0014 | 0 | 3 | 0.143 | 0.1769 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9478 | 127199.367 | 44271.9247 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2258.6375 | 0:240:120 | 0:00 | 0.1374 | 7 | 0.0038 | 0.1625 | 0.1663 | 0.1642 | 0.0014 | 0 | 3 | 0.1374 | 0.1699 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9481 | 127202.637 | 44271.9248 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2303.8103 | 0:240:120 | 0:00 | 0.132 | 7 | 0.0038 | 0.1552 | 0.159 | 0.1569 | 0.0013 | 0 | 3 | 0.132 | 0.1633 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9484 | 127206.053 | 44271.9248 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2349.8865 | 0:240:120 | 0:00 | 0.1268 | 7 | 0.0039 | 0.1488 | 0.1527 | 0.1511 | 0.0013 | 0 | 3 | 0.1268 | 0.1569 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9487 | 127209.598 | 44271.9248 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2396.8842 | 0:240:120 | 0:00 | 0.1218 | 7 | 0.0032 | 0.1436 | 0.1468 | 0.1452 | 0.0013 | 0 | 3 | 0.1218 | 0.1507 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9490 | 127213.26 | 44271.9249 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2444.8219 | 0:240:120 | 0:00 | 0.1171 | 7 | 0.0029 | 0.1381 | 0.141 | 0.1394 | 0.0009 | 0 | 3 | 0.1171 | 0.1448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9493 | 127216.84 | 44271.9249 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2493.7184 | 0:240:120 | 0:00 | 0.1125 | 7 | 0.0025 | 0.1331 | 0.1356 | 0.1343 | 0.0009 | 0 | 3 | 0.1125 | 0.1391 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9496 | 127220.234 | 44271.925 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2543.5927 | 0:240:120 | 0:00 | 0.1081 | 7 | 0.0027 | 0.1274 | 0.1301 | 0.1287 | 0.001 | 0 | 3 | 0.1081 | 0.1337 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9499 | 127223.512 | 44271.925 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2594.4646 | 0:240:120 | 0:00 | 0.1039 | 7 | 0.0029 | 0.123 | 0.1259 | 0.1243 | 0.0011 | 0 | 3 | 0.1039 | 0.1284 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9502 | 127226.825 | 44271.925 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2646.3539 | 0:240:120 | 0:00 | 0.0998 | 7 | 0.0041 | 0.1172 | 0.1213 | 0.1193 | 0.0013 | 0 | 3 | 0.0998 | 0.1234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9505 | 127230.119 | 44271.9251 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2699.2809 | 0:240:120 | 0:00 | 0.0959 | 7 | 0.0023 | 0.1139 | 0.1162 | 0.1148 | 0.0008 | 0 | 3 | 0.0959 | 0.1186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9508 | 127233.555 | 44271.9251 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2753.2666 | 0:240:120 | 0:00 | 0.0922 | 7 | 0.0033 | 0.109 | 0.1123 | 0.1106 | 0.0011 | 0 | 3 | 0.0922 | 0.1139 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9511 | 127237.032 | 44271.9252 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2808.3319 | 0:240:120 | 0:00 | 0.0886 | 7 | 0.0036 | 0.1039 | 0.1075 | 0.1057 | 0.0013 | 0 | 3 | 0.0886 | 0.1095 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9514 | 127240.617 | 44271.9252 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2864.4985 | 0:240:120 | 0:00 | 0.0851 | 7 | 0.0036 | 0.0997 | 0.1033 | 0.1014 | 0.0013 | 0 | 3 | 0.0851 | 0.1052 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9517 | 127243.904 | 44271.9252 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2921.7885 | 0:240:120 | 0:00 | 0.0818 | 7 | 0.0028 | 0.097 | 0.0998 | 0.098 | 0.001 | 0 | 3 | 0.0818 | 0.1011 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9520 | 127247.474 | 44271.9253 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2980.2243 | 0:240:120 | 0:00 | 0.0786 | 7 | 0.0027 | 0.0929 | 0.0956 | 0.0942 | 0.0009 | 0 | 3 | 0.0786 | 0.0971 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9523 | 127250.748 | 44271.9253 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3039.8288 | 0:240:120 | 0:00 | 0.0755 | 7 | 0.0027 | 0.0896 | 0.0923 | 0.091 | 0.001 | 0 | 3 | 0.0755 | 0.0933 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9526 | 127254.004 | 44271.9254 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3100.6253 | 0:240:120 | 0:00 | 0.0726 | 7 | 0.0033 | 0.0854 | 0.0887 | 0.0869 | 0.0013 | 0 | 3 | 0.0726 | 0.0897 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9529 | 127257.298 | 44271.9254 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3162.6378 | 0:240:120 | 0:00 | 0.0697 | 7 | 0.0041 | 0.0814 | 0.0855 | 0.0836 | 0.0016 | 0 | 3 | 0.0697 | 0.0862 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9532 | 127260.575 | 44271.9254 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3225.8906 | 0:240:120 | 0:00 | 0.067 | 7 | 0.0038 | 0.078 | 0.0818 | 0.0803 | 0.0014 | 0 | 3 | 0.067 | 0.0828 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9535 | 127264.062 | 44271.9255 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3290.4084 | 0:240:120 | 0:00 | 0.0644 | 7 | 0.0038 | 0.075 | 0.0788 | 0.0768 | 0.0012 | 0 | 3 | 0.0644 | 0.0796 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9538 | 127267.602 | 44271.9255 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3356.2166 | 0:240:120 | 0:00 | 0.0619 | 7 | 0.0036 | 0.0728 | 0.0764 | 0.0742 | 0.0011 | 0 | 3 | 0.0619 | 0.0765 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9541 | 127270.878 | 44271.9255 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3423.3409 | 0:240:120 | 0:00 | 0.0595 | 7 | 0.003 | 0.0701 | 0.0731 | 0.0719 | 0.0011 | 0 | 3 | 0.0595 | 0.0735 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9544 | 127274.049 | 44271.9256 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3491.8077 | 0:240:120 | 0:00 | 0.0572 | 7 | 0.0028 | 0.0668 | 0.0696 | 0.0684 | 0.001 | 0 | 3 | 0.0572 | 0.0706 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9547 | 127277.323 | 44271.9256 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3561.6439 | 0:240:120 | 0:00 | 0.0549 | 7 | 0.0038 | 0.0636 | 0.0674 | 0.0659 | 0.0015 | 0 | 3 | 0.0549 | 0.0679 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9550 | 127280.573 | 44271.9257 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3632.8768 | 0:240:120 | 0:00 | 0.0528 | 7 | 0.0033 | 0.0618 | 0.0651 | 0.0636 | 0.001 | 0 | 3 | 0.0528 | 0.0652 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9553 | 127284.04 | 44271.9257 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3705.5343 | 0:240:120 | 0:00 | 0.0507 | 7 | 0.002 | 0.0603 | 0.0623 | 0.0614 | 0.0007 | 0 | 3 | 0.0507 | 0.0627 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9556 | 127287.345 | 44271.9257 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3779.645 | 0:240:120 | 0:00 | 0.0488 | 7 | 0.0022 | 0.0577 | 0.0599 | 0.0588 | 0.0009 | 0 | 3 | 0.0488 | 0.0602 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9559 | 127290.705 | 44271.9258 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3855.2379 | 0:240:120 | 0:00 | 0.0469 | 7 | 0.0041 | 0.0541 | 0.0582 | 0.0563 | 0.0013 | 0 | 3 | 0.0469 | 0.0579 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
9562 | 127293.938 | 44271.9258 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3932.3426 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0027 | 0.0526 | 0.0553 | 0.0541 | 0.001 | 0 | 3 | 0.045 | 0.0556 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9565 | 127297.309 | 44271.9259 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4010.9895 | 0:240:120 | 0:00 | 0.0433 | 7 | 0.0031 | 0.0506 | 0.0537 | 0.0526 | 0.0011 | 0 | 3 | 0.0433 | 0.0535 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
9568 | 127300.811 | 44271.9259 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4091.2093 | 0:240:120 | 0:00 | 0.0416 | 7 | 0.0041 | 0.0479 | 0.052 | 0.0502 | 0.0013 | 0 | 3 | 0.0416 | 0.0516 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
9571 | 127304.074 | 44271.9259 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4173.0335 | 0:240:120 | 0:00 | 0.04 | 7 | 0.0026 | 0.0468 | 0.0494 | 0.0485 | 0.001 | 0 | 3 | 0.04 | 0.05 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9574 | 127307.364 | 44271.926 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4256.4941 | 0:240:120 | 0:00 | 0.0384 | 7 | 0.0032 | 0.0447 | 0.0479 | 0.0465 | 0.0011 | 0 | 3 | 0.0384 | 0.0484 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9577 | 127310.512 | 44271.926 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4341.624 | 0:240:120 | 0:00 | 0.0369 | 7 | 0.0029 | 0.0437 | 0.0466 | 0.0451 | 0.0011 | 0 | 3 | 0.0369 | 0.0469 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9580 | 127313.701 | 44271.926 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4428.4565 | 0:240:120 | 0:00 | 0.0355 | 7 | 0.0033 | 0.0416 | 0.0449 | 0.0432 | 0.0011 | 0 | 3 | 0.0355 | 0.0455 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9583 | 127316.774 | 44271.9261 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4517.0256 | 0:240:120 | 0:00 | 0.0341 | 7 | 0.0027 | 0.0401 | 0.0428 | 0.0415 | 0.0009 | 0 | 3 | 0.0341 | 0.0441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9586 | 127319.941 | 44271.9261 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4607.3661 | 0:240:120 | 0:00 | 0.0328 | 7 | 0.0032 | 0.0381 | 0.0413 | 0.0397 | 0.0011 | 0 | 3 | 0.0328 | 0.0428 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9589 | 127323.133 | 44271.9262 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4699.5135 | 0:240:120 | 0:00 | 0.0315 | 7 | 0.0036 | 0.0367 | 0.0403 | 0.0386 | 0.0013 | 0 | 3 | 0.0315 | 0.0415 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9592 | 127326.105 | 44271.9262 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4793.5037 | 0:240:120 | 0:00 | 0.0303 | 7 | 0.0029 | 0.0358 | 0.0387 | 0.0373 | 0.001 | 0 | 3 | 0.0303 | 0.0403 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9595 | 127329.214 | 44271.9262 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4889.3738 | 0:240:120 | 0:00 | 0.0291 | 7 | 0.0022 | 0.0346 | 0.0368 | 0.0359 | 0.0009 | 0 | 3 | 0.0291 | 0.0391 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9598 | 127332.266 | 44271.9263 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4987.1613 | 0:240:120 | 0:00 | 0.028 | 7 | 0.0029 | 0.033 | 0.0359 | 0.0347 | 0.0011 | 0 | 3 | 0.028 | 0.038 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9601 | 127335.331 | 44271.9263 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5086.9045 | 0:240:120 | 0:00 | 0.0269 | 7 | 0.0033 | 0.0314 | 0.0347 | 0.0333 | 0.0013 | 0 | 3 | 0.0269 | 0.0369 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9604 | 127338.539 | 44271.9263 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5188.6426 | 0:240:120 | 0:00 | 0.0258 | 7 | 0.003 | 0.0299 | 0.0329 | 0.0321 | 0.0011 | 0 | 3 | 0.0258 | 0.0358 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9607 | 127341.669 | 44271.9264 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5292.4155 | 0:240:120 | 0:00 | 0.0248 | 7 | 0.003 | 0.029 | 0.032 | 0.0307 | 0.0012 | 0 | 3 | 0.0248 | 0.0348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9610 | 127344.865 | 44271.9264 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5398.2638 | 0:240:120 | 0:00 | 0.0239 | 7 | 0.0021 | 0.0287 | 0.0308 | 0.0302 | 0.0008 | 0 | 3 | 0.0239 | 0.0339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9613 | 127347.949 | 44271.9264 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5506.229 | 0:240:120 | 0:00 | 0.0229 | 7 | 0.0038 | 0.0266 | 0.0304 | 0.0287 | 0.0016 | 0 | 3 | 0.0229 | 0.0329 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9616 | 127351.124 | 44271.9265 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5616.3536 | 0:240:120 | 0:00 | 0.022 | 7 | 0.0021 | 0.0271 | 0.0292 | 0.0281 | 0.0007 | 0 | 3 | 0.022 | 0.032 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9619 | 127354.461 | 44271.9265 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5728.6807 | 0:240:120 | 0:00 | 0.0212 | 7 | 0.0043 | 0.025 | 0.0293 | 0.0273 | 0.0014 | 0 | 3 | 0.0212 | 0.0312 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9622 | 127357.519 | 44271.9265 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5843.2543 | 0:240:120 | 0:00 | 0.0204 | 7 | 0.003 | 0.024 | 0.027 | 0.026 | 0.0011 | 0 | 3 | 0.0204 | 0.0304 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9625 | 127360.505 | 44271.9266 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5960.1194 | 0:240:120 | 0:00 | 0.0196 | 7 | 0.0029 | 0.0237 | 0.0266 | 0.0257 | 0.0012 | 0 | 3 | 0.0196 | 0.0296 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9628 | 127363.602 | 44271.9266 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6079.3218 | 0:240:120 | 0:00 | 0.0188 | 7 | 0.0032 | 0.0231 | 0.0263 | 0.025 | 0.0013 | 0 | 3 | 0.0188 | 0.0288 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9631 | 127366.686 | 44271.9267 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6200.9082 | 0:240:120 | 0:00 | 0.0181 | 7 | 0.0025 | 0.0231 | 0.0256 | 0.0244 | 0.001 | 0 | 3 | 0.0181 | 0.0281 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9634 | 127369.86 | 44271.9267 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6324.9264 | 0:240:120 | 0:00 | 0.0174 | 7 | 0.0026 | 0.0224 | 0.025 | 0.0238 | 0.0009 | 0 | 3 | 0.0174 | 0.0274 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9637 | 127372.952 | 44271.9267 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6451.4249 | 0:240:120 | 0:00 | 0.0167 | 7 | 0.0041 | 0.0211 | 0.0252 | 0.0231 | 0.0014 | 0 | 3 | 0.0167 | 0.0267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9640 | 127376.269 | 44271.9268 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6580.4534 | 0:240:120 | 0:00 | 0.0161 | 7 | 0.0039 | 0.0199 | 0.0238 | 0.0224 | 0.0014 | 0 | 3 | 0.0161 | 0.0261 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9643 | 127379.549 | 44271.9268 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6712.0625 | 0:240:120 | 0:00 | 0.0154 | 7 | 0.0027 | 0.0203 | 0.023 | 0.0221 | 0.0011 | 0 | 3 | 0.0154 | 0.0254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9646 | 127382.55 | 44271.9268 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6846.3037 | 0:240:120 | 0:00 | 0.0148 | 7 | 0.0029 | 0.0197 | 0.0226 | 0.0214 | 0.0012 | 0 | 3 | 0.0148 | 0.0248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9649 | 127385.928 | 44271.9269 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6983.2298 | 0:240:120 | 0:00 | 0.0143 | 7 | 0.0042 | 0.0188 | 0.023 | 0.021 | 0.0014 | 0 | 3 | 0.0143 | 0.0243 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9652 | 127389.014 | 44271.9269 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7122.8944 | 0:240:120 | 0:00 | 0.0137 | 7 | 0.005 | 0.0182 | 0.0232 | 0.0206 | 0.0016 | 0 | 3 | 0.0137 | 0.0237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9655 | 127392.329 | 44271.927 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7265.3523 | 0:240:120 | 0:00 | 0.0132 | 7 | 0.0035 | 0.0181 | 0.0216 | 0.0202 | 0.0011 | 0 | 3 | 0.0132 | 0.0232 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9658 | 127395.446 | 44271.927 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7410.6593 | 0:240:120 | 0:00 | 0.0127 | 7 | 0.003 | 0.0177 | 0.0207 | 0.0194 | 0.0012 | 0 | 3 | 0.0127 | 0.0227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9661 | 127398.417 | 44271.927 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7558.8725 | 0:240:120 | 0:00 | 0.0122 | 7 | 0.0029 | 0.0181 | 0.021 | 0.0196 | 0.0011 | 0 | 3 | 0.0122 | 0.0222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9664 | 127401.745 | 44271.9271 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7710.05 | 0:240:120 | 0:00 | 0.0117 | 7 | 0.0025 | 0.018 | 0.0205 | 0.0191 | 0.0009 | 0 | 3 | 0.0117 | 0.0217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9667 | 127404.817 | 44271.9271 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7864.251 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.0017 | 0.0179 | 0.0196 | 0.0185 | 0.0006 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9670 | 127408.039 | 44271.9271 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8021.536 | 0:240:120 | 0:00 | 0.0108 | 7 | 0.0019 | 0.0179 | 0.0198 | 0.0184 | 0.0007 | 0 | 3 | 0.0108 | 0.0208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9673 | 127411.125 | 44271.9272 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8181.9667 | 0:240:120 | 0:00 | 0.0104 | 7 | 0.0023 | 0.0167 | 0.019 | 0.0179 | 0.0007 | 0 | 3 | 0.0104 | 0.0204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9676 | 127414.128 | 44271.9272 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8335.6239 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0021 | 0.0165 | 0.0186 | 0.0173 | 0.0006 | 0 | 3 | 0.01 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9679 | 127417.145 | 44271.9272 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8502.3364 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0007 | 0.0164 | 0.0171 | 0.0169 | 0.0003 | 0 | 3 | 0.0096 | 0.016 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9682 | 127420.146 | 44271.9273 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8672.3831 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0014 | 0.0155 | 0.0169 | 0.0163 | 0.0006 | 0 | 3 | 0.0092 | 0.016 | NP | NP | 1-0-0-1-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
9685 | 127423.216 | 44271.9273 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8845.8308 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0026 | 0.0148 | 0.0174 | 0.0162 | 0.001 | 0 | 3 | 0.0089 | 0.016 | NP | NP | 1-1-0-1-0-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
9688 | 127426.192 | 44271.9273 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9022.7474 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0029 | 0.0148 | 0.0177 | 0.0159 | 0.0012 | 0 | 3 | 0.0085 | 0.016 | P | NP | 1-1-0-1-1-0-1-0-0 | NP | 0-0-0-0-0-0-0-0-0
9691 | 127429.112 | 44271.9274 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9203.2023 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0029 | 0.014 | 0.0169 | 0.0156 | 0.0009 | 0 | 3 | 0.0082 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
9694 | 127432.054 | 44271.9274 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9387.2664 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0053 | 0.0124 | 0.0177 | 0.0153 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
9697 | 127435.377 | 44271.9275 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9575.0117 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0044 | 0.0128 | 0.0172 | 0.0147 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
9700 | 127438.465 | 44271.9275 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9766.5119 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0052 | 0.012 | 0.0172 | 0.0143 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
9703 | 127441.548 | 44271.9275 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9961.8422 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0042 | 0.0125 | 0.0167 | 0.0143 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
9706 | 127444.715 | 44271.9276 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10161.079 | 0:240:120 | 0:00 | 0.0067 | 7 | 0.0046 | 0.0118 | 0.0164 | 0.0141 | 0.0018 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
9709 | 127447.801 | 44271.9276 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10364.3006 | 0:240:120 | 0:00 | 0.0065 | 7 | 0.0045 | 0.0112 | 0.0157 | 0.0136 | 0.0017 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9712 | 127450.865 | 44271.9276 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10571.5866 | 0:240:120 | 0:00 | 0.0062 | 7 | 0.0055 | 0.0114 | 0.0169 | 0.0137 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
9715 | 127453.955 | 44271.9277 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10783.0184 | 0:240:120 | 0:00 | 0.006 | 7 | 0.004 | 0.0118 | 0.0158 | 0.0138 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9718 | 127456.942 | 44271.9277 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10998.6787 | 0:240:120 | 0:00 | 0.0057 | 7 | 0.004 | 0.0117 | 0.0157 | 0.0137 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9721 | 127460.357 | 44271.9277 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11218.6523 | 0:240:120 | 0:00 | 0.0055 | 7 | 0.004 | 0.012 | 0.016 | 0.0138 | 0.0014 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9724 | 127463.532 | 44271.9278 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11443.0253 | 0:240:120 | 0:00 | 0.0053 | 7 | 0.0056 | 0.011 | 0.0166 | 0.0134 | 0.002 | 0 | 3 | 0.008 | 0.016 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
9727 | 127466.518 | 44271.9278 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11671.8859 | 0:240:120 | 0:00 | 0.0051 | 7 | 0.0049 | 0.0108 | 0.0157 | 0.0134 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9730 | 127469.644 | 44271.9278 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11905.3236 | 0:240:120 | 0:00 | 0.0049 | 7 | 0.0056 | 0.0104 | 0.016 | 0.0131 | 0.0021 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9733 | 127833.241 | 44271.9321 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 248.3 | 0:240:120 | 0:00 | 44.7577 | 7 | 71.1508 | 339.1123 | 410.2631 | 359.0805 | 29.4876 | 869.5177 | 3 | 44.7577 | 182.7372 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9736 | 128923.16 | 44271.9447 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 253.2 | 0:240:120 | 0:00 | 38.6376 | 7 | 64.029 | 207.0926 | 271.1216 | 227.8403 | 31.1329 | 969.2565 | 3 | 38.6376 | 119.9196 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9739 | 129538.779 | 44271.9518 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 258.3 | 0:240:120 | 0:00 | 33.74 | 7 | 0.0175 | 71.6745 | 71.692 | 71.6793 | 0.0056 | 0 | 3 | 33.74 | 87.858 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9742 | 129749.378 | 44271.9542 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 263.5 | 0:240:120 | 0:00 | 29.8098 | 7 | 3.4854 | 60.7005 | 64.1859 | 63.0545 | 1.6951 | 2.8733 | 3 | 29.8098 | 68.7416 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9745 | 129937.531 | 44271.9564 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 268.8 | 0:240:120 | 0:00 | 26.5893 | 7 | 3.7459 | 52.946 | 56.6919 | 54.3959 | 1.7533 | 3.0742 | 3 | 26.5893 | 56.0593 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
9748 | 130103.285 | 44271.9583 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 274.1 | 0:240:120 | 0:00 | 23.9504 | 7 | 3.7511 | 45.4472 | 49.1983 | 46.6996 | 1.8736 | 3.5105 | 3 | 23.9504 | 47.1814 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
9751 | 130242.669 | 44271.9599 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 279.6 | 0:240:120 | 0:00 | 21.6738 | 7 | 0.4734 | 37.486 | 37.9594 | 37.8281 | 0.2023 | 0.0409 | 3 | 21.6738 | 40.4085 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9754 | 130354.45 | 44271.9612 | Vista Speed | T | 100T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 285.2 | 0:240:120 | 0:00 | 19.7263 | 7 | 1.2399 | 31.7331 | 32.973 | 32.2446 | 0.5658 | 0.3202 | 3 | 19.7263 | 35.1656 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9757 | 131197.628 | 44271.971 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 330 | 0:240:120 | 0:00 | 74.299 | 7 | 69.8794 | 703.2331 | 773.1125 | 730.6382 | 32.3129 | 1044.1216 | 3 | 74.299 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9760 | 133380.097 | 44271.9963 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 336.6 | 0:240:120 | 0:00 | 60.3332 | 7 | 69.9532 | 563.4012 | 633.3544 | 591.2793 | 32.1585 | 1034.1671 | 3 | 60.3332 | 788.682 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9763 | 135143.062 | 44272.0167 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 343.332 | 0:240:120 | 0:00 | 50.4807 | 7 | 69.889 | 423.6141 | 493.5031 | 447.3892 | 34.5995 | 1197.1269 | 3 | 50.4807 | 255.3629 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9766 | 136486.797 | 44272.0322 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 350.1986 | 0:240:120 | 0:00 | 43.162 | 7 | 69.8706 | 283.9012 | 353.7718 | 307.1948 | 34.9319 | 1220.2353 | 3 | 43.162 | 150.0244 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9769 | 137369.739 | 44272.0424 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 357.2026 | 0:240:120 | 0:00 | 37.5146 | 7 | 29.0968 | 144.1686 | 173.2654 | 153.4013 | 13.869 | 192.3483 | 3 | 37.5146 | 105.0354 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
9772 | 137786.358 | 44272.0473 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 364.3467 | 0:240:120 | 0:00 | 33.0275 | 7 | 2.1147 | 68.3303 | 70.445 | 70.0223 | 0.7317 | 0.5354 | 3 | 33.0275 | 80.0956 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9775 | 137993.166 | 44272.0496 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 371.6336 | 0:240:120 | 0:00 | 29.3788 | 7 | 3.8707 | 58.8403 | 62.711 | 61.4197 | 1.9333 | 3.7377 | 3 | 29.3788 | 64.2541 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9778 | 138176.658 | 44272.0518 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 379.0663 | 0:240:120 | 0:00 | 26.3555 | 7 | 3.8686 | 51.1072 | 54.9758 | 53.5752 | 1.8596 | 3.4579 | 3 | 26.3555 | 53.3067 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
9781 | 138336.565 | 44272.0536 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 386.6476 | 0:240:120 | 0:00 | 23.8113 | 7 | 3.7933 | 43.3695 | 47.1628 | 44.5915 | 1.833 | 3.3599 | 3 | 23.8113 | 45.2938 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
9784 | 138469.157 | 44272.0552 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 394.3805 | 0:240:120 | 0:00 | 21.6419 | 7 | 1.2823 | 34.3564 | 35.6387 | 35.2104 | 0.6397 | 0.4092 | 3 | 21.6419 | 39.1787 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9787 | 138576.535 | 44272.0564 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 402.2682 | 0:240:120 | 0:00 | 19.7716 | 7 | 1.2835 | 31.7939 | 33.0774 | 32.2425 | 0.626 | 0.3918 | 3 | 19.7716 | 34.3618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9790 | 138674.881 | 44272.0575 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 410.3135 | 0:240:120 | 0:00 | 18.1434 | 7 | 1.2835 | 27.9525 | 29.236 | 28.8069 | 0.64 | 0.4096 | 3 | 18.1434 | 30.4716 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9793 | 138762.942 | 44272.0586 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 418.5198 | 0:240:120 | 0:00 | 16.7143 | 7 | 1.2842 | 25.3901 | 26.6743 | 25.9993 | 0.5577 | 0.311 | 3 | 16.7143 | 27.2664 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9796 | 138842.383 | 44272.0595 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 426.8902 | 0:240:120 | 0:00 | 15.4506 | 7 | 0.6345 | 22.1974 | 22.8319 | 22.6195 | 0.3165 | 0.1002 | 3 | 15.4506 | 24.5817 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9799 | 138912.552 | 44272.0603 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 435.428 | 0:240:120 | 0:00 | 14.3259 | 7 | 0.6366 | 20.9256 | 21.5622 | 21.1382 | 0.3174 | 0.1007 | 3 | 14.3259 | 22.3015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9802 | 138978.261 | 44272.061 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 444.1366 | 0:240:120 | 0:00 | 13.3193 | 7 | 0.6342 | 19.0232 | 19.6574 | 19.4451 | 0.3162 | 0.1 | 3 | 13.3193 | 20.3423 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9805 | 139038.492 | 44272.0617 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 453.0193 | 0:240:120 | 0:00 | 12.4135 | 7 | 0.6351 | 17.119 | 17.7541 | 17.5417 | 0.3168 | 0.1004 | 3 | 12.4135 | 18.6418 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9808 | 139093.413 | 44272.0624 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 462.0797 | 0:240:120 | 0:00 | 11.5948 | 7 | 0.754 | 15.7304 | 16.4844 | 16.108 | 0.3247 | 0.1054 | 3 | 11.5948 | 17.1529 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9811 | 139144.703 | 44272.063 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 471.3213 | 0:240:120 | 0:00 | 10.8517 | 7 | 0.5022 | 14.8506 | 15.3528 | 15.0736 | 0.2172 | 0.0472 | 3 | 10.8517 | 15.8394 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9814 | 139192.475 | 44272.0635 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 480.7477 | 0:240:120 | 0:00 | 10.1745 | 7 | 0.3787 | 13.8439 | 14.2226 | 14.0726 | 0.1739 | 0.0302 | 3 | 10.1745 | 14.6727 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9817 | 139236.89 | 44272.064 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 490.3626 | 0:240:120 | 0:00 | 9.5554 | 7 | 0.3777 | 12.714 | 13.0917 | 12.9585 | 0.1837 | 0.0338 | 3 | 9.5554 | 13.6302 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9820 | 139278.345 | 44272.0645 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 500.1699 | 0:240:120 | 0:00 | 8.9876 | 7 | 0.2511 | 11.9669 | 12.218 | 12.1332 | 0.1242 | 0.0154 | 3 | 8.9876 | 12.6937 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9823 | 139317.321 | 44272.065 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 510.1733 | 0:240:120 | 0:00 | 8.4653 | 7 | 0.3766 | 11.0965 | 11.4731 | 11.3284 | 0.1697 | 0.0288 | 3 | 8.4653 | 11.8485 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9826 | 139353.858 | 44272.0654 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 520.3768 | 0:240:120 | 0:00 | 7.9835 | 7 | 0.498 | 10.2294 | 10.7274 | 10.4865 | 0.2165 | 0.0469 | 3 | 7.9835 | 11.0822 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9829 | 139388.597 | 44272.0658 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 530.7843 | 0:240:120 | 0:00 | 7.538 | 7 | 0.351 | 9.7045 | 10.0555 | 9.8793 | 0.1513 | 0.0229 | 3 | 7.538 | 10.3849 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9832 | 139421.195 | 44272.0662 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 541.4 | 0:240:120 | 0:00 | 7.1252 | 7 | 0.301 | 9.1786 | 9.4796 | 9.33 | 0.1221 | 0.0149 | 3 | 7.1252 | 9.748 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9835 | 139451.931 | 44272.0665 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 552.228 | 0:240:120 | 0:00 | 6.7419 | 7 | 0.25 | 8.5799 | 8.8299 | 8.7513 | 0.1158 | 0.0134 | 3 | 6.7419 | 9.1644 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9838 | 139480.99 | 44272.0669 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 563.2725 | 0:240:120 | 0:00 | 6.3851 | 7 | 0.2604 | 8.0884 | 8.3488 | 8.218 | 0.1125 | 0.0127 | 3 | 6.3851 | 8.628 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9841 | 139508.463 | 44272.0672 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 574.538 | 0:240:120 | 0:00 | 6.0526 | 7 | 0.1419 | 7.7002 | 7.8421 | 7.7873 | 0.0651 | 0.0042 | 3 | 6.0526 | 8.1338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9844 | 139534.522 | 44272.0675 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 586.0287 | 0:240:120 | 0:00 | 5.7421 | 7 | 0.2601 | 7.1804 | 7.4405 | 7.3098 | 0.1118 | 0.0125 | 3 | 5.7421 | 7.6771 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9847 | 139559.469 | 44272.0678 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 597.7493 | 0:240:120 | 0:00 | 5.4517 | 7 | 0.1523 | 6.8299 | 6.9822 | 6.9363 | 0.0685 | 0.0047 | 3 | 5.4517 | 7.2542 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9850 | 139583.17 | 44272.0681 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 609.7043 | 0:240:120 | 0:00 | 5.1797 | 7 | 0.1989 | 6.4846 | 6.6835 | 6.5834 | 0.0857 | 0.0073 | 3 | 5.1797 | 6.8617 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9853 | 139605.734 | 44272.0683 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 621.8984 | 0:240:120 | 0:00 | 4.9246 | 7 | 0.178 | 6.1079 | 6.2859 | 6.1927 | 0.077 | 0.0059 | 3 | 4.9246 | 6.4967 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9856 | 139627.11 | 44272.0686 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 634.3364 | 0:240:120 | 0:00 | 4.685 | 7 | 0.1564 | 5.7941 | 5.9505 | 5.892 | 0.074 | 0.0055 | 3 | 4.685 | 6.1567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9859 | 139648.187 | 44272.0688 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 647.0231 | 0:240:120 | 0:00 | 4.4597 | 7 | 0.159 | 5.4815 | 5.6405 | 5.5855 | 0.0778 | 0.0061 | 3 | 4.4597 | 5.8394 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9862 | 139667.843 | 44272.069 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 659.9636 | 0:240:120 | 0:00 | 4.2476 | 7 | 0.1271 | 5.2129 | 5.34 | 5.2968 | 0.0621 | 0.0039 | 3 | 4.2476 | 5.5427 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9865 | 139686.547 | 44272.0692 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 673.1628 | 0:240:120 | 0:00 | 4.0477 | 7 | 0.1277 | 4.9591 | 5.0868 | 5.0434 | 0.0626 | 0.0039 | 3 | 4.0477 | 5.265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9868 | 139704.912 | 44272.0695 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 686.6261 | 0:240:120 | 0:00 | 3.8591 | 7 | 0.1154 | 4.7172 | 4.8326 | 4.7863 | 0.0523 | 0.0027 | 3 | 3.8591 | 5.0046 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9871 | 139722.529 | 44272.0697 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 700.3586 | 0:240:120 | 0:00 | 3.681 | 7 | 0.1041 | 4.5105 | 4.6146 | 4.5613 | 0.0446 | 0.002 | 3 | 3.681 | 4.7602 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9874 | 139739.305 | 44272.0699 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 714.3658 | 0:240:120 | 0:00 | 3.5128 | 7 | 0.1037 | 4.3019 | 4.4056 | 4.353 | 0.0446 | 0.002 | 3 | 3.5128 | 4.5304 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9877 | 139755.272 | 44272.07 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 728.6531 | 0:240:120 | 0:00 | 3.3535 | 7 | 0.0878 | 4.0772 | 4.165 | 4.1344 | 0.0425 | 0.0018 | 3 | 3.3535 | 4.3142 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9880 | 139770.489 | 44272.0702 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 743.2262 | 0:240:120 | 0:00 | 3.2028 | 7 | 0.0865 | 3.9034 | 3.9899 | 3.9462 | 0.0372 | 0.0014 | 3 | 3.2028 | 4.1105 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9883 | 139785.483 | 44272.0704 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 758.0907 | 0:240:120 | 0:00 | 3.06 | 7 | 0.0866 | 3.7075 | 3.7941 | 3.7592 | 0.0387 | 0.0015 | 3 | 3.06 | 3.9184 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9886 | 139799.539 | 44272.0706 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 773.2525 | 0:240:120 | 0:00 | 2.9246 | 7 | 0.0887 | 3.5454 | 3.6341 | 3.5942 | 0.035 | 0.0012 | 3 | 2.9246 | 3.737 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9889 | 139813.189 | 44272.0707 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 788.7175 | 0:240:120 | 0:00 | 2.7962 | 7 | 0.0615 | 3.3898 | 3.4513 | 3.4198 | 0.0264 | 0.0007 | 3 | 2.7962 | 3.5657 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9892 | 139826.32 | 44272.0709 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 804.4919 | 0:240:120 | 0:00 | 2.6742 | 7 | 0.0629 | 3.233 | 3.2959 | 3.2655 | 0.0269 | 0.0007 | 3 | 2.6742 | 3.4036 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9895 | 139839.105 | 44272.071 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 820.5817 | 0:240:120 | 0:00 | 2.5583 | 7 | 0.0591 | 3.0862 | 3.1453 | 3.118 | 0.0249 | 0.0006 | 3 | 2.5583 | 3.2502 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9898 | 139851.467 | 44272.0712 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 836.9934 | 0:240:120 | 0:00 | 2.4482 | 7 | 0.0565 | 2.9509 | 3.0074 | 2.982 | 0.0243 | 0.0006 | 3 | 2.4482 | 3.105 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9901 | 139863.586 | 44272.0713 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 853.7332 | 0:240:120 | 0:00 | 2.3434 | 7 | 0.0468 | 2.8227 | 2.8695 | 2.8461 | 0.0198 | 0.0004 | 3 | 2.3434 | 2.9672 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9904 | 139875.084 | 44272.0714 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 870.8079 | 0:240:120 | 0:00 | 2.2437 | 7 | 0.0553 | 2.6985 | 2.7538 | 2.7281 | 0.0222 | 0.0005 | 3 | 2.2437 | 2.8366 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9907 | 139886.109 | 44272.0716 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 888.2241 | 0:240:120 | 0:00 | 2.1488 | 7 | 0.0614 | 2.5748 | 2.6362 | 2.6082 | 0.0265 | 0.0007 | 3 | 2.1488 | 2.7126 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9910 | 139896.925 | 44272.0717 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 905.9885 | 0:240:120 | 0:00 | 2.0584 | 7 | 0.0417 | 2.4717 | 2.5134 | 2.4933 | 0.0177 | 0.0003 | 3 | 2.0584 | 2.5948 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9913 | 139907.48 | 44272.0718 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 924.1083 | 0:240:120 | 0:00 | 1.9722 | 7 | 0.0558 | 2.3587 | 2.4145 | 2.3887 | 0.0236 | 0.0006 | 3 | 1.9722 | 2.4829 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9916 | 139917.372 | 44272.0719 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 942.5905 | 0:240:120 | 0:00 | 1.89 | 7 | 0.0496 | 2.2556 | 2.3052 | 2.2828 | 0.0198 | 0.0004 | 3 | 1.89 | 2.3764 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9919 | 139927.178 | 44272.072 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 961.4423 | 0:240:120 | 0:00 | 1.8117 | 7 | 0.0443 | 2.1703 | 2.2146 | 2.192 | 0.0182 | 0.0003 | 3 | 1.8117 | 2.2751 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9922 | 139937.03 | 44272.0721 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 980.6711 | 0:240:120 | 0:00 | 1.7369 | 7 | 0.046 | 2.0759 | 2.1219 | 2.1002 | 0.0195 | 0.0004 | 3 | 1.7369 | 2.1787 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9925 | 139946.339 | 44272.0723 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1000.2845 | 0:240:120 | 0:00 | 1.6655 | 7 | 0.0425 | 1.9901 | 2.0326 | 2.0133 | 0.0183 | 0.0003 | 3 | 1.6655 | 2.0869 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9928 | 139955.222 | 44272.0724 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1020.2902 | 0:240:120 | 0:00 | 1.5974 | 7 | 0.0394 | 1.9085 | 1.9479 | 1.9284 | 0.0163 | 0.0003 | 3 | 1.5974 | 1.9994 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9931 | 139964.254 | 44272.0725 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1040.696 | 0:240:120 | 0:00 | 1.5322 | 7 | 0.0381 | 1.8197 | 1.8578 | 1.8405 | 0.0163 | 0.0003 | 3 | 1.5322 | 1.916 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9934 | 139972.772 | 44272.0726 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1061.51 | 0:240:120 | 0:00 | 1.47 | 7 | 0.0351 | 1.7496 | 1.7847 | 1.7684 | 0.0151 | 0.0002 | 3 | 1.47 | 1.8364 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9937 | 139981.071 | 44272.0727 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1082.7402 | 0:240:120 | 0:00 | 1.4106 | 7 | 0.0422 | 1.6727 | 1.7149 | 1.6953 | 0.0176 | 0.0003 | 3 | 1.4106 | 1.7605 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9940 | 139989.178 | 44272.0727 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1104.395 | 0:240:120 | 0:00 | 1.3537 | 7 | 0.0304 | 1.6109 | 1.6413 | 1.6273 | 0.0132 | 0.0002 | 3 | 1.3537 | 1.688 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9943 | 139996.941 | 44272.0728 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1126.4829 | 0:240:120 | 0:00 | 1.2993 | 7 | 0.0279 | 1.5434 | 1.5713 | 1.5586 | 0.012 | 0.0001 | 3 | 1.2993 | 1.6189 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9946 | 140004.538 | 44272.0729 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1149.0125 | 0:240:120 | 0:00 | 1.2473 | 7 | 0.0283 | 1.481 | 1.5093 | 1.4943 | 0.0111 | 0.0001 | 3 | 1.2473 | 1.5528 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9949 | 140012.158 | 44272.073 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1171.9928 | 0:240:120 | 0:00 | 1.1975 | 7 | 0.0298 | 1.4188 | 1.4486 | 1.4347 | 0.0121 | 0.0001 | 3 | 1.1975 | 1.4897 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9952 | 140019.346 | 44272.0731 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1195.4326 | 0:240:120 | 0:00 | 1.1498 | 7 | 0.0238 | 1.3653 | 1.3891 | 1.3778 | 0.0099 | 0.0001 | 3 | 1.1498 | 1.4293 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9955 | 140026.24 | 44272.0732 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1219.3413 | 0:240:120 | 0:00 | 1.1042 | 7 | 0.0434 | 1.2912 | 1.3346 | 1.3178 | 0.0169 | 0.0003 | 3 | 1.1042 | 1.3716 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9958 | 140033.053 | 44272.0733 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1243.7281 | 0:240:120 | 0:00 | 1.0605 | 7 | 0.0473 | 1.2387 | 1.286 | 1.2647 | 0.0147 | 0.0002 | 3 | 1.0605 | 1.3165 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9961 | 140039.861 | 44272.0733 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1268.6027 | 0:240:120 | 0:00 | 1.0186 | 7 | 0.032 | 1.1961 | 1.2281 | 1.2141 | 0.0111 | 0.0001 | 3 | 1.0186 | 1.2637 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9964 | 140046.278 | 44272.0734 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1293.9747 | 0:240:120 | 0:00 | 0.9785 | 7 | 0.0437 | 1.1507 | 1.1944 | 1.1692 | 0.0121 | 0.0001 | 3 | 0.9785 | 1.2132 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9967 | 140052.773 | 44272.0735 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1319.8542 | 0:240:120 | 0:00 | 0.9401 | 7 | 0.0248 | 1.1015 | 1.1263 | 1.1178 | 0.009 | 0.0001 | 3 | 0.9401 | 1.1649 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9970 | 140059.094 | 44272.0736 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1346.2513 | 0:240:120 | 0:00 | 0.9032 | 7 | 0.0375 | 1.056 | 1.0935 | 1.0778 | 0.0133 | 0.0002 | 3 | 0.9032 | 1.1186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9973 | 140065.055 | 44272.0736 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1373.1763 | 0:240:120 | 0:00 | 0.8679 | 7 | 0.0395 | 1.008 | 1.0475 | 1.0298 | 0.0131 | 0.0002 | 3 | 0.8679 | 1.0743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9976 | 140071.03 | 44272.0737 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1400.6399 | 0:240:120 | 0:00 | 0.834 | 7 | 0.0353 | 0.9713 | 1.0066 | 0.9896 | 0.0121 | 0.0001 | 3 | 0.834 | 1.0318 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9979 | 140076.962 | 44272.0738 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1428.6526 | 0:240:120 | 0:00 | 0.8016 | 7 | 0.0333 | 0.9359 | 0.9692 | 0.9527 | 0.0119 | 0.0001 | 3 | 0.8016 | 0.9912 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9982 | 140082.609 | 44272.0738 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1457.2257 | 0:240:120 | 0:00 | 0.7704 | 7 | 0.0245 | 0.8996 | 0.9241 | 0.912 | 0.0094 | 0.0001 | 3 | 0.7704 | 0.9522 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9985 | 140088.353 | 44272.0739 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1486.3702 | 0:240:120 | 0:00 | 0.7406 | 7 | 0.0235 | 0.8672 | 0.8907 | 0.8793 | 0.0086 | 0.0001 | 3 | 0.7406 | 0.9149 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9988 | 140093.959 | 44272.074 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1516.0976 | 0:240:120 | 0:00 | 0.7119 | 7 | 0.0188 | 0.8343 | 0.8531 | 0.8446 | 0.0073 | 0.0001 | 3 | 0.7119 | 0.8791 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9991 | 140099.493 | 44272.074 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1546.4196 | 0:240:120 | 0:00 | 0.6844 | 7 | 0.0142 | 0.8057 | 0.8199 | 0.8117 | 0.0051 | 0 | 3 | 0.6844 | 0.8447 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9994 | 140104.997 | 44272.0741 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1577.348 | 0:240:120 | 0:00 | 0.658 | 7 | 0.024 | 0.7651 | 0.7891 | 0.7779 | 0.0088 | 0.0001 | 3 | 0.658 | 0.8118 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
9997 | 140110.615 | 44272.0742 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1608.8949 | 0:240:120 | 0:00 | 0.6326 | 7 | 0.0176 | 0.7406 | 0.7582 | 0.7494 | 0.0065 | 0 | 3 | 0.6326 | 0.7803 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10000 | 140115.692 | 44272.0742 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1641.0728 | 0:240:120 | 0:00 | 0.6083 | 7 | 0.0244 | 0.7069 | 0.7313 | 0.72 | 0.0074 | 0.0001 | 3 | 0.6083 | 0.75 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10003 | 140120.836 | 44272.0743 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1673.8943 | 0:240:120 | 0:00 | 0.585 | 7 | 0.018 | 0.6822 | 0.7002 | 0.6923 | 0.0065 | 0 | 3 | 0.585 | 0.7209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10006 | 140125.801 | 44272.0743 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1707.3722 | 0:240:120 | 0:00 | 0.5625 | 7 | 0.0161 | 0.6566 | 0.6727 | 0.665 | 0.0054 | 0 | 3 | 0.5625 | 0.6931 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10009 | 140130.912 | 44272.0744 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1741.5196 | 0:240:120 | 0:00 | 0.541 | 7 | 0.0146 | 0.6331 | 0.6477 | 0.6405 | 0.0046 | 0 | 3 | 0.541 | 0.6663 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10012 | 140135.669 | 44272.0744 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1776.35 | 0:240:120 | 0:00 | 0.5203 | 7 | 0.0138 | 0.6079 | 0.6217 | 0.6151 | 0.005 | 0 | 3 | 0.5203 | 0.6407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10015 | 140140.406 | 44272.0745 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1811.877 | 0:240:120 | 0:00 | 0.5005 | 7 | 0.0135 | 0.5863 | 0.5998 | 0.5943 | 0.0047 | 0 | 3 | 0.5005 | 0.616 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10018 | 140145.278 | 44272.0746 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1848.1145 | 0:240:120 | 0:00 | 0.4814 | 7 | 0.0113 | 0.563 | 0.5743 | 0.5689 | 0.0043 | 0 | 3 | 0.4814 | 0.5923 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10021 | 140149.934 | 44272.0746 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1885.0768 | 0:240:120 | 0:00 | 0.463 | 7 | 0.0162 | 0.5403 | 0.5565 | 0.5473 | 0.005 | 0 | 3 | 0.463 | 0.5696 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10024 | 140154.491 | 44272.0747 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1922.7784 | 0:240:120 | 0:00 | 0.4454 | 7 | 0.0148 | 0.5187 | 0.5335 | 0.527 | 0.0049 | 0 | 3 | 0.4454 | 0.5478 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10027 | 140159.064 | 44272.0747 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1961.2339 | 0:240:120 | 0:00 | 0.4285 | 7 | 0.0126 | 0.5009 | 0.5135 | 0.5065 | 0.0052 | 0 | 3 | 0.4285 | 0.5269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10030 | 140163.735 | 44272.0748 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2000.4586 | 0:240:120 | 0:00 | 0.4122 | 7 | 0.0115 | 0.4808 | 0.4923 | 0.4869 | 0.0036 | 0 | 3 | 0.4122 | 0.5067 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10033 | 140168.327 | 44272.0748 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2040.4678 | 0:240:120 | 0:00 | 0.3966 | 7 | 0.0113 | 0.4639 | 0.4752 | 0.4686 | 0.0041 | 0 | 3 | 0.3966 | 0.4874 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10036 | 140172.823 | 44272.0749 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2081.2771 | 0:240:120 | 0:00 | 0.3816 | 7 | 0.0121 | 0.446 | 0.4581 | 0.4511 | 0.0039 | 0 | 3 | 0.3816 | 0.4688 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10039 | 140177.317 | 44272.0749 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2122.9027 | 0:240:120 | 0:00 | 0.3671 | 7 | 0.0099 | 0.4269 | 0.4368 | 0.4324 | 0.0036 | 0 | 3 | 0.3671 | 0.451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10042 | 140181.499 | 44272.075 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2165.3607 | 0:240:120 | 0:00 | 0.3533 | 7 | 0.0125 | 0.4108 | 0.4233 | 0.4172 | 0.0047 | 0 | 3 | 0.3533 | 0.4339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10045 | 140185.717 | 44272.075 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2208.6679 | 0:240:120 | 0:00 | 0.3399 | 7 | 0.0077 | 0.3977 | 0.4054 | 0.4011 | 0.0028 | 0 | 3 | 0.3399 | 0.4174 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10048 | 140189.891 | 44272.0751 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2252.8413 | 0:240:120 | 0:00 | 0.3271 | 7 | 0.0089 | 0.38 | 0.3889 | 0.3853 | 0.003 | 0 | 3 | 0.3271 | 0.4015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10051 | 140195.34 | 44272.0751 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2297.8981 | 0:240:120 | 0:00 | 0.3147 | 7 | 0.009 | 0.3654 | 0.3744 | 0.3703 | 0.003 | 0 | 3 | 0.3147 | 0.3863 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10054 | 140199.388 | 44272.0752 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2343.8561 | 0:240:120 | 0:00 | 0.3029 | 7 | 0.0113 | 0.3516 | 0.3629 | 0.3567 | 0.0034 | 0 | 3 | 0.3029 | 0.3717 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10057 | 140203.757 | 44272.0752 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2390.7332 | 0:240:120 | 0:00 | 0.2915 | 7 | 0.0053 | 0.3422 | 0.3475 | 0.3447 | 0.0018 | 0 | 3 | 0.2915 | 0.3576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10060 | 140208.04 | 44272.0753 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2438.5479 | 0:240:120 | 0:00 | 0.2805 | 7 | 0.0088 | 0.3279 | 0.3367 | 0.331 | 0.003 | 0 | 3 | 0.2805 | 0.3441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10063 | 140212.006 | 44272.0753 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2487.3188 | 0:240:120 | 0:00 | 0.27 | 7 | 0.0082 | 0.3153 | 0.3235 | 0.3184 | 0.003 | 0 | 3 | 0.27 | 0.3311 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10066 | 140215.848 | 44272.0754 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2537.0652 | 0:240:120 | 0:00 | 0.2598 | 7 | 0.0094 | 0.3016 | 0.311 | 0.3059 | 0.0036 | 0 | 3 | 0.2598 | 0.3186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10069 | 140219.637 | 44272.0754 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2587.8065 | 0:240:120 | 0:00 | 0.2501 | 7 | 0.0064 | 0.2907 | 0.2971 | 0.294 | 0.002 | 0 | 3 | 0.2501 | 0.3066 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10072 | 140223.607 | 44272.0755 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2639.5627 | 0:240:120 | 0:00 | 0.2407 | 7 | 0.0063 | 0.2809 | 0.2872 | 0.2837 | 0.0022 | 0 | 3 | 0.2407 | 0.2951 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10075 | 140227.467 | 44272.0755 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2692.3539 | 0:240:120 | 0:00 | 0.2317 | 7 | 0.0063 | 0.2701 | 0.2764 | 0.273 | 0.0022 | 0 | 3 | 0.2317 | 0.284 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10078 | 140231.325 | 44272.0756 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2746.201 | 0:240:120 | 0:00 | 0.223 | 7 | 0.0062 | 0.2603 | 0.2665 | 0.2624 | 0.0019 | 0 | 3 | 0.223 | 0.2733 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10081 | 140235.091 | 44272.0756 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2801.125 | 0:240:120 | 0:00 | 0.2146 | 7 | 0.0077 | 0.2489 | 0.2566 | 0.2528 | 0.0025 | 0 | 3 | 0.2146 | 0.263 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10084 | 140239.037 | 44272.0756 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2857.1475 | 0:240:120 | 0:00 | 0.2066 | 7 | 0.0037 | 0.2414 | 0.2451 | 0.2432 | 0.0013 | 0 | 3 | 0.2066 | 0.2532 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10087 | 140243.104 | 44272.0757 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2914.2905 | 0:240:120 | 0:00 | 0.1989 | 7 | 0.0052 | 0.2315 | 0.2367 | 0.2333 | 0.0018 | 0 | 3 | 0.1989 | 0.2436 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10090 | 140246.828 | 44272.0757 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2972.5763 | 0:240:120 | 0:00 | 0.1914 | 7 | 0.0052 | 0.2239 | 0.2291 | 0.2259 | 0.0018 | 0 | 3 | 0.1914 | 0.2345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10093 | 140250.697 | 44272.0758 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3032.0278 | 0:240:120 | 0:00 | 0.1843 | 7 | 0.0055 | 0.2141 | 0.2196 | 0.2164 | 0.0022 | 0 | 3 | 0.1843 | 0.2257 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10096 | 140254.61 | 44272.0758 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3092.6683 | 0:240:120 | 0:00 | 0.1774 | 7 | 0.005 | 0.2069 | 0.2119 | 0.2088 | 0.0019 | 0 | 3 | 0.1774 | 0.2173 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10099 | 140258.451 | 44272.0759 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3154.5217 | 0:240:120 | 0:00 | 0.1707 | 7 | 0.0043 | 0.199 | 0.2033 | 0.2009 | 0.0017 | 0 | 3 | 0.1707 | 0.2091 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10102 | 140262.004 | 44272.0759 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3217.6121 | 0:240:120 | 0:00 | 0.1644 | 7 | 0.0057 | 0.1914 | 0.1971 | 0.1938 | 0.0023 | 0 | 3 | 0.1644 | 0.2013 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10105 | 140265.389 | 44272.0759 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3281.9644 | 0:240:120 | 0:00 | 0.1582 | 7 | 0.0053 | 0.1844 | 0.1897 | 0.1859 | 0.002 | 0 | 3 | 0.1582 | 0.1938 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10108 | 140268.923 | 44272.076 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3347.6037 | 0:240:120 | 0:00 | 0.1523 | 7 | 0.0045 | 0.1774 | 0.1819 | 0.1795 | 0.0014 | 0 | 3 | 0.1523 | 0.1865 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10111 | 140272.469 | 44272.076 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3414.5557 | 0:240:120 | 0:00 | 0.1467 | 7 | 0.0036 | 0.1705 | 0.1741 | 0.1722 | 0.0014 | 0 | 3 | 0.1467 | 0.1795 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10114 | 140275.856 | 44272.0761 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3482.8469 | 0:240:120 | 0:00 | 0.1412 | 7 | 0.0038 | 0.1646 | 0.1684 | 0.1662 | 0.0016 | 0 | 3 | 0.1412 | 0.1728 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10117 | 140279.599 | 44272.0761 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3552.5038 | 0:240:120 | 0:00 | 0.1359 | 7 | 0.004 | 0.1579 | 0.1619 | 0.1601 | 0.0013 | 0 | 3 | 0.1359 | 0.1664 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10120 | 140283.014 | 44272.0762 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3623.5539 | 0:240:120 | 0:00 | 0.1309 | 7 | 0.0036 | 0.1529 | 0.1565 | 0.1542 | 0.0015 | 0 | 3 | 0.1309 | 0.1602 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10123 | 140286.65 | 44272.0762 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3696.025 | 0:240:120 | 0:00 | 0.126 | 7 | 0.0046 | 0.1463 | 0.1509 | 0.1482 | 0.0016 | 0 | 3 | 0.126 | 0.1542 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10126 | 140290.075 | 44272.0762 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3769.9455 | 0:240:120 | 0:00 | 0.1213 | 7 | 0.0035 | 0.1408 | 0.1443 | 0.1423 | 0.0014 | 0 | 3 | 0.1213 | 0.1484 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10129 | 140293.451 | 44272.0763 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3845.3444 | 0:240:120 | 0:00 | 0.1168 | 7 | 0.0036 | 0.1359 | 0.1395 | 0.1375 | 0.0012 | 0 | 3 | 0.1168 | 0.1429 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10132 | 140296.976 | 44272.0763 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3922.2512 | 0:240:120 | 0:00 | 0.1124 | 7 | 0.0042 | 0.1303 | 0.1345 | 0.1324 | 0.0016 | 0 | 3 | 0.1124 | 0.1376 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10135 | 140300.248 | 44272.0763 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4000.6963 | 0:240:120 | 0:00 | 0.1083 | 7 | 0.0026 | 0.1257 | 0.1283 | 0.1271 | 0.0009 | 0 | 3 | 0.1083 | 0.1325 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10138 | 140303.574 | 44272.0764 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4080.7102 | 0:240:120 | 0:00 | 0.1042 | 7 | 0.0027 | 0.1219 | 0.1246 | 0.123 | 0.0011 | 0 | 3 | 0.1042 | 0.1275 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10141 | 140306.975 | 44272.0764 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4162.3244 | 0:240:120 | 0:00 | 0.1004 | 7 | 0.0036 | 0.1164 | 0.12 | 0.1182 | 0.0014 | 0 | 3 | 0.1004 | 0.1228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10144 | 140310.276 | 44272.0765 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4245.5709 | 0:240:120 | 0:00 | 0.0966 | 7 | 0.0031 | 0.1124 | 0.1155 | 0.1139 | 0.0009 | 0 | 3 | 0.0966 | 0.1182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10147 | 140313.625 | 44272.0765 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4330.4823 | 0:240:120 | 0:00 | 0.093 | 7 | 0.0015 | 0.1091 | 0.1106 | 0.1096 | 0.0007 | 0 | 3 | 0.093 | 0.1138 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10150 | 140316.949 | 44272.0765 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4417.092 | 0:240:120 | 0:00 | 0.0896 | 7 | 0.0028 | 0.1041 | 0.1069 | 0.1054 | 0.0011 | 0 | 3 | 0.0896 | 0.1096 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10153 | 140320.293 | 44272.0766 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4505.4338 | 0:240:120 | 0:00 | 0.0862 | 7 | 0.0043 | 0.0995 | 0.1038 | 0.1011 | 0.0014 | 0 | 3 | 0.0862 | 0.1055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10156 | 140323.788 | 44272.0766 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4595.5425 | 0:240:120 | 0:00 | 0.083 | 7 | 0.0028 | 0.0963 | 0.0991 | 0.0982 | 0.0012 | 0 | 3 | 0.083 | 0.1016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10159 | 140326.998 | 44272.0767 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4687.4533 | 0:240:120 | 0:00 | 0.08 | 7 | 0.0035 | 0.0924 | 0.0959 | 0.0943 | 0.0012 | 0 | 3 | 0.08 | 0.0978 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10162 | 140330.498 | 44272.0767 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4781.2024 | 0:240:120 | 0:00 | 0.077 | 7 | 0.0027 | 0.0893 | 0.092 | 0.0908 | 0.001 | 0 | 3 | 0.077 | 0.0942 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10165 | 140334.172 | 44272.0767 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4876.8264 | 0:240:120 | 0:00 | 0.0741 | 7 | 0.0031 | 0.0862 | 0.0893 | 0.0874 | 0.001 | 0 | 3 | 0.0741 | 0.0907 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10168 | 140337.446 | 44272.0768 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4974.363 | 0:240:120 | 0:00 | 0.0714 | 7 | 0.0032 | 0.0825 | 0.0857 | 0.0842 | 0.0011 | 0 | 3 | 0.0714 | 0.0873 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10171 | 140340.748 | 44272.0768 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5073.8502 | 0:240:120 | 0:00 | 0.0687 | 7 | 0.0023 | 0.0796 | 0.0819 | 0.0812 | 0.0008 | 0 | 3 | 0.0687 | 0.0841 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10174 | 140343.932 | 44272.0769 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5175.3272 | 0:240:120 | 0:00 | 0.0662 | 7 | 0.0025 | 0.0766 | 0.0791 | 0.0779 | 0.0009 | 0 | 3 | 0.0662 | 0.0809 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10177 | 140347.139 | 44272.0769 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5278.8338 | 0:240:120 | 0:00 | 0.0637 | 7 | 0.003 | 0.0739 | 0.0769 | 0.0756 | 0.0011 | 0 | 3 | 0.0637 | 0.0779 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10180 | 140350.482 | 44272.0769 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5384.4104 | 0:240:120 | 0:00 | 0.0614 | 7 | 0.0032 | 0.071 | 0.0742 | 0.0726 | 0.0011 | 0 | 3 | 0.0614 | 0.075 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10183 | 140353.889 | 44272.077 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5492.0987 | 0:240:120 | 0:00 | 0.0591 | 7 | 0.0029 | 0.0686 | 0.0715 | 0.0699 | 0.0009 | 0 | 3 | 0.0591 | 0.0723 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10186 | 140357.196 | 44272.077 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5601.9406 | 0:240:120 | 0:00 | 0.0569 | 7 | 0.0034 | 0.0656 | 0.069 | 0.0674 | 0.0012 | 0 | 3 | 0.0569 | 0.0696 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10189 | 140360.56 | 44272.077 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5713.9794 | 0:240:120 | 0:00 | 0.0548 | 7 | 0.0042 | 0.0623 | 0.0665 | 0.0647 | 0.0013 | 0 | 3 | 0.0548 | 0.067 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10192 | 140364.007 | 44272.0771 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5828.259 | 0:240:120 | 0:00 | 0.0528 | 7 | 0.0033 | 0.0607 | 0.064 | 0.0623 | 0.0012 | 0 | 3 | 0.0528 | 0.0645 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10195 | 140367.155 | 44272.0771 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5944.8242 | 0:240:120 | 0:00 | 0.0508 | 7 | 0.0024 | 0.059 | 0.0614 | 0.0601 | 0.0009 | 0 | 3 | 0.0508 | 0.0621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10198 | 140370.662 | 44272.0772 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6063.7207 | 0:240:120 | 0:00 | 0.0489 | 7 | 0.0029 | 0.056 | 0.0589 | 0.058 | 0.0011 | 0 | 3 | 0.0489 | 0.0598 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10201 | 140374.058 | 44272.0772 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6184.9951 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0027 | 0.0545 | 0.0572 | 0.0561 | 0.001 | 0 | 3 | 0.0471 | 0.0576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10204 | 140377.36 | 44272.0772 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6308.695 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0035 | 0.0519 | 0.0554 | 0.0539 | 0.0013 | 0 | 3 | 0.0454 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10207 | 140380.64 | 44272.0773 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6434.8689 | 0:240:120 | 0:00 | 0.0437 | 7 | 0.0032 | 0.0498 | 0.053 | 0.0516 | 0.0012 | 0 | 3 | 0.0437 | 0.0537 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10210 | 140384.049 | 44272.0773 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6563.5663 | 0:240:120 | 0:00 | 0.0421 | 7 | 0.0029 | 0.0481 | 0.051 | 0.05 | 0.0014 | 0 | 3 | 0.0421 | 0.0521 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10213 | 140387.222 | 44272.0774 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6694.8376 | 0:240:120 | 0:00 | 0.0405 | 7 | 0.003 | 0.0465 | 0.0495 | 0.0481 | 0.001 | 0 | 3 | 0.0405 | 0.0505 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10216 | 140390.419 | 44272.0774 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6828.7344 | 0:240:120 | 0:00 | 0.039 | 7 | 0.0029 | 0.0446 | 0.0475 | 0.0464 | 0.0009 | 0 | 3 | 0.039 | 0.049 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10219 | 140393.579 | 44272.0774 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6965.3091 | 0:240:120 | 0:00 | 0.0376 | 7 | 0.004 | 0.0427 | 0.0467 | 0.0445 | 0.0014 | 0 | 3 | 0.0376 | 0.0476 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10222 | 140396.877 | 44272.0775 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7104.6152 | 0:240:120 | 0:00 | 0.0362 | 7 | 0.0022 | 0.0416 | 0.0438 | 0.0431 | 0.0008 | 0 | 3 | 0.0362 | 0.0462 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10225 | 140400.078 | 44272.0775 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7246.7075 | 0:240:120 | 0:00 | 0.0348 | 7 | 0.0038 | 0.0399 | 0.0437 | 0.042 | 0.0013 | 0 | 3 | 0.0348 | 0.0448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10228 | 140403.199 | 44272.0775 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7391.6417 | 0:240:120 | 0:00 | 0.0336 | 7 | 0.0021 | 0.0393 | 0.0414 | 0.0404 | 0.0008 | 0 | 3 | 0.0336 | 0.0436 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10231 | 140406.387 | 44272.0776 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7539.4745 | 0:240:120 | 0:00 | 0.0323 | 7 | 0.0027 | 0.0373 | 0.04 | 0.0388 | 0.001 | 0 | 3 | 0.0323 | 0.0423 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10234 | 140409.465 | 44272.0776 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7690.264 | 0:240:120 | 0:00 | 0.0311 | 7 | 0.0025 | 0.036 | 0.0385 | 0.0374 | 0.0008 | 0 | 3 | 0.0311 | 0.0411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10237 | 140412.544 | 44272.0776 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7844.0693 | 0:240:120 | 0:00 | 0.03 | 7 | 0.0038 | 0.0337 | 0.0375 | 0.0359 | 0.0013 | 0 | 3 | 0.03 | 0.04 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10240 | 140415.617 | 44272.0777 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8000.9507 | 0:240:120 | 0:00 | 0.0289 | 7 | 0.0023 | 0.0342 | 0.0365 | 0.0351 | 0.0008 | 0 | 3 | 0.0289 | 0.0389 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10243 | 140418.652 | 44272.0777 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8160.9697 | 0:240:120 | 0:00 | 0.0278 | 7 | 0.0024 | 0.0328 | 0.0352 | 0.0338 | 0.0008 | 0 | 3 | 0.0278 | 0.0378 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10246 | 140422.176 | 44272.0778 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8324.1891 | 0:240:120 | 0:00 | 0.0268 | 7 | 0.0027 | 0.0318 | 0.0345 | 0.0333 | 0.0008 | 0 | 3 | 0.0268 | 0.0368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10249 | 140425.285 | 44272.0778 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8490.6729 | 0:240:120 | 0:00 | 0.0258 | 7 | 0.003 | 0.0309 | 0.0339 | 0.0327 | 0.001 | 0 | 3 | 0.0258 | 0.0358 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10252 | 140428.561 | 44272.0778 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8660.4863 | 0:240:120 | 0:00 | 0.0248 | 7 | 0.0037 | 0.0298 | 0.0335 | 0.0318 | 0.0013 | 0 | 3 | 0.0248 | 0.0348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10255 | 140431.744 | 44272.0779 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8833.6961 | 0:240:120 | 0:00 | 0.0239 | 7 | 0.0034 | 0.0289 | 0.0323 | 0.0308 | 0.0014 | 0 | 3 | 0.0239 | 0.0339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10258 | 140434.816 | 44272.0779 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9010.37 | 0:240:120 | 0:00 | 0.023 | 7 | 0.0025 | 0.0281 | 0.0306 | 0.0297 | 0.0011 | 0 | 3 | 0.023 | 0.033 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10261 | 140437.972 | 44272.0779 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9190.5774 | 0:240:120 | 0:00 | 0.0222 | 7 | 0.0026 | 0.0279 | 0.0305 | 0.0291 | 0.0009 | 0 | 3 | 0.0222 | 0.0322 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10264 | 140441.085 | 44272.078 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9374.3889 | 0:240:120 | 0:00 | 0.0213 | 7 | 0.0041 | 0.0256 | 0.0297 | 0.0282 | 0.0014 | 0 | 3 | 0.0213 | 0.0313 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10267 | 140444.15 | 44272.078 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9561.8767 | 0:240:120 | 0:00 | 0.0206 | 7 | 0.0041 | 0.0253 | 0.0294 | 0.0272 | 0.0014 | 0 | 3 | 0.0206 | 0.0306 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10270 | 140447.401 | 44272.0781 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9753.1142 | 0:240:120 | 0:00 | 0.0198 | 7 | 0.003 | 0.0243 | 0.0273 | 0.0261 | 0.001 | 0 | 3 | 0.0198 | 0.0298 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10273 | 140450.812 | 44272.0781 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9948.1765 | 0:240:120 | 0:00 | 0.0191 | 7 | 0.0024 | 0.0248 | 0.0272 | 0.026 | 0.0009 | 0 | 3 | 0.0191 | 0.0291 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10276 | 140453.883 | 44272.0781 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10147.14 | 0:240:120 | 0:00 | 0.0184 | 7 | 0.0039 | 0.0224 | 0.0263 | 0.0248 | 0.0013 | 0 | 3 | 0.0184 | 0.0284 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10279 | 140457.214 | 44272.0782 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10350.0829 | 0:240:120 | 0:00 | 0.0177 | 7 | 0.0031 | 0.022 | 0.0251 | 0.0238 | 0.0011 | 0 | 3 | 0.0177 | 0.0277 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10282 | 140460.368 | 44272.0782 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10557.0845 | 0:240:120 | 0:00 | 0.017 | 7 | 0.0045 | 0.0203 | 0.0248 | 0.023 | 0.0017 | 0 | 3 | 0.017 | 0.027 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10285 | 140463.582 | 44272.0782 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10768.2262 | 0:240:120 | 0:00 | 0.0164 | 7 | 0.0036 | 0.0202 | 0.0238 | 0.0223 | 0.0014 | 0 | 3 | 0.0164 | 0.0264 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10288 | 140466.534 | 44272.0783 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10983.5907 | 0:240:120 | 0:00 | 0.0158 | 7 | 0.0045 | 0.0188 | 0.0233 | 0.0215 | 0.0017 | 0 | 3 | 0.0158 | 0.0258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10291 | 140469.63 | 44272.0783 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11203.2625 | 0:240:120 | 0:00 | 0.0152 | 7 | 0.0042 | 0.0188 | 0.023 | 0.0211 | 0.0016 | 0 | 3 | 0.0152 | 0.0252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10294 | 140472.652 | 44272.0783 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11427.3278 | 0:240:120 | 0:00 | 0.0146 | 7 | 0.0035 | 0.0184 | 0.0219 | 0.0206 | 0.0013 | 0 | 3 | 0.0146 | 0.0246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10297 | 140475.827 | 44272.0784 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11655.8744 | 0:240:120 | 0:00 | 0.0141 | 7 | 0.0039 | 0.0184 | 0.0223 | 0.0203 | 0.0015 | 0 | 3 | 0.0141 | 0.0241 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10300 | 140478.786 | 44272.0784 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11888.9918 | 0:240:120 | 0:00 | 0.0136 | 7 | 0.0042 | 0.0175 | 0.0217 | 0.0189 | 0.002 | 0 | 3 | 0.0136 | 0.0236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10303 | 140842.394 | 44272.0826 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 346.8 | 0:240:120 | 0:00 | 46.5148 | 7 | 76.9742 | 346.6418 | 423.616 | 368.7955 | 30.1548 | 909.3136 | 3 | 46.5148 | 188.7308 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
10306 | 141948.739 | 44272.0954 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 353.7 | 0:240:120 | 0:00 | 40.1536 | 7 | 64.5053 | 214.0252 | 278.5305 | 232.9166 | 28.7333 | 825.6049 | 3 | 40.1536 | 123.6633 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
10309 | 142578.368 | 44272.1027 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 360.8 | 0:240:120 | 0:00 | 35.1224 | 7 | 0.0083 | 74.3083 | 74.3166 | 74.3136 | 0.0027 | 0 | 3 | 35.1224 | 90.8533 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10312 | 142796.595 | 44272.1052 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 368 | 0:240:120 | 0:00 | 31.0997 | 7 | 3.8659 | 62.7125 | 66.5784 | 65.2914 | 1.9282 | 3.718 | 3 | 31.0997 | 71.3193 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10315 | 142991.648 | 44272.1075 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 375.3 | 0:240:120 | 0:00 | 27.8122 | 7 | 3.8709 | 54.9733 | 58.8442 | 57.5522 | 1.9325 | 3.7344 | 3 | 27.8122 | 58.3679 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
10318 | 143163.449 | 44272.1095 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 382.9 | 0:240:120 | 0:00 | 25.0101 | 7 | 3.8721 | 47.2358 | 51.1079 | 48.5274 | 1.9342 | 3.741 | 3 | 25.0101 | 48.9472 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
10321 | 143308.294 | 44272.1112 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 390.5 | 0:240:120 | 0:00 | 22.6836 | 7 | 3.5454 | 35.9611 | 39.5065 | 38.3396 | 1.746 | 3.0483 | 3 | 22.6836 | 42.0396 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10324 | 143424.649 | 44272.1125 | Vista Speed | T | 140T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 398.3 | 0:240:120 | 0:00 | 20.6744 | 7 | 1.2813 | 33.0776 | 34.3589 | 33.9307 | 0.6397 | 0.4092 | 3 | 20.6744 | 36.638 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10327 | 144271.243 | 44272.1223 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 528 | 0:240:120 | 0:00 | 74.299 | 7 | 69.8701 | 703.2368 | 773.1069 | 749.8155 | 34.933 | 1220.3133 | 3 | 74.299 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10330 | 146453.625 | 44272.1476 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 538.56 | 0:240:120 | 0:00 | 60.3332 | 7 | 69.9549 | 563.4028 | 633.3577 | 610.0019 | 34.9461 | 1221.2282 | 3 | 60.3332 | 788.682 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10333 | 148217.173 | 44272.168 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 549.3312 | 0:240:120 | 0:00 | 50.4807 | 7 | 69.8881 | 423.6148 | 493.5029 | 465.1459 | 31.9205 | 1018.918 | 3 | 50.4807 | 255.3629 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
10336 | 149560.946 | 44272.1835 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 560.3178 | 0:240:120 | 0:00 | 43.162 | 7 | 69.8642 | 283.9075 | 353.7717 | 307.5727 | 34.6534 | 1200.8552 | 3 | 43.162 | 150.0244 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
10339 | 150485.493 | 44272.1942 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 571.5242 | 0:240:120 | 0:00 | 37.5146 | 7 | 91.9509 | 122.0848 | 214.0357 | 162.2483 | 39.6279 | 1570.3672 | 3 | 37.5146 | 105.0354 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
10342 | 150987.132 | 44272.2 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 582.9547 | 0:240:120 | 0:00 | 33.0275 | 7 | 4.4909 | 66.5751 | 71.066 | 69.2599 | 2.0213 | 4.0858 | 3 | 33.0275 | 80.0956 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10345 | 151194.678 | 44272.2024 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 594.6138 | 0:240:120 | 0:00 | 29.3788 | 7 | 3.8697 | 58.8412 | 62.7109 | 61.4196 | 1.9331 | 3.7369 | 3 | 29.3788 | 64.2541 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10348 | 151378.028 | 44272.2046 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 606.506 | 0:240:120 | 0:00 | 26.3555 | 7 | 3.8686 | 51.1063 | 54.9749 | 53.6841 | 1.9327 | 3.7353 | 3 | 26.3555 | 53.3067 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
10351 | 151538.106 | 44272.2064 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 618.6362 | 0:240:120 | 0:00 | 23.8113 | 7 | 7.2589 | 39.9814 | 47.2403 | 43.6952 | 2.9493 | 8.6984 | 3 | 23.8113 | 45.2938 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
10354 | 151671.023 | 44272.208 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 631.0089 | 0:240:120 | 0:00 | 21.6419 | 7 | 1.2821 | 34.3567 | 35.6388 | 35.2101 | 0.6397 | 0.4092 | 3 | 21.6419 | 39.1787 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10357 | 151778.542 | 44272.2092 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 643.6291 | 0:240:120 | 0:00 | 19.7716 | 7 | 1.2829 | 31.7954 | 33.0783 | 32.5065 | 0.5663 | 0.3207 | 3 | 19.7716 | 34.3618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10360 | 151876.923 | 44272.2103 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 656.5016 | 0:240:120 | 0:00 | 18.1434 | 7 | 1.5263 | 27.9526 | 29.4789 | 28.8527 | 0.6798 | 0.4621 | 3 | 18.1434 | 30.4716 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10363 | 151965.258 | 44272.2114 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 669.6317 | 0:240:120 | 0:00 | 16.7143 | 7 | 1.2831 | 25.3921 | 26.6752 | 26.111 | 0.5729 | 0.3282 | 3 | 16.7143 | 27.2664 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10366 | 152044.911 | 44272.2123 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 683.0243 | 0:240:120 | 0:00 | 15.4506 | 7 | 0.6354 | 22.1965 | 22.8319 | 22.6193 | 0.3168 | 0.1004 | 3 | 15.4506 | 24.5817 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10369 | 152115.175 | 44272.2131 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 696.6848 | 0:240:120 | 0:00 | 14.3259 | 7 | 1.1552 | 20.4077 | 21.5629 | 21.0043 | 0.456 | 0.2079 | 3 | 14.3259 | 22.3015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10372 | 152181.105 | 44272.2139 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 710.6185 | 0:240:120 | 0:00 | 13.3193 | 7 | 0.6353 | 19.0228 | 19.6581 | 19.4456 | 0.3168 | 0.1003 | 3 | 13.3193 | 20.3423 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10375 | 152241.233 | 44272.2146 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 724.8309 | 0:240:120 | 0:00 | 12.4135 | 7 | 0.6812 | 17.1173 | 17.7985 | 17.5493 | 0.3243 | 0.1051 | 3 | 12.4135 | 18.6418 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10378 | 152296.265 | 44272.2152 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 739.3275 | 0:240:120 | 0:00 | 11.5948 | 7 | 0.7545 | 15.7291 | 16.4836 | 16.1063 | 0.3261 | 0.1063 | 3 | 11.5948 | 17.1529 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10381 | 152347.51 | 44272.2158 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 754.114 | 0:240:120 | 0:00 | 10.8517 | 7 | 0.7357 | 14.6196 | 15.3553 | 14.9945 | 0.3039 | 0.0924 | 3 | 10.8517 | 15.8394 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10384 | 152395.353 | 44272.2163 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 769.1963 | 0:240:120 | 0:00 | 10.1745 | 7 | 0.3854 | 13.8376 | 14.223 | 13.9901 | 0.1829 | 0.0335 | 3 | 10.1745 | 14.6727 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10387 | 152439.948 | 44272.2169 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 784.5802 | 0:240:120 | 0:00 | 9.5554 | 7 | 0.3788 | 12.7134 | 13.0922 | 12.9229 | 0.1681 | 0.0282 | 3 | 9.5554 | 13.6302 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10390 | 152481.144 | 44272.2173 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 800.2718 | 0:240:120 | 0:00 | 8.9876 | 7 | 0.2505 | 11.9679 | 12.2184 | 12.106 | 0.1092 | 0.0119 | 3 | 8.9876 | 12.6937 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10393 | 152520.251 | 44272.2178 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 816.2773 | 0:240:120 | 0:00 | 8.4653 | 7 | 0.3647 | 11.109 | 11.4737 | 11.2929 | 0.1471 | 0.0216 | 3 | 8.4653 | 11.8485 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10396 | 152557.028 | 44272.2182 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 832.6028 | 0:240:120 | 0:00 | 7.9835 | 7 | 0.4976 | 10.2305 | 10.7281 | 10.4787 | 0.2151 | 0.0463 | 3 | 7.9835 | 11.0822 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10399 | 152591.843 | 44272.2186 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 849.2549 | 0:240:120 | 0:00 | 7.538 | 7 | 0.3509 | 9.7046 | 10.0555 | 9.8795 | 0.1515 | 0.023 | 3 | 7.538 | 10.3849 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10402 | 152624.587 | 44272.219 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 866.24 | 0:240:120 | 0:00 | 7.1252 | 7 | 0.2983 | 9.1795 | 9.4778 | 9.3336 | 0.1261 | 0.0159 | 3 | 7.1252 | 9.748 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10405 | 152655.331 | 44272.2193 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 883.5648 | 0:240:120 | 0:00 | 6.7419 | 7 | 0.1759 | 8.6538 | 8.8297 | 8.7705 | 0.0866 | 0.0075 | 3 | 6.7419 | 9.1644 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10408 | 152684.357 | 44272.2197 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 901.2361 | 0:240:120 | 0:00 | 6.3851 | 7 | 0.2603 | 8.0885 | 8.3488 | 8.2179 | 0.1125 | 0.0127 | 3 | 6.3851 | 8.628 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10411 | 152711.884 | 44272.22 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 919.2608 | 0:240:120 | 0:00 | 6.0526 | 7 | 0.1436 | 7.6996 | 7.8432 | 7.7874 | 0.0655 | 0.0043 | 3 | 6.0526 | 8.1338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10414 | 152738.126 | 44272.2203 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 937.646 | 0:240:120 | 0:00 | 5.7421 | 7 | 0.2582 | 7.1817 | 7.4399 | 7.3103 | 0.1115 | 0.0124 | 3 | 5.7421 | 7.6771 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10417 | 152763.248 | 44272.2206 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 956.3989 | 0:240:120 | 0:00 | 5.4517 | 7 | 0.1017 | 6.8823 | 6.984 | 6.949 | 0.0493 | 0.0024 | 3 | 5.4517 | 7.2542 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10420 | 152786.98 | 44272.2209 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 975.5269 | 0:240:120 | 0:00 | 5.1797 | 7 | 0.1987 | 6.4853 | 6.684 | 6.584 | 0.0854 | 0.0073 | 3 | 5.1797 | 6.8617 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10423 | 152809.546 | 44272.2211 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 995.0374 | 0:240:120 | 0:00 | 4.9246 | 7 | 0.1772 | 6.1087 | 6.2859 | 6.1928 | 0.0769 | 0.0059 | 3 | 4.9246 | 6.4967 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10426 | 152830.849 | 44272.2214 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1014.9382 | 0:240:120 | 0:00 | 4.685 | 7 | 0.1566 | 5.7945 | 5.9511 | 5.8925 | 0.0735 | 0.0054 | 3 | 4.685 | 6.1567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10429 | 152851.285 | 44272.2216 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1035.2369 | 0:240:120 | 0:00 | 4.4597 | 7 | 0.1571 | 5.4808 | 5.6379 | 5.5914 | 0.0687 | 0.0047 | 3 | 4.4597 | 5.8394 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10432 | 152871.059 | 44272.2218 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1055.9417 | 0:240:120 | 0:00 | 4.2476 | 7 | 0.1253 | 5.2153 | 5.3406 | 5.3002 | 0.0574 | 0.0033 | 3 | 4.2476 | 5.5427 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10435 | 152889.77 | 44272.2221 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1077.0605 | 0:240:120 | 0:00 | 4.0477 | 7 | 0.1285 | 4.9586 | 5.0871 | 5.0439 | 0.0616 | 0.0038 | 3 | 4.0477 | 5.265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10438 | 152908.032 | 44272.2223 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1098.6017 | 0:240:120 | 0:00 | 3.8591 | 7 | 0.1154 | 4.7178 | 4.8332 | 4.7917 | 0.055 | 0.003 | 3 | 3.8591 | 5.0046 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10441 | 152925.751 | 44272.2225 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1120.5738 | 0:240:120 | 0:00 | 3.681 | 7 | 0.1036 | 4.5094 | 4.613 | 4.5607 | 0.0446 | 0.002 | 3 | 3.681 | 4.7602 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10444 | 152942.334 | 44272.2227 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1142.9852 | 0:240:120 | 0:00 | 3.5128 | 7 | 0.1045 | 4.3023 | 4.4068 | 4.3534 | 0.0445 | 0.002 | 3 | 3.5128 | 4.5304 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10447 | 152958.544 | 44272.2229 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1165.8449 | 0:240:120 | 0:00 | 3.3535 | 7 | 0.0993 | 4.0771 | 4.1764 | 4.1363 | 0.0445 | 0.002 | 3 | 3.3535 | 4.3142 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10450 | 152974.095 | 44272.223 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1189.1618 | 0:240:120 | 0:00 | 3.2028 | 7 | 0.0869 | 3.9042 | 3.9911 | 3.9466 | 0.0372 | 0.0014 | 3 | 3.2028 | 4.1105 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10453 | 152989.117 | 44272.2232 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1212.9451 | 0:240:120 | 0:00 | 3.06 | 7 | 0.0977 | 3.7079 | 3.8056 | 3.7584 | 0.0413 | 0.0017 | 3 | 3.06 | 3.9184 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10456 | 153003.543 | 44272.2234 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1237.204 | 0:240:120 | 0:00 | 2.9246 | 7 | 0.1296 | 3.5051 | 3.6347 | 3.5734 | 0.0459 | 0.0021 | 3 | 2.9246 | 3.737 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10459 | 153017.229 | 44272.2235 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1261.9481 | 0:240:120 | 0:00 | 2.7962 | 7 | 0.1084 | 3.3469 | 3.4553 | 3.4159 | 0.0413 | 0.0017 | 3 | 2.7962 | 3.5657 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10462 | 153030.527 | 44272.2237 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1287.187 | 0:240:120 | 0:00 | 2.6742 | 7 | 0.0855 | 3.2253 | 3.3108 | 3.2619 | 0.0303 | 0.0009 | 3 | 2.6742 | 3.4036 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10465 | 153043.195 | 44272.2238 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1312.9308 | 0:240:120 | 0:00 | 2.5583 | 7 | 0.1073 | 3.0551 | 3.1624 | 3.1137 | 0.0408 | 0.0017 | 3 | 2.5583 | 3.2502 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10468 | 153055.6 | 44272.224 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1339.1894 | 0:240:120 | 0:00 | 2.4482 | 7 | 0.1175 | 2.9052 | 3.0227 | 2.9716 | 0.042 | 0.0018 | 3 | 2.4482 | 3.105 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10471 | 153067.381 | 44272.2241 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1365.9732 | 0:240:120 | 0:00 | 2.3434 | 7 | 0.1079 | 2.7796 | 2.8875 | 2.8335 | 0.0376 | 0.0014 | 3 | 2.3434 | 2.9672 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10474 | 153078.741 | 44272.2242 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1393.2926 | 0:240:120 | 0:00 | 2.2437 | 7 | 0.1161 | 2.6455 | 2.7616 | 2.7122 | 0.0412 | 0.0017 | 3 | 2.2437 | 2.8366 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10477 | 153089.782 | 44272.2244 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1421.1585 | 0:240:120 | 0:00 | 2.1488 | 7 | 0.0813 | 2.5518 | 2.6331 | 2.5988 | 0.0313 | 0.001 | 3 | 2.1488 | 2.7126 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10480 | 153100.314 | 44272.2245 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1449.5816 | 0:240:120 | 0:00 | 2.0584 | 7 | 0.095 | 2.4314 | 2.5264 | 2.4857 | 0.0308 | 0.0009 | 3 | 2.0584 | 2.5948 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10483 | 153110.743 | 44272.2246 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1478.5733 | 0:240:120 | 0:00 | 1.9722 | 7 | 0.1037 | 2.333 | 2.4367 | 2.3816 | 0.0355 | 0.0013 | 3 | 1.9722 | 2.4829 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10486 | 153121.081 | 44272.2247 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1508.1447 | 0:240:120 | 0:00 | 1.89 | 7 | 0.0726 | 2.2457 | 2.3183 | 2.2802 | 0.0257 | 0.0007 | 3 | 1.89 | 2.3764 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10489 | 153130.963 | 44272.2249 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1538.3076 | 0:240:120 | 0:00 | 1.8117 | 7 | 0.0651 | 2.1518 | 2.2169 | 2.1854 | 0.024 | 0.0006 | 3 | 1.8117 | 2.2751 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10492 | 153140.406 | 44272.225 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1569.0738 | 0:240:120 | 0:00 | 1.7369 | 7 | 0.0877 | 2.0443 | 2.132 | 2.0863 | 0.0316 | 0.001 | 3 | 1.7369 | 2.1787 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10495 | 153149.665 | 44272.2251 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1600.4553 | 0:240:120 | 0:00 | 1.6655 | 7 | 0.0695 | 1.9663 | 2.0358 | 2.0027 | 0.0264 | 0.0007 | 3 | 1.6655 | 2.0869 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10498 | 153158.744 | 44272.2252 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1632.4644 | 0:240:120 | 0:00 | 1.5974 | 7 | 0.0491 | 1.8857 | 1.9348 | 1.9134 | 0.019 | 0.0004 | 3 | 1.5974 | 1.9994 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10501 | 153167.395 | 44272.2253 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1665.1137 | 0:240:120 | 0:00 | 1.5322 | 7 | 0.0478 | 1.8079 | 1.8557 | 1.8349 | 0.0173 | 0.0003 | 3 | 1.5322 | 1.916 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10504 | 153176.216 | 44272.2254 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1698.4159 | 0:240:120 | 0:00 | 1.47 | 7 | 0.048 | 1.738 | 1.786 | 1.7607 | 0.0158 | 0.0002 | 3 | 1.47 | 1.8364 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10507 | 153184.468 | 44272.2255 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1732.3843 | 0:240:120 | 0:00 | 1.4106 | 7 | 0.0502 | 1.6611 | 1.7113 | 1.6908 | 0.0187 | 0.0003 | 3 | 1.4106 | 1.7605 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10510 | 153192.377 | 44272.2256 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1767.0319 | 0:240:120 | 0:00 | 1.3537 | 7 | 0.05 | 1.5923 | 1.6423 | 1.6204 | 0.0179 | 0.0003 | 3 | 1.3537 | 1.688 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10513 | 153200.181 | 44272.2257 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1802.3726 | 0:240:120 | 0:00 | 1.2993 | 7 | 0.0437 | 1.5278 | 1.5715 | 1.5507 | 0.016 | 0.0003 | 3 | 1.2993 | 1.6189 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10516 | 153207.894 | 44272.2257 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1838.42 | 0:240:120 | 0:00 | 1.2473 | 7 | 0.0396 | 1.4735 | 1.5131 | 1.4896 | 0.0142 | 0.0002 | 3 | 1.2473 | 1.5528 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10519 | 153215.224 | 44272.2258 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1875.1884 | 0:240:120 | 0:00 | 1.1975 | 7 | 0.0396 | 1.4098 | 1.4494 | 1.4323 | 0.0128 | 0.0002 | 3 | 1.1975 | 1.4897 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10522 | 153222.401 | 44272.2259 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1912.6922 | 0:240:120 | 0:00 | 1.1498 | 7 | 0.0355 | 1.356 | 1.3915 | 1.3745 | 0.0136 | 0.0002 | 3 | 1.1498 | 1.4293 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10525 | 153229.487 | 44272.226 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1950.946 | 0:240:120 | 0:00 | 1.1042 | 7 | 0.0315 | 1.2999 | 1.3314 | 1.3158 | 0.0123 | 0.0002 | 3 | 1.1042 | 1.3716 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10528 | 153236.299 | 44272.2261 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1989.965 | 0:240:120 | 0:00 | 1.0605 | 7 | 0.0376 | 1.2431 | 1.2807 | 1.2615 | 0.0143 | 0.0002 | 3 | 1.0605 | 1.3165 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10531 | 153243.046 | 44272.2262 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2029.7643 | 0:240:120 | 0:00 | 1.0186 | 7 | 0.0293 | 1.1933 | 1.2226 | 1.2109 | 0.0113 | 0.0001 | 3 | 1.0186 | 1.2637 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10534 | 153249.645 | 44272.2262 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2070.3596 | 0:240:120 | 0:00 | 0.9785 | 7 | 0.03 | 1.1492 | 1.1792 | 1.1636 | 0.0109 | 0.0001 | 3 | 0.9785 | 1.2132 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10537 | 153256.337 | 44272.2263 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2111.7667 | 0:240:120 | 0:00 | 0.9401 | 7 | 0.0375 | 1.1001 | 1.1376 | 1.1172 | 0.0118 | 0.0001 | 3 | 0.9401 | 1.1649 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10540 | 153262.565 | 44272.2264 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2154.0021 | 0:240:120 | 0:00 | 0.9032 | 7 | 0.0294 | 1.0547 | 1.0841 | 1.0728 | 0.0093 | 0.0001 | 3 | 0.9032 | 1.1186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10543 | 153268.855 | 44272.2264 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2197.0821 | 0:240:120 | 0:00 | 0.8679 | 7 | 0.0253 | 1.0186 | 1.0439 | 1.0321 | 0.0101 | 0.0001 | 3 | 0.8679 | 1.0743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10546 | 153275.068 | 44272.2265 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2241.0238 | 0:240:120 | 0:00 | 0.834 | 7 | 0.0335 | 0.9731 | 1.0066 | 0.9899 | 0.0109 | 0.0001 | 3 | 0.834 | 1.0318 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10549 | 153281.219 | 44272.2266 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2285.8442 | 0:240:120 | 0:00 | 0.8016 | 7 | 0.0292 | 0.9359 | 0.9651 | 0.9514 | 0.0118 | 0.0001 | 3 | 0.8016 | 0.9912 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10552 | 153287.061 | 44272.2267 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2331.5611 | 0:240:120 | 0:00 | 0.7704 | 7 | 0.0271 | 0.8981 | 0.9252 | 0.9119 | 0.0097 | 0.0001 | 3 | 0.7704 | 0.9522 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10555 | 153292.79 | 44272.2267 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2378.1923 | 0:240:120 | 0:00 | 0.7406 | 7 | 0.0262 | 0.8622 | 0.8884 | 0.8764 | 0.009 | 0.0001 | 3 | 0.7406 | 0.9149 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10558 | 153298.313 | 44272.2268 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2425.7562 | 0:240:120 | 0:00 | 0.7119 | 7 | 0.0187 | 0.8312 | 0.8499 | 0.8417 | 0.0074 | 0.0001 | 3 | 0.7119 | 0.8791 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10561 | 153303.966 | 44272.2269 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2474.2713 | 0:240:120 | 0:00 | 0.6844 | 7 | 0.0223 | 0.7977 | 0.82 | 0.8095 | 0.0083 | 0.0001 | 3 | 0.6844 | 0.8447 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10564 | 153309.314 | 44272.2269 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2523.7567 | 0:240:120 | 0:00 | 0.658 | 7 | 0.0195 | 0.7675 | 0.787 | 0.7776 | 0.0073 | 0.0001 | 3 | 0.658 | 0.8118 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10567 | 153314.635 | 44272.227 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2574.2319 | 0:240:120 | 0:00 | 0.6326 | 7 | 0.0171 | 0.7387 | 0.7558 | 0.7468 | 0.0061 | 0 | 3 | 0.6326 | 0.7803 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10570 | 153319.838 | 44272.227 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2625.7165 | 0:240:120 | 0:00 | 0.6083 | 7 | 0.0209 | 0.709 | 0.7299 | 0.7196 | 0.0071 | 0.0001 | 3 | 0.6083 | 0.75 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10573 | 153325.109 | 44272.2271 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2678.2308 | 0:240:120 | 0:00 | 0.585 | 7 | 0.0127 | 0.6859 | 0.6986 | 0.6922 | 0.0046 | 0 | 3 | 0.585 | 0.7209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10576 | 153330.182 | 44272.2272 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2731.7955 | 0:240:120 | 0:00 | 0.5625 | 7 | 0.0158 | 0.6559 | 0.6717 | 0.6642 | 0.006 | 0 | 3 | 0.5625 | 0.6931 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10579 | 153335.312 | 44272.2272 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2786.4314 | 0:240:120 | 0:00 | 0.541 | 7 | 0.0133 | 0.6323 | 0.6456 | 0.6392 | 0.0048 | 0 | 3 | 0.541 | 0.6663 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10582 | 153340.198 | 44272.2273 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2842.16 | 0:240:120 | 0:00 | 0.5203 | 7 | 0.0137 | 0.6082 | 0.6219 | 0.6141 | 0.0048 | 0 | 3 | 0.5203 | 0.6407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10585 | 153345.189 | 44272.2273 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2899.0032 | 0:240:120 | 0:00 | 0.5005 | 7 | 0.0114 | 0.5867 | 0.5981 | 0.5913 | 0.0043 | 0 | 3 | 0.5005 | 0.616 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10588 | 153349.725 | 44272.2274 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2956.9833 | 0:240:120 | 0:00 | 0.4814 | 7 | 0.0148 | 0.5603 | 0.5751 | 0.5677 | 0.0046 | 0 | 3 | 0.4814 | 0.5923 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10591 | 153354.333 | 44272.2274 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3016.1229 | 0:240:120 | 0:00 | 0.463 | 7 | 0.0142 | 0.5386 | 0.5528 | 0.5456 | 0.0049 | 0 | 3 | 0.463 | 0.5696 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10594 | 153358.741 | 44272.2275 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3076.4454 | 0:240:120 | 0:00 | 0.4454 | 7 | 0.0123 | 0.5185 | 0.5308 | 0.5245 | 0.0042 | 0 | 3 | 0.4454 | 0.5478 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10597 | 153363.485 | 44272.2275 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3137.9743 | 0:240:120 | 0:00 | 0.4285 | 7 | 0.0111 | 0.4987 | 0.5098 | 0.5047 | 0.004 | 0 | 3 | 0.4285 | 0.5269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10600 | 153367.985 | 44272.2276 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3200.7338 | 0:240:120 | 0:00 | 0.4122 | 7 | 0.0102 | 0.4817 | 0.4919 | 0.4857 | 0.0039 | 0 | 3 | 0.4122 | 0.5067 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10603 | 153372.771 | 44272.2277 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3264.7485 | 0:240:120 | 0:00 | 0.3966 | 7 | 0.0118 | 0.4617 | 0.4735 | 0.4676 | 0.004 | 0 | 3 | 0.3966 | 0.4874 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10606 | 153377.09 | 44272.2277 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3330.0434 | 0:240:120 | 0:00 | 0.3816 | 7 | 0.0081 | 0.4455 | 0.4536 | 0.4496 | 0.0031 | 0 | 3 | 0.3816 | 0.4688 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10609 | 153381.367 | 44272.2278 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3396.6443 | 0:240:120 | 0:00 | 0.3671 | 7 | 0.0091 | 0.4277 | 0.4368 | 0.4315 | 0.0036 | 0 | 3 | 0.3671 | 0.451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10612 | 153385.743 | 44272.2278 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3464.5772 | 0:240:120 | 0:00 | 0.3533 | 7 | 0.0078 | 0.4126 | 0.4204 | 0.4157 | 0.0031 | 0 | 3 | 0.3533 | 0.4339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10615 | 153390.046 | 44272.2279 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3533.8687 | 0:240:120 | 0:00 | 0.3399 | 7 | 0.0088 | 0.3951 | 0.4039 | 0.3995 | 0.0035 | 0 | 3 | 0.3399 | 0.4174 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10618 | 153394.051 | 44272.2279 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3604.5461 | 0:240:120 | 0:00 | 0.3271 | 7 | 0.0075 | 0.3823 | 0.3898 | 0.3854 | 0.003 | 0 | 3 | 0.3271 | 0.4015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10621 | 153398.022 | 44272.2279 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3676.637 | 0:240:120 | 0:00 | 0.3147 | 7 | 0.0079 | 0.3653 | 0.3732 | 0.3694 | 0.0028 | 0 | 3 | 0.3147 | 0.3863 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10624 | 153402.115 | 44272.228 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3750.1698 | 0:240:120 | 0:00 | 0.3029 | 7 | 0.0075 | 0.352 | 0.3595 | 0.3555 | 0.0026 | 0 | 3 | 0.3029 | 0.3717 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10627 | 153406.399 | 44272.228 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3825.1732 | 0:240:120 | 0:00 | 0.2915 | 7 | 0.0075 | 0.3395 | 0.347 | 0.343 | 0.0029 | 0 | 3 | 0.2915 | 0.3576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10630 | 153410.574 | 44272.2281 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3901.6766 | 0:240:120 | 0:00 | 0.2805 | 7 | 0.0075 | 0.3262 | 0.3337 | 0.3295 | 0.0029 | 0 | 3 | 0.2805 | 0.3441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10633 | 153414.563 | 44272.2281 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3979.7101 | 0:240:120 | 0:00 | 0.27 | 7 | 0.0063 | 0.3142 | 0.3205 | 0.3173 | 0.0025 | 0 | 3 | 0.27 | 0.3311 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10636 | 153418.782 | 44272.2282 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4059.3043 | 0:240:120 | 0:00 | 0.2598 | 7 | 0.0065 | 0.3023 | 0.3088 | 0.305 | 0.0027 | 0 | 3 | 0.2598 | 0.3186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10639 | 153422.499 | 44272.2282 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4140.4904 | 0:240:120 | 0:00 | 0.2501 | 7 | 0.005 | 0.2907 | 0.2957 | 0.2931 | 0.0017 | 0 | 3 | 0.2501 | 0.3066 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10642 | 153426.293 | 44272.2283 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4223.3002 | 0:240:120 | 0:00 | 0.2407 | 7 | 0.0063 | 0.2795 | 0.2858 | 0.282 | 0.0026 | 0 | 3 | 0.2407 | 0.2951 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10645 | 153430.251 | 44272.2283 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4307.7662 | 0:240:120 | 0:00 | 0.2317 | 7 | 0.0063 | 0.2689 | 0.2752 | 0.2716 | 0.0026 | 0 | 3 | 0.2317 | 0.284 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10648 | 153434.056 | 44272.2284 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4393.9216 | 0:240:120 | 0:00 | 0.223 | 7 | 0.0057 | 0.2592 | 0.2649 | 0.2614 | 0.0022 | 0 | 3 | 0.223 | 0.2733 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10651 | 153437.896 | 44272.2284 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4481.8 | 0:240:120 | 0:00 | 0.2146 | 7 | 0.006 | 0.2488 | 0.2548 | 0.2516 | 0.0022 | 0 | 3 | 0.2146 | 0.263 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10654 | 153441.626 | 44272.2284 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4571.436 | 0:240:120 | 0:00 | 0.2066 | 7 | 0.0051 | 0.24 | 0.2451 | 0.2422 | 0.002 | 0 | 3 | 0.2066 | 0.2532 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10657 | 153445.459 | 44272.2285 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4662.8647 | 0:240:120 | 0:00 | 0.1989 | 7 | 0.0052 | 0.2309 | 0.2361 | 0.2326 | 0.0018 | 0 | 3 | 0.1989 | 0.2436 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10660 | 153449.37 | 44272.2285 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4756.122 | 0:240:120 | 0:00 | 0.1914 | 7 | 0.0056 | 0.2224 | 0.228 | 0.2247 | 0.0023 | 0 | 3 | 0.1914 | 0.2345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10663 | 153452.891 | 44272.2286 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4851.2445 | 0:240:120 | 0:00 | 0.1843 | 7 | 0.0049 | 0.2135 | 0.2184 | 0.2156 | 0.002 | 0 | 3 | 0.1843 | 0.2257 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10666 | 153456.607 | 44272.2286 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4948.2693 | 0:240:120 | 0:00 | 0.1774 | 7 | 0.005 | 0.2057 | 0.2107 | 0.2078 | 0.0019 | 0 | 3 | 0.1774 | 0.2173 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10669 | 153460.549 | 44272.2287 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5047.2347 | 0:240:120 | 0:00 | 0.1707 | 7 | 0.0035 | 0.1985 | 0.202 | 0.1999 | 0.0014 | 0 | 3 | 0.1707 | 0.2091 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10672 | 153463.859 | 44272.2287 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5148.1794 | 0:240:120 | 0:00 | 0.1644 | 7 | 0.0044 | 0.1912 | 0.1956 | 0.193 | 0.0017 | 0 | 3 | 0.1644 | 0.2013 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10675 | 153467.178 | 44272.2287 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5251.143 | 0:240:120 | 0:00 | 0.1582 | 7 | 0.0036 | 0.1837 | 0.1873 | 0.1851 | 0.0016 | 0 | 3 | 0.1582 | 0.1938 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10678 | 153470.812 | 44272.2288 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5356.1659 | 0:240:120 | 0:00 | 0.1523 | 7 | 0.0045 | 0.1779 | 0.1824 | 0.1792 | 0.0017 | 0 | 3 | 0.1523 | 0.1865 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10681 | 153474.317 | 44272.2288 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5463.2892 | 0:240:120 | 0:00 | 0.1467 | 7 | 0.0034 | 0.1706 | 0.174 | 0.1717 | 0.0014 | 0 | 3 | 0.1467 | 0.1795 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10684 | 153477.891 | 44272.2289 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5572.555 | 0:240:120 | 0:00 | 0.1412 | 7 | 0.0024 | 0.1645 | 0.1669 | 0.1655 | 0.0011 | 0 | 3 | 0.1412 | 0.1728 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10687 | 153481.25 | 44272.2289 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5684.0061 | 0:240:120 | 0:00 | 0.1359 | 7 | 0.0033 | 0.1581 | 0.1614 | 0.1594 | 0.0013 | 0 | 3 | 0.1359 | 0.1664 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10690 | 153484.725 | 44272.2289 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5797.6862 | 0:240:120 | 0:00 | 0.1309 | 7 | 0.0037 | 0.1518 | 0.1555 | 0.1532 | 0.0014 | 0 | 3 | 0.1309 | 0.1602 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10693 | 153488.135 | 44272.229 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5913.6399 | 0:240:120 | 0:00 | 0.126 | 7 | 0.004 | 0.1459 | 0.1499 | 0.1478 | 0.0016 | 0 | 3 | 0.126 | 0.1542 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10696 | 153491.416 | 44272.229 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6031.9127 | 0:240:120 | 0:00 | 0.1213 | 7 | 0.0051 | 0.1402 | 0.1453 | 0.142 | 0.0019 | 0 | 3 | 0.1213 | 0.1484 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10699 | 153494.839 | 44272.2291 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6152.551 | 0:240:120 | 0:00 | 0.1168 | 7 | 0.0033 | 0.135 | 0.1383 | 0.137 | 0.0011 | 0 | 3 | 0.1168 | 0.1429 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10702 | 153498.409 | 44272.2291 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6275.602 | 0:240:120 | 0:00 | 0.1124 | 7 | 0.0041 | 0.1297 | 0.1338 | 0.1314 | 0.0017 | 0 | 3 | 0.1124 | 0.1376 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10705 | 153501.754 | 44272.2291 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6401.114 | 0:240:120 | 0:00 | 0.1083 | 7 | 0.0029 | 0.1254 | 0.1283 | 0.1263 | 0.0012 | 0 | 3 | 0.1083 | 0.1325 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10708 | 153505.057 | 44272.2292 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6529.1363 | 0:240:120 | 0:00 | 0.1042 | 7 | 0.0035 | 0.1214 | 0.1249 | 0.1224 | 0.0013 | 0 | 3 | 0.1042 | 0.1275 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10711 | 153508.341 | 44272.2292 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6659.719 | 0:240:120 | 0:00 | 0.1004 | 7 | 0.0036 | 0.1155 | 0.1191 | 0.1173 | 0.0014 | 0 | 3 | 0.1004 | 0.1228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10714 | 153511.943 | 44272.2293 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6792.9134 | 0:240:120 | 0:00 | 0.0966 | 7 | 0.004 | 0.1115 | 0.1155 | 0.1132 | 0.0015 | 0 | 3 | 0.0966 | 0.1182 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10717 | 153515.403 | 44272.2293 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6928.7717 | 0:240:120 | 0:00 | 0.093 | 7 | 0.003 | 0.1076 | 0.1106 | 0.1095 | 0.0011 | 0 | 3 | 0.093 | 0.1138 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10720 | 153518.923 | 44272.2293 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7067.3471 | 0:240:120 | 0:00 | 0.0896 | 7 | 0.0029 | 0.1035 | 0.1064 | 0.1049 | 0.0011 | 0 | 3 | 0.0896 | 0.1096 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10723 | 153522.286 | 44272.2294 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7208.6941 | 0:240:120 | 0:00 | 0.0862 | 7 | 0.0028 | 0.0991 | 0.1019 | 0.1007 | 0.0011 | 0 | 3 | 0.0862 | 0.1055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10726 | 153525.573 | 44272.2294 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7352.868 | 0:240:120 | 0:00 | 0.083 | 7 | 0.0038 | 0.0949 | 0.0987 | 0.0969 | 0.0015 | 0 | 3 | 0.083 | 0.1016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10729 | 153529.259 | 44272.2295 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7499.9253 | 0:240:120 | 0:00 | 0.08 | 7 | 0.0034 | 0.0912 | 0.0946 | 0.0932 | 0.0011 | 0 | 3 | 0.08 | 0.0978 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10732 | 153532.683 | 44272.2295 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7649.9238 | 0:240:120 | 0:00 | 0.077 | 7 | 0.0036 | 0.0881 | 0.0917 | 0.0904 | 0.0011 | 0 | 3 | 0.077 | 0.0942 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10735 | 153536.203 | 44272.2295 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7802.9223 | 0:240:120 | 0:00 | 0.0741 | 7 | 0.0037 | 0.0847 | 0.0884 | 0.0868 | 0.0013 | 0 | 3 | 0.0741 | 0.0907 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10738 | 153539.408 | 44272.2296 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7958.9807 | 0:240:120 | 0:00 | 0.0714 | 7 | 0.0039 | 0.0811 | 0.085 | 0.0834 | 0.0014 | 0 | 3 | 0.0714 | 0.0873 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10741 | 153542.728 | 44272.2296 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8118.1604 | 0:240:120 | 0:00 | 0.0687 | 7 | 0.0031 | 0.0788 | 0.0819 | 0.0804 | 0.0011 | 0 | 3 | 0.0687 | 0.0841 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10744 | 153546.164 | 44272.2297 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8280.5236 | 0:240:120 | 0:00 | 0.0662 | 7 | 0.0031 | 0.0756 | 0.0787 | 0.077 | 0.0012 | 0 | 3 | 0.0662 | 0.0809 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10747 | 153549.439 | 44272.2297 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8446.134 | 0:240:120 | 0:00 | 0.0637 | 7 | 0.0036 | 0.0732 | 0.0768 | 0.0752 | 0.0012 | 0 | 3 | 0.0637 | 0.0779 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10750 | 153552.743 | 44272.2297 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8615.0567 | 0:240:120 | 0:00 | 0.0614 | 7 | 0.0031 | 0.0696 | 0.0727 | 0.0717 | 0.001 | 0 | 3 | 0.0614 | 0.075 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10753 | 153556.035 | 44272.2298 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8787.3579 | 0:240:120 | 0:00 | 0.0591 | 7 | 0.0034 | 0.0677 | 0.0711 | 0.0695 | 0.0012 | 0 | 3 | 0.0591 | 0.0723 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10756 | 153559.591 | 44272.2298 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8963.105 | 0:240:120 | 0:00 | 0.0569 | 7 | 0.0025 | 0.0656 | 0.0681 | 0.0668 | 0.0009 | 0 | 3 | 0.0569 | 0.0696 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10759 | 153562.883 | 44272.2299 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9142.3671 | 0:240:120 | 0:00 | 0.0548 | 7 | 0.0023 | 0.0629 | 0.0652 | 0.0644 | 0.0008 | 0 | 3 | 0.0548 | 0.067 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10762 | 153566.188 | 44272.2299 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9325.2145 | 0:240:120 | 0:00 | 0.0528 | 7 | 0.003 | 0.0602 | 0.0632 | 0.0619 | 0.0009 | 0 | 3 | 0.0528 | 0.0645 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10765 | 153569.424 | 44272.2299 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9511.7187 | 0:240:120 | 0:00 | 0.0508 | 7 | 0.0029 | 0.0576 | 0.0605 | 0.0595 | 0.0013 | 0 | 3 | 0.0508 | 0.0621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10768 | 153572.679 | 44272.23 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9701.9531 | 0:240:120 | 0:00 | 0.0489 | 7 | 0.0023 | 0.0561 | 0.0584 | 0.0575 | 0.0009 | 0 | 3 | 0.0489 | 0.0598 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10771 | 153575.984 | 44272.23 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9895.9922 | 0:240:120 | 0:00 | 0.0471 | 7 | 0.0039 | 0.0531 | 0.057 | 0.0557 | 0.0014 | 0 | 3 | 0.0471 | 0.0576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10774 | 153579.281 | 44272.23 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10093.912 | 0:240:120 | 0:00 | 0.0454 | 7 | 0.0028 | 0.0514 | 0.0542 | 0.0531 | 0.001 | 0 | 3 | 0.0454 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10777 | 153582.552 | 44272.2301 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10295.7903 | 0:240:120 | 0:00 | 0.0437 | 7 | 0.0015 | 0.0505 | 0.052 | 0.0515 | 0.0006 | 0 | 3 | 0.0437 | 0.0537 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10780 | 153585.724 | 44272.2301 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10501.7061 | 0:240:120 | 0:00 | 0.0421 | 7 | 0.003 | 0.0481 | 0.0511 | 0.0497 | 0.0011 | 0 | 3 | 0.0421 | 0.0521 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10783 | 153588.971 | 44272.2302 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10711.7402 | 0:240:120 | 0:00 | 0.0405 | 7 | 0.003 | 0.0456 | 0.0486 | 0.0479 | 0.001 | 0 | 3 | 0.0405 | 0.0505 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10786 | 153592.057 | 44272.2302 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10925.975 | 0:240:120 | 0:00 | 0.039 | 7 | 0.0047 | 0.0434 | 0.0481 | 0.046 | 0.0017 | 0 | 3 | 0.039 | 0.049 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10789 | 153595.24 | 44272.2302 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11144.4945 | 0:240:120 | 0:00 | 0.0376 | 7 | 0.0028 | 0.0427 | 0.0455 | 0.0444 | 0.0009 | 0 | 3 | 0.0376 | 0.0476 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10792 | 153598.652 | 44272.2303 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11367.3844 | 0:240:120 | 0:00 | 0.0362 | 7 | 0.0031 | 0.041 | 0.0441 | 0.0427 | 0.0011 | 0 | 3 | 0.0362 | 0.0462 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10795 | 153601.801 | 44272.2303 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11594.7321 | 0:240:120 | 0:00 | 0.0348 | 7 | 0.003 | 0.0396 | 0.0426 | 0.0414 | 0.001 | 0 | 3 | 0.0348 | 0.0448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10798 | 153604.761 | 44272.2303 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11826.6267 | 0:240:120 | 0:00 | 0.0336 | 7 | 0.0042 | 0.0375 | 0.0417 | 0.04 | 0.0015 | 0 | 3 | 0.0336 | 0.0436 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10801 | 154003.415 | 44272.235 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 554.8 | 0:240:120 | 0:00 | 46.5678 | 7 | 118.7764 | 304.8423 | 423.6187 | 370.7832 | 38.2002 | 1459.2537 | 3 | 46.5678 | 189.4467 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
10804 | 155137.557 | 44272.2481 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 565.9 | 0:240:120 | 0:00 | 40.1637 | 7 | 69.877 | 214.035 | 283.912 | 237.4266 | 34.8639 | 1215.4947 | 3 | 40.1637 | 123.7413 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
10807 | 155852.566 | 44272.2564 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 577.2 | 0:240:120 | 0:00 | 35.1537 | 7 | 72.6657 | 71.5095 | 144.1752 | 96.7586 | 35.5781 | 1265.8042 | 3 | 35.1537 | 91.0249 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
10810 | 156210.711 | 44272.2605 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 588.8 | 0:240:120 | 0:00 | 31.0997 | 7 | 3.9053 | 62.7085 | 66.6138 | 65.2949 | 1.9387 | 3.7584 | 3 | 31.0997 | 71.3193 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10813 | 156405.601 | 44272.2628 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 600.6 | 0:240:120 | 0:00 | 27.7817 | 7 | 3.8683 | 54.9743 | 58.8426 | 57.5519 | 1.9321 | 3.733 | 3 | 27.7817 | 58.2582 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
10816 | 156577.287 | 44272.2647 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 612.6 | 0:240:120 | 0:00 | 25.0185 | 7 | 3.8691 | 47.2399 | 51.109 | 49.106 | 1.6847 | 2.8382 | 3 | 25.0185 | 48.9734 | NP | NP | 0-1-1-0-1-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
10819 | 156725.458 | 44272.2665 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 624.8 | 0:240:120 | 0:00 | 22.6836 | 7 | 7.6218 | 35.637 | 43.2588 | 39.4289 | 3.2515 | 10.5726 | 3 | 22.6836 | 42.0396 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
10822 | 156849.206 | 44272.2679 | Vista Speed | T | 200T | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 637.3 | 0:240:120 | 0:00 | 20.6715 | 7 | 1.283 | 33.0772 | 34.3602 | 33.9307 | 0.6396 | 0.4091 | 3 | 20.6715 | 36.6304 | P | P | P | NP | 0-0-0-0-0-0-0-0-0

## Tap_Charac-20210310 131817-Comp (hidden)
Index | Time Interval | Timestamp | Curve Family | Type | Amp Type | Test Type | Trip Type | Interrupter# | Start Type | PE | DT1 | DT2 | OCC Freq | Source Freq | Current | Phase A:B:C | X/R:Angle | Expected Time | P_Select | Max Delta | Min Time | Max Time | Average | Std Dev | Variance | Count | Min T Spec | Max T Spec | Ave T Result | T Result | Indiv T | TC Result | Indiv TC
1 | 54.237 | 44265.555 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 18 | 0:240:120 | 0:00 | 4.8381 | 7 | 16.2281 | 34.6029 | 50.831 | 40.881 | 7.3 | 53.2901 | 3 | 4.8381 | Inf | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4 | 187.58 | 44265.5565 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 18.36 | 0:240:120 | 0:00 | 4.2787 | 7 | 17.9176 | 12.3366 | 30.2542 | 19.3928 | 8.2551 | 68.1462 | 3 | 4.2787 | 43.3984 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
7 | 260.152 | 44265.5574 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 18.7272 | 0:240:120 | 0:00 | 3.8202 | 7 | 0.9671 | 9.04 | 10.0071 | 9.37 | 0.4598 | 0.2114 | 3 | 3.8202 | 21.2569 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
10 | 291.185 | 44265.5577 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.1017 | 0:240:120 | 0:00 | 3.4379 | 7 | 0.9532 | 7.753 | 8.7062 | 8.1359 | 0.4244 | 0.1801 | 3 | 3.4379 | 13.8809 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
13 | 318.26 | 44265.558 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.4838 | 0:240:120 | 0:00 | 3.1143 | 7 | 0.9276 | 6.4908 | 7.4184 | 6.8111 | 0.4507 | 0.2031 | 3 | 3.1143 | 10.1963 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
16 | 341.529 | 44265.5583 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.8735 | 0:240:120 | 0:00 | 2.8372 | 7 | 1.0083 | 5.1161 | 6.1244 | 5.5023 | 0.467 | 0.2181 | 3 | 2.8372 | 7.9882 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
19 | 361.134 | 44265.5585 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 20.2709 | 0:240:120 | 0:00 | 2.5974 | 7 | 0.3729 | 4.4671 | 4.84 | 4.6225 | 0.1645 | 0.0271 | 3 | 2.5974 | 6.5184 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
22 | 377.484 | 44265.5587 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 20.6763 | 0:240:120 | 0:00 | 2.3878 | 7 | 0.3254 | 4.0165 | 4.3419 | 4.1341 | 0.153 | 0.0234 | 3 | 2.3878 | 5.4705 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
25 | 392.653 | 44265.5589 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 21.0899 | 0:240:120 | 0:00 | 2.2034 | 7 | 0.4089 | 3.5001 | 3.909 | 3.6821 | 0.1761 | 0.031 | 3 | 2.2034 | 4.6862 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
28 | 406.494 | 44265.5591 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 21.5117 | 0:240:120 | 0:00 | 2.0398 | 7 | 0.3509 | 3.0858 | 3.4367 | 3.221 | 0.1581 | 0.025 | 3 | 2.0398 | 4.0776 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
31 | 419.072 | 44265.5592 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 21.9419 | 0:240:120 | 0:00 | 1.894 | 7 | 0.1928 | 2.8375 | 3.0303 | 2.9143 | 0.0871 | 0.0076 | 3 | 1.894 | 3.5921 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
34 | 430.59 | 44265.5593 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 22.3807 | 0:240:120 | 0:00 | 1.7631 | 7 | 0.2185 | 2.5815 | 2.8 | 2.6735 | 0.0965 | 0.0093 | 3 | 1.7631 | 3.196 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
37 | 441.268 | 44265.5595 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 22.8284 | 0:240:120 | 0:00 | 1.6451 | 7 | 0.2174 | 2.3235 | 2.5409 | 2.4231 | 0.0881 | 0.0078 | 3 | 1.6451 | 2.867 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
40 | 451.373 | 44265.5596 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.2849 | 0:240:120 | 0:00 | 1.5383 | 7 | 0.1413 | 2.1488 | 2.2901 | 2.2047 | 0.0606 | 0.0037 | 3 | 1.5383 | 2.5896 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
43 | 460.74 | 44265.5597 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.7506 | 0:240:120 | 0:00 | 1.4412 | 7 | 0.1333 | 1.9899 | 2.1232 | 2.0465 | 0.0578 | 0.0033 | 3 | 1.4412 | 2.3527 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
46 | 469.668 | 44265.5598 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.2256 | 0:240:120 | 0:00 | 1.3526 | 7 | 0.1328 | 1.8276 | 1.9604 | 1.8908 | 0.0541 | 0.0029 | 3 | 1.3526 | 2.1483 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
49 | 478.067 | 44265.5599 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.7101 | 0:240:120 | 0:00 | 1.2715 | 7 | 0.1114 | 1.6878 | 1.7992 | 1.7335 | 0.0471 | 0.0022 | 3 | 1.2715 | 1.9702 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
52 | 486.04 | 44265.56 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.2043 | 0:240:120 | 0:00 | 1.1971 | 7 | 0.0894 | 1.5839 | 1.6733 | 1.6218 | 0.0388 | 0.0015 | 3 | 1.1971 | 1.8137 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
55 | 493.681 | 44265.5601 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.7084 | 0:240:120 | 0:00 | 1.1285 | 7 | 0.0978 | 1.4697 | 1.5675 | 1.5134 | 0.0424 | 0.0018 | 3 | 1.1285 | 1.6754 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
58 | 500.994 | 44265.5602 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.2226 | 0:240:120 | 0:00 | 1.0652 | 7 | 0.0857 | 1.3661 | 1.4518 | 1.404 | 0.0365 | 0.0013 | 3 | 1.0652 | 1.5522 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
61 | 507.972 | 44265.5602 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.7471 | 0:240:120 | 0:00 | 1.0066 | 7 | 0.0713 | 1.2827 | 1.354 | 1.3153 | 0.0301 | 0.0009 | 3 | 1.0066 | 1.4419 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
64 | 514.667 | 44265.5603 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 27.282 | 0:240:120 | 0:00 | 0.9522 | 7 | 0.0745 | 1.2034 | 1.2779 | 1.2366 | 0.0309 | 0.001 | 3 | 0.9522 | 1.3428 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
67 | 521.203 | 44265.5604 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 27.8276 | 0:240:120 | 0:00 | 0.9017 | 7 | 0.0667 | 1.1243 | 1.191 | 1.1541 | 0.0282 | 0.0008 | 3 | 0.9017 | 1.2531 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
70 | 527.474 | 44265.5605 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.3842 | 0:240:120 | 0:00 | 0.8546 | 7 | 0.0635 | 1.0592 | 1.1227 | 1.0894 | 0.0266 | 0.0007 | 3 | 0.8546 | 1.1718 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
73 | 533.767 | 44265.5605 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.9519 | 0:240:120 | 0:00 | 0.8108 | 7 | 0.0561 | 0.9999 | 1.056 | 1.0261 | 0.0233 | 0.0005 | 3 | 0.8108 | 1.0977 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
76 | 539.577 | 44265.5606 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.5309 | 0:240:120 | 0:00 | 0.7698 | 7 | 0.0475 | 0.9403 | 0.9878 | 0.9633 | 0.0193 | 0.0004 | 3 | 0.7698 | 1.03 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
79 | 545.39 | 44265.5607 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.1215 | 0:240:120 | 0:00 | 0.7314 | 7 | 0.0459 | 0.8894 | 0.9353 | 0.9112 | 0.0192 | 0.0004 | 3 | 0.7314 | 0.9692 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
82 | 550.883 | 44265.5607 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.724 | 0:240:120 | 0:00 | 0.6954 | 7 | 0.0412 | 0.8436 | 0.8848 | 0.862 | 0.0178 | 0.0003 | 3 | 0.6954 | 0.9175 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
85 | 556.251 | 44265.5608 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.3384 | 0:240:120 | 0:00 | 0.6617 | 7 | 0.0348 | 0.8036 | 0.8384 | 0.8195 | 0.015 | 0.0002 | 3 | 0.6617 | 0.8694 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
88 | 561.52 | 44265.5609 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.9652 | 0:240:120 | 0:00 | 0.63 | 7 | 0.0349 | 0.7628 | 0.7977 | 0.7776 | 0.0149 | 0.0002 | 3 | 0.63 | 0.8245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
91 | 566.63 | 44265.5609 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.6045 | 0:240:120 | 0:00 | 0.6002 | 7 | 0.0324 | 0.7237 | 0.7561 | 0.7387 | 0.0138 | 0.0002 | 3 | 0.6002 | 0.7826 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
94 | 571.472 | 44265.561 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.2566 | 0:240:120 | 0:00 | 0.5721 | 7 | 0.0302 | 0.6894 | 0.7196 | 0.7024 | 0.0131 | 0.0002 | 3 | 0.5721 | 0.7434 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
97 | 576.292 | 44265.561 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.9217 | 0:240:120 | 0:00 | 0.5456 | 7 | 0.0313 | 0.6533 | 0.6846 | 0.6672 | 0.0133 | 0.0002 | 3 | 0.5456 | 0.7067 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
100 | 581.025 | 44265.5611 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.6002 | 0:240:120 | 0:00 | 0.5206 | 7 | 0.0268 | 0.6233 | 0.6501 | 0.6355 | 0.0113 | 0.0001 | 3 | 0.5206 | 0.6723 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
103 | 585.687 | 44265.5611 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.2922 | 0:240:120 | 0:00 | 0.497 | 7 | 0.0278 | 0.5939 | 0.6217 | 0.6063 | 0.0116 | 0.0001 | 3 | 0.497 | 0.6399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
106 | 590.352 | 44265.5612 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.998 | 0:240:120 | 0:00 | 0.4747 | 7 | 0.0257 | 0.5661 | 0.5918 | 0.5773 | 0.011 | 0.0001 | 3 | 0.4747 | 0.6095 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
109 | 594.922 | 44265.5613 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.718 | 0:240:120 | 0:00 | 0.4535 | 7 | 0.0215 | 0.5423 | 0.5638 | 0.5517 | 0.0092 | 0.0001 | 3 | 0.4535 | 0.5809 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
112 | 599.335 | 44265.5613 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.4523 | 0:240:120 | 0:00 | 0.4335 | 7 | 0.0199 | 0.5173 | 0.5372 | 0.5261 | 0.0086 | 0.0001 | 3 | 0.4335 | 0.5539 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
115 | 603.758 | 44265.5614 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.2014 | 0:240:120 | 0:00 | 0.4146 | 7 | 0.0177 | 0.4948 | 0.5125 | 0.5022 | 0.0078 | 0.0001 | 3 | 0.4146 | 0.5285 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
118 | 607.945 | 44265.5614 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.9654 | 0:240:120 | 0:00 | 0.3966 | 7 | 0.0197 | 0.4714 | 0.4911 | 0.4798 | 0.0084 | 0.0001 | 3 | 0.3966 | 0.5044 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
121 | 611.98 | 44265.5614 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.7447 | 0:240:120 | 0:00 | 0.3795 | 7 | 0.0179 | 0.4512 | 0.4691 | 0.459 | 0.0078 | 0.0001 | 3 | 0.3795 | 0.4817 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
124 | 616.105 | 44265.5615 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.5396 | 0:240:120 | 0:00 | 0.3633 | 7 | 0.0178 | 0.4299 | 0.4477 | 0.4376 | 0.0076 | 0.0001 | 3 | 0.3633 | 0.4602 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
127 | 620.29 | 44265.5615 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.3504 | 0:240:120 | 0:00 | 0.3479 | 7 | 0.0159 | 0.412 | 0.4279 | 0.4189 | 0.0068 | 0 | 3 | 0.3479 | 0.4398 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
130 | 624.33 | 44265.5616 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.1774 | 0:240:120 | 0:00 | 0.3333 | 7 | 0.016 | 0.3944 | 0.4104 | 0.4009 | 0.007 | 0 | 3 | 0.3333 | 0.4205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
133 | 628.216 | 44265.5616 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.021 | 0:240:120 | 0:00 | 0.3193 | 7 | 0.0158 | 0.3772 | 0.393 | 0.3839 | 0.0068 | 0 | 3 | 0.3193 | 0.4022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
136 | 632.051 | 44265.5617 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.8814 | 0:240:120 | 0:00 | 0.3061 | 7 | 0.0137 | 0.3619 | 0.3756 | 0.3676 | 0.0059 | 0 | 3 | 0.3061 | 0.3849 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
139 | 635.947 | 44265.5617 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.759 | 0:240:120 | 0:00 | 0.2935 | 7 | 0.0136 | 0.3464 | 0.36 | 0.3524 | 0.0057 | 0 | 3 | 0.2935 | 0.3684 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
142 | 639.83 | 44265.5618 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.6542 | 0:240:120 | 0:00 | 0.2814 | 7 | 0.0125 | 0.3322 | 0.3447 | 0.3371 | 0.0054 | 0 | 3 | 0.2814 | 0.3528 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
145 | 643.774 | 44265.5618 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.5673 | 0:240:120 | 0:00 | 0.27 | 7 | 0.0125 | 0.3181 | 0.3306 | 0.3237 | 0.0049 | 0 | 3 | 0.27 | 0.3379 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
148 | 647.614 | 44265.5619 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.4986 | 0:240:120 | 0:00 | 0.259 | 7 | 0.0105 | 0.3059 | 0.3164 | 0.3103 | 0.0045 | 0 | 3 | 0.259 | 0.3237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
151 | 651.097 | 44265.5619 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.4486 | 0:240:120 | 0:00 | 0.2486 | 7 | 0.0118 | 0.2918 | 0.3036 | 0.2973 | 0.0049 | 0 | 3 | 0.2486 | 0.3103 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
154 | 654.688 | 44265.5619 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.4176 | 0:240:120 | 0:00 | 0.2386 | 7 | 0.0103 | 0.2811 | 0.2914 | 0.2853 | 0.0046 | 0 | 3 | 0.2386 | 0.2974 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
157 | 658.299 | 44265.562 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.4059 | 0:240:120 | 0:00 | 0.2291 | 7 | 0.0104 | 0.2688 | 0.2792 | 0.2737 | 0.0042 | 0 | 3 | 0.2291 | 0.2852 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
160 | 661.894 | 44265.562 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.414 | 0:240:120 | 0:00 | 0.2201 | 7 | 0.0098 | 0.2586 | 0.2684 | 0.2627 | 0.0043 | 0 | 3 | 0.2201 | 0.2736 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
163 | 665.514 | 44265.5621 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.4423 | 0:240:120 | 0:00 | 0.2114 | 7 | 0.0093 | 0.248 | 0.2573 | 0.2516 | 0.0038 | 0 | 3 | 0.2114 | 0.2625 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
166 | 669.259 | 44265.5621 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.4912 | 0:240:120 | 0:00 | 0.2031 | 7 | 0.0093 | 0.2373 | 0.2466 | 0.2416 | 0.0037 | 0 | 3 | 0.2031 | 0.2519 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
169 | 672.833 | 44265.5622 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.561 | 0:240:120 | 0:00 | 0.1952 | 7 | 0.0095 | 0.2289 | 0.2384 | 0.2328 | 0.0039 | 0 | 3 | 0.1952 | 0.2418 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
172 | 676.398 | 44265.5622 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.6522 | 0:240:120 | 0:00 | 0.1876 | 7 | 0.0078 | 0.2201 | 0.2279 | 0.2237 | 0.0032 | 0 | 3 | 0.1876 | 0.2321 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
175 | 679.897 | 44265.5622 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.7652 | 0:240:120 | 0:00 | 0.1804 | 7 | 0.0076 | 0.2119 | 0.2195 | 0.2148 | 0.0033 | 0 | 3 | 0.1804 | 0.2229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
178 | 683.324 | 44265.5623 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.9005 | 0:240:120 | 0:00 | 0.1734 | 7 | 0.0089 | 0.2016 | 0.2105 | 0.2056 | 0.0036 | 0 | 3 | 0.1734 | 0.2141 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
181 | 686.686 | 44265.5623 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.0586 | 0:240:120 | 0:00 | 0.1668 | 7 | 0.0073 | 0.1948 | 0.2021 | 0.1979 | 0.003 | 0 | 3 | 0.1668 | 0.2057 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
184 | 689.992 | 44265.5624 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.2397 | 0:240:120 | 0:00 | 0.1604 | 7 | 0.0079 | 0.1868 | 0.1947 | 0.1905 | 0.0032 | 0 | 3 | 0.1604 | 0.1977 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
187 | 693.344 | 44265.5624 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.4445 | 0:240:120 | 0:00 | 0.1544 | 7 | 0.0065 | 0.1804 | 0.1869 | 0.183 | 0.0027 | 0 | 3 | 0.1544 | 0.19 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
190 | 696.565 | 44265.5624 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.6734 | 0:240:120 | 0:00 | 0.1485 | 7 | 0.0073 | 0.1733 | 0.1806 | 0.1765 | 0.0027 | 0 | 3 | 0.1485 | 0.1826 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
193 | 700.019 | 44265.5625 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.9269 | 0:240:120 | 0:00 | 0.1429 | 7 | 0.0054 | 0.1672 | 0.1726 | 0.1695 | 0.0023 | 0 | 3 | 0.1429 | 0.1756 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
196 | 703.289 | 44265.5625 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.2054 | 0:240:120 | 0:00 | 0.1376 | 7 | 0.0062 | 0.1604 | 0.1666 | 0.1635 | 0.0025 | 0 | 3 | 0.1376 | 0.1689 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
199 | 706.634 | 44265.5625 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.5095 | 0:240:120 | 0:00 | 0.1325 | 7 | 0.0053 | 0.1535 | 0.1588 | 0.1562 | 0.002 | 0 | 3 | 0.1325 | 0.1624 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
202 | 709.909 | 44265.5626 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.8397 | 0:240:120 | 0:00 | 0.1276 | 7 | 0.0055 | 0.1489 | 0.1544 | 0.1511 | 0.0021 | 0 | 3 | 0.1276 | 0.1563 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
205 | 713.266 | 44265.5626 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.1965 | 0:240:120 | 0:00 | 0.1229 | 7 | 0.005 | 0.143 | 0.148 | 0.1457 | 0.0018 | 0 | 3 | 0.1229 | 0.1504 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
208 | 716.785 | 44265.5627 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.5804 | 0:240:120 | 0:00 | 0.1183 | 7 | 0.0058 | 0.1371 | 0.1429 | 0.1401 | 0.0021 | 0 | 3 | 0.1183 | 0.1447 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
211 | 720.198 | 44265.5627 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.992 | 0:240:120 | 0:00 | 0.114 | 7 | 0.0062 | 0.1316 | 0.1378 | 0.1346 | 0.0022 | 0 | 3 | 0.114 | 0.1393 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
214 | 723.474 | 44265.5627 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.4319 | 0:240:120 | 0:00 | 0.1098 | 7 | 0.0056 | 0.1269 | 0.1325 | 0.1296 | 0.002 | 0 | 3 | 0.1098 | 0.1341 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
217 | 726.631 | 44265.5628 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.9005 | 0:240:120 | 0:00 | 0.1059 | 7 | 0.0052 | 0.1225 | 0.1277 | 0.1253 | 0.002 | 0 | 3 | 0.1059 | 0.1291 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
220 | 729.958 | 44265.5628 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.3985 | 0:240:120 | 0:00 | 0.102 | 7 | 0.0051 | 0.1179 | 0.123 | 0.1204 | 0.002 | 0 | 3 | 0.102 | 0.1243 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
223 | 732.922 | 44265.5628 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.9265 | 0:240:120 | 0:00 | 0.0984 | 7 | 0.005 | 0.1128 | 0.1178 | 0.1154 | 0.0018 | 0 | 3 | 0.0984 | 0.1198 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
226 | 735.955 | 44265.5629 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.485 | 0:240:120 | 0:00 | 0.0948 | 7 | 0.0041 | 0.11 | 0.1141 | 0.1121 | 0.0015 | 0 | 3 | 0.0948 | 0.1154 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
229 | 738.891 | 44265.5629 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.0747 | 0:240:120 | 0:00 | 0.0915 | 7 | 0.0045 | 0.106 | 0.1105 | 0.1082 | 0.0017 | 0 | 3 | 0.0915 | 0.1112 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
232 | 741.901 | 44265.563 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.6962 | 0:240:120 | 0:00 | 0.0882 | 7 | 0.0051 | 0.1009 | 0.106 | 0.104 | 0.0019 | 0 | 3 | 0.0882 | 0.1071 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
235 | 744.841 | 44265.563 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.3502 | 0:240:120 | 0:00 | 0.0851 | 7 | 0.0046 | 0.0977 | 0.1023 | 0.1001 | 0.0017 | 0 | 3 | 0.0851 | 0.1032 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
238 | 747.765 | 44265.563 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.0372 | 0:240:120 | 0:00 | 0.0821 | 7 | 0.0045 | 0.0941 | 0.0986 | 0.0964 | 0.0016 | 0 | 3 | 0.0821 | 0.0995 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
241 | 750.846 | 44265.5631 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.7579 | 0:240:120 | 0:00 | 0.0792 | 7 | 0.0039 | 0.0914 | 0.0953 | 0.0934 | 0.0015 | 0 | 3 | 0.0792 | 0.096 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
244 | 753.954 | 44265.5631 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.5131 | 0:240:120 | 0:00 | 0.0765 | 7 | 0.0043 | 0.0882 | 0.0925 | 0.0906 | 0.0017 | 0 | 3 | 0.0765 | 0.0925 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
247 | 757.264 | 44265.5631 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.3033 | 0:240:120 | 0:00 | 0.0738 | 7 | 0.0037 | 0.0853 | 0.089 | 0.0871 | 0.0015 | 0 | 3 | 0.0738 | 0.0892 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
250 | 760.262 | 44265.5632 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.1294 | 0:240:120 | 0:00 | 0.0713 | 7 | 0.0046 | 0.0813 | 0.0859 | 0.0837 | 0.0018 | 0 | 3 | 0.0713 | 0.0861 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
253 | 763.27 | 44265.5632 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.992 | 0:240:120 | 0:00 | 0.0688 | 7 | 0.0036 | 0.0785 | 0.0821 | 0.0803 | 0.0013 | 0 | 3 | 0.0688 | 0.0831 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
256 | 766.385 | 44265.5632 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.8918 | 0:240:120 | 0:00 | 0.0665 | 7 | 0.0039 | 0.0763 | 0.0802 | 0.0785 | 0.0016 | 0 | 3 | 0.0665 | 0.0801 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
259 | 769.657 | 44265.5633 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.8297 | 0:240:120 | 0:00 | 0.0642 | 7 | 0.0023 | 0.0745 | 0.0768 | 0.076 | 0.0011 | 0 | 3 | 0.0642 | 0.0774 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
262 | 772.777 | 44265.5633 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.8062 | 0:240:120 | 0:00 | 0.0621 | 7 | 0.0042 | 0.0706 | 0.0748 | 0.0725 | 0.0016 | 0 | 3 | 0.0621 | 0.0747 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
265 | 776.033 | 44265.5633 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.8224 | 0:240:120 | 0:00 | 0.06 | 7 | 0.0035 | 0.068 | 0.0715 | 0.0698 | 0.0012 | 0 | 3 | 0.06 | 0.0721 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
268 | 779.145 | 44265.5634 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.8788 | 0:240:120 | 0:00 | 0.058 | 7 | 0.0051 | 0.0656 | 0.0707 | 0.0682 | 0.0019 | 0 | 3 | 0.058 | 0.0696 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
271 | 782.212 | 44265.5634 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.9764 | 0:240:120 | 0:00 | 0.056 | 7 | 0.0033 | 0.0642 | 0.0675 | 0.0661 | 0.0013 | 0 | 3 | 0.056 | 0.0672 | P | NP | 1-1-1-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
274 | 785.255 | 44265.5635 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.1159 | 0:240:120 | 0:00 | 0.0542 | 7 | 0.0042 | 0.0609 | 0.0651 | 0.063 | 0.0016 | 0 | 3 | 0.0542 | 0.065 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
277 | 788.39 | 44265.5635 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.2982 | 0:240:120 | 0:00 | 0.0524 | 7 | 0.0027 | 0.0596 | 0.0623 | 0.0612 | 0.0011 | 0 | 3 | 0.0524 | 0.0629 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
280 | 791.542 | 44265.5635 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.5242 | 0:240:120 | 0:00 | 0.0507 | 7 | 0.0028 | 0.0578 | 0.0606 | 0.0596 | 0.0011 | 0 | 3 | 0.0507 | 0.0608 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
283 | 794.767 | 44265.5636 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 115.7947 | 0:240:120 | 0:00 | 0.049 | 7 | 0.0027 | 0.0557 | 0.0584 | 0.0573 | 0.001 | 0 | 3 | 0.049 | 0.059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
286 | 797.796 | 44265.5636 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.1106 | 0:240:120 | 0:00 | 0.0475 | 7 | 0.0028 | 0.054 | 0.0568 | 0.0556 | 0.0011 | 0 | 3 | 0.0475 | 0.0575 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
289 | 801.012 | 44265.5636 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.4728 | 0:240:120 | 0:00 | 0.0459 | 7 | 0.0037 | 0.0515 | 0.0552 | 0.0537 | 0.0013 | 0 | 3 | 0.0459 | 0.0559 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
292 | 804.138 | 44265.5637 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 122.8823 | 0:240:120 | 0:00 | 0.0445 | 7 | 0.0031 | 0.0499 | 0.053 | 0.0518 | 0.0012 | 0 | 3 | 0.0445 | 0.0545 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
295 | 807.257 | 44265.5637 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.3399 | 0:240:120 | 0:00 | 0.0431 | 7 | 0.0034 | 0.0477 | 0.0511 | 0.0499 | 0.0012 | 0 | 3 | 0.0431 | 0.0531 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
298 | 810.502 | 44265.5637 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 127.8467 | 0:240:120 | 0:00 | 0.0417 | 7 | 0.0032 | 0.0471 | 0.0503 | 0.0488 | 0.0011 | 0 | 3 | 0.0417 | 0.0517 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
301 | 813.738 | 44265.5638 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.4036 | 0:240:120 | 0:00 | 0.0404 | 7 | 0.0026 | 0.0453 | 0.0479 | 0.0467 | 0.0009 | 0 | 3 | 0.0404 | 0.0504 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
304 | 816.855 | 44265.5638 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.0117 | 0:240:120 | 0:00 | 0.0391 | 7 | 0.0032 | 0.0444 | 0.0476 | 0.046 | 0.0012 | 0 | 3 | 0.0391 | 0.0491 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
307 | 819.978 | 44265.5639 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 135.6719 | 0:240:120 | 0:00 | 0.0379 | 7 | 0.0032 | 0.0424 | 0.0456 | 0.0445 | 0.001 | 0 | 3 | 0.0379 | 0.0479 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
310 | 823.214 | 44265.5639 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.3854 | 0:240:120 | 0:00 | 0.0368 | 7 | 0.0032 | 0.0409 | 0.0441 | 0.0429 | 0.0013 | 0 | 3 | 0.0368 | 0.0468 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
313 | 826.329 | 44265.5639 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.1531 | 0:240:120 | 0:00 | 0.0357 | 7 | 0.0026 | 0.0397 | 0.0423 | 0.0416 | 0.0009 | 0 | 3 | 0.0357 | 0.0457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
316 | 829.383 | 44265.564 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 143.9761 | 0:240:120 | 0:00 | 0.0346 | 7 | 0.0041 | 0.0385 | 0.0426 | 0.0408 | 0.0014 | 0 | 3 | 0.0346 | 0.0446 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
319 | 832.429 | 44265.564 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 146.8557 | 0:240:120 | 0:00 | 0.0336 | 7 | 0.0029 | 0.0372 | 0.0401 | 0.039 | 0.0013 | 0 | 3 | 0.0336 | 0.0436 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
322 | 835.566 | 44265.564 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 149.7928 | 0:240:120 | 0:00 | 0.0326 | 7 | 0.0026 | 0.036 | 0.0386 | 0.038 | 0.0009 | 0 | 3 | 0.0326 | 0.0426 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
325 | 838.574 | 44265.5641 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 152.7886 | 0:240:120 | 0:00 | 0.0316 | 7 | 0.0028 | 0.0353 | 0.0381 | 0.0367 | 0.001 | 0 | 3 | 0.0316 | 0.0416 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
328 | 841.768 | 44265.5641 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 155.8444 | 0:240:120 | 0:00 | 0.0307 | 7 | 0.003 | 0.0344 | 0.0374 | 0.0362 | 0.0013 | 0 | 3 | 0.0307 | 0.0407 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
331 | 845.022 | 44265.5641 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 158.9613 | 0:240:120 | 0:00 | 0.0298 | 7 | 0.004 | 0.0327 | 0.0367 | 0.035 | 0.0013 | 0 | 3 | 0.0298 | 0.0398 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
334 | 848.072 | 44265.5642 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 162.1405 | 0:240:120 | 0:00 | 0.029 | 7 | 0.0041 | 0.0315 | 0.0356 | 0.0339 | 0.0013 | 0 | 3 | 0.029 | 0.039 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
337 | 851.078 | 44265.5642 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.3833 | 0:240:120 | 0:00 | 0.0281 | 7 | 0.003 | 0.0308 | 0.0338 | 0.033 | 0.0011 | 0 | 3 | 0.0281 | 0.0381 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
340 | 854.147 | 44265.5643 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 168.691 | 0:240:120 | 0:00 | 0.0273 | 7 | 0.0037 | 0.0298 | 0.0335 | 0.0322 | 0.0015 | 0 | 3 | 0.0273 | 0.0373 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
343 | 857.278 | 44265.5643 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 172.0648 | 0:240:120 | 0:00 | 0.0266 | 7 | 0.0027 | 0.0298 | 0.0325 | 0.0315 | 0.0009 | 0 | 3 | 0.0266 | 0.0366 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
346 | 860.465 | 44265.5643 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175.5061 | 0:240:120 | 0:00 | 0.0259 | 7 | 0.0038 | 0.0277 | 0.0315 | 0.0301 | 0.0014 | 0 | 3 | 0.0259 | 0.0359 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
349 | 863.485 | 44265.5644 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 179.0162 | 0:240:120 | 0:00 | 0.0252 | 7 | 0.0029 | 0.0273 | 0.0302 | 0.0293 | 0.0012 | 0 | 3 | 0.0252 | 0.0352 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
352 | 866.515 | 44265.5644 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 182.5966 | 0:240:120 | 0:00 | 0.0245 | 7 | 0.0039 | 0.0266 | 0.0305 | 0.0287 | 0.0015 | 0 | 3 | 0.0245 | 0.0345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
355 | 869.679 | 44265.5644 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 186.2485 | 0:240:120 | 0:00 | 0.0238 | 7 | 0.003 | 0.0267 | 0.0297 | 0.0282 | 0.0012 | 0 | 3 | 0.0238 | 0.0338 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
358 | 872.824 | 44265.5645 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 189.9735 | 0:240:120 | 0:00 | 0.0232 | 7 | 0.0031 | 0.0256 | 0.0287 | 0.0273 | 0.0011 | 0 | 3 | 0.0232 | 0.0332 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
361 | 876.084 | 44265.5645 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 193.7729 | 0:240:120 | 0:00 | 0.0226 | 7 | 0.003 | 0.0253 | 0.0283 | 0.0269 | 0.0011 | 0 | 3 | 0.0226 | 0.0326 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
364 | 879.338 | 44265.5645 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 197.6484 | 0:240:120 | 0:00 | 0.022 | 7 | 0.0031 | 0.0247 | 0.0278 | 0.0263 | 0.0011 | 0 | 3 | 0.022 | 0.032 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
367 | 882.467 | 44265.5646 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 201.6014 | 0:240:120 | 0:00 | 0.0215 | 7 | 0.0029 | 0.0234 | 0.0263 | 0.0253 | 0.0012 | 0 | 3 | 0.0215 | 0.0315 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
370 | 885.45 | 44265.5646 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 205.6334 | 0:240:120 | 0:00 | 0.0209 | 7 | 0.0038 | 0.0225 | 0.0263 | 0.0249 | 0.0015 | 0 | 3 | 0.0209 | 0.0309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
373 | 888.477 | 44265.5646 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 209.7461 | 0:240:120 | 0:00 | 0.0204 | 7 | 0.003 | 0.0227 | 0.0257 | 0.0243 | 0.0011 | 0 | 3 | 0.0204 | 0.0304 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
376 | 891.649 | 44265.5647 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 213.941 | 0:240:120 | 0:00 | 0.0199 | 7 | 0.0037 | 0.0218 | 0.0255 | 0.0238 | 0.0014 | 0 | 3 | 0.0199 | 0.0299 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
379 | 894.721 | 44265.5647 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 218.2198 | 0:240:120 | 0:00 | 0.0194 | 7 | 0.0037 | 0.0209 | 0.0246 | 0.0232 | 0.0014 | 0 | 3 | 0.0194 | 0.0294 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
382 | 897.85 | 44265.5648 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 222.5842 | 0:240:120 | 0:00 | 0.019 | 7 | 0.0025 | 0.0214 | 0.0239 | 0.0229 | 0.0009 | 0 | 3 | 0.019 | 0.029 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
385 | 900.953 | 44265.5648 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 227.0359 | 0:240:120 | 0:00 | 0.0185 | 7 | 0.0023 | 0.0212 | 0.0235 | 0.0223 | 0.0008 | 0 | 3 | 0.0185 | 0.0285 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
388 | 905.307 | 44265.5648 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 231.5766 | 0:240:120 | 0:00 | 0.0181 | 7 | 0.0032 | 0.0198 | 0.023 | 0.0218 | 0.0012 | 0 | 3 | 0.0181 | 0.0281 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
391 | 908.375 | 44265.5649 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 236.2081 | 0:240:120 | 0:00 | 0.0177 | 7 | 0.0042 | 0.0195 | 0.0237 | 0.0216 | 0.0015 | 0 | 3 | 0.0177 | 0.0277 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
394 | 911.635 | 44265.5649 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 240.9323 | 0:240:120 | 0:00 | 0.0173 | 7 | 0.0024 | 0.0194 | 0.0218 | 0.021 | 0.0011 | 0 | 3 | 0.0173 | 0.0273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
397 | 914.724 | 44265.565 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 245.7509 | 0:240:120 | 0:00 | 0.0169 | 7 | 0.0041 | 0.0184 | 0.0225 | 0.0208 | 0.0016 | 0 | 3 | 0.0169 | 0.0269 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
400 | 917.979 | 44265.565 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 250.666 | 0:240:120 | 0:00 | 0.0165 | 7 | 0.0032 | 0.0189 | 0.0221 | 0.0206 | 0.001 | 0 | 3 | 0.0165 | 0.0265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
403 | 921.05 | 44265.565 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 255.6793 | 0:240:120 | 0:00 | 0.0162 | 7 | 0.0032 | 0.0184 | 0.0216 | 0.0201 | 0.0011 | 0 | 3 | 0.0162 | 0.0262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
406 | 924.274 | 44265.5651 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 260.7929 | 0:240:120 | 0:00 | 0.0158 | 7 | 0.003 | 0.0183 | 0.0213 | 0.0196 | 0.0012 | 0 | 3 | 0.0158 | 0.0258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
409 | 927.425 | 44265.5651 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 266.0087 | 0:240:120 | 0:00 | 0.0155 | 7 | 0.003 | 0.0177 | 0.0207 | 0.0192 | 0.001 | 0 | 3 | 0.0155 | 0.0255 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
412 | 930.498 | 44265.5651 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 271.3289 | 0:240:120 | 0:00 | 0.0152 | 7 | 0.0028 | 0.0178 | 0.0206 | 0.0191 | 0.0009 | 0 | 3 | 0.0152 | 0.0252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
415 | 933.597 | 44265.5652 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 276.7555 | 0:240:120 | 0:00 | 0.0149 | 7 | 0.0018 | 0.0179 | 0.0197 | 0.0189 | 0.0005 | 0 | 3 | 0.0149 | 0.0249 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
418 | 936.637 | 44265.5652 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 282.2906 | 0:240:120 | 0:00 | 0.0146 | 7 | 0.0019 | 0.0181 | 0.02 | 0.0186 | 0.0007 | 0 | 3 | 0.0146 | 0.0246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
421 | 939.72 | 44265.5652 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 287.9364 | 0:240:120 | 0:00 | 0.0143 | 7 | 0.0018 | 0.0175 | 0.0193 | 0.0181 | 0.0006 | 0 | 3 | 0.0143 | 0.0243 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
424 | 942.779 | 44265.5653 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 293.6951 | 0:240:120 | 0:00 | 0.014 | 7 | 0.002 | 0.0168 | 0.0188 | 0.0176 | 0.0006 | 0 | 3 | 0.014 | 0.024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
427 | 945.837 | 44265.5653 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 299.569 | 0:240:120 | 0:00 | 0.0138 | 7 | 0.0022 | 0.0163 | 0.0185 | 0.0173 | 0.0008 | 0 | 3 | 0.0138 | 0.0238 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
430 | 948.814 | 44265.5653 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 305.5604 | 0:240:120 | 0:00 | 0.0135 | 7 | 0.002 | 0.0162 | 0.0182 | 0.0172 | 0.0009 | 0 | 3 | 0.0135 | 0.0235 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
433 | 951.874 | 44265.5654 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 311.6716 | 0:240:120 | 0:00 | 0.0133 | 7 | 0.0018 | 0.0157 | 0.0175 | 0.0164 | 0.0007 | 0 | 3 | 0.0133 | 0.0233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
436 | 954.95 | 44265.5654 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 317.905 | 0:240:120 | 0:00 | 0.0131 | 7 | 0.0029 | 0.0155 | 0.0184 | 0.0163 | 0.001 | 0 | 3 | 0.0131 | 0.0231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
439 | 957.832 | 44265.5655 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 324.2631 | 0:240:120 | 0:00 | 0.0128 | 7 | 0.0038 | 0.014 | 0.0178 | 0.0161 | 0.0012 | 0 | 3 | 0.0128 | 0.0228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
442 | 960.971 | 44265.5655 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 330.7484 | 0:240:120 | 0:00 | 0.0126 | 7 | 0.0044 | 0.0137 | 0.0181 | 0.0158 | 0.0014 | 0 | 3 | 0.0126 | 0.0226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
445 | 964.047 | 44265.5655 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 337.3634 | 0:240:120 | 0:00 | 0.0124 | 7 | 0.003 | 0.0142 | 0.0172 | 0.0155 | 0.0011 | 0 | 3 | 0.0124 | 0.0224 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
448 | 967.115 | 44265.5656 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 344.1106 | 0:240:120 | 0:00 | 0.0122 | 7 | 0.0042 | 0.0128 | 0.017 | 0.0151 | 0.0017 | 0 | 3 | 0.0122 | 0.0222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
451 | 970.167 | 44265.5656 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 350.9928 | 0:240:120 | 0:00 | 0.012 | 7 | 0.0041 | 0.013 | 0.0171 | 0.0149 | 0.0015 | 0 | 3 | 0.012 | 0.022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
454 | 973.269 | 44265.5656 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 358.0127 | 0:240:120 | 0:00 | 0.0118 | 7 | 0.0029 | 0.0133 | 0.0162 | 0.0148 | 0.0012 | 0 | 3 | 0.0118 | 0.0218 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
457 | 976.534 | 44265.5657 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 365.173 | 0:240:120 | 0:00 | 0.0117 | 7 | 0.0039 | 0.0126 | 0.0165 | 0.0147 | 0.0015 | 0 | 3 | 0.0117 | 0.0217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
460 | 979.83 | 44265.5657 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 372.4764 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0042 | 0.0126 | 0.0168 | 0.0144 | 0.0016 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
463 | 982.987 | 44265.5657 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 379.9259 | 0:240:120 | 0:00 | 0.0113 | 7 | 0.0046 | 0.0119 | 0.0165 | 0.0143 | 0.0017 | 0 | 3 | 0.0113 | 0.0213 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
466 | 986.08 | 44265.5658 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 387.5245 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.0047 | 0.012 | 0.0167 | 0.0143 | 0.0018 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
469 | 989.185 | 44265.5658 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 395.275 | 0:240:120 | 0:00 | 0.011 | 7 | 0.0057 | 0.0115 | 0.0172 | 0.0143 | 0.0021 | 0 | 3 | 0.011 | 0.021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
472 | 992.35 | 44265.5659 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 403.1805 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0045 | 0.012 | 0.0165 | 0.0142 | 0.0019 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
475 | 995.621 | 44265.5659 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 411.2441 | 0:240:120 | 0:00 | 0.0107 | 7 | 0.0054 | 0.0114 | 0.0168 | 0.014 | 0.0018 | 0 | 3 | 0.0107 | 0.0207 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
478 | 998.825 | 44265.5659 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 419.4689 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0046 | 0.0113 | 0.0159 | 0.0139 | 0.0018 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
481 | 1002.103 | 44265.566 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 427.8583 | 0:240:120 | 0:00 | 0.0104 | 7 | 0.0052 | 0.0112 | 0.0164 | 0.0138 | 0.0019 | 0 | 3 | 0.0104 | 0.0204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
484 | 1005.098 | 44265.566 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 436.4155 | 0:240:120 | 0:00 | 0.0103 | 7 | 0.0041 | 0.0112 | 0.0153 | 0.0136 | 0.0014 | 0 | 3 | 0.0103 | 0.0203 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
487 | 1008.362 | 44265.566 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 445.1438 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.0047 | 0.0111 | 0.0158 | 0.0135 | 0.0018 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
490 | 1011.516 | 44265.5661 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 454.0467 | 0:240:120 | 0:00 | 0.0101 | 7 | 0.0053 | 0.0111 | 0.0164 | 0.0135 | 0.0021 | 0 | 3 | 0.0101 | 0.0201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
493 | 1014.619 | 44265.5661 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 459.9405 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0041 | 0.011 | 0.0151 | 0.0134 | 0.0014 | 0 | 3 | 0.01 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
496 | 1017.783 | 44265.5661 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 469.1393 | 0:240:120 | 0:00 | 0.0099 | 7 | 0.005 | 0.0106 | 0.0156 | 0.0131 | 0.0017 | 0 | 3 | 0.0099 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
499 | 1021.078 | 44265.5662 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 478.5221 | 0:240:120 | 0:00 | 0.0098 | 7 | 0.0036 | 0.011 | 0.0146 | 0.0132 | 0.0013 | 0 | 3 | 0.0098 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
502 | 1024.375 | 44265.5662 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 488.0925 | 0:240:120 | 0:00 | 0.0097 | 7 | 0.0041 | 0.0106 | 0.0147 | 0.0128 | 0.0014 | 0 | 3 | 0.0097 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
505 | 1027.556 | 44265.5663 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 497.8544 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0038 | 0.0113 | 0.0151 | 0.0129 | 0.0014 | 0 | 3 | 0.0096 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
508 | 1030.846 | 44265.5663 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 507.8114 | 0:240:120 | 0:00 | 0.0095 | 7 | 0.0048 | 0.0103 | 0.0151 | 0.0124 | 0.0016 | 0 | 3 | 0.0095 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
511 | 1034.034 | 44265.5663 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 517.9677 | 0:240:120 | 0:00 | 0.0094 | 7 | 0.0031 | 0.0105 | 0.0136 | 0.0122 | 0.0011 | 0 | 3 | 0.0094 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
514 | 1037.206 | 44265.5664 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 528.327 | 0:240:120 | 0:00 | 0.0093 | 7 | 0.0046 | 0.0104 | 0.015 | 0.0125 | 0.0016 | 0 | 3 | 0.0093 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
517 | 1040.51 | 44265.5664 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 538.8936 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0051 | 0.0101 | 0.0152 | 0.012 | 0.0016 | 0 | 3 | 0.0092 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
520 | 1043.717 | 44265.5664 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 549.6714 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.0041 | 0.0103 | 0.0144 | 0.0116 | 0.0014 | 0 | 3 | 0.0091 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
523 | 1046.859 | 44265.5665 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 560.6649 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.0052 | 0.01 | 0.0152 | 0.0119 | 0.0017 | 0 | 3 | 0.0091 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
526 | 1050.05 | 44265.5665 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 571.8782 | 0:240:120 | 0:00 | 0.009 | 7 | 0.003 | 0.0106 | 0.0136 | 0.0116 | 0.001 | 0 | 3 | 0.009 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
529 | 1053.167 | 44265.5666 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 583.3157 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0025 | 0.0104 | 0.0129 | 0.0115 | 0.0008 | 0 | 3 | 0.0089 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
532 | 1056.172 | 44265.5666 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 594.982 | 0:240:120 | 0:00 | 0.0088 | 7 | 0.0039 | 0.0096 | 0.0135 | 0.0113 | 0.0011 | 0 | 3 | 0.0088 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
535 | 1059.304 | 44265.5666 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 606.8817 | 0:240:120 | 0:00 | 0.0088 | 7 | 0.0039 | 0.0101 | 0.014 | 0.0112 | 0.0014 | 0 | 3 | 0.0088 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
538 | 1062.505 | 44265.5667 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 619.0193 | 0:240:120 | 0:00 | 0.0087 | 7 | 0.0025 | 0.0097 | 0.0122 | 0.0108 | 0.0009 | 0 | 3 | 0.0087 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
541 | 1065.595 | 44265.5667 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 631.3997 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0059 | 0.0091 | 0.015 | 0.0115 | 0.0018 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
544 | 1068.879 | 44265.5667 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 644.0277 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0021 | 0.0101 | 0.0122 | 0.0106 | 0.0008 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
547 | 1071.996 | 44265.5668 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 656.9082 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0022 | 0.0096 | 0.0118 | 0.0106 | 0.0009 | 0 | 3 | 0.0085 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
550 | 1075.177 | 44265.5668 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 670.0464 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0044 | 0.0096 | 0.014 | 0.011 | 0.0014 | 0 | 3 | 0.0085 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
553 | 1078.278 | 44265.5668 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 683.4473 | 0:240:120 | 0:00 | 0.0084 | 7 | 0.0048 | 0.0096 | 0.0144 | 0.0111 | 0.0015 | 0 | 3 | 0.0084 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
556 | 1081.46 | 44265.5669 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 697.1163 | 0:240:120 | 0:00 | 0.0084 | 7 | 0.0051 | 0.0094 | 0.0145 | 0.0109 | 0.0017 | 0 | 3 | 0.0084 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
559 | 1084.666 | 44265.5669 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 711.0586 | 0:240:120 | 0:00 | 0.0083 | 7 | 0.0038 | 0.0103 | 0.0141 | 0.0113 | 0.0012 | 0 | 3 | 0.0083 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
562 | 1087.884 | 44265.567 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 725.2798 | 0:240:120 | 0:00 | 0.0083 | 7 | 0.0025 | 0.009 | 0.0115 | 0.0103 | 0.0009 | 0 | 3 | 0.0083 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
565 | 1091.09 | 44265.567 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 739.7854 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0024 | 0.0094 | 0.0118 | 0.0104 | 0.0009 | 0 | 3 | 0.0082 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
568 | 1094.295 | 44265.567 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 754.5811 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0101 | 0.0007 | 0 | 3 | 0.0082 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
571 | 1097.502 | 44265.5671 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 769.6727 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0018 | 0.0093 | 0.0111 | 0.01 | 0.0007 | 0 | 3 | 0.0081 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
574 | 1100.704 | 44265.5671 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 785.0662 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0052 | 0.0099 | 0.0151 | 0.0106 | 0.0017 | 0 | 3 | 0.0081 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
577 | 1103.919 | 44265.5671 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 800.7675 | 0:240:120 | 0:00 | 0.008 | 7 | 0.002 | 0.0097 | 0.0117 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
580 | 1107.127 | 44265.5672 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 816.7828 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0023 | 0.009 | 0.0113 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
583 | 1110.247 | 44265.5672 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 833.1185 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
586 | 1113.417 | 44265.5673 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 849.7809 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0016 | 0.0094 | 0.011 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
589 | 1116.641 | 44265.5673 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 866.7765 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
592 | 1119.959 | 44265.5673 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 884.112 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0015 | 0.01 | 0.0115 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
595 | 1123.054 | 44265.5674 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 901.7943 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0018 | 0.0095 | 0.0113 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
598 | 1126.28 | 44265.5674 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 919.8301 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0017 | 0.0097 | 0.0114 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
601 | 1129.385 | 44265.5674 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 919.8809 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0016 | 0.0098 | 0.0114 | 0.0106 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
604 | 1132.376 | 44265.5675 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 938.2786 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0022 | 0.0089 | 0.0111 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
607 | 1135.49 | 44265.5675 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 957.0441 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
610 | 1138.581 | 44265.5675 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 976.185 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
613 | 1141.744 | 44265.5676 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 995.7087 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0015 | 0.0094 | 0.0109 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
616 | 1144.973 | 44265.5676 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1015.6229 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
619 | 1148.276 | 44265.5677 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1035.9353 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0024 | 0.0089 | 0.0113 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
622 | 1151.605 | 44265.5677 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1056.6541 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0012 | 0.0091 | 0.0103 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
625 | 1154.609 | 44265.5677 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1077.7871 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
628 | 1157.738 | 44265.5678 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1099.3429 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0021 | 0.009 | 0.0111 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
631 | 1160.945 | 44265.5678 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1121.3297 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0019 | 0.009 | 0.0109 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
634 | 1164.043 | 44265.5678 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1143.7563 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0095 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
637 | 1167.171 | 44265.5679 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1166.6315 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.0102 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
640 | 1170.311 | 44265.5679 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1189.9641 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0018 | 0.009 | 0.0108 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
643 | 1173.442 | 44265.5679 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1213.7634 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0021 | 0.0094 | 0.0115 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
646 | 1176.566 | 44265.568 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1238.0386 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
649 | 1179.698 | 44265.568 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1262.7994 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0009 | 0.0097 | 0.0106 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
652 | 1182.92 | 44265.5681 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1288.0554 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0019 | 0.0095 | 0.0114 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
655 | 1186.175 | 44265.5681 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1313.8165 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0018 | 0.0093 | 0.0111 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
658 | 1189.516 | 44265.5681 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1340.0928 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0019 | 0.0095 | 0.0114 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
661 | 1192.819 | 44265.5682 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1366.8947 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0105 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
664 | 1195.948 | 44265.5682 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1394.2326 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
667 | 1199.095 | 44265.5682 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1422.1172 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
670 | 1202.425 | 44265.5683 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1450.5596 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.002 | 0.0089 | 0.0109 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
673 | 1205.645 | 44265.5683 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1479.5708 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
676 | 1208.873 | 44265.5684 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1509.1622 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0021 | 0.0093 | 0.0114 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
679 | 1212.018 | 44265.5684 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1539.3454 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.001 | 0.0097 | 0.0107 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
682 | 1215.224 | 44265.5684 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1570.1323 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
685 | 1218.488 | 44265.5685 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1601.535 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0012 | 0.0093 | 0.0105 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
688 | 1221.717 | 44265.5685 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1633.5657 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
691 | 1224.843 | 44265.5685 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1666.237 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.001 | 0.0097 | 0.0107 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
694 | 1228.079 | 44265.5686 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1699.5617 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
697 | 1231.412 | 44265.5686 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1733.553 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0019 | 0.009 | 0.0109 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
700 | 1234.745 | 44265.5687 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1768.224 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
703 | 1237.997 | 44265.5687 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1803.5885 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0022 | 0.009 | 0.0112 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
706 | 1241.232 | 44265.5687 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1839.6603 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0013 | 0.0095 | 0.0108 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
709 | 1244.373 | 44265.5688 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1876.4535 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.001 | 0.0091 | 0.0101 | 0.0096 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
712 | 1247.522 | 44265.5688 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1913.9826 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
715 | 1250.776 | 44265.5688 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1952.2622 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.001 | 0.0098 | 0.0108 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
718 | 1254.01 | 44265.5689 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1991.3075 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
721 | 1257.173 | 44265.5689 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2031.1336 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0014 | 0.0089 | 0.0103 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
724 | 1260.413 | 44265.569 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2071.7563 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0014 | 0.0095 | 0.0109 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
727 | 1263.574 | 44265.569 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2113.1914 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0022 | 0.0089 | 0.0111 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
730 | 1266.709 | 44265.569 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2155.4552 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0024 | 0.0088 | 0.0112 | 0.0096 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
733 | 1269.972 | 44265.5691 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2198.5643 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
736 | 1273.229 | 44265.5691 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2242.5356 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
739 | 1276.397 | 44265.5691 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2287.3863 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0007 | 0.0099 | 0.0106 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
742 | 1279.567 | 44265.5692 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2333.1341 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0012 | 0.0098 | 0.011 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
745 | 1282.815 | 44265.5692 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2379.7967 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0095 | 0.0108 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
748 | 1285.947 | 44265.5692 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2427.3927 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
751 | 1289.324 | 44265.5693 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2475.9405 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0007 | 0.01 | 0.0107 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
754 | 1292.559 | 44265.5693 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2525.4593 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0021 | 0.0092 | 0.0113 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
757 | 1295.713 | 44265.5694 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2575.9685 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
760 | 1298.78 | 44265.5694 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2627.4879 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0021 | 0.0092 | 0.0113 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
763 | 1301.934 | 44265.5694 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2680.0377 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0015 | 0.0092 | 0.0107 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
766 | 1305.195 | 44265.5695 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2733.6384 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
769 | 1308.463 | 44265.5695 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2788.3112 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0006 | 0.01 | 0.0106 | 0.0102 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
772 | 1311.621 | 44265.5695 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2844.0774 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
775 | 1314.895 | 44265.5696 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2900.9589 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0004 | 0.0101 | 0.0105 | 0.0104 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
778 | 1318.15 | 44265.5696 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2958.9781 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
781 | 1321.402 | 44265.5697 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3018.1577 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0008 | 0.0097 | 0.0105 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
784 | 1324.57 | 44265.5697 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3078.5208 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0007 | 0.0095 | 0.0102 | 0.0098 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
787 | 1327.638 | 44265.5697 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3140.0913 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
790 | 1330.909 | 44265.5698 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3202.8931 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
793 | 1334.164 | 44265.5698 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3266.9509 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
796 | 1337.327 | 44265.5698 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3332.29 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0007 | 0.01 | 0.0107 | 0.0103 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
799 | 1340.602 | 44265.5699 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3398.9358 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0021 | 0.0088 | 0.0109 | 0.0096 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
802 | 1343.851 | 44265.5699 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3466.9145 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0022 | 0.0088 | 0.011 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
805 | 1347.126 | 44265.57 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3536.2528 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0021 | 0.0091 | 0.0112 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
808 | 1350.409 | 44265.57 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3606.9778 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0018 | 0.0094 | 0.0112 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
811 | 1353.561 | 44265.57 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3679.1174 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
814 | 1356.829 | 44265.5701 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3752.6997 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.001 | 0.0096 | 0.0106 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
817 | 1360.013 | 44265.5701 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3827.7537 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
820 | 1363.272 | 44265.5701 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3904.3088 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
823 | 1366.566 | 44265.5702 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3982.395 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
826 | 1369.624 | 44265.5702 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4062.0429 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
829 | 1372.887 | 44265.5703 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4143.2837 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0018 | 0.0091 | 0.0109 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
832 | 1376.161 | 44265.5703 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4226.1494 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0015 | 0.0094 | 0.0109 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
835 | 1379.346 | 44265.5703 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4310.6724 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0012 | 0.01 | 0.0112 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
838 | 1382.623 | 44265.5704 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4396.8858 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
841 | 1385.896 | 44265.5704 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4484.8236 | 0:240:120 | 0:00 | 0.007 | 7 | 0.002 | 0.0091 | 0.0111 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
844 | 1389.084 | 44265.5704 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4574.52 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0004 | 0.0099 | 0.0103 | 0.0101 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
847 | 1392.189 | 44265.5705 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4666.0104 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.0098 | 0.0111 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
850 | 1395.462 | 44265.5705 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4759.3306 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0015 | 0.0097 | 0.0112 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
853 | 1398.761 | 44265.5706 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4854.5172 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
856 | 1402.023 | 44265.5706 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4951.6076 | 0:240:120 | 0:00 | 0.007 | 7 | 0.002 | 0.0091 | 0.0111 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
859 | 1405.228 | 44265.5706 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5050.6397 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0015 | 0.0088 | 0.0103 | 0.0093 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
862 | 1408.502 | 44265.5707 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5151.6525 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.0088 | 0.0102 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
865 | 1411.697 | 44265.5707 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5254.6856 | 0:240:120 | 0:00 | 0.007 | 7 | 0.002 | 0.0092 | 0.0112 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
868 | 1414.978 | 44265.5707 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5359.7793 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0008 | 0.0096 | 0.0104 | 0.01 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
871 | 1418.258 | 44265.5708 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5466.9749 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
874 | 1421.548 | 44265.5708 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5576.3144 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0015 | 0.0096 | 0.0111 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
877 | 1424.856 | 44265.5709 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5687.8407 | 0:240:120 | 0:00 | 0.007 | 7 | 0.002 | 0.009 | 0.011 | 0.0095 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
880 | 1428.051 | 44265.5709 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5801.5975 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0001 | 0.0101 | 0.0102 | 0.0102 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
883 | 1431.363 | 44265.5709 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5917.6294 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0008 | 0.0093 | 0.0101 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
886 | 1434.643 | 44265.571 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6035.982 | 0:240:120 | 0:00 | 0.007 | 7 | 0.001 | 0.0092 | 0.0102 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
889 | 1437.822 | 44265.571 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6156.7017 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
892 | 1441.135 | 44265.571 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6279.8357 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0007 | 0.0098 | 0.0105 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
895 | 1444.41 | 44265.5711 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6405.4324 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0004 | 0.0097 | 0.0101 | 0.01 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
898 | 1447.59 | 44265.5711 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6533.5411 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.0095 | 0.0109 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
901 | 1450.776 | 44265.5712 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6664.2119 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
904 | 1454.062 | 44265.5712 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6797.4961 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.0098 | 0.0111 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
907 | 1457.389 | 44265.5712 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6933.446 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
910 | 1460.778 | 44265.5713 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7072.115 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0087 | 0.0106 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
913 | 1463.98 | 44265.5713 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7213.5573 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0021 | 0.0087 | 0.0108 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
916 | 1467.071 | 44265.5713 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7357.8284 | 0:240:120 | 0:00 | 0.007 | 7 | 0.001 | 0.0097 | 0.0107 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
919 | 1470.397 | 44265.5714 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7504.985 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0022 | 0.0089 | 0.0111 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
922 | 1473.689 | 44265.5714 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7655.0847 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0011 | 0.009 | 0.0101 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
925 | 1476.997 | 44265.5715 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7808.1864 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0012 | 0.0091 | 0.0103 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
928 | 1480.193 | 44265.5715 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7964.3501 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.0089 | 0.0103 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
931 | 1483.279 | 44265.5715 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8123.6371 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0021 | 0.0089 | 0.011 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
934 | 1486.486 | 44265.5716 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8286.1098 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
937 | 1489.943 | 44265.5716 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8451.832 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
940 | 1493.24 | 44265.5716 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8620.8687 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
943 | 1496.521 | 44265.5717 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8793.286 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0012 | 0.0088 | 0.01 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
946 | 1499.94 | 44265.5717 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8969.1518 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0006 | 0.0093 | 0.0099 | 0.0096 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
949 | 1503.346 | 44265.5718 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9148.5348 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.0091 | 0.0105 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
952 | 1506.543 | 44265.5718 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9331.5055 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0088 | 0.0104 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
955 | 1509.742 | 44265.5718 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9518.1356 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
958 | 1513.061 | 44265.5719 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9708.4983 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0087 | 0.0103 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
961 | 1516.364 | 44265.5719 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9902.6683 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
964 | 1519.922 | 44265.572 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10100.7217 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
967 | 1523.041 | 44265.572 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10302.7361 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0006 | 0.0099 | 0.0105 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
970 | 1526.326 | 44265.572 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10508.7908 | 0:240:120 | 0:00 | 0.007 | 7 | 0.001 | 0.009 | 0.01 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
973 | 1529.636 | 44265.5721 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10718.9666 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.0089 | 0.0103 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
976 | 1533.065 | 44265.5721 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10933.346 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0015 | 0.0095 | 0.011 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
979 | 1536.276 | 44265.5721 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11152.0129 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.0095 | 0.0109 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
982 | 1539.403 | 44265.5722 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11375.0531 | 0:240:120 | 0:00 | 0.007 | 7 | 0.001 | 0.0089 | 0.0099 | 0.0094 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
985 | 1542.526 | 44265.5722 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11602.5542 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.009 | 0.0109 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
988 | 1545.842 | 44265.5723 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11834.6053 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.0088 | 0.0102 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
991 | 1566.41 | 44265.5725 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 18.5 | 0:240:120 | 0:00 | 4.0924 | 7 | 8.9521 | 9.6134 | 18.5655 | 12.4537 | 4.1461 | 17.19 | 3 | 4.0924 | 31.1198 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
994 | 1615.77 | 44265.5731 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 18.9 | 0:240:120 | 0:00 | 3.6346 | 7 | 0.9488 | 8.3514 | 9.3002 | 8.6944 | 0.4177 | 0.1744 | 3 | 3.6346 | 17.0905 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
997 | 1645.373 | 44265.5734 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.3 | 0:240:120 | 0:00 | 3.2627 | 7 | 0.9791 | 6.9368 | 7.9159 | 7.3315 | 0.4375 | 0.1914 | 3 | 3.2627 | 11.6981 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1000 | 1671.045 | 44265.5737 | Vista Coord | Tap | 15Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 19.7 | 0:240:120 | 0:00 | 2.9548 | 7 | 1.005 | 5.6279 | 6.6329 | 6.0169 | 0.4553 | 0.2073 | 3 | 2.9548 | 8.8458 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1003 | 1763.698 | 44265.5748 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23 | 0:240:120 | 0:00 | 6.5828 | 7 | 18.6261 | 56.9383 | 75.5644 | 64.9357 | 8.1416 | 66.2851 | 3 | 6.5828 | Inf | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1006 | 1970.437 | 44265.5772 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.46 | 0:240:120 | 0:00 | 5.6544 | 7 | 16.2886 | 36.3788 | 52.6674 | 42.5876 | 7.5413 | 56.8705 | 3 | 5.6544 | 45.3051 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1009 | 2110.446 | 44265.5788 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.9292 | 0:240:120 | 0:00 | 4.9323 | 7 | 18.5605 | 13.5547 | 32.1152 | 21.2396 | 8.2084 | 67.3779 | 3 | 4.9323 | 22.2004 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1012 | 2188.151 | 44265.5797 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.4078 | 0:240:120 | 0:00 | 4.355 | 7 | 1.3943 | 9.0857 | 10.48 | 9.6629 | 0.5985 | 0.3582 | 3 | 4.355 | 14.5033 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1015 | 2221.03 | 44265.5801 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.8959 | 0:240:120 | 0:00 | 3.8833 | 7 | 1.0067 | 7.9117 | 8.9184 | 8.3211 | 0.4553 | 0.2073 | 3 | 3.8833 | 10.6581 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1018 | 2249.824 | 44265.5804 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.3939 | 0:240:120 | 0:00 | 3.4908 | 7 | 0.9382 | 6.6227 | 7.5609 | 7.0165 | 0.4105 | 0.1685 | 3 | 3.4908 | 8.3536 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1021 | 2274.455 | 44265.5807 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.9017 | 0:240:120 | 0:00 | 3.1594 | 7 | 1.0953 | 5.2975 | 6.3928 | 5.7363 | 0.4949 | 0.2449 | 3 | 3.1594 | 6.8195 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1024 | 2295.291 | 44265.5809 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.4198 | 0:240:120 | 0:00 | 2.876 | 7 | 0.5176 | 4.5369 | 5.0545 | 4.7455 | 0.2141 | 0.0459 | 3 | 2.876 | 5.7255 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1027 | 2313.281 | 44265.5811 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.9482 | 0:240:120 | 0:00 | 2.6311 | 7 | 0.3889 | 4.0947 | 4.4836 | 4.2652 | 0.1664 | 0.0277 | 3 | 2.6311 | 4.9067 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1030 | 2329.293 | 44265.5813 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 27.4871 | 0:240:120 | 0:00 | 2.4174 | 7 | 0.377 | 3.6114 | 3.9884 | 3.7897 | 0.1576 | 0.0248 | 3 | 2.4174 | 4.2713 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1033 | 2343.834 | 44265.5815 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.0369 | 0:240:120 | 0:00 | 2.2295 | 7 | 0.3948 | 3.1438 | 3.5386 | 3.3325 | 0.1579 | 0.0249 | 3 | 2.2295 | 3.7642 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1036 | 2357.244 | 44265.5816 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.5976 | 0:240:120 | 0:00 | 2.0631 | 7 | 0.2097 | 2.8958 | 3.1055 | 2.9859 | 0.0911 | 0.0083 | 3 | 2.0631 | 3.3506 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1039 | 2369.312 | 44265.5818 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.1696 | 0:240:120 | 0:00 | 1.9147 | 7 | 0.1994 | 2.6576 | 2.857 | 2.7442 | 0.0868 | 0.0075 | 3 | 1.9147 | 3.0069 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1042 | 2380.808 | 44265.5819 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.753 | 0:240:120 | 0:00 | 1.7818 | 7 | 0.2175 | 2.4064 | 2.6239 | 2.5077 | 0.0884 | 0.0078 | 3 | 1.7818 | 2.717 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1045 | 2391.424 | 44265.582 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.348 | 0:240:120 | 0:00 | 1.662 | 7 | 0.1813 | 2.1949 | 2.3762 | 2.2692 | 0.0791 | 0.0063 | 3 | 1.662 | 2.4828 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1048 | 2401.351 | 44265.5822 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.955 | 0:240:120 | 0:00 | 1.5536 | 7 | 0.1132 | 2.0574 | 2.1706 | 2.109 | 0.0469 | 0.0022 | 3 | 1.5536 | 2.2872 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1051 | 2410.97 | 44265.5823 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.5741 | 0:240:120 | 0:00 | 1.4552 | 7 | 0.1188 | 1.9179 | 2.0367 | 1.9664 | 0.0525 | 0.0028 | 3 | 1.4552 | 2.1143 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1054 | 2420.258 | 44265.5824 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.2056 | 0:240:120 | 0:00 | 1.3654 | 7 | 0.1238 | 1.7617 | 1.8855 | 1.814 | 0.0544 | 0.003 | 3 | 1.3654 | 1.9605 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1057 | 2428.938 | 44265.5825 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.8497 | 0:240:120 | 0:00 | 1.2832 | 7 | 0.0785 | 1.6546 | 1.7331 | 1.6881 | 0.0345 | 0.0012 | 3 | 1.2832 | 1.8228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1060 | 2437.171 | 44265.5826 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.5067 | 0:240:120 | 0:00 | 1.2078 | 7 | 0.089 | 1.5443 | 1.6333 | 1.5828 | 0.0386 | 0.0015 | 3 | 1.2078 | 1.6991 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1063 | 2445.152 | 44265.5827 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.1768 | 0:240:120 | 0:00 | 1.1384 | 7 | 0.0861 | 1.4459 | 1.532 | 1.4826 | 0.0367 | 0.0013 | 3 | 1.1384 | 1.5872 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1066 | 2452.97 | 44265.5828 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.8603 | 0:240:120 | 0:00 | 1.0743 | 7 | 0.0711 | 1.3571 | 1.4282 | 1.3866 | 0.0314 | 0.001 | 3 | 1.0743 | 1.4857 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1069 | 2460.268 | 44265.5828 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.5575 | 0:240:120 | 0:00 | 1.015 | 7 | 0.0699 | 1.2754 | 1.3453 | 1.3063 | 0.029 | 0.0008 | 3 | 1.015 | 1.3933 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1072 | 2467.431 | 44265.5829 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.2687 | 0:240:120 | 0:00 | 0.9601 | 7 | 0.0632 | 1.1998 | 1.263 | 1.2258 | 0.0277 | 0.0008 | 3 | 0.9601 | 1.3088 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1075 | 2473.988 | 44265.583 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.9941 | 0:240:120 | 0:00 | 0.909 | 7 | 0.0525 | 1.1332 | 1.1857 | 1.1538 | 0.0235 | 0.0006 | 3 | 0.909 | 1.2313 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1078 | 2480.795 | 44265.5831 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.7339 | 0:240:120 | 0:00 | 0.8615 | 7 | 0.0511 | 1.0701 | 1.1212 | 1.0914 | 0.0224 | 0.0005 | 3 | 0.8615 | 1.16 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1081 | 2487.148 | 44265.5832 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.4886 | 0:240:120 | 0:00 | 0.8171 | 7 | 0.0483 | 1.0111 | 1.0594 | 1.0303 | 0.0217 | 0.0005 | 3 | 0.8171 | 1.0943 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1084 | 2493.722 | 44265.5832 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.2584 | 0:240:120 | 0:00 | 0.7757 | 7 | 0.0448 | 0.955 | 0.9998 | 0.9718 | 0.0203 | 0.0004 | 3 | 0.7757 | 1.0335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1087 | 2500.028 | 44265.5833 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.0436 | 0:240:120 | 0:00 | 0.737 | 7 | 0.0355 | 0.9097 | 0.9452 | 0.9226 | 0.0165 | 0.0003 | 3 | 0.737 | 0.9772 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1090 | 2506.022 | 44265.5834 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.8444 | 0:240:120 | 0:00 | 0.7007 | 7 | 0.0411 | 0.8571 | 0.8982 | 0.8727 | 0.0183 | 0.0003 | 3 | 0.7007 | 0.925 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1093 | 2512.118 | 44265.5834 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.6613 | 0:240:120 | 0:00 | 0.6666 | 7 | 0.0302 | 0.8161 | 0.8463 | 0.8275 | 0.014 | 0.0002 | 3 | 0.6666 | 0.8763 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1096 | 2517.584 | 44265.5835 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.4945 | 0:240:120 | 0:00 | 0.6346 | 7 | 0.0342 | 0.773 | 0.8072 | 0.7868 | 0.0151 | 0.0002 | 3 | 0.6346 | 0.831 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1099 | 2523.161 | 44265.5836 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.3444 | 0:240:120 | 0:00 | 0.6045 | 7 | 0.0312 | 0.7344 | 0.7656 | 0.7461 | 0.0144 | 0.0002 | 3 | 0.6045 | 0.7887 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1102 | 2528.347 | 44265.5836 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.2113 | 0:240:120 | 0:00 | 0.5762 | 7 | 0.0292 | 0.6979 | 0.7271 | 0.7101 | 0.0124 | 0.0002 | 3 | 0.5762 | 0.7491 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1105 | 2533.538 | 44265.5837 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.0955 | 0:240:120 | 0:00 | 0.5494 | 7 | 0.0291 | 0.6636 | 0.6927 | 0.676 | 0.0126 | 0.0002 | 3 | 0.5494 | 0.712 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1108 | 2538.692 | 44265.5837 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.9975 | 0:240:120 | 0:00 | 0.5242 | 7 | 0.025 | 0.6328 | 0.6578 | 0.6421 | 0.011 | 0.0001 | 3 | 0.5242 | 0.6773 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1111 | 2543.743 | 44265.5838 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.9174 | 0:240:120 | 0:00 | 0.5004 | 7 | 0.0261 | 0.6017 | 0.6278 | 0.6126 | 0.0109 | 0.0001 | 3 | 0.5004 | 0.6446 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1114 | 2548.914 | 44265.5839 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.8558 | 0:240:120 | 0:00 | 0.4779 | 7 | 0.0239 | 0.575 | 0.5989 | 0.5849 | 0.0101 | 0.0001 | 3 | 0.4779 | 0.614 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1117 | 2553.735 | 44265.5839 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.8129 | 0:240:120 | 0:00 | 0.4566 | 7 | 0.0214 | 0.5489 | 0.5703 | 0.5569 | 0.0097 | 0.0001 | 3 | 0.4566 | 0.5851 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1120 | 2558.629 | 44265.584 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.7891 | 0:240:120 | 0:00 | 0.4364 | 7 | 0.0213 | 0.5224 | 0.5437 | 0.5313 | 0.009 | 0.0001 | 3 | 0.4364 | 0.5578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1123 | 2563.435 | 44265.584 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.7849 | 0:240:120 | 0:00 | 0.4173 | 7 | 0.0177 | 0.5015 | 0.5192 | 0.5083 | 0.0079 | 0.0001 | 3 | 0.4173 | 0.5322 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1126 | 2568.27 | 44265.5841 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.8006 | 0:240:120 | 0:00 | 0.3992 | 7 | 0.0183 | 0.4779 | 0.4962 | 0.4857 | 0.0078 | 0.0001 | 3 | 0.3992 | 0.5079 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1129 | 2572.757 | 44265.5841 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.8366 | 0:240:120 | 0:00 | 0.382 | 7 | 0.016 | 0.4572 | 0.4732 | 0.4638 | 0.007 | 0 | 3 | 0.382 | 0.485 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1132 | 2577.47 | 44265.5842 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.8934 | 0:240:120 | 0:00 | 0.3657 | 7 | 0.0177 | 0.4356 | 0.4533 | 0.4428 | 0.0079 | 0.0001 | 3 | 0.3657 | 0.4633 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1135 | 2582.006 | 44265.5842 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.9712 | 0:240:120 | 0:00 | 0.3502 | 7 | 0.015 | 0.4169 | 0.4319 | 0.4233 | 0.0063 | 0 | 3 | 0.3502 | 0.4428 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1138 | 2586.372 | 44265.5843 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.0706 | 0:240:120 | 0:00 | 0.3354 | 7 | 0.0148 | 0.3994 | 0.4142 | 0.4054 | 0.0062 | 0 | 3 | 0.3354 | 0.4233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1141 | 2590.746 | 44265.5844 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.1921 | 0:240:120 | 0:00 | 0.3214 | 7 | 0.0127 | 0.3826 | 0.3953 | 0.3882 | 0.0052 | 0 | 3 | 0.3214 | 0.4049 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1144 | 2594.893 | 44265.5844 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.3359 | 0:240:120 | 0:00 | 0.308 | 7 | 0.0136 | 0.3648 | 0.3784 | 0.3702 | 0.0059 | 0 | 3 | 0.308 | 0.3874 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1147 | 2599.255 | 44265.5844 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.5026 | 0:240:120 | 0:00 | 0.2953 | 7 | 0.0126 | 0.3508 | 0.3634 | 0.3555 | 0.0054 | 0 | 3 | 0.2953 | 0.3708 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1150 | 2603.432 | 44265.5845 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.6927 | 0:240:120 | 0:00 | 0.2832 | 7 | 0.0117 | 0.3358 | 0.3475 | 0.34 | 0.0053 | 0 | 3 | 0.2832 | 0.3551 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1153 | 2607.605 | 44265.5845 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.9065 | 0:240:120 | 0:00 | 0.2716 | 7 | 0.0113 | 0.3213 | 0.3326 | 0.326 | 0.0048 | 0 | 3 | 0.2716 | 0.3401 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1156 | 2611.697 | 44265.5846 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.1447 | 0:240:120 | 0:00 | 0.2606 | 7 | 0.0109 | 0.308 | 0.3189 | 0.3127 | 0.0044 | 0 | 3 | 0.2606 | 0.3258 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1159 | 2616.071 | 44265.5846 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.4075 | 0:240:120 | 0:00 | 0.2501 | 7 | 0.0101 | 0.2959 | 0.306 | 0.2998 | 0.0046 | 0 | 3 | 0.2501 | 0.3122 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1162 | 2620.21 | 44265.5847 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.6957 | 0:240:120 | 0:00 | 0.2401 | 7 | 0.0076 | 0.2845 | 0.2921 | 0.2876 | 0.0034 | 0 | 3 | 0.2401 | 0.2993 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1165 | 2624.088 | 44265.5847 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.0096 | 0:240:120 | 0:00 | 0.2305 | 7 | 0.0101 | 0.2718 | 0.2819 | 0.2757 | 0.0043 | 0 | 3 | 0.2305 | 0.287 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1168 | 2628.251 | 44265.5848 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.3498 | 0:240:120 | 0:00 | 0.2214 | 7 | 0.0098 | 0.2608 | 0.2706 | 0.265 | 0.0041 | 0 | 3 | 0.2214 | 0.2753 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1171 | 2632.518 | 44265.5848 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.7168 | 0:240:120 | 0:00 | 0.2127 | 7 | 0.0098 | 0.2493 | 0.2591 | 0.2535 | 0.0039 | 0 | 3 | 0.2127 | 0.2641 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1174 | 2636.823 | 44265.5849 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.1111 | 0:240:120 | 0:00 | 0.2043 | 7 | 0.0089 | 0.2398 | 0.2487 | 0.2436 | 0.0035 | 0 | 3 | 0.2043 | 0.2534 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1177 | 2640.665 | 44265.5849 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.5334 | 0:240:120 | 0:00 | 0.1963 | 7 | 0.0087 | 0.2305 | 0.2392 | 0.2341 | 0.0035 | 0 | 3 | 0.1963 | 0.2433 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1180 | 2644.501 | 44265.585 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.984 | 0:240:120 | 0:00 | 0.1887 | 7 | 0.008 | 0.2212 | 0.2292 | 0.2251 | 0.003 | 0 | 3 | 0.1887 | 0.2336 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1183 | 2648.289 | 44265.585 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.4637 | 0:240:120 | 0:00 | 0.1814 | 7 | 0.008 | 0.213 | 0.221 | 0.2162 | 0.0033 | 0 | 3 | 0.1814 | 0.2243 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1186 | 2651.951 | 44265.5851 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.973 | 0:240:120 | 0:00 | 0.1744 | 7 | 0.0072 | 0.204 | 0.2112 | 0.2073 | 0.0028 | 0 | 3 | 0.1744 | 0.2154 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1189 | 2655.62 | 44265.5851 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.5124 | 0:240:120 | 0:00 | 0.1678 | 7 | 0.0078 | 0.1961 | 0.2039 | 0.1993 | 0.0032 | 0 | 3 | 0.1678 | 0.207 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1192 | 2659.396 | 44265.5851 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.0827 | 0:240:120 | 0:00 | 0.1614 | 7 | 0.0079 | 0.188 | 0.1959 | 0.1917 | 0.0031 | 0 | 3 | 0.1614 | 0.1989 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1195 | 2663.227 | 44265.5852 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.6843 | 0:240:120 | 0:00 | 0.1552 | 7 | 0.0075 | 0.1808 | 0.1883 | 0.1841 | 0.003 | 0 | 3 | 0.1552 | 0.1911 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1198 | 2666.801 | 44265.5852 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.318 | 0:240:120 | 0:00 | 0.1494 | 7 | 0.0051 | 0.1747 | 0.1798 | 0.1771 | 0.002 | 0 | 3 | 0.1494 | 0.1837 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1201 | 2670.505 | 44265.5853 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.9844 | 0:240:120 | 0:00 | 0.1438 | 7 | 0.0062 | 0.1676 | 0.1738 | 0.1705 | 0.0022 | 0 | 3 | 0.1438 | 0.1766 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1204 | 2674.099 | 44265.5853 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.6841 | 0:240:120 | 0:00 | 0.1384 | 7 | 0.0054 | 0.1616 | 0.167 | 0.1641 | 0.0022 | 0 | 3 | 0.1384 | 0.1699 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1207 | 2677.701 | 44265.5854 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.4178 | 0:240:120 | 0:00 | 0.1332 | 7 | 0.0062 | 0.155 | 0.1612 | 0.158 | 0.0022 | 0 | 3 | 0.1332 | 0.1634 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1210 | 2681.159 | 44265.5854 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.1861 | 0:240:120 | 0:00 | 0.1283 | 7 | 0.0063 | 0.1488 | 0.1551 | 0.1518 | 0.0024 | 0 | 3 | 0.1283 | 0.1572 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1213 | 2684.704 | 44265.5854 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.9898 | 0:240:120 | 0:00 | 0.1235 | 7 | 0.0039 | 0.1449 | 0.1488 | 0.1465 | 0.0016 | 0 | 3 | 0.1235 | 0.1512 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1216 | 2688.249 | 44265.5855 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.8296 | 0:240:120 | 0:00 | 0.119 | 7 | 0.0062 | 0.1382 | 0.1444 | 0.1413 | 0.0024 | 0 | 3 | 0.119 | 0.1455 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1219 | 2692.053 | 44265.5855 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.7062 | 0:240:120 | 0:00 | 0.1146 | 7 | 0.0059 | 0.1327 | 0.1386 | 0.1353 | 0.0023 | 0 | 3 | 0.1146 | 0.1401 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1222 | 2695.452 | 44265.5856 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.6204 | 0:240:120 | 0:00 | 0.1105 | 7 | 0.0047 | 0.1284 | 0.1331 | 0.1307 | 0.0019 | 0 | 3 | 0.1105 | 0.1349 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1225 | 2698.922 | 44265.5856 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.5728 | 0:240:120 | 0:00 | 0.1064 | 7 | 0.0043 | 0.1238 | 0.1281 | 0.1258 | 0.0016 | 0 | 3 | 0.1064 | 0.1298 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1228 | 2702.585 | 44265.5856 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.5642 | 0:240:120 | 0:00 | 0.1026 | 7 | 0.0036 | 0.1198 | 0.1234 | 0.1214 | 0.0012 | 0 | 3 | 0.1026 | 0.125 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1231 | 2706.032 | 44265.5857 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.5955 | 0:240:120 | 0:00 | 0.0989 | 7 | 0.0046 | 0.1149 | 0.1195 | 0.1169 | 0.0018 | 0 | 3 | 0.0989 | 0.1204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1234 | 2709.792 | 44265.5857 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.6674 | 0:240:120 | 0:00 | 0.0954 | 7 | 0.0047 | 0.1108 | 0.1155 | 0.1128 | 0.0019 | 0 | 3 | 0.0954 | 0.116 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1237 | 2713.2 | 44265.5858 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.7808 | 0:240:120 | 0:00 | 0.092 | 7 | 0.0046 | 0.1067 | 0.1113 | 0.109 | 0.0015 | 0 | 3 | 0.092 | 0.1118 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1240 | 2716.66 | 44265.5858 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.9364 | 0:240:120 | 0:00 | 0.0887 | 7 | 0.0049 | 0.1025 | 0.1074 | 0.1048 | 0.0017 | 0 | 3 | 0.0887 | 0.1077 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1243 | 2720.297 | 44265.5859 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.1351 | 0:240:120 | 0:00 | 0.0856 | 7 | 0.0041 | 0.0994 | 0.1035 | 0.1012 | 0.0015 | 0 | 3 | 0.0856 | 0.1038 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1246 | 2723.787 | 44265.5859 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.3778 | 0:240:120 | 0:00 | 0.0826 | 7 | 0.005 | 0.0941 | 0.0991 | 0.0969 | 0.0017 | 0 | 3 | 0.0826 | 0.1001 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1249 | 2727.41 | 44265.5859 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.6654 | 0:240:120 | 0:00 | 0.0797 | 7 | 0.0042 | 0.0919 | 0.0961 | 0.0942 | 0.0016 | 0 | 3 | 0.0797 | 0.0965 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1252 | 2730.85 | 44265.586 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.9987 | 0:240:120 | 0:00 | 0.0769 | 7 | 0.0042 | 0.0883 | 0.0925 | 0.0909 | 0.0015 | 0 | 3 | 0.0769 | 0.093 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1255 | 2734.497 | 44265.586 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.3786 | 0:240:120 | 0:00 | 0.0742 | 7 | 0.0043 | 0.0854 | 0.0897 | 0.0873 | 0.0017 | 0 | 3 | 0.0742 | 0.0897 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1258 | 2737.948 | 44265.5861 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.8062 | 0:240:120 | 0:00 | 0.0717 | 7 | 0.0044 | 0.0817 | 0.0861 | 0.0842 | 0.0016 | 0 | 3 | 0.0717 | 0.0866 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1261 | 2741.45 | 44265.5861 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.2823 | 0:240:120 | 0:00 | 0.0692 | 7 | 0.0034 | 0.0794 | 0.0828 | 0.081 | 0.0013 | 0 | 3 | 0.0692 | 0.0835 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1264 | 2744.825 | 44265.5861 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.808 | 0:240:120 | 0:00 | 0.0668 | 7 | 0.0038 | 0.0766 | 0.0804 | 0.0787 | 0.0013 | 0 | 3 | 0.0668 | 0.0806 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1267 | 2748.286 | 44265.5862 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131.3841 | 0:240:120 | 0:00 | 0.0646 | 7 | 0.0037 | 0.0737 | 0.0774 | 0.0759 | 0.0013 | 0 | 3 | 0.0646 | 0.0778 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1270 | 2751.913 | 44265.5862 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.0118 | 0:240:120 | 0:00 | 0.0624 | 7 | 0.0043 | 0.0703 | 0.0746 | 0.073 | 0.0018 | 0 | 3 | 0.0624 | 0.0751 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1273 | 2755.369 | 44265.5863 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.6921 | 0:240:120 | 0:00 | 0.0603 | 7 | 0.0038 | 0.0681 | 0.0719 | 0.0705 | 0.0012 | 0 | 3 | 0.0603 | 0.0725 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1276 | 2758.842 | 44265.5863 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 139.4259 | 0:240:120 | 0:00 | 0.0583 | 7 | 0.0041 | 0.0667 | 0.0708 | 0.069 | 0.0015 | 0 | 3 | 0.0583 | 0.07 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1279 | 2762.277 | 44265.5863 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.2144 | 0:240:120 | 0:00 | 0.0563 | 7 | 0.0038 | 0.064 | 0.0678 | 0.0659 | 0.0013 | 0 | 3 | 0.0563 | 0.0676 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1282 | 2765.729 | 44265.5864 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 145.0587 | 0:240:120 | 0:00 | 0.0545 | 7 | 0.0031 | 0.0622 | 0.0653 | 0.064 | 0.0013 | 0 | 3 | 0.0545 | 0.0653 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1285 | 2769.192 | 44265.5864 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.9599 | 0:240:120 | 0:00 | 0.0527 | 7 | 0.0025 | 0.0602 | 0.0627 | 0.0616 | 0.001 | 0 | 3 | 0.0527 | 0.0632 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1288 | 2772.678 | 44265.5865 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.9191 | 0:240:120 | 0:00 | 0.0509 | 7 | 0.0038 | 0.0575 | 0.0613 | 0.0597 | 0.0014 | 0 | 3 | 0.0509 | 0.0611 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1291 | 2776.128 | 44265.5865 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.9375 | 0:240:120 | 0:00 | 0.0493 | 7 | 0.0041 | 0.0554 | 0.0595 | 0.0574 | 0.0015 | 0 | 3 | 0.0493 | 0.0593 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
1294 | 2779.456 | 44265.5865 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 157.0162 | 0:240:120 | 0:00 | 0.0477 | 7 | 0.0031 | 0.0539 | 0.057 | 0.0558 | 0.0013 | 0 | 3 | 0.0477 | 0.0577 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1297 | 2782.776 | 44265.5866 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.1565 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0025 | 0.0532 | 0.0557 | 0.0544 | 0.0009 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1300 | 2786.229 | 44265.5866 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 163.3597 | 0:240:120 | 0:00 | 0.0447 | 7 | 0.0033 | 0.05 | 0.0533 | 0.0518 | 0.0012 | 0 | 3 | 0.0447 | 0.0547 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1303 | 2789.451 | 44265.5867 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.6269 | 0:240:120 | 0:00 | 0.0433 | 7 | 0.0034 | 0.0488 | 0.0522 | 0.0506 | 0.001 | 0 | 3 | 0.0433 | 0.0533 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1306 | 2792.906 | 44265.5867 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.9594 | 0:240:120 | 0:00 | 0.0419 | 7 | 0.0037 | 0.0465 | 0.0502 | 0.0488 | 0.0016 | 0 | 3 | 0.0419 | 0.0519 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1309 | 2796.263 | 44265.5867 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 173.3586 | 0:240:120 | 0:00 | 0.0406 | 7 | 0.0025 | 0.0462 | 0.0487 | 0.0478 | 0.001 | 0 | 3 | 0.0406 | 0.0506 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1312 | 2799.602 | 44265.5868 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176.8258 | 0:240:120 | 0:00 | 0.0393 | 7 | 0.0033 | 0.0442 | 0.0475 | 0.0462 | 0.0014 | 0 | 3 | 0.0393 | 0.0493 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1315 | 2802.932 | 44265.5868 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 180.3623 | 0:240:120 | 0:00 | 0.0381 | 7 | 0.0027 | 0.0429 | 0.0456 | 0.0443 | 0.001 | 0 | 3 | 0.0381 | 0.0481 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1318 | 2806.243 | 44265.5868 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.9695 | 0:240:120 | 0:00 | 0.037 | 7 | 0.003 | 0.0415 | 0.0445 | 0.0435 | 0.0012 | 0 | 3 | 0.037 | 0.047 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1321 | 2809.702 | 44265.5869 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 187.6489 | 0:240:120 | 0:00 | 0.0358 | 7 | 0.0034 | 0.0401 | 0.0435 | 0.0422 | 0.0014 | 0 | 3 | 0.0358 | 0.0458 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1324 | 2813.139 | 44265.5869 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 191.4019 | 0:240:120 | 0:00 | 0.0348 | 7 | 0.0042 | 0.0384 | 0.0426 | 0.0406 | 0.0013 | 0 | 3 | 0.0348 | 0.0448 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1327 | 2816.588 | 44265.587 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 195.2299 | 0:240:120 | 0:00 | 0.0337 | 7 | 0.0031 | 0.0374 | 0.0405 | 0.0394 | 0.0014 | 0 | 3 | 0.0337 | 0.0437 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1330 | 2819.882 | 44265.587 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 199.1345 | 0:240:120 | 0:00 | 0.0327 | 7 | 0.0033 | 0.0369 | 0.0402 | 0.0388 | 0.0011 | 0 | 3 | 0.0327 | 0.0427 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1333 | 2823.469 | 44265.587 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 203.1172 | 0:240:120 | 0:00 | 0.0318 | 7 | 0.0035 | 0.035 | 0.0385 | 0.0372 | 0.0012 | 0 | 3 | 0.0318 | 0.0418 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1336 | 2826.907 | 44265.5871 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 207.1796 | 0:240:120 | 0:00 | 0.0308 | 7 | 0.0039 | 0.0339 | 0.0378 | 0.036 | 0.0013 | 0 | 3 | 0.0308 | 0.0408 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1339 | 2830.101 | 44265.5871 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 211.3231 | 0:240:120 | 0:00 | 0.0299 | 7 | 0.0038 | 0.0326 | 0.0364 | 0.0349 | 0.0013 | 0 | 3 | 0.0299 | 0.0399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1342 | 2833.324 | 44265.5872 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 215.5496 | 0:240:120 | 0:00 | 0.0291 | 7 | 0.0029 | 0.0324 | 0.0353 | 0.0342 | 0.0013 | 0 | 3 | 0.0291 | 0.0391 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1345 | 2836.689 | 44265.5872 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 219.8606 | 0:240:120 | 0:00 | 0.0283 | 7 | 0.0041 | 0.0306 | 0.0347 | 0.0329 | 0.0014 | 0 | 3 | 0.0283 | 0.0383 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1348 | 2840.076 | 44265.5872 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 224.2578 | 0:240:120 | 0:00 | 0.0275 | 7 | 0.003 | 0.0303 | 0.0333 | 0.0319 | 0.0011 | 0 | 3 | 0.0275 | 0.0375 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1351 | 2843.462 | 44265.5873 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 228.743 | 0:240:120 | 0:00 | 0.0267 | 7 | 0.0031 | 0.0294 | 0.0325 | 0.0311 | 0.0012 | 0 | 3 | 0.0267 | 0.0367 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1354 | 2846.728 | 44265.5873 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 233.3178 | 0:240:120 | 0:00 | 0.026 | 7 | 0.0037 | 0.0282 | 0.0319 | 0.0303 | 0.0013 | 0 | 3 | 0.026 | 0.036 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1357 | 2850.132 | 44265.5874 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.9842 | 0:240:120 | 0:00 | 0.0253 | 7 | 0.0022 | 0.0282 | 0.0304 | 0.0297 | 0.0008 | 0 | 3 | 0.0253 | 0.0353 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1360 | 2853.412 | 44265.5874 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 242.7439 | 0:240:120 | 0:00 | 0.0246 | 7 | 0.0037 | 0.0265 | 0.0302 | 0.0285 | 0.0012 | 0 | 3 | 0.0246 | 0.0346 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1363 | 2856.663 | 44265.5874 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 247.5987 | 0:240:120 | 0:00 | 0.0239 | 7 | 0.0027 | 0.0265 | 0.0292 | 0.0281 | 0.0009 | 0 | 3 | 0.0239 | 0.0339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1366 | 2859.91 | 44265.5875 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 252.5507 | 0:240:120 | 0:00 | 0.0233 | 7 | 0.0034 | 0.0258 | 0.0292 | 0.0276 | 0.0011 | 0 | 3 | 0.0233 | 0.0333 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1369 | 2863.239 | 44265.5875 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 257.6017 | 0:240:120 | 0:00 | 0.0227 | 7 | 0.0026 | 0.0249 | 0.0275 | 0.0269 | 0.0009 | 0 | 3 | 0.0227 | 0.0327 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1372 | 2866.571 | 44265.5875 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 262.7538 | 0:240:120 | 0:00 | 0.0221 | 7 | 0.0025 | 0.0249 | 0.0274 | 0.0261 | 0.001 | 0 | 3 | 0.0221 | 0.0321 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1375 | 2870.282 | 44265.5876 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 268.0088 | 0:240:120 | 0:00 | 0.0215 | 7 | 0.0028 | 0.0236 | 0.0264 | 0.0255 | 0.001 | 0 | 3 | 0.0215 | 0.0315 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1378 | 2873.394 | 44265.5876 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 273.369 | 0:240:120 | 0:00 | 0.021 | 7 | 0.003 | 0.0233 | 0.0263 | 0.0253 | 0.001 | 0 | 3 | 0.021 | 0.031 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1381 | 2876.618 | 44265.5877 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 278.8364 | 0:240:120 | 0:00 | 0.0205 | 7 | 0.0033 | 0.0229 | 0.0262 | 0.0246 | 0.0011 | 0 | 3 | 0.0205 | 0.0305 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1384 | 2879.878 | 44265.5877 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 284.4131 | 0:240:120 | 0:00 | 0.02 | 7 | 0.0032 | 0.0223 | 0.0255 | 0.0239 | 0.0011 | 0 | 3 | 0.02 | 0.03 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1387 | 2882.969 | 44265.5877 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 290.1014 | 0:240:120 | 0:00 | 0.0195 | 7 | 0.0027 | 0.0219 | 0.0246 | 0.0233 | 0.0009 | 0 | 3 | 0.0195 | 0.0295 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1390 | 2886.286 | 44265.5878 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 295.9034 | 0:240:120 | 0:00 | 0.019 | 7 | 0.003 | 0.0216 | 0.0246 | 0.0229 | 0.0009 | 0 | 3 | 0.019 | 0.029 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1393 | 2889.877 | 44265.5878 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 301.8215 | 0:240:120 | 0:00 | 0.0186 | 7 | 0.004 | 0.0205 | 0.0245 | 0.0226 | 0.0013 | 0 | 3 | 0.0186 | 0.0286 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1396 | 2893.297 | 44265.5879 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 307.8579 | 0:240:120 | 0:00 | 0.0182 | 7 | 0.0028 | 0.0202 | 0.023 | 0.022 | 0.0009 | 0 | 3 | 0.0182 | 0.0282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1399 | 2896.939 | 44265.5879 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 314.0151 | 0:240:120 | 0:00 | 0.0177 | 7 | 0.003 | 0.0197 | 0.0227 | 0.0215 | 0.0013 | 0 | 3 | 0.0177 | 0.0277 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1402 | 2900.268 | 44265.5879 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 320.2954 | 0:240:120 | 0:00 | 0.0173 | 7 | 0.0029 | 0.0198 | 0.0227 | 0.0213 | 0.001 | 0 | 3 | 0.0173 | 0.0273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1405 | 2903.624 | 44265.588 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 326.7013 | 0:240:120 | 0:00 | 0.017 | 7 | 0.0028 | 0.0195 | 0.0223 | 0.021 | 0.0011 | 0 | 3 | 0.017 | 0.027 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1408 | 2906.944 | 44265.588 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 333.2353 | 0:240:120 | 0:00 | 0.0166 | 7 | 0.0035 | 0.0186 | 0.0221 | 0.0206 | 0.0013 | 0 | 3 | 0.0166 | 0.0266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1411 | 2910.075 | 44265.588 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 339.9 | 0:240:120 | 0:00 | 0.0162 | 7 | 0.0031 | 0.0179 | 0.021 | 0.02 | 0.0011 | 0 | 3 | 0.0162 | 0.0262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1414 | 2913.417 | 44265.5881 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 346.698 | 0:240:120 | 0:00 | 0.0159 | 7 | 0.0037 | 0.0178 | 0.0215 | 0.0196 | 0.0011 | 0 | 3 | 0.0159 | 0.0259 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1417 | 2916.892 | 44265.5881 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 353.632 | 0:240:120 | 0:00 | 0.0156 | 7 | 0.0022 | 0.0182 | 0.0204 | 0.0195 | 0.0008 | 0 | 3 | 0.0156 | 0.0256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1420 | 2920.127 | 44265.5882 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 360.7046 | 0:240:120 | 0:00 | 0.0152 | 7 | 0.0023 | 0.0181 | 0.0204 | 0.0192 | 0.0008 | 0 | 3 | 0.0152 | 0.0252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1423 | 2923.476 | 44265.5882 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 367.9187 | 0:240:120 | 0:00 | 0.0149 | 7 | 0.0014 | 0.018 | 0.0194 | 0.0185 | 0.0006 | 0 | 3 | 0.0149 | 0.0249 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1426 | 2926.89 | 44265.5882 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 375.2771 | 0:240:120 | 0:00 | 0.0146 | 7 | 0.0016 | 0.0179 | 0.0195 | 0.0187 | 0.0007 | 0 | 3 | 0.0146 | 0.0246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1429 | 2930.111 | 44265.5883 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 382.7826 | 0:240:120 | 0:00 | 0.0144 | 7 | 0.0018 | 0.0169 | 0.0187 | 0.0181 | 0.0006 | 0 | 3 | 0.0144 | 0.0244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1432 | 2933.413 | 44265.5883 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 390.4383 | 0:240:120 | 0:00 | 0.0141 | 7 | 0.0002 | 0.0175 | 0.0177 | 0.0176 | 0.0001 | 0 | 3 | 0.0141 | 0.0241 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1435 | 2936.731 | 44265.5884 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 398.2471 | 0:240:120 | 0:00 | 0.0138 | 7 | 0.0016 | 0.0164 | 0.018 | 0.0172 | 0.0006 | 0 | 3 | 0.0138 | 0.0238 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1438 | 2939.908 | 44265.5884 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 406.212 | 0:240:120 | 0:00 | 0.0136 | 7 | 0.0011 | 0.0166 | 0.0177 | 0.0171 | 0.0003 | 0 | 3 | 0.0136 | 0.0236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1441 | 2943.446 | 44265.5884 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 414.3362 | 0:240:120 | 0:00 | 0.0133 | 7 | 0.0028 | 0.0151 | 0.0179 | 0.0165 | 0.001 | 0 | 3 | 0.0133 | 0.0233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1444 | 2946.745 | 44265.5885 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 422.623 | 0:240:120 | 0:00 | 0.0131 | 7 | 0.0019 | 0.0154 | 0.0173 | 0.0166 | 0.0007 | 0 | 3 | 0.0131 | 0.0231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1447 | 2949.974 | 44265.5885 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 431.0754 | 0:240:120 | 0:00 | 0.0129 | 7 | 0.0021 | 0.015 | 0.0171 | 0.016 | 0.0007 | 0 | 3 | 0.0129 | 0.0229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1450 | 2953.312 | 44265.5885 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 439.6969 | 0:240:120 | 0:00 | 0.0127 | 7 | 0.0031 | 0.0144 | 0.0175 | 0.0158 | 0.0012 | 0 | 3 | 0.0127 | 0.0227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1453 | 2956.85 | 44265.5886 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 448.4909 | 0:240:120 | 0:00 | 0.0124 | 7 | 0.0043 | 0.0136 | 0.0179 | 0.0154 | 0.0013 | 0 | 3 | 0.0124 | 0.0224 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1456 | 2960.098 | 44265.5886 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 457.4607 | 0:240:120 | 0:00 | 0.0122 | 7 | 0.0042 | 0.0131 | 0.0173 | 0.0151 | 0.0016 | 0 | 3 | 0.0122 | 0.0222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1459 | 2963.284 | 44265.5887 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 466.6099 | 0:240:120 | 0:00 | 0.012 | 7 | 0.0041 | 0.0127 | 0.0168 | 0.0151 | 0.0013 | 0 | 3 | 0.012 | 0.022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1462 | 2966.549 | 44265.5887 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 475.9421 | 0:240:120 | 0:00 | 0.0119 | 7 | 0.0041 | 0.0125 | 0.0166 | 0.015 | 0.0014 | 0 | 3 | 0.0119 | 0.0219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1465 | 2969.882 | 44265.5887 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 485.4609 | 0:240:120 | 0:00 | 0.0117 | 7 | 0.0035 | 0.0127 | 0.0162 | 0.0146 | 0.0014 | 0 | 3 | 0.0117 | 0.0217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1468 | 2973.121 | 44265.5888 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 495.1702 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0041 | 0.0127 | 0.0168 | 0.0145 | 0.0015 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1471 | 2976.348 | 44265.5888 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 505.0736 | 0:240:120 | 0:00 | 0.0113 | 7 | 0.0052 | 0.0117 | 0.0169 | 0.0143 | 0.0019 | 0 | 3 | 0.0113 | 0.0213 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1474 | 2979.763 | 44265.5889 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 515.175 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.0041 | 0.0121 | 0.0162 | 0.0143 | 0.0016 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1477 | 2983.175 | 44265.5889 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 525.4785 | 0:240:120 | 0:00 | 0.011 | 7 | 0.0052 | 0.0121 | 0.0173 | 0.0145 | 0.002 | 0 | 3 | 0.011 | 0.021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1480 | 2986.418 | 44265.5889 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 535.9881 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0044 | 0.0117 | 0.0161 | 0.0142 | 0.0015 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1483 | 2989.711 | 44265.589 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 546.7079 | 0:240:120 | 0:00 | 0.0107 | 7 | 0.0047 | 0.0115 | 0.0162 | 0.0139 | 0.0018 | 0 | 3 | 0.0107 | 0.0207 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1486 | 2993.047 | 44265.589 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 557.642 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0041 | 0.0117 | 0.0158 | 0.0138 | 0.0016 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1489 | 2996.364 | 44265.589 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 568.7949 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0035 | 0.0121 | 0.0156 | 0.0136 | 0.0012 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1492 | 2999.691 | 44265.5891 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 580.1708 | 0:240:120 | 0:00 | 0.0103 | 7 | 0.0041 | 0.0111 | 0.0152 | 0.0134 | 0.0016 | 0 | 3 | 0.0103 | 0.0203 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1495 | 3003.366 | 44265.5891 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 591.7742 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.0037 | 0.0116 | 0.0153 | 0.0134 | 0.0014 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1498 | 3006.595 | 44265.5892 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 603.6097 | 0:240:120 | 0:00 | 0.0101 | 7 | 0.0045 | 0.011 | 0.0155 | 0.0135 | 0.0016 | 0 | 3 | 0.0101 | 0.0201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1501 | 3009.899 | 44265.5892 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 613.254 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0042 | 0.0115 | 0.0157 | 0.0133 | 0.0015 | 0 | 3 | 0.01 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1504 | 3013.06 | 44265.5892 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 625.519 | 0:240:120 | 0:00 | 0.0099 | 7 | 0.0052 | 0.0107 | 0.0159 | 0.0133 | 0.0019 | 0 | 3 | 0.0099 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1507 | 3016.373 | 44265.5893 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 638.0294 | 0:240:120 | 0:00 | 0.0098 | 7 | 0.0054 | 0.0106 | 0.016 | 0.0131 | 0.002 | 0 | 3 | 0.0098 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1510 | 3019.701 | 44265.5893 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 650.79 | 0:240:120 | 0:00 | 0.0097 | 7 | 0.0034 | 0.0109 | 0.0143 | 0.013 | 0.0013 | 0 | 3 | 0.0097 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1513 | 3023.018 | 44265.5894 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 663.8058 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0036 | 0.0108 | 0.0144 | 0.0127 | 0.0013 | 0 | 3 | 0.0096 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1516 | 3026.545 | 44265.5894 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 677.0819 | 0:240:120 | 0:00 | 0.0095 | 7 | 0.0035 | 0.0105 | 0.014 | 0.0126 | 0.0013 | 0 | 3 | 0.0095 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1519 | 3029.983 | 44265.5894 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 690.6236 | 0:240:120 | 0:00 | 0.0094 | 7 | 0.0039 | 0.0103 | 0.0142 | 0.0124 | 0.0013 | 0 | 3 | 0.0094 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1522 | 3033.235 | 44265.5895 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 704.436 | 0:240:120 | 0:00 | 0.0093 | 7 | 0.0042 | 0.011 | 0.0152 | 0.0127 | 0.0015 | 0 | 3 | 0.0093 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1525 | 3036.558 | 44265.5895 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 718.5248 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0033 | 0.0101 | 0.0134 | 0.0116 | 0.0012 | 0 | 3 | 0.0092 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1528 | 3039.803 | 44265.5895 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 732.8953 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.0044 | 0.0107 | 0.0151 | 0.0124 | 0.0013 | 0 | 3 | 0.0091 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1531 | 3043.107 | 44265.5896 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 747.5532 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.0029 | 0.0106 | 0.0135 | 0.0115 | 0.0013 | 0 | 3 | 0.0091 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1534 | 3046.443 | 44265.5896 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 762.5042 | 0:240:120 | 0:00 | 0.009 | 7 | 0.003 | 0.0104 | 0.0134 | 0.0114 | 0.0013 | 0 | 3 | 0.009 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1537 | 3049.755 | 44265.5897 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 777.7543 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0025 | 0.0098 | 0.0123 | 0.0111 | 0.0008 | 0 | 3 | 0.0089 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1540 | 3053.084 | 44265.5897 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 793.3094 | 0:240:120 | 0:00 | 0.0088 | 7 | 0.0036 | 0.0095 | 0.0131 | 0.0111 | 0.0014 | 0 | 3 | 0.0088 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1543 | 3056.442 | 44265.5897 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 809.1756 | 0:240:120 | 0:00 | 0.0088 | 7 | 0.0043 | 0.0098 | 0.0141 | 0.0117 | 0.0013 | 0 | 3 | 0.0088 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1546 | 3059.85 | 44265.5898 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 825.3591 | 0:240:120 | 0:00 | 0.0087 | 7 | 0.0051 | 0.0099 | 0.015 | 0.0116 | 0.0018 | 0 | 3 | 0.0087 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1549 | 3063.225 | 44265.5898 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 841.8663 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0025 | 0.0097 | 0.0122 | 0.0105 | 0.0011 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1552 | 3066.633 | 44265.5899 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 858.7036 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0036 | 0.0095 | 0.0131 | 0.0106 | 0.0012 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1555 | 3069.956 | 44265.5899 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 875.8777 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0027 | 0.0099 | 0.0126 | 0.0109 | 0.0009 | 0 | 3 | 0.0085 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1558 | 3073.26 | 44265.5899 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 893.3952 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0027 | 0.0102 | 0.0129 | 0.011 | 0.0009 | 0 | 3 | 0.0085 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1561 | 3076.578 | 44265.59 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 911.2631 | 0:240:120 | 0:00 | 0.0084 | 7 | 0.0017 | 0.0101 | 0.0118 | 0.0108 | 0.0005 | 0 | 3 | 0.0084 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1564 | 3079.809 | 44265.59 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 929.4884 | 0:240:120 | 0:00 | 0.0084 | 7 | 0.0043 | 0.0103 | 0.0146 | 0.0112 | 0.0014 | 0 | 3 | 0.0084 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1567 | 3082.953 | 44265.59 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 948.0782 | 0:240:120 | 0:00 | 0.0083 | 7 | 0.0027 | 0.0091 | 0.0118 | 0.0106 | 0.0009 | 0 | 3 | 0.0083 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1570 | 3086.17 | 44265.5901 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 967.0397 | 0:240:120 | 0:00 | 0.0083 | 7 | 0.0035 | 0.0107 | 0.0142 | 0.0118 | 0.0014 | 0 | 3 | 0.0083 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1573 | 3089.432 | 44265.5901 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 986.3805 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0015 | 0.0098 | 0.0113 | 0.0106 | 0.0006 | 0 | 3 | 0.0082 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1576 | 3092.585 | 44265.5902 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1006.1081 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0019 | 0.0096 | 0.0115 | 0.0103 | 0.0007 | 0 | 3 | 0.0082 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1579 | 3095.886 | 44265.5902 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1026.2303 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0011 | 0.0097 | 0.0108 | 0.0102 | 0.0005 | 0 | 3 | 0.0081 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1582 | 3099.107 | 44265.5902 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1046.7549 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0019 | 0.0095 | 0.0114 | 0.0102 | 0.0007 | 0 | 3 | 0.0081 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1585 | 3102.432 | 44265.5903 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1067.69 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0018 | 0.0093 | 0.0111 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1588 | 3105.904 | 44265.5903 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1089.0438 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1591 | 3109.271 | 44265.5904 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1110.8247 | 0:240:120 | 0:00 | 0.008 | 7 | 0.001 | 0.0097 | 0.0107 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1594 | 3112.55 | 44265.5904 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1133.0412 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.002 | 0.0093 | 0.0113 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1597 | 3115.968 | 44265.5904 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1155.702 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0015 | 0.0102 | 0.0117 | 0.0108 | 0.0005 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1600 | 3119.434 | 44265.5905 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1178.816 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1603 | 3122.47 | 44265.5905 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1202.3923 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0017 | 0.0097 | 0.0114 | 0.0105 | 0.0006 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1606 | 3125.741 | 44265.5905 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1226.4402 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0106 | 0.0005 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1609 | 3128.867 | 44265.5906 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1226.5079 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0013 | 0.0104 | 0.0117 | 0.0107 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1612 | 3132.083 | 44265.5906 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1251.0381 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0026 | 0.009 | 0.0116 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1615 | 3135.287 | 44265.5907 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1276.0588 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0009 | 0.01 | 0.0109 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1618 | 3138.532 | 44265.5907 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1301.58 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1621 | 3141.774 | 44265.5907 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1327.6116 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.001 | 0.0093 | 0.0103 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1624 | 3145.088 | 44265.5908 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1354.1638 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0019 | 0.0089 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1627 | 3148.423 | 44265.5908 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1381.2471 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0012 | 0.0101 | 0.0113 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1630 | 3151.64 | 44265.5908 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1408.8721 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0011 | 0.0095 | 0.0106 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1633 | 3155.008 | 44265.5909 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1437.0495 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1636 | 3158.469 | 44265.5909 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1465.7905 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1639 | 3161.621 | 44265.591 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1495.1063 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0013 | 0.01 | 0.0113 | 0.0105 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1642 | 3164.763 | 44265.591 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1525.0084 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0016 | 0.009 | 0.0106 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1645 | 3167.999 | 44265.591 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1555.5086 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0024 | 0.009 | 0.0114 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1648 | 3171.455 | 44265.5911 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1586.6188 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0017 | 0.009 | 0.0107 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1651 | 3174.653 | 44265.5911 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1618.3512 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1654 | 3177.924 | 44265.5911 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1650.7182 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1657 | 3181.065 | 44265.5912 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1683.7325 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1660 | 3184.614 | 44265.5912 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1717.4072 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0016 | 0.0097 | 0.0113 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1663 | 3187.934 | 44265.5913 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1751.7553 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0006 | 0.01 | 0.0106 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1666 | 3191.276 | 44265.5913 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1786.7904 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1669 | 3194.586 | 44265.5913 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1822.5262 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1672 | 3197.929 | 44265.5914 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1858.9768 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0012 | 0.0091 | 0.0103 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1675 | 3201.238 | 44265.5914 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1896.1563 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1678 | 3204.366 | 44265.5915 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1934.0794 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0013 | 0.0095 | 0.0108 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1681 | 3207.576 | 44265.5915 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1972.761 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0012 | 0.0093 | 0.0105 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1684 | 3211.143 | 44265.5915 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2012.2162 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0013 | 0.0095 | 0.0108 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1687 | 3214.587 | 44265.5916 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2052.4606 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0024 | 0.009 | 0.0114 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1690 | 3217.808 | 44265.5916 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2093.5098 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1693 | 3221.176 | 44265.5916 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2135.38 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0016 | 0.009 | 0.0106 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1696 | 3224.39 | 44265.5917 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2178.0876 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0016 | 0.0097 | 0.0113 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1699 | 3227.639 | 44265.5917 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2221.6493 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1702 | 3230.853 | 44265.5918 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2266.0823 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1705 | 3234.177 | 44265.5918 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2311.404 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1708 | 3237.506 | 44265.5918 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2357.632 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0011 | 0.0094 | 0.0105 | 0.0098 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1711 | 3240.819 | 44265.5919 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2404.7847 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0015 | 0.0092 | 0.0107 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1714 | 3243.958 | 44265.5919 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2452.8804 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0008 | 0.0099 | 0.0107 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1717 | 3247.202 | 44265.5919 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2501.938 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0008 | 0.0097 | 0.0105 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1720 | 3250.451 | 44265.592 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2551.9767 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0005 | 0.0101 | 0.0106 | 0.0104 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1723 | 3253.786 | 44265.592 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2603.0163 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0006 | 0.01 | 0.0106 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1726 | 3256.91 | 44265.5921 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2655.0766 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0024 | 0.0089 | 0.0113 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1729 | 3260.136 | 44265.5921 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2708.1781 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0015 | 0.0093 | 0.0108 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1732 | 3263.502 | 44265.5921 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2762.3417 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1735 | 3266.847 | 44265.5922 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2817.5885 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0022 | 0.0092 | 0.0114 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1738 | 3270.073 | 44265.5922 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2873.9403 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1741 | 3273.312 | 44265.5923 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2931.4191 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1744 | 3276.473 | 44265.5923 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2990.0475 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0012 | 0.0098 | 0.011 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1747 | 3279.799 | 44265.5923 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3049.8484 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0015 | 0.0099 | 0.0114 | 0.0105 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1750 | 3283.031 | 44265.5924 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3110.8454 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1753 | 3286.348 | 44265.5924 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3173.0623 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.002 | 0.009 | 0.011 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1756 | 3289.582 | 44265.5924 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3236.5236 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1759 | 3292.899 | 44265.5925 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3301.254 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0099 | 0.0112 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1762 | 3296.212 | 44265.5925 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3367.2791 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0021 | 0.0089 | 0.011 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1765 | 3299.453 | 44265.5926 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3434.6247 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1768 | 3302.676 | 44265.5926 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3503.3172 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1771 | 3305.905 | 44265.5926 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3573.3835 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1774 | 3309.381 | 44265.5927 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3644.8512 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0021 | 0.0088 | 0.0109 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1777 | 3312.728 | 44265.5927 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3717.7482 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0024 | 0.0088 | 0.0112 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1780 | 3315.928 | 44265.5927 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3792.1032 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0004 | 0.0096 | 0.01 | 0.0098 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1783 | 3319.16 | 44265.5928 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3867.9453 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0095 | 0.0106 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1786 | 3322.548 | 44265.5928 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3945.3042 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0012 | 0.0089 | 0.0101 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1789 | 3325.801 | 44265.5929 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4024.2102 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0002 | 0.0105 | 0.0107 | 0.0106 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1792 | 3328.934 | 44265.5929 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4104.6945 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.001 | 0.0098 | 0.0108 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1795 | 3332.262 | 44265.5929 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4186.7883 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0012 | 0.0097 | 0.0109 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1798 | 3335.501 | 44265.593 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4270.5241 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1801 | 3338.66 | 44265.593 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4355.9346 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0015 | 0.0098 | 0.0113 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1804 | 3341.887 | 44265.593 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4443.0533 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.01 | 0.0111 | 0.0106 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1807 | 3345.057 | 44265.5931 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4531.9143 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0021 | 0.009 | 0.0111 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1810 | 3348.279 | 44265.5931 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4622.5526 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1813 | 3351.408 | 44265.5932 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4715.0037 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1816 | 3355.199 | 44265.5932 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4809.3038 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1819 | 3358.443 | 44265.5932 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4905.4898 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1822 | 3361.682 | 44265.5933 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5003.5996 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.001 | 0.0093 | 0.0103 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1825 | 3364.821 | 44265.5933 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5103.6716 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1828 | 3367.959 | 44265.5933 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5205.7451 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0005 | 0.0101 | 0.0106 | 0.0104 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1831 | 3371.122 | 44265.5934 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5309.86 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1834 | 3374.448 | 44265.5934 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5416.0572 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1837 | 3377.759 | 44265.5935 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5524.3783 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1840 | 3381.016 | 44265.5935 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5634.8659 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0003 | 0.0105 | 0.0108 | 0.0107 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1843 | 3384.328 | 44265.5935 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5747.5632 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1846 | 3387.658 | 44265.5936 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5862.5144 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.0091 | 0.0105 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1849 | 3390.995 | 44265.5936 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5979.7647 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0021 | 0.0092 | 0.0113 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1852 | 3394.213 | 44265.5937 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6099.36 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1855 | 3397.359 | 44265.5937 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6221.3472 | 0:240:120 | 0:00 | 0.007 | 7 | 0.001 | 0.0098 | 0.0108 | 0.0101 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1858 | 3400.744 | 44265.5937 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6345.7742 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0007 | 0.0096 | 0.0103 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1861 | 3403.996 | 44265.5938 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6472.6897 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0003 | 0.0092 | 0.0095 | 0.0094 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1864 | 3407.221 | 44265.5938 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6602.1435 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0007 | 0.0093 | 0.01 | 0.0096 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1867 | 3410.538 | 44265.5938 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6734.1863 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.0097 | 0.0111 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1870 | 3413.766 | 44265.5939 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6868.8701 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0012 | 0.009 | 0.0102 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1873 | 3417.092 | 44265.5939 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7006.2475 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1876 | 3420.573 | 44265.594 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7146.3724 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.009 | 0.0104 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1879 | 3423.808 | 44265.594 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7289.2998 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1882 | 3427.134 | 44265.594 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7435.0858 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1885 | 3430.263 | 44265.5941 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7583.7876 | 0:240:120 | 0:00 | 0.007 | 7 | 0.001 | 0.0089 | 0.0099 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1888 | 3433.419 | 44265.5941 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7735.4633 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0008 | 0.0093 | 0.0101 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1891 | 3436.642 | 44265.5941 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7890.1726 | 0:240:120 | 0:00 | 0.007 | 7 | 0.002 | 0.0091 | 0.0111 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1894 | 3439.97 | 44265.5942 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8047.976 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1897 | 3443.303 | 44265.5942 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8208.9356 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1900 | 3446.469 | 44265.5943 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8373.1143 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1903 | 3449.715 | 44265.5943 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8540.5765 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0018 | 0.0091 | 0.0109 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1906 | 3452.856 | 44265.5943 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8711.3881 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1909 | 3456.093 | 44265.5944 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8885.6158 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.0096 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1912 | 3459.594 | 44265.5944 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9063.3282 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1915 | 3462.927 | 44265.5944 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9244.5947 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0018 | 0.0093 | 0.0111 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1918 | 3466.139 | 44265.5945 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9429.4866 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0022 | 0.0089 | 0.0111 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1921 | 3469.382 | 44265.5945 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9618.0763 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1924 | 3472.706 | 44265.5946 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9810.4379 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1927 | 3476.311 | 44265.5946 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10006.6466 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1930 | 3479.531 | 44265.5946 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10206.7796 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.009 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1933 | 3482.864 | 44265.5947 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10410.9152 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1936 | 3486.096 | 44265.5947 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10619.1335 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1939 | 3489.692 | 44265.5948 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10831.5161 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0009 | 0.0098 | 0.0107 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1942 | 3493.042 | 44265.5948 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11048.1465 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1945 | 3496.274 | 44265.5948 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11269.1094 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0015 | 0.0095 | 0.011 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1948 | 3499.528 | 44265.5949 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11494.4916 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0009 | 0.0096 | 0.0105 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1951 | 3502.668 | 44265.5949 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11724.3814 | 0:240:120 | 0:00 | 0.007 | 7 | 0.001 | 0.0091 | 0.0101 | 0.0096 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1954 | 3505.874 | 44265.5949 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11958.869 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0003 | 0.0098 | 0.0101 | 0.01 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1957 | 3548.904 | 44265.5954 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 23.7 | 0:240:120 | 0:00 | 5.262 | 7 | 20.135 | 21.0636 | 41.1986 | 29.8161 | 8.2533 | 68.1164 | 3 | 5.262 | 29.6164 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1960 | 3651.816 | 44265.5966 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.2 | 0:240:120 | 0:00 | 4.5894 | 7 | 8.9124 | 9.5714 | 18.4838 | 12.4864 | 4.2113 | 17.7349 | 3 | 4.5894 | 17.0905 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1963 | 3700.509 | 44265.5972 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 24.7 | 0:240:120 | 0:00 | 4.0608 | 7 | 0.9717 | 8.311 | 9.2827 | 8.6952 | 0.4144 | 0.1717 | 3 | 4.0608 | 11.9359 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1966 | 3730.321 | 44265.5975 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.1 | 0:240:120 | 0:00 | 3.7131 | 7 | 1.07 | 7.2909 | 8.3609 | 7.7218 | 0.4779 | 0.2284 | 3 | 3.7131 | 9.5812 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1969 | 3757.231 | 44265.5979 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 25.6 | 0:240:120 | 0:00 | 3.349 | 7 | 0.9969 | 6.0044 | 7.0013 | 6.4739 | 0.4172 | 0.1741 | 3 | 3.349 | 7.6584 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1972 | 3779.672 | 44265.5981 | Vista Coord | Tap | 20Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 26.2 | 0:240:120 | 0:00 | 2.9904 | 7 | 0.7857 | 4.697 | 5.4827 | 5.0009 | 0.3518 | 0.1237 | 3 | 2.9904 | 6.1462 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1975 | 3881.274 | 44265.5993 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28 | 0:240:120 | 0:00 | 8.3312 | 7 | 16.4108 | 70.0742 | 86.485 | 78.3442 | 6.3558 | 40.396 | 3 | 8.3312 | Inf | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1978 | 4124.386 | 44265.6021 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.56 | 0:240:120 | 0:00 | 6.9558 | 7 | 17.8246 | 49.5044 | 67.329 | 58.2333 | 7.3718 | 54.3427 | 3 | 6.9558 | 46.5309 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1981 | 4310.007 | 44265.6042 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.1312 | 0:240:120 | 0:00 | 5.9383 | 7 | 19.1108 | 28.7102 | 47.821 | 37.7421 | 8.1592 | 66.5722 | 3 | 5.9383 | 22.8071 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
1984 | 4436.242 | 44265.6057 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.7138 | 0:240:120 | 0:00 | 5.1555 | 7 | 17.4815 | 10.0416 | 27.5231 | 16.5597 | 8.1138 | 65.8341 | 3 | 5.1555 | 14.9035 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1987 | 4503.262 | 44265.6065 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.3081 | 0:240:120 | 0:00 | 4.5349 | 7 | 1.0128 | 8.7579 | 9.7707 | 9.2008 | 0.4238 | 0.1796 | 3 | 4.5349 | 11.109 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1990 | 4534.435 | 44265.6068 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.9143 | 0:240:120 | 0:00 | 4.0313 | 7 | 0.9049 | 7.6227 | 8.5276 | 8.0494 | 0.3852 | 0.1484 | 3 | 4.0313 | 8.8803 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1993 | 4562.088 | 44265.6072 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.5325 | 0:240:120 | 0:00 | 3.6147 | 7 | 1.0407 | 6.4112 | 7.4519 | 6.9 | 0.4411 | 0.1946 | 3 | 3.6147 | 7.3497 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
1996 | 4586.04 | 44265.6074 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.1632 | 0:240:120 | 0:00 | 3.2645 | 7 | 0.9324 | 5.2638 | 6.1962 | 5.6319 | 0.4217 | 0.1778 | 3 | 3.2645 | 6.2343 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
1999 | 4606.308 | 44265.6077 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.8065 | 0:240:120 | 0:00 | 2.9662 | 7 | 0.3283 | 4.547 | 4.8753 | 4.6985 | 0.1376 | 0.0189 | 3 | 2.9662 | 5.3859 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2002 | 4623.634 | 44265.6079 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.4626 | 0:240:120 | 0:00 | 2.7093 | 7 | 0.3458 | 4.1386 | 4.4844 | 4.2762 | 0.1584 | 0.0251 | 3 | 2.7093 | 4.7193 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2005 | 4639.818 | 44265.6081 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.1318 | 0:240:120 | 0:00 | 2.4858 | 7 | 0.371 | 3.6712 | 4.0422 | 3.836 | 0.1525 | 0.0232 | 3 | 2.4858 | 4.1821 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2008 | 4654.72 | 44265.6082 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.8145 | 0:240:120 | 0:00 | 2.2898 | 7 | 0.3529 | 3.2728 | 3.6257 | 3.4068 | 0.166 | 0.0275 | 3 | 2.2898 | 3.7401 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2011 | 4668.256 | 44265.6084 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.5108 | 0:240:120 | 0:00 | 2.1166 | 7 | 0.2015 | 2.954 | 3.1555 | 3.0399 | 0.0825 | 0.0068 | 3 | 2.1166 | 3.3705 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2014 | 4680.571 | 44265.6085 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.221 | 0:240:120 | 0:00 | 1.9625 | 7 | 0.1779 | 2.7481 | 2.926 | 2.8146 | 0.0833 | 0.0069 | 3 | 1.9625 | 3.0569 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2017 | 4692.242 | 44265.6087 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.9454 | 0:240:120 | 0:00 | 1.8247 | 7 | 0.174 | 2.5087 | 2.6827 | 2.5786 | 0.0791 | 0.0063 | 3 | 1.8247 | 2.7877 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2020 | 4703.213 | 44265.6088 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.6843 | 0:240:120 | 0:00 | 1.7007 | 7 | 0.1839 | 2.277 | 2.4609 | 2.355 | 0.0804 | 0.0065 | 3 | 1.7007 | 2.5542 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2023 | 4713.364 | 44265.6089 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.438 | 0:240:120 | 0:00 | 1.5887 | 7 | 0.1174 | 2.1264 | 2.2438 | 2.1709 | 0.0539 | 0.0029 | 3 | 1.5887 | 2.35 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2026 | 4723.089 | 44265.609 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.2068 | 0:240:120 | 0:00 | 1.4871 | 7 | 0.1146 | 1.9772 | 2.0918 | 2.0211 | 0.0525 | 0.0028 | 3 | 1.4871 | 2.1699 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2029 | 4732.378 | 44265.6091 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.9909 | 0:240:120 | 0:00 | 1.3945 | 7 | 0.1062 | 1.8351 | 1.9413 | 1.8718 | 0.0515 | 0.0027 | 3 | 1.3945 | 2.01 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2032 | 4741.236 | 44265.6092 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.7907 | 0:240:120 | 0:00 | 1.3099 | 7 | 0.0906 | 1.6988 | 1.7894 | 1.7306 | 0.0427 | 0.0018 | 3 | 1.3099 | 1.8673 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2035 | 4749.78 | 44265.6093 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.6065 | 0:240:120 | 0:00 | 1.2323 | 7 | 0.0721 | 1.5964 | 1.6685 | 1.6233 | 0.0336 | 0.0011 | 3 | 1.2323 | 1.7391 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2038 | 4757.765 | 44265.6094 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.4387 | 0:240:120 | 0:00 | 1.161 | 7 | 0.077 | 1.4938 | 1.5708 | 1.5216 | 0.0358 | 0.0013 | 3 | 1.161 | 1.6234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2041 | 4765.333 | 44265.6095 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.2874 | 0:240:120 | 0:00 | 1.0952 | 7 | 0.0753 | 1.3922 | 1.4675 | 1.4192 | 0.0359 | 0.0013 | 3 | 1.0952 | 1.5186 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2044 | 4772.931 | 44265.6096 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.1532 | 0:240:120 | 0:00 | 1.0344 | 7 | 0.0558 | 1.3178 | 1.3736 | 1.3392 | 0.0255 | 0.0007 | 3 | 1.0344 | 1.4233 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2047 | 4780.204 | 44265.6097 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.0362 | 0:240:120 | 0:00 | 0.978 | 7 | 0.0596 | 1.2396 | 1.2992 | 1.2617 | 0.0277 | 0.0008 | 3 | 0.978 | 1.3362 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2050 | 4787.124 | 44265.6098 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.937 | 0:240:120 | 0:00 | 0.9257 | 7 | 0.0576 | 1.1598 | 1.2174 | 1.1795 | 0.0273 | 0.0007 | 3 | 0.9257 | 1.2565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2053 | 4793.788 | 44265.6098 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.8557 | 0:240:120 | 0:00 | 0.877 | 7 | 0.0428 | 1.0999 | 1.1427 | 1.1168 | 0.0192 | 0.0004 | 3 | 0.877 | 1.1832 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2056 | 4800.154 | 44265.6099 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.7928 | 0:240:120 | 0:00 | 0.8316 | 7 | 0.0516 | 1.0348 | 1.0864 | 1.0548 | 0.0232 | 0.0005 | 3 | 0.8316 | 1.1157 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2059 | 4806.888 | 44265.61 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.7487 | 0:240:120 | 0:00 | 0.7893 | 7 | 0.0427 | 0.9793 | 1.022 | 0.9946 | 0.02 | 0.0004 | 3 | 0.7893 | 1.0533 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2062 | 4813.075 | 44265.6101 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.7237 | 0:240:120 | 0:00 | 0.7497 | 7 | 0.0375 | 0.9292 | 0.9667 | 0.9434 | 0.0174 | 0.0003 | 3 | 0.7497 | 0.9956 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2065 | 4818.955 | 44265.6101 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.7181 | 0:240:120 | 0:00 | 0.7126 | 7 | 0.0375 | 0.8783 | 0.9158 | 0.8933 | 0.0167 | 0.0003 | 3 | 0.7126 | 0.942 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2068 | 4825.113 | 44265.6102 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.7325 | 0:240:120 | 0:00 | 0.6778 | 7 | 0.0327 | 0.8328 | 0.8655 | 0.8452 | 0.0149 | 0.0002 | 3 | 0.6778 | 0.8922 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2071 | 4830.855 | 44265.6103 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.7671 | 0:240:120 | 0:00 | 0.6451 | 7 | 0.03 | 0.793 | 0.823 | 0.8038 | 0.0141 | 0.0002 | 3 | 0.6451 | 0.8458 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2074 | 4836.286 | 44265.6103 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.8225 | 0:240:120 | 0:00 | 0.6144 | 7 | 0.0331 | 0.7501 | 0.7832 | 0.7624 | 0.015 | 0.0002 | 3 | 0.6144 | 0.8025 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2077 | 4842.009 | 44265.6104 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.8989 | 0:240:120 | 0:00 | 0.5855 | 7 | 0.023 | 0.7172 | 0.7402 | 0.7254 | 0.011 | 0.0001 | 3 | 0.5855 | 0.7621 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2080 | 4847.268 | 44265.6105 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.9969 | 0:240:120 | 0:00 | 0.5582 | 7 | 0.0263 | 0.6801 | 0.7064 | 0.6895 | 0.0125 | 0.0002 | 3 | 0.5582 | 0.7242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2083 | 4852.779 | 44265.6105 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.1168 | 0:240:120 | 0:00 | 0.5325 | 7 | 0.0253 | 0.6469 | 0.6722 | 0.6561 | 0.0117 | 0.0001 | 3 | 0.5325 | 0.6887 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2086 | 4857.764 | 44265.6106 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.2592 | 0:240:120 | 0:00 | 0.5082 | 7 | 0.0209 | 0.6166 | 0.6375 | 0.6244 | 0.0096 | 0.0001 | 3 | 0.5082 | 0.6553 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2089 | 4862.6 | 44265.6106 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.4244 | 0:240:120 | 0:00 | 0.4853 | 7 | 0.0212 | 0.5873 | 0.6085 | 0.5947 | 0.0097 | 0.0001 | 3 | 0.4853 | 0.624 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2092 | 4867.376 | 44265.6107 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.6129 | 0:240:120 | 0:00 | 0.4636 | 7 | 0.0176 | 0.5622 | 0.5798 | 0.5683 | 0.0086 | 0.0001 | 3 | 0.4636 | 0.5945 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2095 | 4872.105 | 44265.6108 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.8251 | 0:240:120 | 0:00 | 0.4431 | 7 | 0.0176 | 0.5354 | 0.553 | 0.5418 | 0.0084 | 0.0001 | 3 | 0.4431 | 0.5668 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2098 | 4876.733 | 44265.6108 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.0616 | 0:240:120 | 0:00 | 0.4236 | 7 | 0.0155 | 0.5107 | 0.5262 | 0.5165 | 0.0072 | 0.0001 | 3 | 0.4236 | 0.5406 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2101 | 4881.489 | 44265.6109 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.3228 | 0:240:120 | 0:00 | 0.4052 | 7 | 0.0168 | 0.4875 | 0.5043 | 0.4933 | 0.0076 | 0.0001 | 3 | 0.4052 | 0.5159 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2104 | 4885.964 | 44265.6109 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.6093 | 0:240:120 | 0:00 | 0.3877 | 7 | 0.0141 | 0.4661 | 0.4802 | 0.4712 | 0.0066 | 0 | 3 | 0.3877 | 0.4925 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2107 | 4890.475 | 44265.611 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.9215 | 0:240:120 | 0:00 | 0.3711 | 7 | 0.0152 | 0.4448 | 0.46 | 0.4503 | 0.0069 | 0 | 3 | 0.3711 | 0.4704 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2110 | 4894.909 | 44265.611 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.2599 | 0:240:120 | 0:00 | 0.3553 | 7 | 0.0142 | 0.425 | 0.4392 | 0.4305 | 0.0062 | 0 | 3 | 0.3553 | 0.4495 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2113 | 4899.214 | 44265.6111 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.6251 | 0:240:120 | 0:00 | 0.3403 | 7 | 0.0146 | 0.4072 | 0.4218 | 0.4125 | 0.006 | 0 | 3 | 0.3403 | 0.4297 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2116 | 4903.744 | 44265.6111 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.0176 | 0:240:120 | 0:00 | 0.326 | 7 | 0.0132 | 0.3894 | 0.4026 | 0.3943 | 0.0056 | 0 | 3 | 0.326 | 0.411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2119 | 4908.038 | 44265.6112 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.438 | 0:240:120 | 0:00 | 0.3124 | 7 | 0.0125 | 0.372 | 0.3845 | 0.3769 | 0.0057 | 0 | 3 | 0.3124 | 0.3932 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2122 | 4912.411 | 44265.6112 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.8867 | 0:240:120 | 0:00 | 0.2995 | 7 | 0.0105 | 0.3566 | 0.3671 | 0.3608 | 0.0046 | 0 | 3 | 0.2995 | 0.3763 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2125 | 4916.625 | 44265.6113 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.3645 | 0:240:120 | 0:00 | 0.2872 | 7 | 0.0114 | 0.3409 | 0.3523 | 0.3455 | 0.0048 | 0 | 3 | 0.2872 | 0.3602 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2128 | 4920.886 | 44265.6113 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.8718 | 0:240:120 | 0:00 | 0.2754 | 7 | 0.0111 | 0.3262 | 0.3373 | 0.331 | 0.0044 | 0 | 3 | 0.2754 | 0.345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2131 | 4925.029 | 44265.6114 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.4092 | 0:240:120 | 0:00 | 0.2643 | 7 | 0.0113 | 0.3128 | 0.3241 | 0.3173 | 0.005 | 0 | 3 | 0.2643 | 0.3305 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2134 | 4929.105 | 44265.6114 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.9774 | 0:240:120 | 0:00 | 0.2536 | 7 | 0.0096 | 0.3006 | 0.3102 | 0.3046 | 0.0042 | 0 | 3 | 0.2536 | 0.3167 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2137 | 4933.107 | 44265.6115 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.5769 | 0:240:120 | 0:00 | 0.2434 | 7 | 0.0094 | 0.2882 | 0.2976 | 0.2921 | 0.0039 | 0 | 3 | 0.2434 | 0.3036 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2140 | 4937.316 | 44265.6115 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.2085 | 0:240:120 | 0:00 | 0.2337 | 7 | 0.0092 | 0.2761 | 0.2853 | 0.28 | 0.004 | 0 | 3 | 0.2337 | 0.2911 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2143 | 4941.29 | 44265.6116 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.8726 | 0:240:120 | 0:00 | 0.2244 | 7 | 0.0074 | 0.2654 | 0.2728 | 0.2682 | 0.0032 | 0 | 3 | 0.2244 | 0.2791 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2146 | 4945.136 | 44265.6116 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.5701 | 0:240:120 | 0:00 | 0.2155 | 7 | 0.0096 | 0.2531 | 0.2627 | 0.2572 | 0.004 | 0 | 3 | 0.2155 | 0.2678 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2149 | 4949.121 | 44265.6116 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.3015 | 0:240:120 | 0:00 | 0.2071 | 7 | 0.0076 | 0.2432 | 0.2508 | 0.2468 | 0.003 | 0 | 3 | 0.2071 | 0.257 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2152 | 4953.029 | 44265.6117 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.0675 | 0:240:120 | 0:00 | 0.199 | 7 | 0.0073 | 0.2349 | 0.2422 | 0.2376 | 0.0032 | 0 | 3 | 0.199 | 0.2466 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2155 | 4956.708 | 44265.6117 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.8689 | 0:240:120 | 0:00 | 0.1912 | 7 | 0.0066 | 0.2258 | 0.2324 | 0.2285 | 0.0029 | 0 | 3 | 0.1912 | 0.2368 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2158 | 4960.375 | 44265.6118 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.7062 | 0:240:120 | 0:00 | 0.1838 | 7 | 0.0064 | 0.2171 | 0.2235 | 0.2197 | 0.0026 | 0 | 3 | 0.1838 | 0.2273 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2161 | 4964.031 | 44265.6118 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.5804 | 0:240:120 | 0:00 | 0.1767 | 7 | 0.0075 | 0.2072 | 0.2147 | 0.2107 | 0.003 | 0 | 3 | 0.1767 | 0.2183 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2164 | 4967.754 | 44265.6119 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.492 | 0:240:120 | 0:00 | 0.17 | 7 | 0.0069 | 0.1989 | 0.2058 | 0.2019 | 0.0028 | 0 | 3 | 0.17 | 0.2097 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2167 | 4971.464 | 44265.6119 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.4418 | 0:240:120 | 0:00 | 0.1635 | 7 | 0.0067 | 0.1913 | 0.198 | 0.1941 | 0.0027 | 0 | 3 | 0.1635 | 0.2015 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2170 | 4975.245 | 44265.6119 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.4306 | 0:240:120 | 0:00 | 0.1573 | 7 | 0.0066 | 0.1838 | 0.1904 | 0.1868 | 0.0026 | 0 | 3 | 0.1573 | 0.1937 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2173 | 4978.641 | 44265.612 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.4593 | 0:240:120 | 0:00 | 0.1513 | 7 | 0.0055 | 0.1777 | 0.1832 | 0.1804 | 0.0021 | 0 | 3 | 0.1513 | 0.1862 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2176 | 4982.302 | 44265.612 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.5284 | 0:240:120 | 0:00 | 0.1456 | 7 | 0.0069 | 0.1699 | 0.1768 | 0.1728 | 0.0028 | 0 | 3 | 0.1456 | 0.179 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2179 | 4985.733 | 44265.6121 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.639 | 0:240:120 | 0:00 | 0.1402 | 7 | 0.0045 | 0.1647 | 0.1692 | 0.1667 | 0.0018 | 0 | 3 | 0.1402 | 0.1721 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2182 | 4989.539 | 44265.6121 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.7918 | 0:240:120 | 0:00 | 0.1349 | 7 | 0.0063 | 0.1572 | 0.1635 | 0.1602 | 0.0023 | 0 | 3 | 0.1349 | 0.1655 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2185 | 4993.306 | 44265.6122 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.9876 | 0:240:120 | 0:00 | 0.1299 | 7 | 0.0063 | 0.1507 | 0.157 | 0.1538 | 0.0023 | 0 | 3 | 0.1299 | 0.1592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2188 | 4996.912 | 44265.6122 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.2274 | 0:240:120 | 0:00 | 0.1251 | 7 | 0.0051 | 0.1459 | 0.151 | 0.1481 | 0.0021 | 0 | 3 | 0.1251 | 0.1532 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2191 | 5000.439 | 44265.6122 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.5119 | 0:240:120 | 0:00 | 0.1205 | 7 | 0.0044 | 0.1406 | 0.145 | 0.1428 | 0.0017 | 0 | 3 | 0.1205 | 0.1474 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2194 | 5003.966 | 44265.6123 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.8422 | 0:240:120 | 0:00 | 0.1161 | 7 | 0.0063 | 0.1347 | 0.141 | 0.1374 | 0.0024 | 0 | 3 | 0.1161 | 0.1419 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2197 | 5007.496 | 44265.6123 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.219 | 0:240:120 | 0:00 | 0.1118 | 7 | 0.0035 | 0.13 | 0.1335 | 0.1321 | 0.0012 | 0 | 3 | 0.1118 | 0.1366 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2200 | 5010.892 | 44265.6124 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.6434 | 0:240:120 | 0:00 | 0.1078 | 7 | 0.0058 | 0.1246 | 0.1304 | 0.1276 | 0.002 | 0 | 3 | 0.1078 | 0.1315 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2203 | 5014.349 | 44265.6124 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.1163 | 0:240:120 | 0:00 | 0.1039 | 7 | 0.0038 | 0.1213 | 0.1251 | 0.123 | 0.0014 | 0 | 3 | 0.1039 | 0.1266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2206 | 5017.76 | 44265.6124 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.6386 | 0:240:120 | 0:00 | 0.1001 | 7 | 0.0049 | 0.116 | 0.1209 | 0.1184 | 0.0018 | 0 | 3 | 0.1001 | 0.122 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2209 | 5021.148 | 44265.6125 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131.2114 | 0:240:120 | 0:00 | 0.0965 | 7 | 0.0043 | 0.1121 | 0.1164 | 0.1144 | 0.0014 | 0 | 3 | 0.0965 | 0.1175 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2212 | 5024.57 | 44265.6125 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.8356 | 0:240:120 | 0:00 | 0.0931 | 7 | 0.0041 | 0.1079 | 0.112 | 0.1102 | 0.0017 | 0 | 3 | 0.0931 | 0.1132 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2215 | 5027.984 | 44265.6126 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.5123 | 0:240:120 | 0:00 | 0.0898 | 7 | 0.0041 | 0.1046 | 0.1087 | 0.1064 | 0.0016 | 0 | 3 | 0.0898 | 0.1091 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2218 | 5031.495 | 44265.6126 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 139.2425 | 0:240:120 | 0:00 | 0.0866 | 7 | 0.0038 | 0.1002 | 0.104 | 0.1024 | 0.0015 | 0 | 3 | 0.0866 | 0.1051 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2221 | 5034.924 | 44265.6126 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.0274 | 0:240:120 | 0:00 | 0.0835 | 7 | 0.004 | 0.0966 | 0.1006 | 0.0988 | 0.0013 | 0 | 3 | 0.0835 | 0.1013 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2224 | 5038.518 | 44265.6127 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.8679 | 0:240:120 | 0:00 | 0.0806 | 7 | 0.0041 | 0.093 | 0.0971 | 0.095 | 0.0015 | 0 | 3 | 0.0806 | 0.0977 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2227 | 5041.959 | 44265.6127 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.7653 | 0:240:120 | 0:00 | 0.0778 | 7 | 0.0032 | 0.0906 | 0.0938 | 0.0922 | 0.0013 | 0 | 3 | 0.0778 | 0.0942 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2230 | 5045.373 | 44265.6128 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.7206 | 0:240:120 | 0:00 | 0.0751 | 7 | 0.0041 | 0.0865 | 0.0906 | 0.0888 | 0.0013 | 0 | 3 | 0.0751 | 0.0908 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2233 | 5048.769 | 44265.6128 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.735 | 0:240:120 | 0:00 | 0.0725 | 7 | 0.0034 | 0.0838 | 0.0872 | 0.0854 | 0.0012 | 0 | 3 | 0.0725 | 0.0876 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2236 | 5052.223 | 44265.6128 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.8097 | 0:240:120 | 0:00 | 0.07 | 7 | 0.004 | 0.0802 | 0.0842 | 0.0823 | 0.0015 | 0 | 3 | 0.07 | 0.0845 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2239 | 5055.667 | 44265.6129 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 159.9459 | 0:240:120 | 0:00 | 0.0676 | 7 | 0.0033 | 0.0778 | 0.0811 | 0.0794 | 0.0012 | 0 | 3 | 0.0676 | 0.0815 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2242 | 5059.078 | 44265.6129 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 163.1448 | 0:240:120 | 0:00 | 0.0653 | 7 | 0.0039 | 0.0748 | 0.0787 | 0.0768 | 0.0011 | 0 | 3 | 0.0653 | 0.0787 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2245 | 5062.508 | 44265.613 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.4077 | 0:240:120 | 0:00 | 0.0631 | 7 | 0.0028 | 0.0731 | 0.0759 | 0.0747 | 0.0012 | 0 | 3 | 0.0631 | 0.076 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2248 | 5065.918 | 44265.613 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.7359 | 0:240:120 | 0:00 | 0.061 | 7 | 0.0029 | 0.0696 | 0.0725 | 0.0711 | 0.0011 | 0 | 3 | 0.061 | 0.0733 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2251 | 5069.521 | 44265.613 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 173.1306 | 0:240:120 | 0:00 | 0.0589 | 7 | 0.0032 | 0.0675 | 0.0707 | 0.0694 | 0.001 | 0 | 3 | 0.0589 | 0.0708 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2254 | 5072.917 | 44265.6131 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176.5932 | 0:240:120 | 0:00 | 0.057 | 7 | 0.0036 | 0.0646 | 0.0682 | 0.067 | 0.0013 | 0 | 3 | 0.057 | 0.0684 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2257 | 5076.286 | 44265.6131 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 180.1251 | 0:240:120 | 0:00 | 0.0551 | 7 | 0.0027 | 0.0631 | 0.0658 | 0.0646 | 0.0011 | 0 | 3 | 0.0551 | 0.0661 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2260 | 5079.699 | 44265.6132 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.7276 | 0:240:120 | 0:00 | 0.0533 | 7 | 0.0031 | 0.061 | 0.0641 | 0.0626 | 0.0012 | 0 | 3 | 0.0533 | 0.0639 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
2263 | 5083.011 | 44265.6132 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 187.4021 | 0:240:120 | 0:00 | 0.0515 | 7 | 0.0022 | 0.059 | 0.0612 | 0.0601 | 0.0008 | 0 | 3 | 0.0515 | 0.0618 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2266 | 5086.423 | 44265.6132 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 191.1502 | 0:240:120 | 0:00 | 0.0498 | 7 | 0.0032 | 0.0567 | 0.0599 | 0.0584 | 0.0011 | 0 | 3 | 0.0498 | 0.0598 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2269 | 5090.182 | 44265.6133 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.9732 | 0:240:120 | 0:00 | 0.0482 | 7 | 0.0028 | 0.0552 | 0.058 | 0.0566 | 0.0009 | 0 | 3 | 0.0482 | 0.0582 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2272 | 5093.832 | 44265.6133 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 198.8726 | 0:240:120 | 0:00 | 0.0467 | 7 | 0.0036 | 0.0527 | 0.0563 | 0.055 | 0.0013 | 0 | 3 | 0.0467 | 0.0567 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2275 | 5097.337 | 44265.6134 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 202.8501 | 0:240:120 | 0:00 | 0.0452 | 7 | 0.0029 | 0.0513 | 0.0542 | 0.053 | 0.0009 | 0 | 3 | 0.0452 | 0.0552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2278 | 5100.652 | 44265.6134 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 206.9071 | 0:240:120 | 0:00 | 0.0437 | 7 | 0.003 | 0.049 | 0.052 | 0.0507 | 0.0012 | 0 | 3 | 0.0437 | 0.0537 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2281 | 5103.951 | 44265.6134 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 211.0452 | 0:240:120 | 0:00 | 0.0424 | 7 | 0.0025 | 0.0481 | 0.0506 | 0.0493 | 0.0009 | 0 | 3 | 0.0424 | 0.0524 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2284 | 5107.343 | 44265.6135 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 215.2661 | 0:240:120 | 0:00 | 0.041 | 7 | 0.0043 | 0.0452 | 0.0495 | 0.0477 | 0.0016 | 0 | 3 | 0.041 | 0.051 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2287 | 5110.644 | 44265.6135 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 219.5715 | 0:240:120 | 0:00 | 0.0397 | 7 | 0.0045 | 0.0442 | 0.0487 | 0.0467 | 0.0013 | 0 | 3 | 0.0397 | 0.0497 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2290 | 5114.28 | 44265.6136 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.9629 | 0:240:120 | 0:00 | 0.0385 | 7 | 0.0032 | 0.0428 | 0.046 | 0.045 | 0.0011 | 0 | 3 | 0.0385 | 0.0485 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2293 | 5117.56 | 44265.6136 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 228.4421 | 0:240:120 | 0:00 | 0.0373 | 7 | 0.0033 | 0.042 | 0.0453 | 0.0441 | 0.0015 | 0 | 3 | 0.0373 | 0.0473 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2296 | 5120.991 | 44265.6136 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 233.011 | 0:240:120 | 0:00 | 0.0362 | 7 | 0.0029 | 0.0408 | 0.0437 | 0.0425 | 0.0011 | 0 | 3 | 0.0362 | 0.0462 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2299 | 5124.368 | 44265.6137 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.6712 | 0:240:120 | 0:00 | 0.0351 | 7 | 0.003 | 0.0391 | 0.0421 | 0.041 | 0.0012 | 0 | 3 | 0.0351 | 0.0451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2302 | 5127.786 | 44265.6137 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 242.4246 | 0:240:120 | 0:00 | 0.0341 | 7 | 0.0041 | 0.0375 | 0.0416 | 0.0397 | 0.0015 | 0 | 3 | 0.0341 | 0.0441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2305 | 5131.228 | 44265.6138 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 247.2731 | 0:240:120 | 0:00 | 0.033 | 7 | 0.0036 | 0.0365 | 0.0401 | 0.0384 | 0.0011 | 0 | 3 | 0.033 | 0.043 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2308 | 5134.607 | 44265.6138 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 252.2186 | 0:240:120 | 0:00 | 0.0321 | 7 | 0.0029 | 0.0356 | 0.0385 | 0.0374 | 0.0009 | 0 | 3 | 0.0321 | 0.0421 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2311 | 5137.878 | 44265.6138 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 257.263 | 0:240:120 | 0:00 | 0.0311 | 7 | 0.0027 | 0.0354 | 0.0381 | 0.037 | 0.001 | 0 | 3 | 0.0311 | 0.0411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2314 | 5140.987 | 44265.6139 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 262.4082 | 0:240:120 | 0:00 | 0.0302 | 7 | 0.0027 | 0.0335 | 0.0362 | 0.0355 | 0.0011 | 0 | 3 | 0.0302 | 0.0402 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2317 | 5144.332 | 44265.6139 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 267.6564 | 0:240:120 | 0:00 | 0.0294 | 7 | 0.0031 | 0.033 | 0.0361 | 0.0345 | 0.0012 | 0 | 3 | 0.0294 | 0.0394 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2320 | 5147.539 | 44265.6139 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 273.0095 | 0:240:120 | 0:00 | 0.0285 | 7 | 0.0015 | 0.0325 | 0.034 | 0.0334 | 0.0006 | 0 | 3 | 0.0285 | 0.0385 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2323 | 5150.847 | 44265.614 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 278.4697 | 0:240:120 | 0:00 | 0.0277 | 7 | 0.0031 | 0.0308 | 0.0339 | 0.0327 | 0.0013 | 0 | 3 | 0.0277 | 0.0377 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2326 | 5154.165 | 44265.614 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 284.0391 | 0:240:120 | 0:00 | 0.027 | 7 | 0.0029 | 0.0302 | 0.0331 | 0.0317 | 0.0011 | 0 | 3 | 0.027 | 0.037 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2329 | 5157.334 | 44265.6141 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 289.7199 | 0:240:120 | 0:00 | 0.0262 | 7 | 0.003 | 0.029 | 0.032 | 0.0307 | 0.0012 | 0 | 3 | 0.0262 | 0.0362 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2332 | 5160.582 | 44265.6141 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 295.5143 | 0:240:120 | 0:00 | 0.0255 | 7 | 0.0037 | 0.0281 | 0.0318 | 0.0299 | 0.0011 | 0 | 3 | 0.0255 | 0.0355 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2335 | 5163.759 | 44265.6141 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 301.4246 | 0:240:120 | 0:00 | 0.0248 | 7 | 0.0029 | 0.028 | 0.0309 | 0.0294 | 0.0011 | 0 | 3 | 0.0248 | 0.0348 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2338 | 5167.032 | 44265.6142 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 307.4531 | 0:240:120 | 0:00 | 0.0241 | 7 | 0.0031 | 0.0264 | 0.0295 | 0.0283 | 0.0013 | 0 | 3 | 0.0241 | 0.0341 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2341 | 5170.28 | 44265.6142 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 313.6021 | 0:240:120 | 0:00 | 0.0235 | 7 | 0.0035 | 0.0257 | 0.0292 | 0.0276 | 0.0012 | 0 | 3 | 0.0235 | 0.0335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2344 | 5173.49 | 44265.6142 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 319.8742 | 0:240:120 | 0:00 | 0.0229 | 7 | 0.0033 | 0.0254 | 0.0287 | 0.0272 | 0.0012 | 0 | 3 | 0.0229 | 0.0329 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2347 | 5176.745 | 44265.6143 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 326.2716 | 0:240:120 | 0:00 | 0.0223 | 7 | 0.0028 | 0.0245 | 0.0273 | 0.0262 | 0.0011 | 0 | 3 | 0.0223 | 0.0323 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2350 | 5180.002 | 44265.6143 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 332.7971 | 0:240:120 | 0:00 | 0.0217 | 7 | 0.003 | 0.0236 | 0.0266 | 0.0254 | 0.0012 | 0 | 3 | 0.0217 | 0.0317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2353 | 5183.233 | 44265.6144 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 339.453 | 0:240:120 | 0:00 | 0.0212 | 7 | 0.0036 | 0.0232 | 0.0268 | 0.0253 | 0.0012 | 0 | 3 | 0.0212 | 0.0312 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2356 | 5186.826 | 44265.6144 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 346.2421 | 0:240:120 | 0:00 | 0.0207 | 7 | 0.0034 | 0.0229 | 0.0263 | 0.0246 | 0.0012 | 0 | 3 | 0.0207 | 0.0307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2359 | 5190.258 | 44265.6144 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 353.1669 | 0:240:120 | 0:00 | 0.0201 | 7 | 0.0024 | 0.0232 | 0.0256 | 0.0244 | 0.0008 | 0 | 3 | 0.0201 | 0.0301 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2362 | 5193.875 | 44265.6145 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 360.2303 | 0:240:120 | 0:00 | 0.0197 | 7 | 0.0028 | 0.0216 | 0.0244 | 0.0234 | 0.0012 | 0 | 3 | 0.0197 | 0.0297 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2365 | 5197.139 | 44265.6145 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 367.4349 | 0:240:120 | 0:00 | 0.0192 | 7 | 0.0021 | 0.0222 | 0.0243 | 0.0232 | 0.0007 | 0 | 3 | 0.0192 | 0.0292 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2368 | 5200.385 | 44265.6146 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 374.7836 | 0:240:120 | 0:00 | 0.0187 | 7 | 0.0035 | 0.0211 | 0.0246 | 0.0226 | 0.0011 | 0 | 3 | 0.0187 | 0.0287 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2371 | 5203.536 | 44265.6146 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 382.2792 | 0:240:120 | 0:00 | 0.0183 | 7 | 0.0031 | 0.0204 | 0.0235 | 0.0223 | 0.0011 | 0 | 3 | 0.0183 | 0.0283 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2374 | 5207.076 | 44265.6146 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 389.9248 | 0:240:120 | 0:00 | 0.0179 | 7 | 0.0025 | 0.0202 | 0.0227 | 0.0216 | 0.0009 | 0 | 3 | 0.0179 | 0.0279 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2377 | 5210.275 | 44265.6147 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 397.7233 | 0:240:120 | 0:00 | 0.0175 | 7 | 0.0025 | 0.0203 | 0.0228 | 0.0214 | 0.0008 | 0 | 3 | 0.0175 | 0.0275 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2380 | 5213.469 | 44265.6147 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 405.6778 | 0:240:120 | 0:00 | 0.0171 | 7 | 0.0021 | 0.02 | 0.0221 | 0.0214 | 0.0008 | 0 | 3 | 0.0171 | 0.0271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2383 | 5216.681 | 44265.6147 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 413.7913 | 0:240:120 | 0:00 | 0.0167 | 7 | 0.0024 | 0.0192 | 0.0216 | 0.0206 | 0.0009 | 0 | 3 | 0.0167 | 0.0267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2386 | 5219.78 | 44265.6148 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 422.0672 | 0:240:120 | 0:00 | 0.0164 | 7 | 0.0033 | 0.0181 | 0.0214 | 0.0201 | 0.0011 | 0 | 3 | 0.0164 | 0.0264 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2389 | 5223.319 | 44265.6148 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 430.5085 | 0:240:120 | 0:00 | 0.016 | 7 | 0.0024 | 0.0187 | 0.0211 | 0.0199 | 0.0009 | 0 | 3 | 0.016 | 0.026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2392 | 5226.749 | 44265.6149 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 439.1187 | 0:240:120 | 0:00 | 0.0157 | 7 | 0.003 | 0.0178 | 0.0208 | 0.0196 | 0.0009 | 0 | 3 | 0.0157 | 0.0257 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2395 | 5229.942 | 44265.6149 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 447.901 | 0:240:120 | 0:00 | 0.0153 | 7 | 0.0029 | 0.0178 | 0.0207 | 0.0194 | 0.001 | 0 | 3 | 0.0153 | 0.0253 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2398 | 5233.348 | 44265.6149 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 456.8591 | 0:240:120 | 0:00 | 0.015 | 7 | 0.0025 | 0.0178 | 0.0203 | 0.0187 | 0.0009 | 0 | 3 | 0.015 | 0.025 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2401 | 5236.528 | 44265.615 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 465.9962 | 0:240:120 | 0:00 | 0.0147 | 7 | 0.0019 | 0.0176 | 0.0195 | 0.0185 | 0.0007 | 0 | 3 | 0.0147 | 0.0247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2404 | 5239.845 | 44265.615 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 475.3162 | 0:240:120 | 0:00 | 0.0145 | 7 | 0.0017 | 0.0173 | 0.019 | 0.0181 | 0.0005 | 0 | 3 | 0.0145 | 0.0245 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2407 | 5243.12 | 44265.615 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 484.8225 | 0:240:120 | 0:00 | 0.0142 | 7 | 0.0016 | 0.0169 | 0.0185 | 0.0179 | 0.0006 | 0 | 3 | 0.0142 | 0.0242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2410 | 5246.388 | 44265.6151 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 494.5189 | 0:240:120 | 0:00 | 0.0139 | 7 | 0.0017 | 0.0166 | 0.0183 | 0.0177 | 0.0006 | 0 | 3 | 0.0139 | 0.0239 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2413 | 5249.576 | 44265.6151 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 504.4093 | 0:240:120 | 0:00 | 0.0137 | 7 | 0.0014 | 0.0163 | 0.0177 | 0.0172 | 0.0005 | 0 | 3 | 0.0137 | 0.0237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2416 | 5252.775 | 44265.6152 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 514.4975 | 0:240:120 | 0:00 | 0.0134 | 7 | 0.0019 | 0.0163 | 0.0182 | 0.0171 | 0.0007 | 0 | 3 | 0.0134 | 0.0234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2419 | 5256.504 | 44265.6152 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 524.7875 | 0:240:120 | 0:00 | 0.0132 | 7 | 0.0017 | 0.016 | 0.0177 | 0.0166 | 0.0007 | 0 | 3 | 0.0132 | 0.0232 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2422 | 5259.781 | 44265.6152 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 535.2832 | 0:240:120 | 0:00 | 0.0129 | 7 | 0.0028 | 0.0147 | 0.0175 | 0.0164 | 0.0009 | 0 | 3 | 0.0129 | 0.0229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2425 | 5263.315 | 44265.6153 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 545.9889 | 0:240:120 | 0:00 | 0.0127 | 7 | 0.0028 | 0.0146 | 0.0174 | 0.016 | 0.001 | 0 | 3 | 0.0127 | 0.0227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2428 | 5266.739 | 44265.6153 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 556.9087 | 0:240:120 | 0:00 | 0.0125 | 7 | 0.003 | 0.014 | 0.017 | 0.0155 | 0.0011 | 0 | 3 | 0.0125 | 0.0225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2431 | 5270.018 | 44265.6154 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 568.0468 | 0:240:120 | 0:00 | 0.0123 | 7 | 0.004 | 0.0131 | 0.0171 | 0.0153 | 0.0016 | 0 | 3 | 0.0123 | 0.0223 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2434 | 5273.412 | 44265.6154 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 579.4078 | 0:240:120 | 0:00 | 0.0121 | 7 | 0.0042 | 0.0134 | 0.0176 | 0.0153 | 0.0014 | 0 | 3 | 0.0121 | 0.0221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2437 | 5276.708 | 44265.6154 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 590.9959 | 0:240:120 | 0:00 | 0.0119 | 7 | 0.0039 | 0.0128 | 0.0167 | 0.015 | 0.0013 | 0 | 3 | 0.0119 | 0.0219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2440 | 5280.232 | 44265.6155 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 602.8158 | 0:240:120 | 0:00 | 0.0117 | 7 | 0.0042 | 0.0125 | 0.0167 | 0.0148 | 0.0017 | 0 | 3 | 0.0117 | 0.0217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2443 | 5283.361 | 44265.6155 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 614.8722 | 0:240:120 | 0:00 | 0.0116 | 7 | 0.0033 | 0.0127 | 0.016 | 0.0146 | 0.0012 | 0 | 3 | 0.0116 | 0.0216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2446 | 5286.554 | 44265.6156 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 627.1696 | 0:240:120 | 0:00 | 0.0114 | 7 | 0.0043 | 0.0124 | 0.0167 | 0.0146 | 0.0017 | 0 | 3 | 0.0114 | 0.0214 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2449 | 5289.638 | 44265.6156 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 639.713 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.0046 | 0.0122 | 0.0168 | 0.0143 | 0.0015 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2452 | 5292.833 | 44265.6156 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 652.5072 | 0:240:120 | 0:00 | 0.0111 | 7 | 0.0049 | 0.0118 | 0.0167 | 0.0142 | 0.0018 | 0 | 3 | 0.0111 | 0.0211 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2455 | 5296.162 | 44265.6157 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 665.5574 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0044 | 0.0117 | 0.0161 | 0.0141 | 0.0017 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2458 | 5299.35 | 44265.6157 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 678.8685 | 0:240:120 | 0:00 | 0.0108 | 7 | 0.0052 | 0.0115 | 0.0167 | 0.0141 | 0.0018 | 0 | 3 | 0.0108 | 0.0208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2461 | 5302.538 | 44265.6157 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 692.4459 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0048 | 0.0115 | 0.0163 | 0.0139 | 0.0017 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2464 | 5305.715 | 44265.6158 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 706.2948 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0042 | 0.0121 | 0.0163 | 0.0139 | 0.0015 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2467 | 5308.913 | 44265.6158 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 720.4207 | 0:240:120 | 0:00 | 0.0104 | 7 | 0.0042 | 0.0115 | 0.0157 | 0.0136 | 0.0016 | 0 | 3 | 0.0104 | 0.0204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2470 | 5312.184 | 44265.6158 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 734.8291 | 0:240:120 | 0:00 | 0.0103 | 7 | 0.0045 | 0.0116 | 0.0161 | 0.0136 | 0.0017 | 0 | 3 | 0.0103 | 0.0203 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2473 | 5315.371 | 44265.6159 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 749.5257 | 0:240:120 | 0:00 | 0.0101 | 7 | 0.0044 | 0.0112 | 0.0156 | 0.0136 | 0.0015 | 0 | 3 | 0.0101 | 0.0201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2476 | 5318.667 | 44265.6159 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 764.5162 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0041 | 0.011 | 0.0151 | 0.0133 | 0.0016 | 0 | 3 | 0.01 | 0.02 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2479 | 5321.942 | 44265.616 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 766.5675 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0034 | 0.012 | 0.0154 | 0.0135 | 0.0012 | 0 | 3 | 0.01 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2482 | 5325.018 | 44265.616 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 781.8988 | 0:240:120 | 0:00 | 0.0099 | 7 | 0.0051 | 0.0105 | 0.0156 | 0.0132 | 0.0019 | 0 | 3 | 0.0099 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2485 | 5328.435 | 44265.616 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 797.5368 | 0:240:120 | 0:00 | 0.0098 | 7 | 0.0042 | 0.0114 | 0.0156 | 0.0132 | 0.0014 | 0 | 3 | 0.0098 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2488 | 5331.703 | 44265.6161 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 813.4875 | 0:240:120 | 0:00 | 0.0097 | 7 | 0.0034 | 0.011 | 0.0144 | 0.0132 | 0.0011 | 0 | 3 | 0.0097 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2491 | 5334.998 | 44265.6161 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 829.7573 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0035 | 0.0112 | 0.0147 | 0.0129 | 0.0013 | 0 | 3 | 0.0096 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2494 | 5338.369 | 44265.6162 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 846.3524 | 0:240:120 | 0:00 | 0.0095 | 7 | 0.0042 | 0.0109 | 0.0151 | 0.0127 | 0.0015 | 0 | 3 | 0.0095 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2497 | 5341.483 | 44265.6162 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 863.2795 | 0:240:120 | 0:00 | 0.0094 | 7 | 0.0034 | 0.0104 | 0.0138 | 0.012 | 0.0013 | 0 | 3 | 0.0094 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2500 | 5344.693 | 44265.6162 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 880.545 | 0:240:120 | 0:00 | 0.0093 | 7 | 0.0046 | 0.0105 | 0.0151 | 0.0125 | 0.0015 | 0 | 3 | 0.0093 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2503 | 5348.094 | 44265.6163 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 898.1559 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.0043 | 0.0109 | 0.0152 | 0.0124 | 0.0015 | 0 | 3 | 0.0092 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2506 | 5351.345 | 44265.6163 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 916.1191 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.0036 | 0.011 | 0.0146 | 0.0123 | 0.0013 | 0 | 3 | 0.0091 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2509 | 5354.747 | 44265.6163 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 934.4414 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.003 | 0.0105 | 0.0135 | 0.0115 | 0.001 | 0 | 3 | 0.0091 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2512 | 5357.956 | 44265.6164 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 953.1303 | 0:240:120 | 0:00 | 0.009 | 7 | 0.0031 | 0.0097 | 0.0128 | 0.0112 | 0.0011 | 0 | 3 | 0.009 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2515 | 5361.147 | 44265.6164 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 972.1929 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0052 | 0.01 | 0.0152 | 0.0119 | 0.0015 | 0 | 3 | 0.0089 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2518 | 5364.262 | 44265.6165 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 991.6367 | 0:240:120 | 0:00 | 0.0088 | 7 | 0.0033 | 0.0102 | 0.0135 | 0.0114 | 0.0012 | 0 | 3 | 0.0088 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2521 | 5367.256 | 44265.6165 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1011.4695 | 0:240:120 | 0:00 | 0.0088 | 7 | 0.0041 | 0.01 | 0.0141 | 0.0115 | 0.0014 | 0 | 3 | 0.0088 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2524 | 5370.766 | 44265.6165 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1031.6989 | 0:240:120 | 0:00 | 0.0087 | 7 | 0.0027 | 0.0101 | 0.0128 | 0.0111 | 0.001 | 0 | 3 | 0.0087 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2527 | 5374.182 | 44265.6166 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1052.3328 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0038 | 0.0104 | 0.0142 | 0.0115 | 0.0012 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2530 | 5377.363 | 44265.6166 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1073.3795 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0037 | 0.0104 | 0.0141 | 0.0116 | 0.0011 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2533 | 5380.653 | 44265.6166 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1094.8471 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0036 | 0.009 | 0.0126 | 0.0105 | 0.0014 | 0 | 3 | 0.0085 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2536 | 5383.985 | 44265.6167 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1116.744 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0028 | 0.0095 | 0.0123 | 0.0106 | 0.0012 | 0 | 3 | 0.0085 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2539 | 5387.172 | 44265.6167 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1139.0789 | 0:240:120 | 0:00 | 0.0084 | 7 | 0.0054 | 0.0097 | 0.0151 | 0.0111 | 0.0019 | 0 | 3 | 0.0084 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2542 | 5390.492 | 44265.6168 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1161.8605 | 0:240:120 | 0:00 | 0.0084 | 7 | 0.003 | 0.0093 | 0.0123 | 0.0104 | 0.0012 | 0 | 3 | 0.0084 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2545 | 5393.996 | 44265.6168 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1185.0977 | 0:240:120 | 0:00 | 0.0083 | 7 | 0.0056 | 0.0096 | 0.0152 | 0.011 | 0.0019 | 0 | 3 | 0.0083 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2548 | 5397.487 | 44265.6168 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1208.7996 | 0:240:120 | 0:00 | 0.0083 | 7 | 0.0025 | 0.0095 | 0.012 | 0.0106 | 0.0011 | 0 | 3 | 0.0083 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2551 | 5400.656 | 44265.6169 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1232.9756 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0043 | 0.01 | 0.0143 | 0.0112 | 0.0013 | 0 | 3 | 0.0082 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2554 | 5403.943 | 44265.6169 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1257.6352 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0053 | 0.0099 | 0.0152 | 0.0111 | 0.0016 | 0 | 3 | 0.0082 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2557 | 5407.218 | 44265.6169 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1282.7879 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0052 | 0.0099 | 0.0151 | 0.0107 | 0.0017 | 0 | 3 | 0.0081 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2560 | 5410.321 | 44265.617 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1308.4436 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.01 | 0.0007 | 0 | 3 | 0.0081 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2563 | 5413.456 | 44265.617 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1334.6125 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0015 | 0.0094 | 0.0109 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2566 | 5417.247 | 44265.6171 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1361.3047 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0023 | 0.0094 | 0.0117 | 0.0102 | 0.0009 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2569 | 5420.396 | 44265.6171 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1388.5308 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0032 | 0.0094 | 0.0126 | 0.0106 | 0.001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2572 | 5423.583 | 44265.6171 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1416.3014 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0021 | 0.0093 | 0.0114 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2575 | 5426.872 | 44265.6172 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1444.6275 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0017 | 0.0097 | 0.0114 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2578 | 5430.07 | 44265.6172 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1473.52 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0018 | 0.0091 | 0.0109 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2581 | 5433.239 | 44265.6172 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1502.9904 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.002 | 0.0096 | 0.0116 | 0.0104 | 0.0008 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2584 | 5436.346 | 44265.6173 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1533.0502 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0011 | 0.0106 | 0.0117 | 0.0108 | 0.0004 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2587 | 5439.786 | 44265.6173 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1533.1349 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2590 | 5443.088 | 44265.6174 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1563.7976 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2593 | 5446.38 | 44265.6174 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1595.0736 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2596 | 5449.484 | 44265.6174 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1626.975 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0011 | 0.0105 | 0.0116 | 0.0107 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2599 | 5452.932 | 44265.6175 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1659.5145 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2602 | 5456.216 | 44265.6175 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1692.7048 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0014 | 0.0095 | 0.0109 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2605 | 5459.857 | 44265.6176 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1726.5589 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0016 | 0.0098 | 0.0114 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2608 | 5463.024 | 44265.6176 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1761.0901 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0021 | 0.0094 | 0.0115 | 0.0104 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2611 | 5466.229 | 44265.6176 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1796.3119 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2614 | 5469.404 | 44265.6177 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1832.2381 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2617 | 5472.682 | 44265.6177 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1868.8829 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2620 | 5475.884 | 44265.6177 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1906.2605 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0015 | 0.0093 | 0.0108 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2623 | 5479.164 | 44265.6178 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1944.3858 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2626 | 5482.331 | 44265.6178 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1983.2735 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2629 | 5485.52 | 44265.6179 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2022.9389 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0018 | 0.009 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2632 | 5488.72 | 44265.6179 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2063.3977 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0011 | 0.0096 | 0.0107 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2635 | 5491.895 | 44265.6179 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2104.6657 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2638 | 5495.108 | 44265.618 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2146.759 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2641 | 5498.192 | 44265.618 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2189.6942 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0022 | 0.009 | 0.0112 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2644 | 5501.5 | 44265.618 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2233.4881 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2647 | 5504.81 | 44265.6181 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2278.1578 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.002 | 0.0094 | 0.0114 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2650 | 5508.211 | 44265.6181 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2323.721 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0025 | 0.009 | 0.0115 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2653 | 5511.366 | 44265.6182 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2370.1954 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0011 | 0.0101 | 0.0112 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2656 | 5514.562 | 44265.6182 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2417.5993 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0018 | 0.0093 | 0.0111 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2659 | 5517.756 | 44265.6182 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2465.9513 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.002 | 0.0093 | 0.0113 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2662 | 5521.293 | 44265.6183 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2515.2703 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2665 | 5524.388 | 44265.6183 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2565.5757 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2668 | 5527.678 | 44265.6183 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2616.8872 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2671 | 5530.762 | 44265.6184 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2669.225 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0022 | 0.0092 | 0.0114 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2674 | 5534.082 | 44265.6184 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2722.6095 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0018 | 0.0091 | 0.0109 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2677 | 5537.503 | 44265.6185 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2777.0617 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0013 | 0.0096 | 0.0109 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2680 | 5540.838 | 44265.6185 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2832.6029 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0019 | 0.0095 | 0.0114 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2683 | 5544.041 | 44265.6185 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2889.255 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0019 | 0.0094 | 0.0113 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2686 | 5547.34 | 44265.6186 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2947.0401 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.002 | 0.009 | 0.011 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2689 | 5550.526 | 44265.6186 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3005.9809 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2692 | 5553.632 | 44265.6186 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3066.1005 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0011 | 0.0101 | 0.0112 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2695 | 5556.918 | 44265.6187 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3127.4225 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0018 | 0.0089 | 0.0107 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2698 | 5560.335 | 44265.6187 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3189.9709 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0014 | 0.0095 | 0.0109 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2701 | 5563.446 | 44265.6188 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3253.7703 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0017 | 0.0089 | 0.0106 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2704 | 5566.647 | 44265.6188 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3318.8458 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2707 | 5569.829 | 44265.6188 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3385.2227 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2710 | 5573.032 | 44265.6189 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3452.9271 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0007 | 0.0098 | 0.0105 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2713 | 5576.127 | 44265.6189 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3521.9857 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2716 | 5579.413 | 44265.6189 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3592.4254 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0002 | 0.0094 | 0.0096 | 0.0094 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2719 | 5582.598 | 44265.619 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3664.2739 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0002 | 0.0105 | 0.0107 | 0.0106 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2722 | 5585.797 | 44265.619 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3737.5594 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2725 | 5589.09 | 44265.6191 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3812.3106 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0101 | 0.0112 | 0.0103 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2728 | 5592.31 | 44265.6191 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3888.5568 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0008 | 0.01 | 0.0108 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2731 | 5595.829 | 44265.6191 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3966.3279 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0021 | 0.009 | 0.0111 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2734 | 5599.04 | 44265.6192 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4045.6545 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0018 | 0.009 | 0.0108 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2737 | 5602.581 | 44265.6192 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4126.5675 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0097 | 0.0108 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2740 | 5605.789 | 44265.6192 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4209.0989 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2743 | 5608.88 | 44265.6193 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4293.2809 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2746 | 5612.397 | 44265.6193 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4379.1465 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2749 | 5615.922 | 44265.6194 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4466.7294 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.01 | 0.0113 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2752 | 5619.251 | 44265.6194 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4556.064 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2755 | 5622.435 | 44265.6194 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4647.1853 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.001 | 0.0101 | 0.0111 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2758 | 5625.713 | 44265.6195 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4740.129 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2761 | 5628.906 | 44265.6195 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4834.9316 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0022 | 0.009 | 0.0112 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2764 | 5632.11 | 44265.6196 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4931.6302 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0017 | 0.0091 | 0.0108 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2767 | 5635.415 | 44265.6196 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5030.2628 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0022 | 0.0088 | 0.011 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2770 | 5638.822 | 44265.6196 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5130.8681 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0012 | 0.0101 | 0.0113 | 0.0106 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2773 | 5642.227 | 44265.6197 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5233.4854 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0008 | 0.0098 | 0.0106 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2776 | 5645.426 | 44265.6197 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5338.1551 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2779 | 5648.601 | 44265.6197 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5444.9182 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2782 | 5652.006 | 44265.6198 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5553.8166 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2785 | 5655.294 | 44265.6198 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5664.8929 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0016 | 0.009 | 0.0106 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2788 | 5658.517 | 44265.6199 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5778.1908 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0012 | 0.009 | 0.0102 | 0.0095 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2791 | 5662.006 | 44265.6199 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5893.7546 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0008 | 0.0099 | 0.0107 | 0.0104 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2794 | 5665.124 | 44265.6199 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6011.6297 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2797 | 5668.509 | 44265.62 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6131.8623 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0006 | 0.0096 | 0.0102 | 0.0098 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2800 | 5671.838 | 44265.62 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6254.4995 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0014 | 0.0097 | 0.0111 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2803 | 5675.055 | 44265.62 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6379.5895 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2806 | 5678.191 | 44265.6201 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6507.1813 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2809 | 5681.643 | 44265.6201 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6637.3249 | 0:240:120 | 0:00 | 0.007 | 7 | 0.002 | 0.0088 | 0.0108 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2812 | 5684.945 | 44265.6202 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6770.0714 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2815 | 5688.473 | 44265.6202 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6905.4729 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2818 | 5691.782 | 44265.6202 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7043.5823 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2821 | 5694.929 | 44265.6203 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7184.454 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2824 | 5698.104 | 44265.6203 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7328.1431 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0014 | 0.0094 | 0.0108 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2827 | 5701.585 | 44265.6204 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7474.7059 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2830 | 5704.905 | 44265.6204 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7624.2 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2833 | 5708.033 | 44265.6204 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7776.684 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2836 | 5711.294 | 44265.6205 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7932.2177 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0008 | 0.0094 | 0.0102 | 0.0098 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2839 | 5714.747 | 44265.6205 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8090.8621 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2842 | 5718.083 | 44265.6205 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8252.6793 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0021 | 0.0091 | 0.0112 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2845 | 5721.202 | 44265.6206 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8417.7329 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2848 | 5724.335 | 44265.6206 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8586.0876 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2851 | 5727.805 | 44265.6207 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8757.8093 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2854 | 5731.051 | 44265.6207 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8932.9655 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.009 | 0.0103 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2857 | 5734.157 | 44265.6207 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9111.6248 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2860 | 5737.434 | 44265.6208 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9293.8573 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0011 | 0.0097 | 0.0108 | 0.0105 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2863 | 5740.587 | 44265.6208 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9479.7345 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0088 | 0.0105 | 0.0094 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2866 | 5743.722 | 44265.6208 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9669.3291 | 0:240:120 | 0:00 | 0.007 | 7 | 0.001 | 0.0092 | 0.0102 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2869 | 5747.132 | 44265.6209 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9862.7157 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2872 | 5750.595 | 44265.6209 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10059.97 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2875 | 5753.903 | 44265.621 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10261.1694 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.0087 | 0.01 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2878 | 5757.059 | 44265.621 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10466.3928 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0006 | 0.01 | 0.0106 | 0.0103 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2881 | 5760.185 | 44265.621 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10675.7207 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0012 | 0.0091 | 0.0103 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2884 | 5763.41 | 44265.6211 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10889.2351 | 0:240:120 | 0:00 | 0.007 | 7 | 0.002 | 0.0091 | 0.0111 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2887 | 5766.532 | 44265.6211 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11107.0198 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2890 | 5770.05 | 44265.6211 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11329.1602 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0092 | 0.0109 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2893 | 5773.258 | 44265.6212 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11555.7434 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0021 | 0.0088 | 0.0109 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2896 | 5776.892 | 44265.6212 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11786.8583 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2899 | 5836.906 | 44265.6219 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 28.8 | 0:240:120 | 0:00 | 6.4909 | 7 | 18.9937 | 38.4307 | 57.4244 | 47.0467 | 7.8924 | 62.2896 | 3 | 6.4909 | 32.4353 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2902 | 5990.946 | 44265.6237 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 29.4 | 0:240:120 | 0:00 | 5.5512 | 7 | 18.6638 | 17.6941 | 36.3579 | 26.0885 | 8.0078 | 64.1242 | 3 | 5.5512 | 18.3428 | NP | NP | 0-1-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2905 | 6080.03 | 44265.6247 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30 | 0:240:120 | 0:00 | 4.8381 | 7 | 4.0234 | 9.3925 | 13.4159 | 10.6691 | 1.7482 | 3.0561 | 3 | 4.8381 | 12.7088 | P | NP | 0-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2908 | 6118.042 | 44265.6252 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 30.6 | 0:240:120 | 0:00 | 4.2787 | 7 | 0.8597 | 8.2396 | 9.0993 | 8.6142 | 0.373 | 0.1391 | 3 | 4.2787 | 9.916 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2911 | 6147.344 | 44265.6255 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.2 | 0:240:120 | 0:00 | 3.8283 | 7 | 0.9729 | 7.0202 | 7.9931 | 7.4903 | 0.413 | 0.1706 | 3 | 3.8283 | 8.104 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2914 | 6173.314 | 44265.6258 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 31.8 | 0:240:120 | 0:00 | 3.4581 | 7 | 1.0255 | 5.8837 | 6.9092 | 6.3118 | 0.4563 | 0.2082 | 3 | 3.4581 | 6.8338 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2917 | 6195.691 | 44265.6261 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 32.5 | 0:240:120 | 0:00 | 3.1018 | 7 | 0.7361 | 4.7088 | 5.4449 | 5.0044 | 0.3303 | 0.1091 | 3 | 3.1018 | 5.7611 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2920 | 6214.162 | 44265.6263 | Vista Coord | Tap | 25Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.1 | 0:240:120 | 0:00 | 2.846 | 7 | 0.3479 | 4.3329 | 4.6808 | 4.4989 | 0.1478 | 0.0219 | 3 | 2.846 | 5.0673 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2923 | 6358.955 | 44265.628 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33 | 0:240:120 | 0:00 | 10.0814 | 7 | 17.5767 | 86.0272 | 103.6039 | 92.5151 | 7.1527 | 51.1605 | 3 | 10.0814 | 9999999 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
2926 | 6653.346 | 44265.6314 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 33.66 | 0:240:120 | 0:00 | 8.1878 | 7 | 17.8789 | 66.865 | 84.7439 | 74.1947 | 7.9479 | 63.1683 | 3 | 8.1878 | 106.9469 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2929 | 6890.327 | 44265.6341 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.3332 | 0:240:120 | 0:00 | 6.8518 | 7 | 17.2275 | 48.057 | 65.2845 | 54.9234 | 7.8517 | 61.6495 | 3 | 6.8518 | 34.6325 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2932 | 7068.387 | 44265.6362 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.0199 | 0:240:120 | 0:00 | 5.8595 | 7 | 16.4989 | 28.1208 | 44.6197 | 34.5092 | 7.5838 | 57.5146 | 3 | 5.8595 | 20.3493 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
2935 | 7183.563 | 44265.6375 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.7203 | 0:240:120 | 0:00 | 5.0937 | 7 | 13.1769 | 10.0041 | 23.181 | 14.4487 | 6.3778 | 40.6767 | 3 | 5.0937 | 14.2491 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2938 | 7242.214 | 44265.6382 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.4347 | 0:240:120 | 0:00 | 4.4853 | 7 | 0.8227 | 8.8374 | 9.6601 | 9.1906 | 0.3525 | 0.1242 | 3 | 4.4853 | 10.8674 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2941 | 7272.946 | 44265.6385 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.1634 | 0:240:120 | 0:00 | 3.9906 | 7 | 0.9362 | 7.5856 | 8.5218 | 8.0246 | 0.3982 | 0.1586 | 3 | 3.9906 | 8.7194 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2944 | 7300.519 | 44265.6389 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.9066 | 0:240:120 | 0:00 | 3.5806 | 7 | 1.0291 | 6.4219 | 7.451 | 6.795 | 0.4913 | 0.2413 | 3 | 3.5806 | 7.235 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2947 | 7324.865 | 44265.6391 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.6648 | 0:240:120 | 0:00 | 3.2356 | 7 | 0.9395 | 5.2804 | 6.2199 | 5.6144 | 0.4337 | 0.1881 | 3 | 3.2356 | 6.1485 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
2950 | 7345.136 | 44265.6394 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.4381 | 0:240:120 | 0:00 | 2.9415 | 7 | 0.3312 | 4.5298 | 4.861 | 4.6702 | 0.1411 | 0.0199 | 3 | 2.9415 | 5.3194 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2953 | 7362.427 | 44265.6396 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 40.2268 | 0:240:120 | 0:00 | 2.6879 | 7 | 0.3517 | 4.135 | 4.4867 | 4.2612 | 0.166 | 0.0276 | 3 | 2.6879 | 4.6662 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2956 | 7378.511 | 44265.6398 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.0314 | 0:240:120 | 0:00 | 2.4671 | 7 | 0.3104 | 3.6978 | 4.0082 | 3.8352 | 0.1347 | 0.0182 | 3 | 2.4671 | 4.1387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2959 | 7393.19 | 44265.6399 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 41.852 | 0:240:120 | 0:00 | 2.2733 | 7 | 0.3513 | 3.2731 | 3.6244 | 3.3954 | 0.171 | 0.0292 | 3 | 2.2733 | 3.7041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2962 | 7406.606 | 44265.6401 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 42.689 | 0:240:120 | 0:00 | 2.102 | 7 | 0.1729 | 2.9663 | 3.1392 | 3.0312 | 0.0779 | 0.0061 | 3 | 2.102 | 3.3401 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2965 | 7418.919 | 44265.6402 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 43.5428 | 0:240:120 | 0:00 | 1.9495 | 7 | 0.1713 | 2.751 | 2.9223 | 2.8123 | 0.0805 | 0.0065 | 3 | 1.9495 | 3.0309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2968 | 7430.533 | 44265.6404 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.4137 | 0:240:120 | 0:00 | 1.813 | 7 | 0.1723 | 2.5087 | 2.681 | 2.569 | 0.0828 | 0.0069 | 3 | 1.813 | 2.7653 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2971 | 7441.39 | 44265.6405 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.3019 | 0:240:120 | 0:00 | 1.6902 | 7 | 0.1818 | 2.2663 | 2.4481 | 2.3396 | 0.0789 | 0.0062 | 3 | 1.6902 | 2.5347 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2974 | 7451.327 | 44265.6406 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.208 | 0:240:120 | 0:00 | 1.5792 | 7 | 0.1085 | 2.1265 | 2.235 | 2.1669 | 0.049 | 0.0024 | 3 | 1.5792 | 2.3328 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2977 | 7461.082 | 44265.6407 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.1321 | 0:240:120 | 0:00 | 1.4784 | 7 | 0.1057 | 1.9856 | 2.0913 | 2.0222 | 0.0512 | 0.0026 | 3 | 1.4784 | 2.1547 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2980 | 7470.179 | 44265.6408 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.0748 | 0:240:120 | 0:00 | 1.3866 | 7 | 0.1045 | 1.8345 | 1.939 | 1.8704 | 0.0514 | 0.0026 | 3 | 1.3866 | 1.9965 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2983 | 7478.976 | 44265.6409 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.0363 | 0:240:120 | 0:00 | 1.3027 | 7 | 0.0869 | 1.6999 | 1.7868 | 1.7299 | 0.0423 | 0.0018 | 3 | 1.3027 | 1.8552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2986 | 7487.415 | 44265.641 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.017 | 0:240:120 | 0:00 | 1.2257 | 7 | 0.0711 | 1.596 | 1.6671 | 1.6211 | 0.0342 | 0.0012 | 3 | 1.2257 | 1.7282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2989 | 7495.352 | 44265.6411 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.0173 | 0:240:120 | 0:00 | 1.1548 | 7 | 0.0703 | 1.4949 | 1.5652 | 1.5205 | 0.0334 | 0.0011 | 3 | 1.1548 | 1.6136 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2992 | 7503.01 | 44265.6412 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.0377 | 0:240:120 | 0:00 | 1.0895 | 7 | 0.0725 | 1.3947 | 1.4672 | 1.4198 | 0.0345 | 0.0012 | 3 | 1.0895 | 1.5097 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2995 | 7510.29 | 44265.6413 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.0784 | 0:240:120 | 0:00 | 1.0291 | 7 | 0.0503 | 1.321 | 1.3713 | 1.3393 | 0.0238 | 0.0006 | 3 | 1.0291 | 1.4151 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
2998 | 7517.323 | 44265.6414 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.14 | 0:240:120 | 0:00 | 0.9731 | 7 | 0.0601 | 1.2333 | 1.2934 | 1.2581 | 0.0257 | 0.0007 | 3 | 0.9731 | 1.3288 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3001 | 7524.049 | 44265.6414 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.2228 | 0:240:120 | 0:00 | 0.9211 | 7 | 0.0523 | 1.1581 | 1.2104 | 1.1763 | 0.0246 | 0.0006 | 3 | 0.9211 | 1.2496 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3004 | 7530.58 | 44265.6415 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.3273 | 0:240:120 | 0:00 | 0.8728 | 7 | 0.0408 | 1.1012 | 1.142 | 1.1161 | 0.019 | 0.0004 | 3 | 0.8728 | 1.1769 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3007 | 7536.989 | 44265.6416 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.4538 | 0:240:120 | 0:00 | 0.8277 | 7 | 0.0429 | 1.0366 | 1.0795 | 1.0515 | 0.0202 | 0.0004 | 3 | 0.8277 | 1.1099 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3010 | 7543.263 | 44265.6417 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.6029 | 0:240:120 | 0:00 | 0.7856 | 7 | 0.0413 | 0.978 | 1.0193 | 0.993 | 0.0195 | 0.0004 | 3 | 0.7856 | 1.048 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3013 | 7549.533 | 44265.6417 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.7749 | 0:240:120 | 0:00 | 0.7462 | 7 | 0.0324 | 0.9283 | 0.9607 | 0.9397 | 0.0155 | 0.0002 | 3 | 0.7462 | 0.9906 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3016 | 7555.171 | 44265.6418 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.9704 | 0:240:120 | 0:00 | 0.7093 | 7 | 0.0391 | 0.8755 | 0.9146 | 0.891 | 0.0172 | 0.0003 | 3 | 0.7093 | 0.9374 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3019 | 7561.232 | 44265.6419 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.1898 | 0:240:120 | 0:00 | 0.6747 | 7 | 0.0318 | 0.83 | 0.8618 | 0.8433 | 0.0139 | 0.0002 | 3 | 0.6747 | 0.8879 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3022 | 7566.747 | 44265.6419 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.4336 | 0:240:120 | 0:00 | 0.6423 | 7 | 0.026 | 0.7919 | 0.8179 | 0.8013 | 0.012 | 0.0001 | 3 | 0.6423 | 0.8418 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3025 | 7572.122 | 44265.642 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.7023 | 0:240:120 | 0:00 | 0.6117 | 7 | 0.029 | 0.7501 | 0.7791 | 0.7608 | 0.0134 | 0.0002 | 3 | 0.6117 | 0.7988 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3028 | 7577.43 | 44265.6421 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.9964 | 0:240:120 | 0:00 | 0.5829 | 7 | 0.0231 | 0.7146 | 0.7377 | 0.7232 | 0.0108 | 0.0001 | 3 | 0.5829 | 0.7586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3031 | 7582.684 | 44265.6421 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.3163 | 0:240:120 | 0:00 | 0.5558 | 7 | 0.025 | 0.6792 | 0.7042 | 0.6882 | 0.0115 | 0.0001 | 3 | 0.5558 | 0.7209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3034 | 7587.916 | 44265.6422 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.6626 | 0:240:120 | 0:00 | 0.5303 | 7 | 0.0218 | 0.645 | 0.6668 | 0.6539 | 0.0097 | 0.0001 | 3 | 0.5303 | 0.6856 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3037 | 7592.941 | 44265.6422 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.0359 | 0:240:120 | 0:00 | 0.5061 | 7 | 0.0187 | 0.6158 | 0.6345 | 0.6233 | 0.0083 | 0.0001 | 3 | 0.5061 | 0.6524 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3040 | 7597.952 | 44265.6423 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.4366 | 0:240:120 | 0:00 | 0.4833 | 7 | 0.0225 | 0.5837 | 0.6062 | 0.5927 | 0.0098 | 0.0001 | 3 | 0.4833 | 0.6213 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3043 | 7602.844 | 44265.6424 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.8653 | 0:240:120 | 0:00 | 0.4617 | 7 | 0.0179 | 0.5609 | 0.5788 | 0.5675 | 0.0081 | 0.0001 | 3 | 0.4617 | 0.592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3046 | 7608.006 | 44265.6424 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.3226 | 0:240:120 | 0:00 | 0.4413 | 7 | 0.0182 | 0.5326 | 0.5508 | 0.5394 | 0.0081 | 0.0001 | 3 | 0.4413 | 0.5644 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3049 | 7612.81 | 44265.6425 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.8091 | 0:240:120 | 0:00 | 0.4219 | 7 | 0.0159 | 0.5094 | 0.5253 | 0.5155 | 0.0068 | 0 | 3 | 0.4219 | 0.5383 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3052 | 7617.504 | 44265.6425 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.3252 | 0:240:120 | 0:00 | 0.4036 | 7 | 0.0166 | 0.4857 | 0.5023 | 0.4921 | 0.0075 | 0.0001 | 3 | 0.4036 | 0.5137 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3055 | 7622.02 | 44265.6426 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.8718 | 0:240:120 | 0:00 | 0.3861 | 7 | 0.0151 | 0.4645 | 0.4796 | 0.4702 | 0.0062 | 0 | 3 | 0.3861 | 0.4905 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3058 | 7626.516 | 44265.6426 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.4492 | 0:240:120 | 0:00 | 0.3696 | 7 | 0.0155 | 0.4431 | 0.4586 | 0.4489 | 0.0066 | 0 | 3 | 0.3696 | 0.4685 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3061 | 7630.855 | 44265.6427 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.0582 | 0:240:120 | 0:00 | 0.3539 | 7 | 0.0128 | 0.4243 | 0.4371 | 0.429 | 0.006 | 0 | 3 | 0.3539 | 0.4477 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3064 | 7635.052 | 44265.6427 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83.6993 | 0:240:120 | 0:00 | 0.339 | 7 | 0.0125 | 0.4055 | 0.418 | 0.4103 | 0.0056 | 0 | 3 | 0.339 | 0.428 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3067 | 7639.453 | 44265.6428 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.3733 | 0:240:120 | 0:00 | 0.3247 | 7 | 0.0131 | 0.387 | 0.4001 | 0.3927 | 0.0053 | 0 | 3 | 0.3247 | 0.4093 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3070 | 7643.75 | 44265.6428 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.0808 | 0:240:120 | 0:00 | 0.3112 | 7 | 0.0115 | 0.3709 | 0.3824 | 0.3757 | 0.0046 | 0 | 3 | 0.3112 | 0.3916 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3073 | 7648.294 | 44265.6429 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.8224 | 0:240:120 | 0:00 | 0.2984 | 7 | 0.0118 | 0.3554 | 0.3672 | 0.3598 | 0.0047 | 0 | 3 | 0.2984 | 0.3748 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3076 | 7652.526 | 44265.6429 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.5989 | 0:240:120 | 0:00 | 0.2861 | 7 | 0.0103 | 0.3406 | 0.3509 | 0.3442 | 0.0048 | 0 | 3 | 0.2861 | 0.3588 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3079 | 7656.64 | 44265.643 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.4108 | 0:240:120 | 0:00 | 0.2744 | 7 | 0.0088 | 0.3269 | 0.3357 | 0.3301 | 0.004 | 0 | 3 | 0.2744 | 0.3437 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3082 | 7660.933 | 44265.643 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 94.259 | 0:240:120 | 0:00 | 0.2633 | 7 | 0.0101 | 0.3122 | 0.3223 | 0.3161 | 0.0045 | 0 | 3 | 0.2633 | 0.3292 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3085 | 7665.095 | 44265.6431 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.1442 | 0:240:120 | 0:00 | 0.2527 | 7 | 0.0101 | 0.2996 | 0.3097 | 0.3033 | 0.0045 | 0 | 3 | 0.2527 | 0.3155 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3088 | 7669.19 | 44265.6431 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.0671 | 0:240:120 | 0:00 | 0.2425 | 7 | 0.0092 | 0.2879 | 0.2971 | 0.2913 | 0.004 | 0 | 3 | 0.2425 | 0.3024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3091 | 7673.104 | 44265.6432 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.0285 | 0:240:120 | 0:00 | 0.2328 | 7 | 0.0093 | 0.2758 | 0.2851 | 0.2793 | 0.0042 | 0 | 3 | 0.2328 | 0.29 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3094 | 7677.239 | 44265.6432 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.029 | 0:240:120 | 0:00 | 0.2236 | 7 | 0.0074 | 0.2651 | 0.2725 | 0.2678 | 0.0032 | 0 | 3 | 0.2236 | 0.2781 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3097 | 7681.338 | 44265.6433 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.0696 | 0:240:120 | 0:00 | 0.2148 | 7 | 0.009 | 0.2526 | 0.2616 | 0.2565 | 0.0037 | 0 | 3 | 0.2148 | 0.2668 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3100 | 7685.169 | 44265.6433 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.151 | 0:240:120 | 0:00 | 0.2063 | 7 | 0.0072 | 0.2434 | 0.2506 | 0.2465 | 0.0029 | 0 | 3 | 0.2063 | 0.256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3103 | 7689.168 | 44265.6434 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 108.274 | 0:240:120 | 0:00 | 0.1983 | 7 | 0.0079 | 0.2338 | 0.2417 | 0.2372 | 0.0029 | 0 | 3 | 0.1983 | 0.2457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3106 | 7692.984 | 44265.6434 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.4395 | 0:240:120 | 0:00 | 0.1906 | 7 | 0.0071 | 0.2245 | 0.2316 | 0.2275 | 0.0028 | 0 | 3 | 0.1906 | 0.2359 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3109 | 7696.525 | 44265.6434 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.6483 | 0:240:120 | 0:00 | 0.1832 | 7 | 0.0068 | 0.2161 | 0.2229 | 0.2187 | 0.0029 | 0 | 3 | 0.1832 | 0.2265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3112 | 7700.079 | 44265.6435 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.9013 | 0:240:120 | 0:00 | 0.1761 | 7 | 0.0064 | 0.2076 | 0.214 | 0.2101 | 0.0024 | 0 | 3 | 0.1761 | 0.2175 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3115 | 7703.864 | 44265.6435 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.1993 | 0:240:120 | 0:00 | 0.1694 | 7 | 0.0068 | 0.1984 | 0.2052 | 0.2014 | 0.0028 | 0 | 3 | 0.1694 | 0.209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3118 | 7707.377 | 44265.6436 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.5433 | 0:240:120 | 0:00 | 0.1629 | 7 | 0.0063 | 0.1912 | 0.1975 | 0.1939 | 0.0022 | 0 | 3 | 0.1629 | 0.2008 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3121 | 7710.909 | 44265.6436 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.9341 | 0:240:120 | 0:00 | 0.1567 | 7 | 0.0064 | 0.1832 | 0.1896 | 0.1863 | 0.0024 | 0 | 3 | 0.1567 | 0.193 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3124 | 7714.437 | 44265.6437 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.3728 | 0:240:120 | 0:00 | 0.1508 | 7 | 0.0049 | 0.1772 | 0.1821 | 0.1796 | 0.0019 | 0 | 3 | 0.1508 | 0.1855 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3127 | 7718.11 | 44265.6437 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 126.8603 | 0:240:120 | 0:00 | 0.1451 | 7 | 0.0054 | 0.1695 | 0.1749 | 0.1722 | 0.0021 | 0 | 3 | 0.1451 | 0.1783 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3130 | 7721.904 | 44265.6437 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 129.3975 | 0:240:120 | 0:00 | 0.1397 | 7 | 0.0051 | 0.1631 | 0.1682 | 0.166 | 0.0018 | 0 | 3 | 0.1397 | 0.1715 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3133 | 7725.503 | 44265.6438 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131.9854 | 0:240:120 | 0:00 | 0.1345 | 7 | 0.0062 | 0.1567 | 0.1629 | 0.16 | 0.0021 | 0 | 3 | 0.1345 | 0.1649 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3136 | 7728.946 | 44265.6438 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 134.6251 | 0:240:120 | 0:00 | 0.1295 | 7 | 0.0047 | 0.1511 | 0.1558 | 0.1535 | 0.0017 | 0 | 3 | 0.1295 | 0.1587 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3139 | 7732.462 | 44265.6439 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.3176 | 0:240:120 | 0:00 | 0.1247 | 7 | 0.0052 | 0.1455 | 0.1507 | 0.148 | 0.0021 | 0 | 3 | 0.1247 | 0.1527 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3142 | 7735.978 | 44265.6439 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 140.064 | 0:240:120 | 0:00 | 0.1201 | 7 | 0.005 | 0.1397 | 0.1447 | 0.1424 | 0.0019 | 0 | 3 | 0.1201 | 0.1469 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3145 | 7739.438 | 44265.6439 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 142.8653 | 0:240:120 | 0:00 | 0.1157 | 7 | 0.0041 | 0.1352 | 0.1393 | 0.137 | 0.0017 | 0 | 3 | 0.1157 | 0.1414 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3148 | 7742.851 | 44265.644 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 145.7226 | 0:240:120 | 0:00 | 0.1115 | 7 | 0.0041 | 0.1303 | 0.1344 | 0.1322 | 0.0015 | 0 | 3 | 0.1115 | 0.1361 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3151 | 7746.277 | 44265.644 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.637 | 0:240:120 | 0:00 | 0.1074 | 7 | 0.0042 | 0.1252 | 0.1294 | 0.1274 | 0.0016 | 0 | 3 | 0.1074 | 0.131 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3154 | 7749.701 | 44265.6441 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 151.6098 | 0:240:120 | 0:00 | 0.1035 | 7 | 0.0038 | 0.121 | 0.1248 | 0.1228 | 0.0014 | 0 | 3 | 0.1035 | 0.1262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3157 | 7753.248 | 44265.6441 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 154.642 | 0:240:120 | 0:00 | 0.0998 | 7 | 0.0039 | 0.1163 | 0.1202 | 0.1184 | 0.0017 | 0 | 3 | 0.0998 | 0.1215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3160 | 7756.639 | 44265.6441 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 157.7348 | 0:240:120 | 0:00 | 0.0962 | 7 | 0.0026 | 0.1126 | 0.1152 | 0.1138 | 0.001 | 0 | 3 | 0.0962 | 0.1171 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3163 | 7760.268 | 44265.6442 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.8895 | 0:240:120 | 0:00 | 0.0928 | 7 | 0.0041 | 0.1074 | 0.1115 | 0.1098 | 0.0013 | 0 | 3 | 0.0928 | 0.1128 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3166 | 7763.862 | 44265.6442 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.1073 | 0:240:120 | 0:00 | 0.0895 | 7 | 0.0037 | 0.1039 | 0.1076 | 0.1059 | 0.0013 | 0 | 3 | 0.0895 | 0.1087 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3169 | 7767.393 | 44265.6443 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 167.3894 | 0:240:120 | 0:00 | 0.0863 | 7 | 0.0048 | 0.0993 | 0.1041 | 0.102 | 0.0017 | 0 | 3 | 0.0863 | 0.1048 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3172 | 7770.769 | 44265.6443 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.7372 | 0:240:120 | 0:00 | 0.0833 | 7 | 0.0028 | 0.097 | 0.0998 | 0.0984 | 0.001 | 0 | 3 | 0.0833 | 0.101 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3175 | 7774.187 | 44265.6443 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 174.152 | 0:240:120 | 0:00 | 0.0804 | 7 | 0.0031 | 0.0931 | 0.0962 | 0.0948 | 0.0013 | 0 | 3 | 0.0804 | 0.0973 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3178 | 7777.834 | 44265.6444 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 177.635 | 0:240:120 | 0:00 | 0.0776 | 7 | 0.0031 | 0.0902 | 0.0933 | 0.092 | 0.0013 | 0 | 3 | 0.0776 | 0.0939 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3181 | 7781.376 | 44265.6444 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 181.1877 | 0:240:120 | 0:00 | 0.0749 | 7 | 0.0041 | 0.0864 | 0.0905 | 0.0886 | 0.0014 | 0 | 3 | 0.0749 | 0.0905 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3184 | 7784.787 | 44265.6445 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 184.8115 | 0:240:120 | 0:00 | 0.0723 | 7 | 0.0037 | 0.0834 | 0.0871 | 0.0853 | 0.0014 | 0 | 3 | 0.0723 | 0.0873 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3187 | 7788.177 | 44265.6445 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 188.5077 | 0:240:120 | 0:00 | 0.0698 | 7 | 0.0035 | 0.0799 | 0.0834 | 0.082 | 0.0013 | 0 | 3 | 0.0698 | 0.0842 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3190 | 7791.615 | 44265.6445 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 192.2778 | 0:240:120 | 0:00 | 0.0674 | 7 | 0.0028 | 0.0775 | 0.0803 | 0.0791 | 0.0011 | 0 | 3 | 0.0674 | 0.0813 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3193 | 7795.012 | 44265.6446 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 196.1234 | 0:240:120 | 0:00 | 0.0651 | 7 | 0.0031 | 0.0755 | 0.0786 | 0.0771 | 0.0013 | 0 | 3 | 0.0651 | 0.0784 | P | NP | 1-1-1-0-1-0-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3196 | 7798.758 | 44265.6446 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 200.0459 | 0:240:120 | 0:00 | 0.0629 | 7 | 0.003 | 0.073 | 0.076 | 0.0745 | 0.0011 | 0 | 3 | 0.0629 | 0.0757 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3199 | 7802.183 | 44265.6447 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 204.0468 | 0:240:120 | 0:00 | 0.0608 | 7 | 0.0041 | 0.0686 | 0.0727 | 0.0707 | 0.0013 | 0 | 3 | 0.0608 | 0.0731 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3202 | 7805.69 | 44265.6447 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.1277 | 0:240:120 | 0:00 | 0.0587 | 7 | 0.003 | 0.0679 | 0.0709 | 0.0695 | 0.0011 | 0 | 3 | 0.0587 | 0.0706 | P | NP | 1-1-1-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3205 | 7809.222 | 44265.6447 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 212.2903 | 0:240:120 | 0:00 | 0.0568 | 7 | 0.0028 | 0.0652 | 0.068 | 0.0668 | 0.0012 | 0 | 3 | 0.0568 | 0.0682 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3208 | 7812.881 | 44265.6448 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 216.5361 | 0:240:120 | 0:00 | 0.0549 | 7 | 0.003 | 0.0626 | 0.0656 | 0.0642 | 0.0009 | 0 | 3 | 0.0549 | 0.0659 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3211 | 7816.308 | 44265.6448 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 220.8668 | 0:240:120 | 0:00 | 0.0531 | 7 | 0.0036 | 0.0605 | 0.0641 | 0.0625 | 0.0013 | 0 | 3 | 0.0531 | 0.0637 | P | NP | 1-1-0-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
3214 | 7819.727 | 44265.6449 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 225.2841 | 0:240:120 | 0:00 | 0.0514 | 7 | 0.0027 | 0.0583 | 0.061 | 0.0598 | 0.0011 | 0 | 3 | 0.0514 | 0.0616 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3217 | 7823.391 | 44265.6449 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 229.7898 | 0:240:120 | 0:00 | 0.0497 | 7 | 0.003 | 0.0563 | 0.0593 | 0.0582 | 0.0012 | 0 | 3 | 0.0497 | 0.0597 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3220 | 7826.991 | 44265.645 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.3856 | 0:240:120 | 0:00 | 0.0481 | 7 | 0.0024 | 0.0552 | 0.0576 | 0.0563 | 0.0008 | 0 | 3 | 0.0481 | 0.0581 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3223 | 7830.41 | 44265.645 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 239.0733 | 0:240:120 | 0:00 | 0.0465 | 7 | 0.0033 | 0.0527 | 0.056 | 0.0548 | 0.0013 | 0 | 3 | 0.0465 | 0.0565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3226 | 7834.172 | 44265.645 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 243.8548 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0025 | 0.0514 | 0.0539 | 0.053 | 0.0011 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3229 | 7837.476 | 44265.6451 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 248.7319 | 0:240:120 | 0:00 | 0.0436 | 7 | 0.0035 | 0.0491 | 0.0526 | 0.051 | 0.0012 | 0 | 3 | 0.0436 | 0.0536 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3232 | 7840.68 | 44265.6451 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 253.7065 | 0:240:120 | 0:00 | 0.0422 | 7 | 0.0031 | 0.048 | 0.0511 | 0.0495 | 0.001 | 0 | 3 | 0.0422 | 0.0522 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3235 | 7844.087 | 44265.6452 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 258.7807 | 0:240:120 | 0:00 | 0.0409 | 7 | 0.0038 | 0.0457 | 0.0495 | 0.048 | 0.0013 | 0 | 3 | 0.0409 | 0.0509 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3238 | 7847.487 | 44265.6452 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 263.9563 | 0:240:120 | 0:00 | 0.0396 | 7 | 0.0029 | 0.0444 | 0.0473 | 0.0464 | 0.001 | 0 | 3 | 0.0396 | 0.0496 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3241 | 7850.879 | 44265.6452 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 269.2354 | 0:240:120 | 0:00 | 0.0384 | 7 | 0.0022 | 0.0434 | 0.0456 | 0.0445 | 0.0009 | 0 | 3 | 0.0384 | 0.0484 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3244 | 7854.2 | 44265.6453 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 274.6201 | 0:240:120 | 0:00 | 0.0372 | 7 | 0.0035 | 0.0417 | 0.0452 | 0.0438 | 0.0013 | 0 | 3 | 0.0372 | 0.0472 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3247 | 7857.375 | 44265.6453 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 280.1125 | 0:240:120 | 0:00 | 0.0361 | 7 | 0.0038 | 0.0404 | 0.0442 | 0.0425 | 0.0013 | 0 | 3 | 0.0361 | 0.0461 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3250 | 7860.493 | 44265.6453 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 285.7147 | 0:240:120 | 0:00 | 0.035 | 7 | 0.003 | 0.0397 | 0.0427 | 0.041 | 0.0011 | 0 | 3 | 0.035 | 0.045 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3253 | 7863.78 | 44265.6454 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 291.429 | 0:240:120 | 0:00 | 0.034 | 7 | 0.004 | 0.0376 | 0.0416 | 0.0399 | 0.0015 | 0 | 3 | 0.034 | 0.044 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3256 | 7866.952 | 44265.6454 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 297.2576 | 0:240:120 | 0:00 | 0.033 | 7 | 0.0032 | 0.0368 | 0.04 | 0.0387 | 0.0013 | 0 | 3 | 0.033 | 0.043 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3259 | 7870.065 | 44265.6455 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 303.2028 | 0:240:120 | 0:00 | 0.032 | 7 | 0.0031 | 0.0354 | 0.0385 | 0.0373 | 0.001 | 0 | 3 | 0.032 | 0.042 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3262 | 7873.243 | 44265.6455 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 309.2668 | 0:240:120 | 0:00 | 0.0311 | 7 | 0.0027 | 0.0354 | 0.0381 | 0.0366 | 0.0009 | 0 | 3 | 0.0311 | 0.0411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3265 | 7876.48 | 44265.6455 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 315.4522 | 0:240:120 | 0:00 | 0.0302 | 7 | 0.0031 | 0.0341 | 0.0372 | 0.0357 | 0.0012 | 0 | 3 | 0.0302 | 0.0402 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3268 | 7879.819 | 44265.6456 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 321.7612 | 0:240:120 | 0:00 | 0.0293 | 7 | 0.0042 | 0.0324 | 0.0366 | 0.0348 | 0.0014 | 0 | 3 | 0.0293 | 0.0393 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3271 | 7883.141 | 44265.6456 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 328.1964 | 0:240:120 | 0:00 | 0.0285 | 7 | 0.0029 | 0.032 | 0.0349 | 0.0335 | 0.0009 | 0 | 3 | 0.0285 | 0.0385 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3274 | 7886.496 | 44265.6456 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 334.7604 | 0:240:120 | 0:00 | 0.0277 | 7 | 0.003 | 0.0312 | 0.0342 | 0.033 | 0.0011 | 0 | 3 | 0.0277 | 0.0377 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3277 | 7889.672 | 44265.6457 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 341.4556 | 0:240:120 | 0:00 | 0.0269 | 7 | 0.0027 | 0.0305 | 0.0332 | 0.0317 | 0.0009 | 0 | 3 | 0.0269 | 0.0369 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3280 | 7892.897 | 44265.6457 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 348.2847 | 0:240:120 | 0:00 | 0.0261 | 7 | 0.0025 | 0.0291 | 0.0316 | 0.0308 | 0.001 | 0 | 3 | 0.0261 | 0.0361 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3283 | 7896.088 | 44265.6458 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 355.2504 | 0:240:120 | 0:00 | 0.0254 | 7 | 0.0038 | 0.0276 | 0.0314 | 0.0298 | 0.0014 | 0 | 3 | 0.0254 | 0.0354 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3286 | 7899.405 | 44265.6458 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 362.3554 | 0:240:120 | 0:00 | 0.0247 | 7 | 0.0026 | 0.0276 | 0.0302 | 0.0294 | 0.001 | 0 | 3 | 0.0247 | 0.0347 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3289 | 7902.654 | 44265.6458 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 369.6025 | 0:240:120 | 0:00 | 0.0241 | 7 | 0.0029 | 0.027 | 0.0299 | 0.0285 | 0.001 | 0 | 3 | 0.0241 | 0.0341 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3292 | 7905.858 | 44265.6459 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 376.9945 | 0:240:120 | 0:00 | 0.0234 | 7 | 0.0034 | 0.0253 | 0.0287 | 0.0275 | 0.0013 | 0 | 3 | 0.0234 | 0.0334 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3295 | 7909.034 | 44265.6459 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 384.5344 | 0:240:120 | 0:00 | 0.0228 | 7 | 0.0036 | 0.0253 | 0.0289 | 0.0273 | 0.0012 | 0 | 3 | 0.0228 | 0.0328 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3298 | 7912.087 | 44265.6459 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 392.2251 | 0:240:120 | 0:00 | 0.0222 | 7 | 0.0029 | 0.0247 | 0.0276 | 0.0264 | 0.0013 | 0 | 3 | 0.0222 | 0.0322 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3301 | 7915.525 | 44265.646 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 400.0696 | 0:240:120 | 0:00 | 0.0217 | 7 | 0.0022 | 0.0242 | 0.0264 | 0.0258 | 0.001 | 0 | 3 | 0.0217 | 0.0317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3304 | 7918.789 | 44265.646 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 408.071 | 0:240:120 | 0:00 | 0.0211 | 7 | 0.003 | 0.0235 | 0.0265 | 0.025 | 0.0011 | 0 | 3 | 0.0211 | 0.0311 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3307 | 7922.083 | 44265.6461 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 416.2324 | 0:240:120 | 0:00 | 0.0206 | 7 | 0.0021 | 0.0233 | 0.0254 | 0.0245 | 0.0008 | 0 | 3 | 0.0206 | 0.0306 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3310 | 7925.551 | 44265.6461 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 424.5571 | 0:240:120 | 0:00 | 0.0201 | 7 | 0.003 | 0.0225 | 0.0255 | 0.0243 | 0.0011 | 0 | 3 | 0.0201 | 0.0301 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3313 | 7928.748 | 44265.6461 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 433.0482 | 0:240:120 | 0:00 | 0.0196 | 7 | 0.0036 | 0.0212 | 0.0248 | 0.0232 | 0.0012 | 0 | 3 | 0.0196 | 0.0296 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3316 | 7931.998 | 44265.6462 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 441.7092 | 0:240:120 | 0:00 | 0.0191 | 7 | 0.0027 | 0.0219 | 0.0246 | 0.0231 | 0.001 | 0 | 3 | 0.0191 | 0.0291 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3319 | 7935.59 | 44265.6462 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 450.5434 | 0:240:120 | 0:00 | 0.0187 | 7 | 0.0029 | 0.0216 | 0.0245 | 0.0226 | 0.0009 | 0 | 3 | 0.0187 | 0.0287 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3322 | 7939.025 | 44265.6463 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 459.5542 | 0:240:120 | 0:00 | 0.0183 | 7 | 0.0027 | 0.0204 | 0.0231 | 0.0221 | 0.001 | 0 | 3 | 0.0183 | 0.0283 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3325 | 7942.417 | 44265.6463 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 468.7453 | 0:240:120 | 0:00 | 0.0178 | 7 | 0.0034 | 0.0193 | 0.0227 | 0.0214 | 0.0015 | 0 | 3 | 0.0178 | 0.0278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3328 | 7945.991 | 44265.6463 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 478.1202 | 0:240:120 | 0:00 | 0.0174 | 7 | 0.0042 | 0.0188 | 0.023 | 0.0211 | 0.0014 | 0 | 3 | 0.0174 | 0.0274 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3331 | 7949.205 | 44265.6464 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 487.6826 | 0:240:120 | 0:00 | 0.0171 | 7 | 0.0031 | 0.0197 | 0.0228 | 0.0212 | 0.001 | 0 | 3 | 0.0171 | 0.0271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3334 | 7952.495 | 44265.6464 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 497.4363 | 0:240:120 | 0:00 | 0.0167 | 7 | 0.0039 | 0.0185 | 0.0224 | 0.0207 | 0.0014 | 0 | 3 | 0.0167 | 0.0267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3337 | 7955.609 | 44265.6464 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 507.385 | 0:240:120 | 0:00 | 0.0163 | 7 | 0.003 | 0.0188 | 0.0218 | 0.0204 | 0.0009 | 0 | 3 | 0.0163 | 0.0263 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3340 | 7958.819 | 44265.6465 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 517.5327 | 0:240:120 | 0:00 | 0.016 | 7 | 0.0023 | 0.0181 | 0.0204 | 0.0196 | 0.0009 | 0 | 3 | 0.016 | 0.026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3343 | 7961.893 | 44265.6465 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 527.8834 | 0:240:120 | 0:00 | 0.0156 | 7 | 0.0024 | 0.0181 | 0.0205 | 0.0198 | 0.001 | 0 | 3 | 0.0156 | 0.0256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3346 | 7965.113 | 44265.6466 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 538.441 | 0:240:120 | 0:00 | 0.0153 | 7 | 0.0022 | 0.0177 | 0.0199 | 0.0192 | 0.0008 | 0 | 3 | 0.0153 | 0.0253 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3349 | 7968.718 | 44265.6466 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 549.2099 | 0:240:120 | 0:00 | 0.015 | 7 | 0.0016 | 0.0178 | 0.0194 | 0.0186 | 0.0007 | 0 | 3 | 0.015 | 0.025 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3352 | 7971.929 | 44265.6466 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 560.1941 | 0:240:120 | 0:00 | 0.0147 | 7 | 0.0015 | 0.0177 | 0.0192 | 0.0186 | 0.0007 | 0 | 3 | 0.0147 | 0.0247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3355 | 7975.221 | 44265.6467 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 571.3979 | 0:240:120 | 0:00 | 0.0144 | 7 | 0.0024 | 0.017 | 0.0194 | 0.0184 | 0.0008 | 0 | 3 | 0.0144 | 0.0244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3358 | 7978.65 | 44265.6467 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 582.8259 | 0:240:120 | 0:00 | 0.0142 | 7 | 0.0019 | 0.0167 | 0.0186 | 0.0178 | 0.0007 | 0 | 3 | 0.0142 | 0.0242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3361 | 7981.819 | 44265.6467 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 594.4824 | 0:240:120 | 0:00 | 0.0139 | 7 | 0.0015 | 0.0164 | 0.0179 | 0.0174 | 0.0005 | 0 | 3 | 0.0139 | 0.0239 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3364 | 7984.994 | 44265.6468 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 606.3721 | 0:240:120 | 0:00 | 0.0136 | 7 | 0.0013 | 0.0167 | 0.018 | 0.0172 | 0.0006 | 0 | 3 | 0.0136 | 0.0236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3367 | 7988.229 | 44265.6468 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 618.4995 | 0:240:120 | 0:00 | 0.0134 | 7 | 0.002 | 0.0157 | 0.0177 | 0.0165 | 0.0007 | 0 | 3 | 0.0134 | 0.0234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3370 | 7991.62 | 44265.6469 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 630.8695 | 0:240:120 | 0:00 | 0.0132 | 7 | 0.0033 | 0.0148 | 0.0181 | 0.0166 | 0.001 | 0 | 3 | 0.0132 | 0.0232 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3373 | 7995.036 | 44265.6469 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 643.4869 | 0:240:120 | 0:00 | 0.0129 | 7 | 0.0026 | 0.0152 | 0.0178 | 0.0163 | 0.0009 | 0 | 3 | 0.0129 | 0.0229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3376 | 7998.348 | 44265.6469 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 656.3566 | 0:240:120 | 0:00 | 0.0127 | 7 | 0.0029 | 0.0146 | 0.0175 | 0.016 | 0.0012 | 0 | 3 | 0.0127 | 0.0227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3379 | 8001.543 | 44265.647 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 669.4838 | 0:240:120 | 0:00 | 0.0125 | 7 | 0.0033 | 0.0136 | 0.0169 | 0.0155 | 0.0011 | 0 | 3 | 0.0125 | 0.0225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3382 | 8004.73 | 44265.647 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 682.8734 | 0:240:120 | 0:00 | 0.0123 | 7 | 0.003 | 0.0141 | 0.0171 | 0.0154 | 0.0011 | 0 | 3 | 0.0123 | 0.0223 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3385 | 8008.11 | 44265.6471 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 696.5309 | 0:240:120 | 0:00 | 0.0121 | 7 | 0.0042 | 0.0128 | 0.017 | 0.0152 | 0.0016 | 0 | 3 | 0.0121 | 0.0221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3388 | 8011.217 | 44265.6471 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 710.4615 | 0:240:120 | 0:00 | 0.0119 | 7 | 0.0034 | 0.0131 | 0.0165 | 0.0149 | 0.0012 | 0 | 3 | 0.0119 | 0.0219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3391 | 8014.531 | 44265.6471 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 724.6708 | 0:240:120 | 0:00 | 0.0117 | 7 | 0.0041 | 0.0129 | 0.017 | 0.0147 | 0.0015 | 0 | 3 | 0.0117 | 0.0217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3394 | 8017.918 | 44265.6472 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 739.1642 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0042 | 0.0121 | 0.0163 | 0.0145 | 0.0015 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3397 | 8021.188 | 44265.6472 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 753.9475 | 0:240:120 | 0:00 | 0.0114 | 7 | 0.0055 | 0.0117 | 0.0172 | 0.0143 | 0.0023 | 0 | 3 | 0.0114 | 0.0214 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3400 | 8024.391 | 44265.6472 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 769.0264 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.0054 | 0.0119 | 0.0173 | 0.0143 | 0.0018 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3403 | 8027.712 | 44265.6473 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 784.4069 | 0:240:120 | 0:00 | 0.0111 | 7 | 0.0052 | 0.0119 | 0.0171 | 0.0143 | 0.0018 | 0 | 3 | 0.0111 | 0.0211 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3406 | 8030.988 | 44265.6473 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 800.0951 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0046 | 0.012 | 0.0166 | 0.0143 | 0.0016 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3409 | 8034.108 | 44265.6474 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 816.097 | 0:240:120 | 0:00 | 0.0108 | 7 | 0.0041 | 0.0121 | 0.0162 | 0.0141 | 0.0016 | 0 | 3 | 0.0108 | 0.0208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3412 | 8037.299 | 44265.6474 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 832.4189 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0047 | 0.0113 | 0.016 | 0.0136 | 0.0017 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3415 | 8040.696 | 44265.6474 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 849.0673 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0042 | 0.0113 | 0.0155 | 0.0136 | 0.0017 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3418 | 8043.973 | 44265.6475 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 866.0486 | 0:240:120 | 0:00 | 0.0104 | 7 | 0.0045 | 0.0115 | 0.016 | 0.0137 | 0.0018 | 0 | 3 | 0.0104 | 0.0204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3421 | 8047.161 | 44265.6475 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 883.3696 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.0042 | 0.0117 | 0.0159 | 0.0135 | 0.0016 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3424 | 8050.425 | 44265.6475 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 901.037 | 0:240:120 | 0:00 | 0.0101 | 7 | 0.0042 | 0.011 | 0.0152 | 0.0133 | 0.0015 | 0 | 3 | 0.0101 | 0.0201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3427 | 8053.625 | 44265.6476 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 919.0577 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0052 | 0.011 | 0.0162 | 0.0134 | 0.0017 | 0 | 3 | 0.01 | 0.02 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3430 | 8056.949 | 44265.6476 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 919.8809 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0044 | 0.0108 | 0.0152 | 0.0132 | 0.0015 | 0 | 3 | 0.01 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3433 | 8060.341 | 44265.6477 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 938.2786 | 0:240:120 | 0:00 | 0.0099 | 7 | 0.0043 | 0.0108 | 0.0151 | 0.0131 | 0.0016 | 0 | 3 | 0.0099 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3436 | 8063.71 | 44265.6477 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 957.0441 | 0:240:120 | 0:00 | 0.0098 | 7 | 0.0047 | 0.0108 | 0.0155 | 0.013 | 0.0018 | 0 | 3 | 0.0098 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3439 | 8067.004 | 44265.6477 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 976.185 | 0:240:120 | 0:00 | 0.0097 | 7 | 0.0036 | 0.0109 | 0.0145 | 0.013 | 0.0013 | 0 | 3 | 0.0097 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3442 | 8070.386 | 44265.6478 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 995.7087 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0041 | 0.011 | 0.0151 | 0.013 | 0.0016 | 0 | 3 | 0.0096 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3445 | 8073.57 | 44265.6478 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1015.6229 | 0:240:120 | 0:00 | 0.0095 | 7 | 0.004 | 0.0106 | 0.0146 | 0.0126 | 0.0013 | 0 | 3 | 0.0095 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3448 | 8076.836 | 44265.6478 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1035.9353 | 0:240:120 | 0:00 | 0.0094 | 7 | 0.0043 | 0.0108 | 0.0151 | 0.0126 | 0.0014 | 0 | 3 | 0.0094 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3451 | 8080.151 | 44265.6479 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1056.6541 | 0:240:120 | 0:00 | 0.0093 | 7 | 0.0038 | 0.0104 | 0.0142 | 0.0121 | 0.0013 | 0 | 3 | 0.0093 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3454 | 8083.353 | 44265.6479 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1077.7871 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.003 | 0.0104 | 0.0134 | 0.0117 | 0.0012 | 0 | 3 | 0.0092 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3457 | 8086.537 | 44265.648 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1099.3429 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.0023 | 0.0105 | 0.0128 | 0.0116 | 0.001 | 0 | 3 | 0.0091 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3460 | 8089.713 | 44265.648 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1121.3297 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.004 | 0.0102 | 0.0142 | 0.012 | 0.0012 | 0 | 3 | 0.0091 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3463 | 8092.872 | 44265.648 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1143.7563 | 0:240:120 | 0:00 | 0.009 | 7 | 0.003 | 0.0105 | 0.0135 | 0.0115 | 0.0014 | 0 | 3 | 0.009 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3466 | 8096.171 | 44265.6481 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1166.6315 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0039 | 0.0102 | 0.0141 | 0.0116 | 0.0013 | 0 | 3 | 0.0089 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3469 | 8099.364 | 44265.6481 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1189.9641 | 0:240:120 | 0:00 | 0.0088 | 7 | 0.003 | 0.0102 | 0.0132 | 0.0114 | 0.0011 | 0 | 3 | 0.0088 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3472 | 8102.466 | 44265.6481 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1213.7634 | 0:240:120 | 0:00 | 0.0088 | 7 | 0.0031 | 0.0095 | 0.0126 | 0.0107 | 0.0012 | 0 | 3 | 0.0088 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3475 | 8105.752 | 44265.6482 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1238.0386 | 0:240:120 | 0:00 | 0.0087 | 7 | 0.0031 | 0.0097 | 0.0128 | 0.0108 | 0.0012 | 0 | 3 | 0.0087 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3478 | 8108.837 | 44265.6482 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1262.7994 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0047 | 0.0103 | 0.015 | 0.0114 | 0.0015 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3481 | 8112.015 | 44265.6483 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1288.0554 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0037 | 0.0094 | 0.0131 | 0.0107 | 0.0015 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3484 | 8115.327 | 44265.6483 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1313.8165 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0052 | 0.0099 | 0.0151 | 0.0118 | 0.0019 | 0 | 3 | 0.0085 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3487 | 8118.478 | 44265.6483 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1340.0928 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0028 | 0.0097 | 0.0125 | 0.0106 | 0.0009 | 0 | 3 | 0.0085 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3490 | 8122.313 | 44265.6484 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1366.8947 | 0:240:120 | 0:00 | 0.0084 | 7 | 0.0031 | 0.0098 | 0.0129 | 0.0109 | 0.0012 | 0 | 3 | 0.0084 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3493 | 8125.611 | 44265.6484 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1394.2326 | 0:240:120 | 0:00 | 0.0084 | 7 | 0.0027 | 0.009 | 0.0117 | 0.0103 | 0.001 | 0 | 3 | 0.0084 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3496 | 8128.913 | 44265.6484 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1422.1172 | 0:240:120 | 0:00 | 0.0083 | 7 | 0.0026 | 0.0091 | 0.0117 | 0.01 | 0.0012 | 0 | 3 | 0.0083 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3499 | 8132.121 | 44265.6485 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1450.5596 | 0:240:120 | 0:00 | 0.0083 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.01 | 0.0008 | 0 | 3 | 0.0083 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3502 | 8135.399 | 44265.6485 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1479.5708 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0022 | 0.0092 | 0.0114 | 0.0104 | 0.0007 | 0 | 3 | 0.0082 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3505 | 8138.662 | 44265.6486 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1509.1622 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.01 | 0.0006 | 0 | 3 | 0.0082 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3508 | 8141.952 | 44265.6486 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1539.3454 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0018 | 0.0095 | 0.0113 | 0.0103 | 0.0007 | 0 | 3 | 0.0081 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3511 | 8145.113 | 44265.6486 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1570.1323 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0015 | 0.0097 | 0.0112 | 0.0104 | 0.0005 | 0 | 3 | 0.0081 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3514 | 8148.63 | 44265.6487 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1601.535 | 0:240:120 | 0:00 | 0.008 | 7 | 0.002 | 0.009 | 0.011 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3517 | 8152.001 | 44265.6487 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1633.5657 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0021 | 0.0092 | 0.0113 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3520 | 8155.353 | 44265.6488 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1666.237 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0003 | 0.0098 | 0.0101 | 0.0099 | 0.0001 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3523 | 8158.517 | 44265.6488 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1699.5617 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0017 | 0.009 | 0.0107 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3526 | 8161.914 | 44265.6488 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1733.553 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0023 | 0.0091 | 0.0114 | 0.0103 | 0.0008 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3529 | 8165.228 | 44265.6489 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1768.224 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0022 | 0.0092 | 0.0114 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3532 | 8168.72 | 44265.6489 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1803.5885 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.002 | 0.0095 | 0.0115 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3535 | 8171.914 | 44265.6489 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1839.6603 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3538 | 8175.119 | 44265.649 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1839.7619 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0018 | 0.0092 | 0.011 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3541 | 8178.348 | 44265.649 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1876.5571 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0012 | 0.0089 | 0.0101 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3544 | 8181.509 | 44265.6491 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1914.0883 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0019 | 0.0091 | 0.011 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3547 | 8184.703 | 44265.6491 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1952.37 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3550 | 8187.962 | 44265.6491 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1991.4174 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0016 | 0.0099 | 0.0115 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3553 | 8191.066 | 44265.6492 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2031.2458 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0018 | 0.0091 | 0.0109 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3556 | 8194.486 | 44265.6492 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2071.8707 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0017 | 0.0099 | 0.0116 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3559 | 8197.681 | 44265.6492 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2113.3081 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3562 | 8200.809 | 44265.6493 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2155.5743 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0021 | 0.0094 | 0.0115 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3565 | 8204.005 | 44265.6493 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2198.6858 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0012 | 0.0095 | 0.0107 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3568 | 8207.166 | 44265.6494 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2242.6595 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0013 | 0.0101 | 0.0114 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3571 | 8210.565 | 44265.6494 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2287.5127 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0018 | 0.0093 | 0.0111 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3574 | 8213.872 | 44265.6494 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2333.2629 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0022 | 0.0092 | 0.0114 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3577 | 8217.03 | 44265.6495 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2379.9282 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0023 | 0.009 | 0.0113 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3580 | 8220.213 | 44265.6495 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2427.5267 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0018 | 0.0091 | 0.0109 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3583 | 8223.376 | 44265.6495 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2476.0773 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3586 | 8226.684 | 44265.6496 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2525.5988 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0019 | 0.0095 | 0.0114 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3589 | 8229.966 | 44265.6496 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2576.1108 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3592 | 8233.169 | 44265.6497 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2627.633 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3595 | 8236.339 | 44265.6497 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2680.1857 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3598 | 8239.42 | 44265.6497 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2733.7894 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0014 | 0.0099 | 0.0113 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3601 | 8242.874 | 44265.6498 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2788.4652 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3604 | 8246.177 | 44265.6498 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2844.2345 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0012 | 0.0096 | 0.0108 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3607 | 8249.359 | 44265.6498 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2901.1192 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3610 | 8252.739 | 44265.6499 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2959.1415 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0012 | 0.0102 | 0.0114 | 0.0106 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3613 | 8255.933 | 44265.6499 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3018.3244 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0018 | 0.0096 | 0.0114 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3616 | 8259.246 | 44265.65 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3078.6909 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0011 | 0.009 | 0.0101 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3619 | 8262.43 | 44265.65 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3140.2647 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.002 | 0.0093 | 0.0113 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3622 | 8265.689 | 44265.65 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3203.07 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0006 | 0.0101 | 0.0107 | 0.0105 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3625 | 8268.987 | 44265.6501 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3267.1314 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0013 | 0.0097 | 0.011 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3628 | 8272.172 | 44265.6501 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3332.474 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0021 | 0.0092 | 0.0113 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3631 | 8275.35 | 44265.6501 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3399.1235 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0021 | 0.0089 | 0.011 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3634 | 8278.516 | 44265.6502 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3467.1059 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3637 | 8282.023 | 44265.6502 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3536.4481 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0001 | 0.0105 | 0.0106 | 0.0105 | 0 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3640 | 8285.216 | 44265.6503 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3607.177 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0019 | 0.0095 | 0.0114 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3643 | 8288.507 | 44265.6503 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3679.3206 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.001 | 0.0095 | 0.0105 | 0.0099 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3646 | 8291.887 | 44265.6503 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3752.907 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0099 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3649 | 8295.152 | 44265.6504 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3827.9651 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3652 | 8298.334 | 44265.6504 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3904.5244 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0021 | 0.0093 | 0.0114 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3655 | 8301.668 | 44265.6504 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3982.6149 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3658 | 8305.077 | 44265.6505 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4062.2672 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3661 | 8308.333 | 44265.6505 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4143.5125 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3664 | 8311.776 | 44265.6506 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4226.3828 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0013 | 0.0101 | 0.0114 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3667 | 8315.188 | 44265.6506 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4310.9105 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3670 | 8318.345 | 44265.6506 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4397.1287 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0018 | 0.0088 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3673 | 8321.619 | 44265.6507 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4485.0712 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0014 | 0.0097 | 0.0111 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3676 | 8324.766 | 44265.6507 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4574.7727 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3679 | 8327.94 | 44265.6508 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4666.2681 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3682 | 8331.241 | 44265.6508 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4759.5935 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0002 | 0.0096 | 0.0098 | 0.0097 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3685 | 8334.349 | 44265.6508 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4854.7853 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0096 | 0.0107 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3688 | 8337.557 | 44265.6509 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4951.8811 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3691 | 8341.203 | 44265.6509 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5050.9187 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0018 | 0.009 | 0.0108 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3694 | 8344.61 | 44265.6509 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5151.937 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0095 | 0.0108 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3697 | 8347.805 | 44265.651 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5254.9758 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.002 | 0.0089 | 0.0109 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3700 | 8350.988 | 44265.651 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5360.0753 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0095 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3703 | 8354.255 | 44265.6511 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5467.2768 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3706 | 8357.542 | 44265.6511 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5576.6223 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0023 | 0.0089 | 0.0112 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3709 | 8360.799 | 44265.6511 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5688.1548 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3712 | 8364.296 | 44265.6512 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5801.9179 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0024 | 0.0088 | 0.0112 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3715 | 8367.507 | 44265.6512 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5917.9562 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0015 | 0.0093 | 0.0108 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3718 | 8370.574 | 44265.6512 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6036.3154 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0089 | 0.01 | 0.0095 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3721 | 8373.785 | 44265.6513 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6157.0417 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.001 | 0.0088 | 0.0098 | 0.0096 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3724 | 8376.935 | 44265.6513 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6280.1825 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0016 | 0.0096 | 0.0112 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3727 | 8380.228 | 44265.6514 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6405.7862 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0008 | 0.0093 | 0.0101 | 0.0098 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3730 | 8383.298 | 44265.6514 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6533.9019 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3733 | 8386.562 | 44265.6514 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6664.5799 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.002 | 0.0092 | 0.0112 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3736 | 8389.725 | 44265.6515 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6797.8715 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3739 | 8392.923 | 44265.6515 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6933.829 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0016 | 0.009 | 0.0106 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3742 | 8396.215 | 44265.6515 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7072.5055 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0017 | 0.0095 | 0.0112 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3745 | 8399.313 | 44265.6516 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7213.9556 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.001 | 0.0092 | 0.0102 | 0.0096 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3748 | 8402.567 | 44265.6516 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7358.2348 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.002 | 0.0091 | 0.0111 | 0.0097 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3751 | 8405.754 | 44265.6517 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7505.3994 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0018 | 0.0091 | 0.0109 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3754 | 8408.947 | 44265.6517 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7655.5074 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0021 | 0.0091 | 0.0112 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3757 | 8412.184 | 44265.6517 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7808.6176 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3760 | 8415.299 | 44265.6518 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7964.7899 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3763 | 8418.546 | 44265.6518 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8124.0857 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0089 | 0.0105 | 0.0097 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3766 | 8421.842 | 44265.6518 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8286.5675 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0015 | 0.0092 | 0.0107 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3769 | 8424.938 | 44265.6519 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8452.2988 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3772 | 8428.087 | 44265.6519 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8621.3448 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0012 | 0.0092 | 0.0104 | 0.0095 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3775 | 8431.352 | 44265.652 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8793.7717 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0088 | 0.0107 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3778 | 8434.856 | 44265.652 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8969.6471 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0009 | 0.0095 | 0.0104 | 0.01 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3781 | 8438.155 | 44265.652 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9149.04 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0023 | 0.0088 | 0.0111 | 0.0096 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3784 | 8441.328 | 44265.6521 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9332.0209 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3787 | 8444.735 | 44265.6521 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9518.6613 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3790 | 8448.016 | 44265.6521 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9709.0345 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0088 | 0.0104 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3793 | 8451.455 | 44265.6522 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9903.2152 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0094 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3796 | 8454.618 | 44265.6522 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10101.2795 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.0092 | 0.0105 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3799 | 8457.812 | 44265.6523 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10303.3051 | 0:240:120 | 0:00 | 0.007 | 7 | 0.002 | 0.0091 | 0.0111 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3802 | 8461.125 | 44265.6523 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10509.3712 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0094 | 0.0111 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3805 | 8464.239 | 44265.6523 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10719.5586 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3808 | 8467.327 | 44265.6524 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10933.9498 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0091 | 0.011 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3811 | 8470.721 | 44265.6524 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11152.6288 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0022 | 0.0088 | 0.011 | 0.0095 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3814 | 8473.995 | 44265.6524 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11375.6813 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0102 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3817 | 8477.268 | 44265.6525 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11603.195 | 0:240:120 | 0:00 | 0.007 | 7 | 0.001 | 0.0101 | 0.0111 | 0.0105 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3820 | 8480.54 | 44265.6525 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11835.2589 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0012 | 0.009 | 0.0102 | 0.0096 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3823 | 8532.207 | 44265.6531 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 34.7 | 0:240:120 | 0:00 | 6.2855 | 7 | 16.406 | 32.9755 | 49.3815 | 40.5789 | 6.6128 | 43.7293 | 3 | 6.2855 | 25.2165 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3826 | 8663.851 | 44265.6546 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 35.4 | 0:240:120 | 0:00 | 5.4191 | 7 | 15.6508 | 14.1398 | 29.7906 | 21.2945 | 6.5886 | 43.409 | 3 | 5.4191 | 16.525 | NP | NP | 0-1-0-0-1-0-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
3829 | 8736.813 | 44265.6555 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.1 | 0:240:120 | 0:00 | 4.7525 | 7 | 1.0511 | 9.2646 | 10.3157 | 9.6886 | 0.4483 | 0.201 | 3 | 4.7525 | 12.2339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3832 | 8769.542 | 44265.6559 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 36.8 | 0:240:120 | 0:00 | 4.2239 | 7 | 0.9606 | 8.0831 | 9.0437 | 8.5221 | 0.4112 | 0.1691 | 3 | 4.2239 | 9.6774 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3835 | 8798.769 | 44265.6562 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 37.5 | 0:240:120 | 0:00 | 3.7947 | 7 | 0.9951 | 6.9904 | 7.9855 | 7.3849 | 0.457 | 0.2088 | 3 | 3.7947 | 7.9813 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3838 | 8824.475 | 44265.6565 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 38.3 | 0:240:120 | 0:00 | 3.3937 | 7 | 0.8847 | 5.7989 | 6.6836 | 6.1285 | 0.4108 | 0.1687 | 3 | 3.3937 | 6.6297 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3841 | 8846.171 | 44265.6568 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.1 | 0:240:120 | 0:00 | 3.0639 | 7 | 0.6718 | 4.7095 | 5.3813 | 4.9583 | 0.3172 | 0.1006 | 3 | 3.0639 | 5.6544 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3844 | 8864.623 | 44265.657 | Vista Coord | Tap | 30Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 39.8 | 0:240:120 | 0:00 | 2.82 | 7 | 0.3435 | 4.3288 | 4.6723 | 4.4567 | 0.1618 | 0.0262 | 3 | 2.82 | 4.9997 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3847 | 8983.161 | 44265.6583 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44 | 0:240:120 | 0:00 | 10.0814 | 7 | 16.4962 | 88.2625 | 104.7587 | 94.2695 | 7.8786 | 62.0722 | 3 | 10.0814 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3850 | 9281.443 | 44265.6618 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 44.88 | 0:240:120 | 0:00 | 8.1878 | 7 | 16.7387 | 69.0771 | 85.8158 | 75.3158 | 7.8753 | 62.0211 | 3 | 8.1878 | 106.9469 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3853 | 9522.938 | 44265.6646 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 45.7776 | 0:240:120 | 0:00 | 6.8518 | 7 | 17.7318 | 49.1046 | 66.8364 | 55.7086 | 8.3774 | 70.1801 | 3 | 6.8518 | 34.6325 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3856 | 9707.263 | 44265.6667 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.6932 | 0:240:120 | 0:00 | 5.8595 | 7 | 18.1989 | 29.4044 | 47.6033 | 35.6655 | 8.9274 | 79.6976 | 3 | 5.8595 | 20.3493 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
3859 | 9832.318 | 44265.6682 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.627 | 0:240:120 | 0:00 | 5.0937 | 7 | 16.5755 | 10.1136 | 26.6891 | 15.5982 | 8.118 | 65.9012 | 3 | 5.0937 | 14.2491 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3862 | 9897.727 | 44265.6689 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.5796 | 0:240:120 | 0:00 | 4.4853 | 7 | 0.7427 | 9.0287 | 9.7714 | 9.2804 | 0.3653 | 0.1334 | 3 | 4.4853 | 10.8674 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3865 | 9929.174 | 44265.6693 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.5511 | 0:240:120 | 0:00 | 3.9906 | 7 | 0.6738 | 7.8603 | 8.5341 | 8.1323 | 0.301 | 0.0906 | 3 | 3.9906 | 8.7194 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3868 | 9956.933 | 44265.6696 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50.5422 | 0:240:120 | 0:00 | 3.5806 | 7 | 0.9603 | 6.5086 | 7.4689 | 6.9077 | 0.4239 | 0.1797 | 3 | 3.5806 | 7.235 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3871 | 9981.215 | 44265.6699 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51.553 | 0:240:120 | 0:00 | 3.2356 | 7 | 0.9827 | 5.3697 | 6.3524 | 5.6957 | 0.4828 | 0.2331 | 3 | 3.2356 | 6.1485 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
3874 | 10001.979 | 44265.6701 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.5841 | 0:240:120 | 0:00 | 2.9415 | 7 | 0.2609 | 4.6532 | 4.9141 | 4.7429 | 0.1212 | 0.0147 | 3 | 2.9415 | 5.3194 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3877 | 10019.264 | 44265.6703 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.6358 | 0:240:120 | 0:00 | 2.6879 | 7 | 0.3411 | 4.155 | 4.4961 | 4.2757 | 0.1653 | 0.0273 | 3 | 2.6879 | 4.6662 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3880 | 10035.244 | 44265.6705 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 54.7085 | 0:240:120 | 0:00 | 2.4671 | 7 | 0.272 | 3.7928 | 4.0648 | 3.8865 | 0.1307 | 0.0171 | 3 | 2.4671 | 4.1387 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3883 | 10049.912 | 44265.6707 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.8026 | 0:240:120 | 0:00 | 2.2733 | 7 | 0.3413 | 3.2886 | 3.6299 | 3.4196 | 0.1588 | 0.0252 | 3 | 2.2733 | 3.7041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3886 | 10063.392 | 44265.6708 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.9187 | 0:240:120 | 0:00 | 2.102 | 7 | 0.1593 | 3.0084 | 3.1677 | 3.0646 | 0.0758 | 0.0057 | 3 | 2.102 | 3.3401 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3889 | 10076.13 | 44265.671 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.0571 | 0:240:120 | 0:00 | 1.9495 | 7 | 0.1731 | 2.762 | 2.9351 | 2.8217 | 0.0849 | 0.0072 | 3 | 1.9495 | 3.0309 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3892 | 10087.685 | 44265.6711 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.2182 | 0:240:120 | 0:00 | 1.813 | 7 | 0.1645 | 2.5166 | 2.6811 | 2.5926 | 0.0675 | 0.0046 | 3 | 1.813 | 2.7653 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3895 | 10098.324 | 44265.6712 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.4026 | 0:240:120 | 0:00 | 1.6902 | 7 | 0.1734 | 2.2891 | 2.4625 | 2.3639 | 0.0745 | 0.0055 | 3 | 1.6902 | 2.5347 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3898 | 10108.648 | 44265.6714 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.6106 | 0:240:120 | 0:00 | 1.5792 | 7 | 0.1024 | 2.1394 | 2.2418 | 2.1752 | 0.0493 | 0.0024 | 3 | 1.5792 | 2.3328 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3901 | 10118.234 | 44265.6715 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.8428 | 0:240:120 | 0:00 | 1.4784 | 7 | 0.1016 | 1.9906 | 2.0922 | 2.0275 | 0.0484 | 0.0023 | 3 | 1.4784 | 2.1547 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3904 | 10127.708 | 44265.6716 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.0997 | 0:240:120 | 0:00 | 1.3866 | 7 | 0.1018 | 1.8374 | 1.9392 | 1.877 | 0.0471 | 0.0022 | 3 | 1.3866 | 1.9965 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3907 | 10136.485 | 44265.6717 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.3817 | 0:240:120 | 0:00 | 1.3027 | 7 | 0.0856 | 1.7009 | 1.7865 | 1.7326 | 0.0405 | 0.0016 | 3 | 1.3027 | 1.8552 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3910 | 10144.771 | 44265.6718 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.6893 | 0:240:120 | 0:00 | 1.2257 | 7 | 0.07 | 1.5989 | 1.6689 | 1.6238 | 0.0329 | 0.0011 | 3 | 1.2257 | 1.7282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3913 | 10152.972 | 44265.6719 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 68.0231 | 0:240:120 | 0:00 | 1.1548 | 7 | 0.0688 | 1.4977 | 1.5665 | 1.5219 | 0.0331 | 0.0011 | 3 | 1.1548 | 1.6136 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3916 | 10160.429 | 44265.672 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.3836 | 0:240:120 | 0:00 | 1.0895 | 7 | 0.0687 | 1.397 | 1.4657 | 1.4208 | 0.0334 | 0.0011 | 3 | 1.0895 | 1.5097 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3919 | 10167.817 | 44265.672 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 70.7712 | 0:240:120 | 0:00 | 1.0291 | 7 | 0.0506 | 1.3238 | 1.3744 | 1.3411 | 0.0246 | 0.0006 | 3 | 1.0291 | 1.4151 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3922 | 10175.018 | 44265.6721 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.1867 | 0:240:120 | 0:00 | 0.9731 | 7 | 0.0531 | 1.2439 | 1.297 | 1.2639 | 0.0243 | 0.0006 | 3 | 0.9731 | 1.3288 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3925 | 10182.247 | 44265.6722 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.6304 | 0:240:120 | 0:00 | 0.9211 | 7 | 0.05 | 1.1593 | 1.2093 | 1.1768 | 0.0241 | 0.0006 | 3 | 0.9211 | 1.2496 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3928 | 10188.935 | 44265.6723 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.103 | 0:240:120 | 0:00 | 0.8728 | 7 | 0.0365 | 1.1054 | 1.1419 | 1.1182 | 0.0175 | 0.0003 | 3 | 0.8728 | 1.1769 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3931 | 10195.169 | 44265.6724 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.6051 | 0:240:120 | 0:00 | 0.8277 | 7 | 0.0441 | 1.0375 | 1.0816 | 1.0535 | 0.0203 | 0.0004 | 3 | 0.8277 | 1.1099 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3934 | 10201.428 | 44265.6724 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.1372 | 0:240:120 | 0:00 | 0.7856 | 7 | 0.0391 | 0.9804 | 1.0195 | 0.9946 | 0.0184 | 0.0003 | 3 | 0.7856 | 1.048 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3937 | 10207.481 | 44265.6725 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.6999 | 0:240:120 | 0:00 | 0.7462 | 7 | 0.0312 | 0.9282 | 0.9594 | 0.9396 | 0.0147 | 0.0002 | 3 | 0.7462 | 0.9906 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3940 | 10213.568 | 44265.6726 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.2939 | 0:240:120 | 0:00 | 0.7093 | 7 | 0.0349 | 0.8808 | 0.9157 | 0.8938 | 0.0158 | 0.0002 | 3 | 0.7093 | 0.9374 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3943 | 10219.476 | 44265.6726 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 82.9198 | 0:240:120 | 0:00 | 0.6747 | 7 | 0.027 | 0.8351 | 0.8621 | 0.8449 | 0.0123 | 0.0002 | 3 | 0.6747 | 0.8879 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3946 | 10225.001 | 44265.6727 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.5782 | 0:240:120 | 0:00 | 0.6423 | 7 | 0.0255 | 0.7926 | 0.8181 | 0.8018 | 0.012 | 0.0001 | 3 | 0.6423 | 0.8418 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3949 | 10230.357 | 44265.6728 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.2697 | 0:240:120 | 0:00 | 0.6117 | 7 | 0.0267 | 0.7516 | 0.7783 | 0.761 | 0.0125 | 0.0002 | 3 | 0.6117 | 0.7988 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3952 | 10235.721 | 44265.6728 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 87.9951 | 0:240:120 | 0:00 | 0.5829 | 7 | 0.0223 | 0.7157 | 0.738 | 0.7235 | 0.0104 | 0.0001 | 3 | 0.5829 | 0.7586 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3955 | 10240.881 | 44265.6729 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.755 | 0:240:120 | 0:00 | 0.5558 | 7 | 0.0242 | 0.6796 | 0.7038 | 0.6885 | 0.0103 | 0.0001 | 3 | 0.5558 | 0.7209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3958 | 10245.95 | 44265.673 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.5501 | 0:240:120 | 0:00 | 0.5303 | 7 | 0.0201 | 0.6465 | 0.6666 | 0.6538 | 0.0094 | 0.0001 | 3 | 0.5303 | 0.6856 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3961 | 10250.907 | 44265.673 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.3811 | 0:240:120 | 0:00 | 0.5061 | 7 | 0.0167 | 0.6181 | 0.6348 | 0.6242 | 0.0076 | 0.0001 | 3 | 0.5061 | 0.6524 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3964 | 10255.781 | 44265.6731 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.2488 | 0:240:120 | 0:00 | 0.4833 | 7 | 0.021 | 0.5857 | 0.6067 | 0.5941 | 0.0091 | 0.0001 | 3 | 0.4833 | 0.6213 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3967 | 10260.629 | 44265.6731 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 97.1537 | 0:240:120 | 0:00 | 0.4617 | 7 | 0.0187 | 0.5598 | 0.5785 | 0.5671 | 0.008 | 0.0001 | 3 | 0.4617 | 0.592 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3970 | 10265.155 | 44265.6732 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.0968 | 0:240:120 | 0:00 | 0.4413 | 7 | 0.0155 | 0.5346 | 0.5501 | 0.5403 | 0.0071 | 0.0001 | 3 | 0.4413 | 0.5644 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3973 | 10269.886 | 44265.6732 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.0788 | 0:240:120 | 0:00 | 0.4219 | 7 | 0.0146 | 0.5105 | 0.5251 | 0.5159 | 0.0066 | 0 | 3 | 0.4219 | 0.5383 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3976 | 10274.543 | 44265.6733 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 103.1003 | 0:240:120 | 0:00 | 0.4036 | 7 | 0.0139 | 0.4879 | 0.5018 | 0.4929 | 0.0066 | 0 | 3 | 0.4036 | 0.5137 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3979 | 10278.974 | 44265.6733 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 105.1623 | 0:240:120 | 0:00 | 0.3861 | 7 | 0.0113 | 0.4665 | 0.4778 | 0.4705 | 0.0054 | 0 | 3 | 0.3861 | 0.4905 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3982 | 10283.457 | 44265.6734 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.2656 | 0:240:120 | 0:00 | 0.3696 | 7 | 0.0132 | 0.4453 | 0.4585 | 0.4502 | 0.006 | 0 | 3 | 0.3696 | 0.4685 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3985 | 10287.808 | 44265.6734 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.4109 | 0:240:120 | 0:00 | 0.3539 | 7 | 0.013 | 0.4245 | 0.4375 | 0.4297 | 0.0057 | 0 | 3 | 0.3539 | 0.4477 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3988 | 10292.195 | 44265.6735 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 111.5991 | 0:240:120 | 0:00 | 0.339 | 7 | 0.0116 | 0.4072 | 0.4188 | 0.4115 | 0.0052 | 0 | 3 | 0.339 | 0.428 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3991 | 10296.331 | 44265.6735 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.8311 | 0:240:120 | 0:00 | 0.3247 | 7 | 0.0107 | 0.3899 | 0.4006 | 0.3936 | 0.0049 | 0 | 3 | 0.3247 | 0.4093 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3994 | 10300.53 | 44265.6736 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 116.1077 | 0:240:120 | 0:00 | 0.3112 | 7 | 0.0096 | 0.3724 | 0.382 | 0.3761 | 0.0043 | 0 | 3 | 0.3112 | 0.3916 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
3997 | 10304.462 | 44265.6736 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 118.4299 | 0:240:120 | 0:00 | 0.2984 | 7 | 0.0106 | 0.3558 | 0.3664 | 0.36 | 0.0045 | 0 | 3 | 0.2984 | 0.3748 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4000 | 10308.602 | 44265.6737 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.7985 | 0:240:120 | 0:00 | 0.2861 | 7 | 0.0091 | 0.3427 | 0.3518 | 0.3458 | 0.0042 | 0 | 3 | 0.2861 | 0.3588 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4003 | 10312.838 | 44265.6737 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.2144 | 0:240:120 | 0:00 | 0.2744 | 7 | 0.0091 | 0.3263 | 0.3354 | 0.3304 | 0.0039 | 0 | 3 | 0.2744 | 0.3437 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4006 | 10316.936 | 44265.6738 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.6787 | 0:240:120 | 0:00 | 0.2633 | 7 | 0.0099 | 0.313 | 0.3229 | 0.3168 | 0.004 | 0 | 3 | 0.2633 | 0.3292 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4009 | 10321.071 | 44265.6738 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.1923 | 0:240:120 | 0:00 | 0.2527 | 7 | 0.0104 | 0.2997 | 0.3101 | 0.304 | 0.0044 | 0 | 3 | 0.2527 | 0.3155 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4012 | 10325.083 | 44265.6739 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.7561 | 0:240:120 | 0:00 | 0.2425 | 7 | 0.008 | 0.2884 | 0.2964 | 0.2917 | 0.0033 | 0 | 3 | 0.2425 | 0.3024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4015 | 10329.133 | 44265.6739 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.3713 | 0:240:120 | 0:00 | 0.2328 | 7 | 0.008 | 0.2763 | 0.2843 | 0.2795 | 0.0035 | 0 | 3 | 0.2328 | 0.29 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4018 | 10333.149 | 44265.674 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 136.0387 | 0:240:120 | 0:00 | 0.2236 | 7 | 0.008 | 0.2651 | 0.2731 | 0.268 | 0.0034 | 0 | 3 | 0.2236 | 0.2781 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4021 | 10337.375 | 44265.674 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 138.7595 | 0:240:120 | 0:00 | 0.2148 | 7 | 0.0085 | 0.2535 | 0.262 | 0.2567 | 0.0037 | 0 | 3 | 0.2148 | 0.2668 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4024 | 10341.337 | 44265.6741 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.5347 | 0:240:120 | 0:00 | 0.2063 | 7 | 0.0075 | 0.2433 | 0.2508 | 0.2468 | 0.003 | 0 | 3 | 0.2063 | 0.256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4027 | 10345.327 | 44265.6741 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.3654 | 0:240:120 | 0:00 | 0.1983 | 7 | 0.0067 | 0.2353 | 0.242 | 0.2377 | 0.0029 | 0 | 3 | 0.1983 | 0.2457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4030 | 10349.111 | 44265.6741 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 147.2527 | 0:240:120 | 0:00 | 0.1906 | 7 | 0.0062 | 0.2258 | 0.232 | 0.2282 | 0.0025 | 0 | 3 | 0.1906 | 0.2359 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4033 | 10352.888 | 44265.6742 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 150.1977 | 0:240:120 | 0:00 | 0.1832 | 7 | 0.0056 | 0.2171 | 0.2227 | 0.2195 | 0.0023 | 0 | 3 | 0.1832 | 0.2265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4036 | 10356.409 | 44265.6742 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 153.2017 | 0:240:120 | 0:00 | 0.1761 | 7 | 0.0052 | 0.2083 | 0.2135 | 0.2105 | 0.002 | 0 | 3 | 0.1761 | 0.2175 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4039 | 10360.034 | 44265.6743 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 156.2657 | 0:240:120 | 0:00 | 0.1694 | 7 | 0.0048 | 0.2006 | 0.2054 | 0.2023 | 0.002 | 0 | 3 | 0.1694 | 0.209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4042 | 10363.678 | 44265.6743 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 159.391 | 0:240:120 | 0:00 | 0.1629 | 7 | 0.0055 | 0.1915 | 0.197 | 0.1939 | 0.002 | 0 | 3 | 0.1629 | 0.2008 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4045 | 10367.732 | 44265.6744 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 162.5788 | 0:240:120 | 0:00 | 0.1567 | 7 | 0.0052 | 0.1846 | 0.1898 | 0.1867 | 0.002 | 0 | 3 | 0.1567 | 0.193 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4048 | 10371.252 | 44265.6744 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.8304 | 0:240:120 | 0:00 | 0.1508 | 7 | 0.0051 | 0.178 | 0.1831 | 0.1799 | 0.0019 | 0 | 3 | 0.1508 | 0.1855 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4051 | 10374.901 | 44265.6744 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.147 | 0:240:120 | 0:00 | 0.1451 | 7 | 0.0052 | 0.1711 | 0.1763 | 0.1729 | 0.0022 | 0 | 3 | 0.1451 | 0.1783 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4054 | 10378.334 | 44265.6745 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 172.53 | 0:240:120 | 0:00 | 0.1397 | 7 | 0.0035 | 0.165 | 0.1685 | 0.1666 | 0.0013 | 0 | 3 | 0.1397 | 0.1715 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4057 | 10381.947 | 44265.6745 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175.9806 | 0:240:120 | 0:00 | 0.1345 | 7 | 0.0063 | 0.1567 | 0.163 | 0.16 | 0.0023 | 0 | 3 | 0.1345 | 0.1649 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4060 | 10385.579 | 44265.6746 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 179.5002 | 0:240:120 | 0:00 | 0.1295 | 7 | 0.0043 | 0.1516 | 0.1559 | 0.1539 | 0.0017 | 0 | 3 | 0.1295 | 0.1587 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4063 | 10389.165 | 44265.6746 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.0902 | 0:240:120 | 0:00 | 0.1247 | 7 | 0.0053 | 0.1459 | 0.1512 | 0.1482 | 0.0019 | 0 | 3 | 0.1247 | 0.1527 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4066 | 10392.948 | 44265.6747 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 186.752 | 0:240:120 | 0:00 | 0.1201 | 7 | 0.0041 | 0.1408 | 0.1449 | 0.1427 | 0.0016 | 0 | 3 | 0.1201 | 0.1469 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4069 | 10396.481 | 44265.6747 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 190.487 | 0:240:120 | 0:00 | 0.1157 | 7 | 0.0046 | 0.1347 | 0.1393 | 0.137 | 0.0016 | 0 | 3 | 0.1157 | 0.1414 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4072 | 10400.01 | 44265.6747 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 194.2968 | 0:240:120 | 0:00 | 0.1115 | 7 | 0.0041 | 0.1301 | 0.1342 | 0.1323 | 0.0013 | 0 | 3 | 0.1115 | 0.1361 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4075 | 10403.53 | 44265.6748 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 198.1827 | 0:240:120 | 0:00 | 0.1074 | 7 | 0.0028 | 0.1261 | 0.1289 | 0.1275 | 0.0009 | 0 | 3 | 0.1074 | 0.131 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4078 | 10406.94 | 44265.6748 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 202.1463 | 0:240:120 | 0:00 | 0.1035 | 7 | 0.0045 | 0.1203 | 0.1248 | 0.1231 | 0.0017 | 0 | 3 | 0.1035 | 0.1262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4081 | 10410.379 | 44265.6749 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 206.1893 | 0:240:120 | 0:00 | 0.0998 | 7 | 0.0049 | 0.1158 | 0.1207 | 0.1182 | 0.0016 | 0 | 3 | 0.0998 | 0.1215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4084 | 10413.755 | 44265.6749 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 210.3131 | 0:240:120 | 0:00 | 0.0962 | 7 | 0.0042 | 0.1116 | 0.1158 | 0.114 | 0.0018 | 0 | 3 | 0.0962 | 0.1171 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4087 | 10417.151 | 44265.6749 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 214.5193 | 0:240:120 | 0:00 | 0.0928 | 7 | 0.0038 | 0.1075 | 0.1113 | 0.11 | 0.0014 | 0 | 3 | 0.0928 | 0.1128 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4090 | 10420.574 | 44265.675 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 218.8097 | 0:240:120 | 0:00 | 0.0895 | 7 | 0.0033 | 0.1041 | 0.1074 | 0.1061 | 0.0014 | 0 | 3 | 0.0895 | 0.1087 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4093 | 10424 | 44265.675 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.1859 | 0:240:120 | 0:00 | 0.0863 | 7 | 0.0038 | 0.0999 | 0.1037 | 0.1021 | 0.0013 | 0 | 3 | 0.0863 | 0.1048 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4096 | 10427.652 | 44265.6751 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 227.6496 | 0:240:120 | 0:00 | 0.0833 | 7 | 0.0028 | 0.097 | 0.0998 | 0.0982 | 0.001 | 0 | 3 | 0.0833 | 0.101 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4099 | 10431.005 | 44265.6751 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 232.2026 | 0:240:120 | 0:00 | 0.0804 | 7 | 0.0022 | 0.094 | 0.0962 | 0.095 | 0.0009 | 0 | 3 | 0.0804 | 0.0973 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4102 | 10434.416 | 44265.6751 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 236.8467 | 0:240:120 | 0:00 | 0.0776 | 7 | 0.0038 | 0.0894 | 0.0932 | 0.0917 | 0.0013 | 0 | 3 | 0.0776 | 0.0939 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4105 | 10437.906 | 44265.6752 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 241.5836 | 0:240:120 | 0:00 | 0.0749 | 7 | 0.0032 | 0.0872 | 0.0904 | 0.0892 | 0.0012 | 0 | 3 | 0.0749 | 0.0905 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4108 | 10441.302 | 44265.6752 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 246.4153 | 0:240:120 | 0:00 | 0.0723 | 7 | 0.0038 | 0.0836 | 0.0874 | 0.0854 | 0.0014 | 0 | 3 | 0.0723 | 0.0873 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4111 | 10444.884 | 44265.6753 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 251.3436 | 0:240:120 | 0:00 | 0.0698 | 7 | 0.003 | 0.0802 | 0.0832 | 0.0819 | 0.0011 | 0 | 3 | 0.0698 | 0.0842 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4114 | 10448.294 | 44265.6753 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.3704 | 0:240:120 | 0:00 | 0.0674 | 7 | 0.0021 | 0.0779 | 0.08 | 0.0792 | 0.0007 | 0 | 3 | 0.0674 | 0.0813 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4117 | 10451.823 | 44265.6753 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 261.4979 | 0:240:120 | 0:00 | 0.0651 | 7 | 0.0036 | 0.0749 | 0.0785 | 0.077 | 0.0013 | 0 | 3 | 0.0651 | 0.0784 | P | NP | 0-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4120 | 10455.224 | 44265.6754 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 266.7278 | 0:240:120 | 0:00 | 0.0629 | 7 | 0.0031 | 0.0723 | 0.0754 | 0.0741 | 0.0011 | 0 | 3 | 0.0629 | 0.0757 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4123 | 10458.532 | 44265.6754 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 272.0624 | 0:240:120 | 0:00 | 0.0608 | 7 | 0.0029 | 0.0696 | 0.0725 | 0.0712 | 0.0012 | 0 | 3 | 0.0608 | 0.0731 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4126 | 10461.953 | 44265.6755 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 277.5036 | 0:240:120 | 0:00 | 0.0587 | 7 | 0.0024 | 0.0687 | 0.0711 | 0.0699 | 0.0009 | 0 | 3 | 0.0587 | 0.0706 | P | NP | 1-1-0-1-1-0-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4129 | 10465.357 | 44265.6755 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 283.0537 | 0:240:120 | 0:00 | 0.0568 | 7 | 0.0026 | 0.0653 | 0.0679 | 0.0669 | 0.0009 | 0 | 3 | 0.0568 | 0.0682 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4132 | 10468.775 | 44265.6755 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 288.7148 | 0:240:120 | 0:00 | 0.0549 | 7 | 0.0026 | 0.0626 | 0.0652 | 0.0643 | 0.001 | 0 | 3 | 0.0549 | 0.0659 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4135 | 10472.426 | 44265.6756 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.4891 | 0:240:120 | 0:00 | 0.0531 | 7 | 0.0024 | 0.0612 | 0.0636 | 0.0625 | 0.0009 | 0 | 3 | 0.0531 | 0.0637 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4138 | 10475.898 | 44265.6756 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 300.3788 | 0:240:120 | 0:00 | 0.0514 | 7 | 0.0027 | 0.0583 | 0.061 | 0.0599 | 0.0009 | 0 | 3 | 0.0514 | 0.0616 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4141 | 10479.312 | 44265.6757 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 306.3864 | 0:240:120 | 0:00 | 0.0497 | 7 | 0.0027 | 0.0569 | 0.0596 | 0.0584 | 0.0009 | 0 | 3 | 0.0497 | 0.0597 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4144 | 10482.979 | 44265.6757 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 312.5141 | 0:240:120 | 0:00 | 0.0481 | 7 | 0.0027 | 0.0551 | 0.0578 | 0.0566 | 0.001 | 0 | 3 | 0.0481 | 0.0581 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4147 | 10486.355 | 44265.6757 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 318.7644 | 0:240:120 | 0:00 | 0.0465 | 7 | 0.0037 | 0.0523 | 0.056 | 0.0545 | 0.0014 | 0 | 3 | 0.0465 | 0.0565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4150 | 10489.898 | 44265.6758 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 325.1397 | 0:240:120 | 0:00 | 0.045 | 7 | 0.0031 | 0.0511 | 0.0542 | 0.0529 | 0.001 | 0 | 3 | 0.045 | 0.055 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4153 | 10493.181 | 44265.6758 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 331.6425 | 0:240:120 | 0:00 | 0.0436 | 7 | 0.0033 | 0.0489 | 0.0522 | 0.0506 | 0.0013 | 0 | 3 | 0.0436 | 0.0536 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4156 | 10496.33 | 44265.6759 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 338.2754 | 0:240:120 | 0:00 | 0.0422 | 7 | 0.0038 | 0.0476 | 0.0514 | 0.0497 | 0.0013 | 0 | 3 | 0.0422 | 0.0522 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4159 | 10499.801 | 44265.6759 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 345.0409 | 0:240:120 | 0:00 | 0.0409 | 7 | 0.004 | 0.0455 | 0.0495 | 0.0478 | 0.0014 | 0 | 3 | 0.0409 | 0.0509 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4162 | 10503.455 | 44265.6759 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 351.9417 | 0:240:120 | 0:00 | 0.0396 | 7 | 0.003 | 0.0447 | 0.0477 | 0.0467 | 0.001 | 0 | 3 | 0.0396 | 0.0496 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4165 | 10506.763 | 44265.676 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 358.9805 | 0:240:120 | 0:00 | 0.0384 | 7 | 0.0029 | 0.043 | 0.0459 | 0.0449 | 0.0011 | 0 | 3 | 0.0384 | 0.0484 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4168 | 10510.084 | 44265.676 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 366.1601 | 0:240:120 | 0:00 | 0.0372 | 7 | 0.0018 | 0.0434 | 0.0452 | 0.0443 | 0.0006 | 0 | 3 | 0.0372 | 0.0472 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4171 | 10513.332 | 44265.676 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 373.4833 | 0:240:120 | 0:00 | 0.0361 | 7 | 0.0029 | 0.0402 | 0.0431 | 0.0421 | 0.0011 | 0 | 3 | 0.0361 | 0.0461 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4174 | 10516.604 | 44265.6761 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 380.953 | 0:240:120 | 0:00 | 0.035 | 7 | 0.0022 | 0.0395 | 0.0417 | 0.0408 | 0.0008 | 0 | 3 | 0.035 | 0.045 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4177 | 10519.783 | 44265.6761 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 388.5721 | 0:240:120 | 0:00 | 0.034 | 7 | 0.003 | 0.0378 | 0.0408 | 0.0397 | 0.0012 | 0 | 3 | 0.034 | 0.044 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4180 | 10522.986 | 44265.6762 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 396.3435 | 0:240:120 | 0:00 | 0.033 | 7 | 0.0032 | 0.0365 | 0.0397 | 0.0385 | 0.0012 | 0 | 3 | 0.033 | 0.043 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4183 | 10526.281 | 44265.6762 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 404.2704 | 0:240:120 | 0:00 | 0.032 | 7 | 0.0024 | 0.0361 | 0.0385 | 0.0374 | 0.0009 | 0 | 3 | 0.032 | 0.042 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4186 | 10529.568 | 44265.6762 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 412.3558 | 0:240:120 | 0:00 | 0.0311 | 7 | 0.0024 | 0.0353 | 0.0377 | 0.0367 | 0.001 | 0 | 3 | 0.0311 | 0.0411 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4189 | 10532.778 | 44265.6763 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 420.6029 | 0:240:120 | 0:00 | 0.0302 | 7 | 0.0029 | 0.0337 | 0.0366 | 0.0355 | 0.0011 | 0 | 3 | 0.0302 | 0.0402 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4192 | 10536.168 | 44265.6763 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 429.015 | 0:240:120 | 0:00 | 0.0293 | 7 | 0.004 | 0.0323 | 0.0363 | 0.0345 | 0.0013 | 0 | 3 | 0.0293 | 0.0393 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4195 | 10539.427 | 44265.6763 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 437.5953 | 0:240:120 | 0:00 | 0.0285 | 7 | 0.0023 | 0.0321 | 0.0344 | 0.0332 | 0.0007 | 0 | 3 | 0.0285 | 0.0385 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4198 | 10542.728 | 44265.6764 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 446.3472 | 0:240:120 | 0:00 | 0.0277 | 7 | 0.0035 | 0.0306 | 0.0341 | 0.0328 | 0.0013 | 0 | 3 | 0.0277 | 0.0377 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4201 | 10546.324 | 44265.6764 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 455.2741 | 0:240:120 | 0:00 | 0.0269 | 7 | 0.0024 | 0.0304 | 0.0328 | 0.032 | 0.001 | 0 | 3 | 0.0269 | 0.0369 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4204 | 10549.612 | 44265.6765 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 464.3796 | 0:240:120 | 0:00 | 0.0261 | 7 | 0.0027 | 0.0292 | 0.0319 | 0.0307 | 0.001 | 0 | 3 | 0.0261 | 0.0361 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4207 | 10552.896 | 44265.6765 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 473.6672 | 0:240:120 | 0:00 | 0.0254 | 7 | 0.0031 | 0.0281 | 0.0312 | 0.0299 | 0.0012 | 0 | 3 | 0.0254 | 0.0354 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4210 | 10556.345 | 44265.6765 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 483.1405 | 0:240:120 | 0:00 | 0.0247 | 7 | 0.0022 | 0.0278 | 0.03 | 0.0292 | 0.0008 | 0 | 3 | 0.0247 | 0.0347 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4213 | 10559.381 | 44265.6766 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 492.8033 | 0:240:120 | 0:00 | 0.0241 | 7 | 0.0022 | 0.0273 | 0.0295 | 0.0283 | 0.0008 | 0 | 3 | 0.0241 | 0.0341 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4216 | 10562.605 | 44265.6766 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 502.6594 | 0:240:120 | 0:00 | 0.0234 | 7 | 0.0027 | 0.0262 | 0.0289 | 0.0277 | 0.001 | 0 | 3 | 0.0234 | 0.0334 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4219 | 10565.922 | 44265.6767 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 512.7126 | 0:240:120 | 0:00 | 0.0228 | 7 | 0.0036 | 0.0252 | 0.0288 | 0.027 | 0.0013 | 0 | 3 | 0.0228 | 0.0328 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4222 | 10568.934 | 44265.6767 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 522.9668 | 0:240:120 | 0:00 | 0.0222 | 7 | 0.0032 | 0.0247 | 0.0279 | 0.0266 | 0.0012 | 0 | 3 | 0.0222 | 0.0322 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4225 | 10572.19 | 44265.6767 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 533.4262 | 0:240:120 | 0:00 | 0.0217 | 7 | 0.0027 | 0.0241 | 0.0268 | 0.0256 | 0.001 | 0 | 3 | 0.0217 | 0.0317 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4228 | 10575.724 | 44265.6768 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 544.0947 | 0:240:120 | 0:00 | 0.0211 | 7 | 0.0029 | 0.0236 | 0.0265 | 0.025 | 0.001 | 0 | 3 | 0.0211 | 0.0311 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4231 | 10578.924 | 44265.6768 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 554.9766 | 0:240:120 | 0:00 | 0.0206 | 7 | 0.0022 | 0.0235 | 0.0257 | 0.0246 | 0.0008 | 0 | 3 | 0.0206 | 0.0306 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4234 | 10582.147 | 44265.6768 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 566.0761 | 0:240:120 | 0:00 | 0.0201 | 7 | 0.0028 | 0.0229 | 0.0257 | 0.0243 | 0.0011 | 0 | 3 | 0.0201 | 0.0301 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4237 | 10585.403 | 44265.6769 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 577.3976 | 0:240:120 | 0:00 | 0.0196 | 7 | 0.0031 | 0.0219 | 0.025 | 0.0234 | 0.001 | 0 | 3 | 0.0196 | 0.0296 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4240 | 10588.505 | 44265.6769 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 588.9456 | 0:240:120 | 0:00 | 0.0191 | 7 | 0.0027 | 0.0219 | 0.0246 | 0.0232 | 0.0009 | 0 | 3 | 0.0191 | 0.0291 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4243 | 10591.627 | 44265.677 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 600.7245 | 0:240:120 | 0:00 | 0.0187 | 7 | 0.0028 | 0.0203 | 0.0231 | 0.0222 | 0.0013 | 0 | 3 | 0.0187 | 0.0287 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4246 | 10594.818 | 44265.677 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 612.739 | 0:240:120 | 0:00 | 0.0183 | 7 | 0.0036 | 0.02 | 0.0236 | 0.0223 | 0.0014 | 0 | 3 | 0.0183 | 0.0283 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4249 | 10597.924 | 44265.677 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 624.9938 | 0:240:120 | 0:00 | 0.0178 | 7 | 0.0034 | 0.0195 | 0.0229 | 0.0217 | 0.0012 | 0 | 3 | 0.0178 | 0.0278 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4252 | 10601.121 | 44265.6771 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 637.4937 | 0:240:120 | 0:00 | 0.0174 | 7 | 0.0036 | 0.0195 | 0.0231 | 0.0215 | 0.0013 | 0 | 3 | 0.0174 | 0.0274 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4255 | 10604.31 | 44265.6771 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 650.2435 | 0:240:120 | 0:00 | 0.0171 | 7 | 0.0036 | 0.0189 | 0.0225 | 0.021 | 0.0013 | 0 | 3 | 0.0171 | 0.0271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4258 | 10607.515 | 44265.6771 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 663.2484 | 0:240:120 | 0:00 | 0.0167 | 7 | 0.0033 | 0.019 | 0.0223 | 0.0208 | 0.001 | 0 | 3 | 0.0167 | 0.0267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4261 | 10610.613 | 44265.6772 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 676.5134 | 0:240:120 | 0:00 | 0.0163 | 7 | 0.0026 | 0.0191 | 0.0217 | 0.0205 | 0.001 | 0 | 3 | 0.0163 | 0.0263 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4264 | 10614.126 | 44265.6772 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 690.0436 | 0:240:120 | 0:00 | 0.016 | 7 | 0.0033 | 0.0183 | 0.0216 | 0.0199 | 0.0011 | 0 | 3 | 0.016 | 0.026 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4267 | 10617.394 | 44265.6773 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 703.8445 | 0:240:120 | 0:00 | 0.0156 | 7 | 0.0024 | 0.0184 | 0.0208 | 0.0197 | 0.0008 | 0 | 3 | 0.0156 | 0.0256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4270 | 10620.481 | 44265.6773 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 717.9214 | 0:240:120 | 0:00 | 0.0153 | 7 | 0.0028 | 0.018 | 0.0208 | 0.0194 | 0.0011 | 0 | 3 | 0.0153 | 0.0253 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4273 | 10624.211 | 44265.6773 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 732.2798 | 0:240:120 | 0:00 | 0.015 | 7 | 0.0026 | 0.0177 | 0.0203 | 0.0188 | 0.001 | 0 | 3 | 0.015 | 0.025 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4276 | 10627.435 | 44265.6774 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 746.9254 | 0:240:120 | 0:00 | 0.0147 | 7 | 0.0016 | 0.0174 | 0.019 | 0.0182 | 0.0006 | 0 | 3 | 0.0147 | 0.0247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4279 | 10630.749 | 44265.6774 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 761.8639 | 0:240:120 | 0:00 | 0.0144 | 7 | 0.0013 | 0.0174 | 0.0187 | 0.018 | 0.0004 | 0 | 3 | 0.0144 | 0.0244 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4282 | 10634.461 | 44265.6774 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 777.1012 | 0:240:120 | 0:00 | 0.0142 | 7 | 0.0015 | 0.0169 | 0.0184 | 0.0178 | 0.0006 | 0 | 3 | 0.0142 | 0.0242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4285 | 10637.635 | 44265.6775 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 792.6432 | 0:240:120 | 0:00 | 0.0139 | 7 | 0.0016 | 0.0165 | 0.0181 | 0.0176 | 0.0005 | 0 | 3 | 0.0139 | 0.0239 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4288 | 10640.849 | 44265.6775 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 808.4961 | 0:240:120 | 0:00 | 0.0136 | 7 | 0.0016 | 0.0162 | 0.0178 | 0.017 | 0.0007 | 0 | 3 | 0.0136 | 0.0236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4291 | 10644.335 | 44265.6776 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 824.666 | 0:240:120 | 0:00 | 0.0134 | 7 | 0.0024 | 0.0162 | 0.0186 | 0.0171 | 0.0007 | 0 | 3 | 0.0134 | 0.0234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4294 | 10647.536 | 44265.6776 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 841.1593 | 0:240:120 | 0:00 | 0.0132 | 7 | 0.0021 | 0.0154 | 0.0175 | 0.0163 | 0.0007 | 0 | 3 | 0.0132 | 0.0232 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4297 | 10651.043 | 44265.6776 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 857.9825 | 0:240:120 | 0:00 | 0.0129 | 7 | 0.0032 | 0.0145 | 0.0177 | 0.0161 | 0.0011 | 0 | 3 | 0.0129 | 0.0229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4300 | 10654.127 | 44265.6777 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 875.1422 | 0:240:120 | 0:00 | 0.0127 | 7 | 0.0033 | 0.0144 | 0.0177 | 0.016 | 0.0011 | 0 | 3 | 0.0127 | 0.0227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4303 | 10657.293 | 44265.6777 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 892.645 | 0:240:120 | 0:00 | 0.0125 | 7 | 0.0035 | 0.0138 | 0.0173 | 0.0157 | 0.0013 | 0 | 3 | 0.0125 | 0.0225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4306 | 10660.569 | 44265.6778 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 910.4979 | 0:240:120 | 0:00 | 0.0123 | 7 | 0.0041 | 0.0131 | 0.0172 | 0.0153 | 0.0015 | 0 | 3 | 0.0123 | 0.0223 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4309 | 10663.877 | 44265.6778 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 928.7079 | 0:240:120 | 0:00 | 0.0121 | 7 | 0.0033 | 0.0137 | 0.017 | 0.0153 | 0.0012 | 0 | 3 | 0.0121 | 0.0221 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4312 | 10667.146 | 44265.6778 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 947.282 | 0:240:120 | 0:00 | 0.0119 | 7 | 0.0034 | 0.0136 | 0.017 | 0.015 | 0.0012 | 0 | 3 | 0.0119 | 0.0219 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4315 | 10670.251 | 44265.6779 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 966.2277 | 0:240:120 | 0:00 | 0.0117 | 7 | 0.0034 | 0.0129 | 0.0163 | 0.0145 | 0.0013 | 0 | 3 | 0.0117 | 0.0217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4318 | 10673.511 | 44265.6779 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 985.5522 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0041 | 0.0126 | 0.0167 | 0.0145 | 0.0016 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4321 | 10677.116 | 44265.6779 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1005.2633 | 0:240:120 | 0:00 | 0.0114 | 7 | 0.005 | 0.0118 | 0.0168 | 0.0143 | 0.0018 | 0 | 3 | 0.0114 | 0.0214 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4324 | 10680.598 | 44265.678 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1025.3685 | 0:240:120 | 0:00 | 0.0112 | 7 | 0.0043 | 0.0125 | 0.0168 | 0.0145 | 0.0017 | 0 | 3 | 0.0112 | 0.0212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4327 | 10683.791 | 44265.678 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1045.8759 | 0:240:120 | 0:00 | 0.0111 | 7 | 0.0041 | 0.0121 | 0.0162 | 0.014 | 0.0016 | 0 | 3 | 0.0111 | 0.0211 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4330 | 10687.018 | 44265.6781 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1066.7934 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0046 | 0.0114 | 0.016 | 0.014 | 0.0018 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4333 | 10690.173 | 44265.6781 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1088.1293 | 0:240:120 | 0:00 | 0.0108 | 7 | 0.0046 | 0.0114 | 0.016 | 0.0139 | 0.0017 | 0 | 3 | 0.0108 | 0.0208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4336 | 10693.278 | 44265.6781 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1109.8919 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0052 | 0.0115 | 0.0167 | 0.0138 | 0.0018 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4339 | 10696.699 | 44265.6782 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1132.0897 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0043 | 0.0116 | 0.0159 | 0.014 | 0.0018 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4342 | 10699.898 | 44265.6782 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1154.7315 | 0:240:120 | 0:00 | 0.0104 | 7 | 0.0052 | 0.0112 | 0.0164 | 0.0137 | 0.0018 | 0 | 3 | 0.0104 | 0.0204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4345 | 10703.378 | 44265.6782 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1177.8261 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.0052 | 0.011 | 0.0162 | 0.0136 | 0.0019 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4348 | 10706.786 | 44265.6783 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1201.3827 | 0:240:120 | 0:00 | 0.0101 | 7 | 0.0042 | 0.0108 | 0.015 | 0.0135 | 0.0014 | 0 | 3 | 0.0101 | 0.0201 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4351 | 10710.21 | 44265.6783 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1225.4103 | 0:240:120 | 0:00 | 0.01 | 7 | 0.004 | 0.0113 | 0.0153 | 0.0134 | 0.0016 | 0 | 3 | 0.01 | 0.02 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4354 | 10713.51 | 44265.6784 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1226.5079 | 0:240:120 | 0:00 | 0.01 | 7 | 0.0044 | 0.0113 | 0.0157 | 0.0136 | 0.0016 | 0 | 3 | 0.01 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4357 | 10717.009 | 44265.6784 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1251.0381 | 0:240:120 | 0:00 | 0.0099 | 7 | 0.0046 | 0.0108 | 0.0154 | 0.0133 | 0.0017 | 0 | 3 | 0.0099 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4360 | 10720.235 | 44265.6784 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1276.0588 | 0:240:120 | 0:00 | 0.0098 | 7 | 0.0047 | 0.0105 | 0.0152 | 0.0132 | 0.0017 | 0 | 3 | 0.0098 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4363 | 10723.315 | 44265.6785 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1301.58 | 0:240:120 | 0:00 | 0.0097 | 7 | 0.0041 | 0.0111 | 0.0152 | 0.0134 | 0.0018 | 0 | 3 | 0.0097 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4366 | 10726.56 | 44265.6785 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1327.6116 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0038 | 0.0104 | 0.0142 | 0.0128 | 0.0012 | 0 | 3 | 0.0096 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4369 | 10730.027 | 44265.6786 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1354.1638 | 0:240:120 | 0:00 | 0.0095 | 7 | 0.0033 | 0.0104 | 0.0137 | 0.0124 | 0.0014 | 0 | 3 | 0.0095 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4372 | 10733.116 | 44265.6786 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1381.2471 | 0:240:120 | 0:00 | 0.0094 | 7 | 0.0037 | 0.0108 | 0.0145 | 0.0126 | 0.0015 | 0 | 3 | 0.0094 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4375 | 10736.231 | 44265.6786 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1408.8721 | 0:240:120 | 0:00 | 0.0093 | 7 | 0.0026 | 0.0103 | 0.0129 | 0.012 | 0.0009 | 0 | 3 | 0.0093 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4378 | 10739.646 | 44265.6787 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1437.0495 | 0:240:120 | 0:00 | 0.0092 | 7 | 0.003 | 0.0112 | 0.0142 | 0.0126 | 0.0012 | 0 | 3 | 0.0092 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4381 | 10743.084 | 44265.6787 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1465.7905 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.0041 | 0.0109 | 0.015 | 0.0124 | 0.0014 | 0 | 3 | 0.0091 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4384 | 10746.177 | 44265.6787 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1495.1063 | 0:240:120 | 0:00 | 0.0091 | 7 | 0.0038 | 0.0105 | 0.0143 | 0.0117 | 0.0013 | 0 | 3 | 0.0091 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4387 | 10749.394 | 44265.6788 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1525.0084 | 0:240:120 | 0:00 | 0.009 | 7 | 0.0034 | 0.0102 | 0.0136 | 0.0115 | 0.0012 | 0 | 3 | 0.009 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4390 | 10752.681 | 44265.6788 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1555.5086 | 0:240:120 | 0:00 | 0.0089 | 7 | 0.0052 | 0.0099 | 0.0151 | 0.0122 | 0.0018 | 0 | 3 | 0.0089 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4393 | 10755.881 | 44265.6789 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1586.6188 | 0:240:120 | 0:00 | 0.0088 | 7 | 0.0052 | 0.0098 | 0.015 | 0.0117 | 0.0015 | 0 | 3 | 0.0088 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4396 | 10759.05 | 44265.6789 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1618.3512 | 0:240:120 | 0:00 | 0.0088 | 7 | 0.0049 | 0.0096 | 0.0145 | 0.0116 | 0.0016 | 0 | 3 | 0.0088 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4399 | 10762.359 | 44265.6789 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1650.7182 | 0:240:120 | 0:00 | 0.0087 | 7 | 0.0046 | 0.0096 | 0.0142 | 0.0113 | 0.0014 | 0 | 3 | 0.0087 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4402 | 10765.552 | 44265.679 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1683.7325 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0053 | 0.0097 | 0.015 | 0.0116 | 0.0017 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4405 | 10768.947 | 44265.679 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1717.4072 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0032 | 0.0095 | 0.0127 | 0.0107 | 0.0012 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4408 | 10772.029 | 44265.679 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1751.7553 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0029 | 0.0095 | 0.0124 | 0.0106 | 0.0013 | 0 | 3 | 0.0085 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4411 | 10775.139 | 44265.6791 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1786.7904 | 0:240:120 | 0:00 | 0.0085 | 7 | 0.0041 | 0.0093 | 0.0134 | 0.011 | 0.0015 | 0 | 3 | 0.0085 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4414 | 10778.461 | 44265.6791 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1822.5262 | 0:240:120 | 0:00 | 0.0084 | 7 | 0.0041 | 0.0094 | 0.0135 | 0.0111 | 0.0014 | 0 | 3 | 0.0084 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4417 | 10781.865 | 44265.6792 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1858.9768 | 0:240:120 | 0:00 | 0.0084 | 7 | 0.0036 | 0.0094 | 0.013 | 0.0107 | 0.0012 | 0 | 3 | 0.0084 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4420 | 10784.954 | 44265.6792 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1896.1563 | 0:240:120 | 0:00 | 0.0083 | 7 | 0.0042 | 0.009 | 0.0132 | 0.0108 | 0.0013 | 0 | 3 | 0.0083 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4423 | 10788.137 | 44265.6792 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1934.0794 | 0:240:120 | 0:00 | 0.0083 | 7 | 0.0016 | 0.0103 | 0.0119 | 0.0109 | 0.0007 | 0 | 3 | 0.0083 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4426 | 10791.652 | 44265.6793 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1972.761 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0027 | 0.0096 | 0.0123 | 0.0109 | 0.0008 | 0 | 3 | 0.0082 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4429 | 10794.872 | 44265.6793 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2012.2162 | 0:240:120 | 0:00 | 0.0082 | 7 | 0.0053 | 0.0092 | 0.0145 | 0.0111 | 0.0015 | 0 | 3 | 0.0082 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4432 | 10798.064 | 44265.6793 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2052.4606 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0026 | 0.0096 | 0.0122 | 0.0103 | 0.0009 | 0 | 3 | 0.0081 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4435 | 10801.269 | 44265.6794 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2093.5098 | 0:240:120 | 0:00 | 0.0081 | 7 | 0.0016 | 0.0099 | 0.0115 | 0.0107 | 0.0005 | 0 | 3 | 0.0081 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4438 | 10804.476 | 44265.6794 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2135.38 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0103 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4441 | 10807.549 | 44265.6795 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2178.0876 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0013 | 0.01 | 0.0113 | 0.0103 | 0.0005 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4444 | 10810.769 | 44265.6795 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2221.6493 | 0:240:120 | 0:00 | 0.008 | 7 | 0.0062 | 0.0089 | 0.0151 | 0.0105 | 0.0019 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4447 | 10813.963 | 44265.6795 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2266.0823 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0052 | 0.0099 | 0.0151 | 0.011 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4450 | 10817.241 | 44265.6796 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2311.404 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.002 | 0.0091 | 0.0111 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4453 | 10820.305 | 44265.6796 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2357.632 | 0:240:120 | 0:00 | 0.0079 | 7 | 0.0052 | 0.0099 | 0.0151 | 0.0108 | 0.0016 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4456 | 10823.578 | 44265.6796 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2404.7847 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0019 | 0.0096 | 0.0115 | 0.0102 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4459 | 10827.257 | 44265.6797 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2452.8804 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0019 | 0.0095 | 0.0114 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4462 | 10830.537 | 44265.6797 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2453.0158 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0017 | 0.0096 | 0.0113 | 0.0104 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4465 | 10833.946 | 44265.6798 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2502.0762 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0013 | 0.0103 | 0.0116 | 0.0106 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4468 | 10837.238 | 44265.6798 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2552.1177 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4471 | 10840.449 | 44265.6798 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2603.16 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0062 | 0.0089 | 0.0151 | 0.0106 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4474 | 10843.541 | 44265.6799 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2655.2232 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0003 | 0.0104 | 0.0107 | 0.0106 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4477 | 10846.645 | 44265.6799 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2708.3277 | 0:240:120 | 0:00 | 0.0077 | 7 | 0.0018 | 0.0095 | 0.0113 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4480 | 10849.911 | 44265.6799 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2762.4943 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0016 | 0.0091 | 0.0107 | 0.0097 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4483 | 10853.113 | 44265.68 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2817.7441 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0009 | 0.01 | 0.0109 | 0.0103 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4486 | 10856.304 | 44265.68 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2874.099 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0025 | 0.009 | 0.0115 | 0.0103 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4489 | 10859.452 | 44265.6801 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2931.581 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0013 | 0.0094 | 0.0107 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4492 | 10862.737 | 44265.6801 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2990.2126 | 0:240:120 | 0:00 | 0.0076 | 7 | 0.0024 | 0.0091 | 0.0115 | 0.0103 | 0.0009 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4495 | 10865.908 | 44265.6801 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3050.0169 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0018 | 0.009 | 0.0108 | 0.01 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4498 | 10869.099 | 44265.6802 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3111.0172 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0018 | 0.0095 | 0.0113 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4501 | 10872.507 | 44265.6802 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3173.2376 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0016 | 0.0095 | 0.0111 | 0.0099 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4504 | 10875.612 | 44265.6802 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3236.7023 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0022 | 0.0091 | 0.0113 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4507 | 10878.821 | 44265.6803 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3301.4364 | 0:240:120 | 0:00 | 0.0075 | 7 | 0.0011 | 0.0092 | 0.0103 | 0.0097 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4510 | 10881.912 | 44265.6803 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3367.4651 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0013 | 0.01 | 0.0113 | 0.0105 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4513 | 10885.095 | 44265.6804 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3434.8144 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0018 | 0.0089 | 0.0107 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4516 | 10888.357 | 44265.6804 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3503.5107 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0056 | 0.0095 | 0.0151 | 0.0105 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4519 | 10891.841 | 44265.6804 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3573.5809 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0013 | 0.0097 | 0.011 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4522 | 10895.061 | 44265.6805 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3645.0525 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0005 | 0.0103 | 0.0108 | 0.0106 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4525 | 10898.169 | 44265.6805 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3717.9535 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0017 | 0.0093 | 0.011 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4528 | 10901.506 | 44265.6805 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3792.3126 | 0:240:120 | 0:00 | 0.0074 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.0102 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4531 | 10904.961 | 44265.6806 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3868.1589 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0017 | 0.0089 | 0.0106 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4534 | 10908.057 | 44265.6806 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3945.5221 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4537 | 10911.329 | 44265.6807 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4024.4325 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0058 | 0.0091 | 0.0149 | 0.0104 | 0.0018 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4540 | 10914.615 | 44265.6807 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4104.9211 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0054 | 0.0096 | 0.015 | 0.0107 | 0.0017 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4543 | 10917.794 | 44265.6807 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4187.0196 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0017 | 0.0098 | 0.0115 | 0.0104 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4546 | 10920.982 | 44265.6808 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4270.76 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0002 | 0.0098 | 0.01 | 0.0099 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4549 | 10924.176 | 44265.6808 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4356.1752 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0012 | 0.0091 | 0.0103 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4552 | 10927.455 | 44265.6808 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4443.2987 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0014 | 0.0091 | 0.0105 | 0.0099 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4555 | 10930.545 | 44265.6809 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4532.1646 | 0:240:120 | 0:00 | 0.0073 | 7 | 0.0047 | 0.0095 | 0.0142 | 0.0106 | 0.0014 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4558 | 10933.733 | 44265.6809 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4622.8079 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0105 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4561 | 10936.861 | 44265.6809 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4715.2641 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0101 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4564 | 10940.032 | 44265.681 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4809.5694 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0014 | 0.0092 | 0.0106 | 0.0101 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4567 | 10943.32 | 44265.681 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4905.7608 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.006 | 0.009 | 0.015 | 0.011 | 0.0022 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-0-1-1-1-1-1-0 | NP | 0-0-0-0-0-0-0-0-0
4570 | 10946.479 | 44265.6811 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5003.876 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0016 | 0.0092 | 0.0108 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4573 | 10949.582 | 44265.6811 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5103.9535 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.005 | 0.009 | 0.014 | 0.0102 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4576 | 10952.991 | 44265.6811 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5206.0326 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0013 | 0.009 | 0.0103 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4579 | 10956.186 | 44265.6812 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5310.1532 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0016 | 0.0098 | 0.0114 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4582 | 10959.379 | 44265.6812 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5416.3563 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0022 | 0.009 | 0.0112 | 0.0101 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4585 | 10962.565 | 44265.6812 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5524.6834 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0021 | 0.009 | 0.0111 | 0.0099 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4588 | 10965.755 | 44265.6813 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5635.1771 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.001 | 0.0099 | 0.0109 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4591 | 10968.925 | 44265.6813 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5747.8806 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0014 | 0.0091 | 0.0105 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4594 | 10972.036 | 44265.6814 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5862.8382 | 0:240:120 | 0:00 | 0.0072 | 7 | 0.0016 | 0.0094 | 0.011 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4597 | 10975.322 | 44265.6814 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5980.095 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0099 | 0.011 | 0.0105 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4600 | 10978.545 | 44265.6814 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6099.6969 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0018 | 0.0089 | 0.0107 | 0.0095 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4603 | 10981.631 | 44265.6815 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6221.6908 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0014 | 0.0088 | 0.0102 | 0.0094 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4606 | 10984.716 | 44265.6815 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6346.1246 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0019 | 0.0092 | 0.0111 | 0.01 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4609 | 10987.903 | 44265.6815 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6473.0471 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0005 | 0.0102 | 0.0107 | 0.0105 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4612 | 10991.008 | 44265.6816 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6602.5081 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0097 | 0.0108 | 0.0104 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4615 | 10994.292 | 44265.6816 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6734.5582 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0097 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4618 | 10997.478 | 44265.6817 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6869.2494 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0014 | 0.0091 | 0.0105 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4621 | 11000.68 | 44265.6817 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7006.6344 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0019 | 0.0093 | 0.0112 | 0.01 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4624 | 11003.948 | 44265.6817 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7146.7671 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0093 | 0.0106 | 0.01 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4627 | 11007.364 | 44265.6818 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7289.7024 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0006 | 0.0099 | 0.0105 | 0.0102 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4630 | 11010.703 | 44265.6818 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7435.4965 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0022 | 0.0088 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4633 | 11013.807 | 44265.6818 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7584.2064 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0014 | 0.009 | 0.0104 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4636 | 11016.904 | 44265.6819 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7735.8905 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0015 | 0.0096 | 0.0111 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4639 | 11020.101 | 44265.6819 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7890.6083 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0004 | 0.0096 | 0.01 | 0.0099 | 0.0002 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4642 | 11023.293 | 44265.6819 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8048.4205 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0003 | 0.0105 | 0.0108 | 0.0106 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4645 | 11026.398 | 44265.682 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8209.3889 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0021 | 0.0089 | 0.011 | 0.0098 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4648 | 11029.813 | 44265.682 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8373.5767 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0017 | 0.009 | 0.0107 | 0.0098 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4651 | 11033.004 | 44265.6821 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8541.0482 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0006 | 0.01 | 0.0106 | 0.0104 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4654 | 11036.183 | 44265.6821 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8711.8692 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0096 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4657 | 11039.502 | 44265.6821 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8886.1066 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0013 | 0.0089 | 0.0102 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4660 | 11042.675 | 44265.6822 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9063.8287 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0006 | 0.0095 | 0.0101 | 0.0098 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4663 | 11045.899 | 44265.6822 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9245.1053 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0015 | 0.0091 | 0.0106 | 0.0096 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4666 | 11048.973 | 44265.6822 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9430.0074 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.001 | 0.0097 | 0.0107 | 0.0101 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4669 | 11052.283 | 44265.6823 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9618.6075 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0102 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4672 | 11055.473 | 44265.6823 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9810.9797 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0003 | 0.0094 | 0.0097 | 0.0096 | 0.0001 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4675 | 11058.781 | 44265.6824 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10007.1993 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0015 | 0.0092 | 0.0107 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4678 | 11061.951 | 44265.6824 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10207.3432 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0088 | 0.0099 | 0.0094 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4681 | 11065.071 | 44265.6824 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10411.4901 | 0:240:120 | 0:00 | 0.0071 | 7 | 0.0011 | 0.0098 | 0.0109 | 0.0101 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4684 | 11068.458 | 44265.6825 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10619.7199 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0012 | 0.0094 | 0.0106 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4687 | 11071.908 | 44265.6825 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10832.1143 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0008 | 0.0095 | 0.0103 | 0.0099 | 0.0003 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4690 | 11075.197 | 44265.6826 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11048.7566 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0016 | 0.0093 | 0.0109 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4693 | 11078.632 | 44265.6826 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11269.7317 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0019 | 0.0089 | 0.0108 | 0.0102 | 0.0008 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4696 | 11082.271 | 44265.6826 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11495.1264 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0013 | 0.0091 | 0.0104 | 0.0097 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4699 | 11085.334 | 44265.6827 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11725.0289 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0017 | 0.0093 | 0.011 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4702 | 11088.504 | 44265.6827 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11959.5295 | 0:240:120 | 0:00 | 0.007 | 7 | 0.0018 | 0.0088 | 0.0106 | 0.0098 | 0.0007 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4705 | 11144.401 | 44265.6834 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 46.2 | 0:240:120 | 0:00 | 6.3574 | 7 | 17.6233 | 38.4814 | 56.1047 | 43.9232 | 8.0676 | 65.0855 | 3 | 6.3574 | 26.1911 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4708 | 11290.831 | 44265.685 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 47.2 | 0:240:120 | 0:00 | 5.4191 | 7 | 13.9969 | 18.9234 | 32.9203 | 23.8418 | 6.6459 | 44.1678 | 3 | 5.4191 | 16.525 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4711 | 11371.305 | 44265.686 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 48.1 | 0:240:120 | 0:00 | 4.7736 | 7 | 2.9185 | 9.5509 | 12.4694 | 10.4237 | 1.318 | 1.7371 | 3 | 4.7736 | 12.3494 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4714 | 11408.268 | 44265.6864 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 49.1 | 0:240:120 | 0:00 | 4.207 | 7 | 0.7499 | 8.2973 | 9.0472 | 8.6145 | 0.3317 | 0.11 | 3 | 4.207 | 9.6051 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4717 | 11437.329 | 44265.6867 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 50 | 0:240:120 | 0:00 | 3.7947 | 7 | 0.7892 | 7.2041 | 7.9933 | 7.5151 | 0.3609 | 0.1302 | 3 | 3.7947 | 7.9813 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4720 | 11463.49 | 44265.687 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 51 | 0:240:120 | 0:00 | 3.4164 | 7 | 1.037 | 5.902 | 6.939 | 6.2744 | 0.4973 | 0.2473 | 3 | 3.4164 | 6.7013 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4723 | 11486.061 | 44265.6873 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 52.1 | 0:240:120 | 0:00 | 3.0733 | 7 | 0.6488 | 4.8251 | 5.4739 | 5.0441 | 0.3159 | 0.0998 | 3 | 3.0733 | 5.6807 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4726 | 11505.095 | 44265.6875 | Vista Coord | Tap | 40Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 53.1 | 0:240:120 | 0:00 | 2.8119 | 7 | 0.301 | 4.371 | 4.672 | 4.5018 | 0.1291 | 0.0167 | 3 | 2.8119 | 4.979 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4729 | 11623.955 | 44265.6889 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55 | 0:240:120 | 0:00 | 10.0814 | 7 | 12.893 | 91.9179 | 104.8109 | 97.0808 | 5.8689 | 34.4442 | 3 | 10.0814 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4732 | 11931.727 | 44265.6925 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 55.6303 | 0:240:120 | 0:00 | 8.9056 | 7 | 16.2136 | 79.037 | 95.2506 | 86.0503 | 6.9402 | 48.1657 | 3 | 8.9056 | 781.9267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4735 | 12209.444 | 44265.6957 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 56.2815 | 0:240:120 | 0:00 | 7.9392 | 7 | 16.4071 | 67.5734 | 83.9805 | 73.4083 | 7.8428 | 61.5089 | 3 | 7.9392 | 80.0928 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4738 | 12446.92 | 44265.6984 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.1021 | 0:240:120 | 0:00 | 6.9744 | 7 | 9.8791 | 57.0549 | 66.934 | 60.483 | 4.838 | 23.4067 | 3 | 6.9744 | 37.3526 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4741 | 12631.732 | 44265.7006 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.2714 | 0:240:120 | 0:00 | 5.9314 | 7 | 12.8538 | 35.1254 | 47.9792 | 40.6073 | 5.6142 | 31.5198 | 3 | 5.9314 | 21.077 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4744 | 12759.844 | 44265.702 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 59.4495 | 0:240:120 | 0:00 | 5.1426 | 7 | 18.6875 | 10.3217 | 29.0092 | 17.7442 | 8.5961 | 73.8937 | 3 | 5.1426 | 14.5669 | NP | NP | 0-1-1-0-0-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4747 | 12830.99 | 44265.7029 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60.511 | 0:240:120 | 0:00 | 4.5842 | 7 | 0.9012 | 9.1875 | 10.0887 | 9.5607 | 0.4063 | 0.1651 | 3 | 4.5842 | 11.3539 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4750 | 12862.748 | 44265.7032 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.0411 | 0:240:120 | 0:00 | 3.9535 | 7 | 0.6262 | 7.8916 | 8.5178 | 8.1267 | 0.2938 | 0.0863 | 3 | 3.9535 | 8.5755 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4753 | 12890.569 | 44265.7036 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 63.3468 | 0:240:120 | 0:00 | 3.5306 | 7 | 1.0365 | 6.4164 | 7.4529 | 6.7803 | 0.5037 | 0.2537 | 3 | 3.5306 | 7.0691 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4756 | 12913.907 | 44265.7038 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 65.3466 | 0:240:120 | 0:00 | 3.0238 | 7 | 0.6584 | 4.7135 | 5.3719 | 4.9691 | 0.3039 | 0.0924 | 3 | 3.0238 | 5.5432 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4759 | 12932.118 | 44265.704 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 67.3585 | 0:240:120 | 0:00 | 2.6331 | 7 | 0.2283 | 4.1476 | 4.3759 | 4.2229 | 0.1106 | 0.0122 | 3 | 2.6331 | 4.532 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4762 | 12947.535 | 44265.7042 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 69.7114 | 0:240:120 | 0:00 | 2.2789 | 7 | 0.2334 | 3.3953 | 3.6287 | 3.4873 | 0.107 | 0.0115 | 3 | 2.2789 | 3.7162 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4765 | 12960.659 | 44265.7044 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.6 | 0:240:120 | 0:00 | 1.9466 | 7 | 0.1741 | 2.7627 | 2.9368 | 2.8215 | 0.0856 | 0.0073 | 3 | 1.9466 | 3.0252 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4768 | 12972.368 | 44265.7045 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.9025 | 0:240:120 | 0:00 | 1.9168 | 7 | 0.121 | 2.7321 | 2.8531 | 2.7813 | 0.0537 | 0.0029 | 3 | 1.9168 | 2.9664 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4771 | 12983.46 | 44265.7046 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.7173 | 0:240:120 | 0:00 | 1.5999 | 7 | 0.0698 | 2.1829 | 2.2527 | 2.2079 | 0.0326 | 0.0011 | 3 | 1.5999 | 2.3701 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4774 | 12992.849 | 44265.7047 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.1525 | 0:240:120 | 0:00 | 1.3317 | 7 | 0.0963 | 1.7409 | 1.8372 | 1.7781 | 0.0444 | 0.002 | 3 | 1.3317 | 1.9038 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4777 | 13001.115 | 44265.7048 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 85.844 | 0:240:120 | 0:00 | 1.1227 | 7 | 0.0631 | 1.4618 | 1.5249 | 1.4838 | 0.0297 | 0.0009 | 3 | 1.1227 | 1.5623 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4780 | 13008.641 | 44265.7049 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.8072 | 0:240:120 | 0:00 | 0.9561 | 7 | 0.0525 | 1.2187 | 1.2712 | 1.2397 | 0.0238 | 0.0006 | 3 | 0.9561 | 1.3027 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4783 | 13015.875 | 44265.705 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95.7583 | 0:240:120 | 0:00 | 0.8276 | 7 | 0.0417 | 1.0397 | 1.0814 | 1.0568 | 0.0185 | 0.0003 | 3 | 0.8276 | 1.1098 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4786 | 13022.141 | 44265.7051 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 101.5047 | 0:240:120 | 0:00 | 0.7113 | 7 | 0.029 | 0.8868 | 0.9158 | 0.8974 | 0.0136 | 0.0002 | 3 | 0.7113 | 0.9403 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4789 | 13027.864 | 44265.7052 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.822 | 0:240:120 | 0:00 | 0.6119 | 7 | 0.0253 | 0.7527 | 0.778 | 0.7617 | 0.0116 | 0.0001 | 3 | 0.6119 | 0.7991 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4792 | 13033.248 | 44265.7052 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 115.3691 | 0:240:120 | 0:00 | 0.5202 | 7 | 0.02 | 0.6345 | 0.6545 | 0.6424 | 0.009 | 0.0001 | 3 | 0.5202 | 0.6718 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4795 | 13038.097 | 44265.7053 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.8303 | 0:240:120 | 0:00 | 0.4416 | 7 | 0.0142 | 0.5362 | 0.5504 | 0.5416 | 0.0062 | 0 | 3 | 0.4416 | 0.5648 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4798 | 13042.885 | 44265.7053 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 129.074 | 0:240:120 | 0:00 | 0.4022 | 7 | 0.0157 | 0.4866 | 0.5023 | 0.4925 | 0.0067 | 0 | 3 | 0.4022 | 0.5119 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4801 | 13047.378 | 44265.7054 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 137.4131 | 0:240:120 | 0:00 | 0.3502 | 7 | 0.0098 | 0.4225 | 0.4323 | 0.4261 | 0.0043 | 0 | 3 | 0.3502 | 0.4429 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4804 | 13051.747 | 44265.7054 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 148.7244 | 0:240:120 | 0:00 | 0.2954 | 7 | 0.0112 | 0.3525 | 0.3637 | 0.3574 | 0.0046 | 0 | 3 | 0.2954 | 0.371 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4807 | 13056.057 | 44265.7055 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 158.1437 | 0:240:120 | 0:00 | 0.2597 | 7 | 0.0082 | 0.3094 | 0.3176 | 0.3126 | 0.0035 | 0 | 3 | 0.2597 | 0.3246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4810 | 13060.368 | 44265.7055 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 171.3393 | 0:240:120 | 0:00 | 0.2202 | 7 | 0.0062 | 0.2621 | 0.2683 | 0.2645 | 0.0024 | 0 | 3 | 0.2202 | 0.2737 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4813 | 13064.685 | 44265.7056 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 182.8057 | 0:240:120 | 0:00 | 0.1932 | 7 | 0.0046 | 0.2295 | 0.2341 | 0.2318 | 0.0018 | 0 | 3 | 0.1932 | 0.2392 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4816 | 13068.466 | 44265.7056 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 192.81 | 0:240:120 | 0:00 | 0.1738 | 7 | 0.0049 | 0.205 | 0.2099 | 0.2074 | 0.0018 | 0 | 3 | 0.1738 | 0.2146 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4819 | 13072.186 | 44265.7057 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 209.116 | 0:240:120 | 0:00 | 0.1482 | 7 | 0.0051 | 0.1745 | 0.1796 | 0.1772 | 0.0015 | 0 | 3 | 0.1482 | 0.1823 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4822 | 13075.738 | 44265.7057 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 222.437 | 0:240:120 | 0:00 | 0.1316 | 7 | 0.0042 | 0.1543 | 0.1585 | 0.1564 | 0.0017 | 0 | 3 | 0.1316 | 0.1614 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4825 | 13079.207 | 44265.7057 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 239.415 | 0:240:120 | 0:00 | 0.1145 | 7 | 0.0042 | 0.133 | 0.1372 | 0.1353 | 0.0015 | 0 | 3 | 0.1145 | 0.1399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4828 | 13082.635 | 44265.7058 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.173 | 0:240:120 | 0:00 | 0.1009 | 7 | 0.0041 | 0.1176 | 0.1217 | 0.1199 | 0.0015 | 0 | 3 | 0.1009 | 0.123 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4831 | 13086.24 | 44265.7058 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 275.675 | 0:240:120 | 0:00 | 0.0882 | 7 | 0.0033 | 0.1029 | 0.1062 | 0.1048 | 0.0013 | 0 | 3 | 0.0882 | 0.1071 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4834 | 13089.792 | 44265.7059 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 297.285 | 0:240:120 | 0:00 | 0.077 | 7 | 0.0031 | 0.0896 | 0.0927 | 0.091 | 0.0011 | 0 | 3 | 0.077 | 0.0932 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4837 | 13093.436 | 44265.7059 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 325.14 | 0:240:120 | 0:00 | 0.0657 | 7 | 0.0026 | 0.0762 | 0.0788 | 0.0774 | 0.001 | 0 | 3 | 0.0657 | 0.0792 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4840 | 13096.881 | 44265.7059 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 356.679 | 0:240:120 | 0:00 | 0.056 | 7 | 0.0022 | 0.0645 | 0.0667 | 0.0659 | 0.0008 | 0 | 3 | 0.056 | 0.0672 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4843 | 13100.265 | 44265.706 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 380.059 | 0:240:120 | 0:00 | 0.0503 | 7 | 0.0023 | 0.0583 | 0.0606 | 0.0593 | 0.0007 | 0 | 3 | 0.0503 | 0.0604 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
4846 | 13103.626 | 44265.706 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 400.362 | 0:240:120 | 0:00 | 0.0462 | 7 | 0.0027 | 0.0526 | 0.0553 | 0.0543 | 0.0011 | 0 | 3 | 0.0462 | 0.0562 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4849 | 13107.03 | 44265.7061 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 440.136 | 0:240:120 | 0:00 | 0.0396 | 7 | 0.0029 | 0.0444 | 0.0473 | 0.0463 | 0.001 | 0 | 3 | 0.0396 | 0.0496 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4852 | 13110.228 | 44265.7061 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 468.499 | 0:240:120 | 0:00 | 0.0359 | 7 | 0.0023 | 0.0409 | 0.0432 | 0.0422 | 0.001 | 0 | 3 | 0.0359 | 0.0459 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4855 | 13113.612 | 44265.7061 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 504.432 | 0:240:120 | 0:00 | 0.0321 | 7 | 0.0031 | 0.0362 | 0.0393 | 0.0376 | 0.0012 | 0 | 3 | 0.0321 | 0.0421 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4858 | 13117.255 | 44265.7062 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 566 | 0:240:120 | 0:00 | 0.0271 | 7 | 0.0028 | 0.0304 | 0.0332 | 0.032 | 0.001 | 0 | 3 | 0.0271 | 0.0371 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4861 | 13120.441 | 44265.7062 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 609.637 | 0:240:120 | 0:00 | 0.0244 | 7 | 0.0041 | 0.0267 | 0.0308 | 0.0288 | 0.0014 | 0 | 3 | 0.0244 | 0.0344 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4864 | 13123.646 | 44265.7063 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 648.923 | 0:240:120 | 0:00 | 0.0225 | 7 | 0.0041 | 0.0243 | 0.0284 | 0.0266 | 0.0014 | 0 | 3 | 0.0225 | 0.0325 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4867 | 13127.054 | 44265.7063 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 714.877 | 0:240:120 | 0:00 | 0.0198 | 7 | 0.0033 | 0.022 | 0.0253 | 0.0237 | 0.0011 | 0 | 3 | 0.0198 | 0.0298 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4870 | 13130.306 | 44265.7063 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 767.307 | 0:240:120 | 0:00 | 0.0182 | 7 | 0.0042 | 0.0199 | 0.0241 | 0.022 | 0.0015 | 0 | 3 | 0.0182 | 0.0282 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4873 | 13133.604 | 44265.7064 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 833.065 | 0:240:120 | 0:00 | 0.0166 | 7 | 0.0041 | 0.0182 | 0.0223 | 0.0205 | 0.0012 | 0 | 3 | 0.0166 | 0.0266 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4876 | 13136.79 | 44265.7064 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 882 | 0:240:120 | 0:00 | 0.0156 | 7 | 0.0032 | 0.018 | 0.0212 | 0.0196 | 0.0013 | 0 | 3 | 0.0156 | 0.0256 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4879 | 13140.083 | 44265.7064 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 932 | 0:240:120 | 0:00 | 0.0147 | 7 | 0.0016 | 0.0176 | 0.0192 | 0.0182 | 0.0006 | 0 | 3 | 0.0147 | 0.0247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4882 | 13143.159 | 44265.7065 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 980 | 0:240:120 | 0:00 | 0.014 | 7 | 0.0019 | 0.0167 | 0.0186 | 0.0176 | 0.0006 | 0 | 3 | 0.014 | 0.024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4885 | 13146.279 | 44265.7065 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1030 | 0:240:120 | 0:00 | 0.0134 | 7 | 0.0018 | 0.0162 | 0.018 | 0.0171 | 0.0006 | 0 | 3 | 0.0134 | 0.0234 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4888 | 13149.554 | 44265.7066 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1100 | 0:240:120 | 0:00 | 0.0126 | 7 | 0.0025 | 0.0145 | 0.017 | 0.0158 | 0.0009 | 0 | 3 | 0.0126 | 0.0226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4891 | 13153.214 | 44265.7066 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1175 | 0:240:120 | 0:00 | 0.012 | 7 | 0.0032 | 0.0132 | 0.0164 | 0.0149 | 0.0011 | 0 | 3 | 0.012 | 0.022 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4894 | 13156.447 | 44265.7066 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1260 | 0:240:120 | 0:00 | 0.0114 | 7 | 0.0042 | 0.0127 | 0.0169 | 0.0145 | 0.0016 | 0 | 3 | 0.0114 | 0.0214 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4897 | 13159.637 | 44265.7067 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1340 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0052 | 0.0114 | 0.0166 | 0.014 | 0.0019 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4900 | 13162.859 | 44265.7067 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1422.396 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0042 | 0.0118 | 0.016 | 0.0139 | 0.0014 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4903 | 13166.034 | 44265.7067 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1681.1548 | 0:240:120 | 0:00 | 0.0095 | 7 | 0.0041 | 0.0108 | 0.0149 | 0.0127 | 0.0014 | 0 | 3 | 0.0095 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4906 | 13169.451 | 44265.7068 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2161.4847 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0031 | 0.009 | 0.0121 | 0.0107 | 0.0011 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4909 | 13172.878 | 44265.7068 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3122.1446 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0012 | 0.0096 | 0.0108 | 0.0101 | 0.0004 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4912 | 13233.928 | 44265.7075 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 57.7 | 0:240:120 | 0:00 | 6.4013 | 7 | 10.8062 | 46.6489 | 57.4551 | 50.6827 | 5.0911 | 25.9192 | 3 | 6.4013 | 26.8122 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4915 | 13390.557 | 44265.7093 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 58.9 | 0:240:120 | 0:00 | 5.4844 | 7 | 17.0631 | 21.4109 | 38.474 | 28.4455 | 7.6495 | 58.5144 | 3 | 5.4844 | 17.0323 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4918 | 13490.114 | 44265.7105 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 60 | 0:240:120 | 0:00 | 4.8381 | 7 | 9.9648 | 9.5738 | 19.5386 | 12.9732 | 4.9129 | 24.1368 | 3 | 4.8381 | 12.7088 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4921 | 13541.42 | 44265.7111 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 61.3 | 0:240:120 | 0:00 | 4.2375 | 7 | 0.7792 | 8.5127 | 9.2919 | 8.7708 | 0.3829 | 0.1466 | 3 | 4.2375 | 9.736 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4924 | 13571.364 | 44265.7114 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 62.7 | 0:240:120 | 0:00 | 3.7292 | 7 | 0.9938 | 6.9978 | 7.9916 | 7.4448 | 0.4308 | 0.1856 | 3 | 3.7292 | 7.7463 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4927 | 13596.753 | 44265.7117 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 64.3 | 0:240:120 | 0:00 | 3.2712 | 7 | 0.9893 | 5.428 | 6.4173 | 5.9257 | 0.3878 | 0.1504 | 3 | 3.2712 | 6.2543 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4930 | 13617.597 | 44265.712 | Vista Coord | Tap | 50Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 66.4 | 0:240:120 | 0:00 | 2.8071 | 7 | 0.2391 | 4.4333 | 4.6724 | 4.5373 | 0.102 | 0.0104 | 3 | 2.8071 | 4.9666 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4933 | 13736.202 | 44265.7133 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 71.5 | 0:240:120 | 0:00 | 10.0814 | 7 | 9.6215 | 95.1925 | 104.814 | 98.4572 | 4.7673 | 22.7268 | 3 | 10.0814 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4936 | 14044.206 | 44265.7169 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.0423 | 0:240:120 | 0:00 | 9.2726 | 7 | 9.525 | 85.8667 | 95.3917 | 89.039 | 4.7553 | 22.6129 | 3 | 9.2726 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4939 | 14326.443 | 44265.7202 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 72.6011 | 0:240:120 | 0:00 | 8.5601 | 7 | 12.315 | 76.3974 | 88.7124 | 80.5154 | 6.0672 | 36.811 | 3 | 8.5601 | 200.1886 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4942 | 14583.143 | 44265.7232 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 73.7627 | 0:240:120 | 0:00 | 7.3705 | 7 | 14.2311 | 62.152 | 76.3831 | 67.9799 | 6.4089 | 41.0745 | 3 | 7.3705 | 48.8887 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4945 | 14805.71 | 44265.7257 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.5338 | 0:240:120 | 0:00 | 6.7413 | 7 | 16.6454 | 50.2026 | 66.848 | 56.8445 | 7.54 | 56.8514 | 3 | 6.7413 | 32.4286 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4948 | 14982.965 | 44265.7278 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.1816 | 0:240:120 | 0:00 | 5.6887 | 7 | 11.4864 | 29.0336 | 40.52 | 32.8507 | 5.711 | 32.6158 | 3 | 5.6887 | 18.7464 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
4951 | 15088.043 | 44265.729 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 77.6226 | 0:240:120 | 0:00 | 4.9944 | 7 | 10.9449 | 10.0869 | 21.0318 | 13.6398 | 5.3257 | 28.3629 | 3 | 4.9944 | 13.6272 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4954 | 15141.874 | 44265.7296 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 79.255 | 0:240:120 | 0:00 | 4.3784 | 7 | 0.5344 | 9.031 | 9.5654 | 9.2119 | 0.2647 | 0.0701 | 3 | 4.3784 | 10.3644 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4957 | 15172.007 | 44265.73 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 81.2603 | 0:240:120 | 0:00 | 3.7921 | 7 | 0.5394 | 7.4628 | 8.0022 | 7.644 | 0.2681 | 0.0719 | 3 | 3.7921 | 7.9717 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
4960 | 15196.583 | 44265.7303 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 84.7154 | 0:240:120 | 0:00 | 3.0641 | 7 | 0.6737 | 4.8412 | 5.5149 | 5.0645 | 0.3306 | 0.1093 | 3 | 3.0641 | 5.655 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4963 | 15214.967 | 44265.7305 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.6853 | 0:240:120 | 0:00 | 2.4927 | 7 | 0.3447 | 3.8055 | 4.1502 | 3.9379 | 0.1599 | 0.0256 | 3 | 2.4927 | 4.198 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4966 | 15229.334 | 44265.7306 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.3262 | 0:240:120 | 0:00 | 2.0308 | 7 | 0.0957 | 2.9324 | 3.0281 | 2.9647 | 0.046 | 0.0021 | 3 | 2.0308 | 3.194 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4969 | 15240.75 | 44265.7308 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 100.1715 | 0:240:120 | 0:00 | 1.5763 | 7 | 0.1031 | 2.1428 | 2.2459 | 2.1773 | 0.0508 | 0.0026 | 3 | 1.5763 | 2.3277 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4972 | 15250.02 | 44265.7309 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 106.9607 | 0:240:120 | 0:00 | 1.2758 | 7 | 0.0636 | 1.6706 | 1.7342 | 1.701 | 0.0268 | 0.0007 | 3 | 1.2758 | 1.8106 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4975 | 15258.263 | 44265.731 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.4991 | 0:240:120 | 0:00 | 1.0687 | 7 | 0.0577 | 1.3741 | 1.4318 | 1.3952 | 0.0274 | 0.0008 | 3 | 1.0687 | 1.477 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4978 | 15265.405 | 44265.731 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 120.5556 | 0:240:120 | 0:00 | 0.9023 | 7 | 0.0416 | 1.1424 | 1.184 | 1.1566 | 0.0202 | 0.0004 | 3 | 0.9023 | 1.2212 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4981 | 15271.635 | 44265.7311 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 130.1003 | 0:240:120 | 0:00 | 0.7376 | 7 | 0.0278 | 0.9266 | 0.9544 | 0.9365 | 0.0126 | 0.0002 | 3 | 0.7376 | 0.9781 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4984 | 15277.362 | 44265.7312 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.0838 | 0:240:120 | 0:00 | 0.6023 | 7 | 0.0228 | 0.7415 | 0.7643 | 0.7496 | 0.0106 | 0.0001 | 3 | 0.6023 | 0.7855 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4987 | 15282.613 | 44265.7312 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 152.5392 | 0:240:120 | 0:00 | 0.5 | 7 | 0.0155 | 0.6121 | 0.6276 | 0.6178 | 0.0072 | 0.0001 | 3 | 0.5 | 0.644 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4990 | 15287.548 | 44265.7313 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 164.582 | 0:240:120 | 0:00 | 0.42 | 7 | 0.0114 | 0.5108 | 0.5222 | 0.5156 | 0.005 | 0 | 3 | 0.42 | 0.5358 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4993 | 15292.259 | 44265.7314 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 176.6545 | 0:240:120 | 0:00 | 0.3589 | 7 | 0.0119 | 0.4317 | 0.4436 | 0.4369 | 0.005 | 0 | 3 | 0.3589 | 0.4543 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4996 | 15296.617 | 44265.7314 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 191.5958 | 0:240:120 | 0:00 | 0.3012 | 7 | 0.0078 | 0.3618 | 0.3696 | 0.3653 | 0.0033 | 0 | 3 | 0.3012 | 0.3785 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
4999 | 15300.708 | 44265.7315 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 203.3086 | 0:240:120 | 0:00 | 0.2658 | 7 | 0.0066 | 0.3185 | 0.3251 | 0.3211 | 0.0027 | 0 | 3 | 0.2658 | 0.3325 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5002 | 15304.468 | 44265.7315 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 218.4479 | 0:240:120 | 0:00 | 0.2291 | 7 | 0.0052 | 0.2735 | 0.2787 | 0.2759 | 0.002 | 0 | 3 | 0.2291 | 0.2852 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5005 | 15308.27 | 44265.7315 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 238.021 | 0:240:120 | 0:00 | 0.1926 | 7 | 0.0038 | 0.2292 | 0.233 | 0.231 | 0.0014 | 0 | 3 | 0.1926 | 0.2385 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5008 | 15311.985 | 44265.7316 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 263.036 | 0:240:120 | 0:00 | 0.1581 | 7 | 0.0036 | 0.1868 | 0.1904 | 0.1887 | 0.0012 | 0 | 3 | 0.1581 | 0.1947 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5011 | 15315.367 | 44265.7316 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 287.474 | 0:240:120 | 0:00 | 0.1331 | 7 | 0.0036 | 0.1568 | 0.1604 | 0.1589 | 0.0011 | 0 | 3 | 0.1331 | 0.1633 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5014 | 15318.855 | 44265.7317 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 318.896 | 0:240:120 | 0:00 | 0.1094 | 7 | 0.003 | 0.1285 | 0.1315 | 0.1302 | 0.0012 | 0 | 3 | 0.1094 | 0.1335 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5017 | 15322.199 | 44265.7317 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 351.311 | 0:240:120 | 0:00 | 0.0915 | 7 | 0.0025 | 0.1073 | 0.1098 | 0.1088 | 0.001 | 0 | 3 | 0.0915 | 0.1112 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5020 | 15325.591 | 44265.7317 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 400.963 | 0:240:120 | 0:00 | 0.0721 | 7 | 0.0031 | 0.0841 | 0.0872 | 0.0856 | 0.0012 | 0 | 3 | 0.0721 | 0.0871 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5023 | 15329.177 | 44265.7318 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 446.343 | 0:240:120 | 0:00 | 0.0598 | 7 | 0.0027 | 0.0689 | 0.0716 | 0.0703 | 0.0009 | 0 | 3 | 0.0598 | 0.0719 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5026 | 15332.437 | 44265.7318 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 497.375 | 0:240:120 | 0:00 | 0.0498 | 7 | 0.0028 | 0.057 | 0.0598 | 0.0584 | 0.001 | 0 | 3 | 0.0498 | 0.0598 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5029 | 15336.608 | 44265.7319 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 557.135 | 0:240:120 | 0:00 | 0.0413 | 7 | 0.0027 | 0.0468 | 0.0495 | 0.0482 | 0.001 | 0 | 3 | 0.0413 | 0.0513 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5032 | 15339.9 | 44265.7319 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 626.026 | 0:240:120 | 0:00 | 0.0344 | 7 | 0.0016 | 0.0397 | 0.0413 | 0.0405 | 0.0006 | 0 | 3 | 0.0344 | 0.0444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5035 | 15343.136 | 44265.7319 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 715.25 | 0:240:120 | 0:00 | 0.0282 | 7 | 0.0025 | 0.0315 | 0.034 | 0.0331 | 0.0008 | 0 | 3 | 0.0282 | 0.0382 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5038 | 15346.405 | 44265.732 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 788.774 | 0:240:120 | 0:00 | 0.0246 | 7 | 0.004 | 0.0267 | 0.0307 | 0.0289 | 0.0012 | 0 | 3 | 0.0246 | 0.0346 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5041 | 15349.606 | 44265.732 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 899.32 | 0:240:120 | 0:00 | 0.0207 | 7 | 0.0031 | 0.0231 | 0.0262 | 0.0249 | 0.0011 | 0 | 3 | 0.0207 | 0.0307 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5044 | 15352.975 | 44265.7321 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1007.372 | 0:240:120 | 0:00 | 0.018 | 7 | 0.0028 | 0.0202 | 0.023 | 0.0219 | 0.0012 | 0 | 3 | 0.018 | 0.028 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5047 | 15356.241 | 44265.7321 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1125.886 | 0:240:120 | 0:00 | 0.0159 | 7 | 0.0027 | 0.0179 | 0.0206 | 0.0197 | 0.0011 | 0 | 3 | 0.0159 | 0.0259 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5050 | 15359.647 | 44265.7321 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1215.634 | 0:240:120 | 0:00 | 0.0147 | 7 | 0.0017 | 0.0173 | 0.019 | 0.0181 | 0.0006 | 0 | 3 | 0.0147 | 0.0247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5053 | 15362.849 | 44265.7322 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1421.761 | 0:240:120 | 0:00 | 0.0127 | 7 | 0.0032 | 0.0145 | 0.0177 | 0.016 | 0.0012 | 0 | 3 | 0.0127 | 0.0227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5056 | 15366.246 | 44265.7322 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1791.377 | 0:240:120 | 0:00 | 0.0107 | 7 | 0.0047 | 0.0114 | 0.0161 | 0.0137 | 0.0018 | 0 | 3 | 0.0107 | 0.0207 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5059 | 15369.35 | 44265.7323 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2117.2599 | 0:240:120 | 0:00 | 0.0097 | 7 | 0.0036 | 0.0115 | 0.0151 | 0.013 | 0.0014 | 0 | 3 | 0.0097 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5062 | 15372.418 | 44265.7323 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2722.1913 | 0:240:120 | 0:00 | 0.0087 | 7 | 0.0051 | 0.0094 | 0.0145 | 0.011 | 0.0016 | 0 | 3 | 0.0087 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5065 | 15375.505 | 44265.7323 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3932.0541 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0046 | 0.0095 | 0.0141 | 0.0106 | 0.0015 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5068 | 15445.974 | 44265.7331 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 74.1 | 0:240:120 | 0:00 | 7.0821 | 7 | 9.9877 | 57.4509 | 67.4386 | 60.7558 | 4.955 | 24.5518 | 3 | 7.0821 | 40.025 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5071 | 15637.42 | 44265.7354 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 75.4 | 0:240:120 | 0:00 | 6.1462 | 7 | 14.9097 | 38.5112 | 53.4209 | 43.5299 | 7.3589 | 54.154 | 3 | 6.1462 | 23.4666 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5074 | 15777.523 | 44265.737 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 76.9 | 0:240:120 | 0:00 | 5.3214 | 7 | 11.1941 | 19.5617 | 30.7558 | 23.2026 | 5.4582 | 29.7916 | 3 | 5.3214 | 15.7997 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5077 | 15851.994 | 44265.7378 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 78.4 | 0:240:120 | 0:00 | 4.6822 | 7 | 0.68 | 9.5614 | 10.2414 | 9.773 | 0.3144 | 0.0989 | 3 | 4.6822 | 11.858 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5080 | 15884.466 | 44265.7382 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 80.3 | 0:240:120 | 0:00 | 4.0535 | 7 | 0.9981 | 7.993 | 8.9911 | 8.3342 | 0.4889 | 0.239 | 3 | 4.0535 | 8.969 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5083 | 15912.361 | 44265.7385 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 83 | 0:240:120 | 0:00 | 3.3902 | 7 | 1.0063 | 5.937 | 6.9433 | 6.3471 | 0.4522 | 0.2045 | 3 | 3.3902 | 6.6188 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5086 | 15933.822 | 44265.7388 | Vista Coord | Tap | 65Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 86.7 | 0:240:120 | 0:00 | 2.7519 | 7 | 0.3353 | 4.3247 | 4.66 | 4.4359 | 0.1661 | 0.0276 | 3 | 2.7519 | 4.8261 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5089 | 16052.217 | 44265.7402 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88 | 0:240:120 | 0:00 | 10.0814 | 7 | 9.4734 | 95.3399 | 104.8133 | 98.4999 | 4.7349 | 22.4194 | 3 | 10.0814 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5092 | 16360.496 | 44265.7437 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 88.7117 | 0:240:120 | 0:00 | 9.2233 | 7 | 9.4748 | 85.8695 | 95.3443 | 89.0279 | 4.7363 | 22.4321 | 3 | 9.2233 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5095 | 16640.514 | 44265.747 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 89.4531 | 0:240:120 | 0:00 | 8.4671 | 7 | 9.9372 | 76.3977 | 86.3349 | 79.7016 | 4.9469 | 24.4714 | 3 | 8.4671 | 165.3721 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5098 | 16892.392 | 44265.7499 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 90.6719 | 0:240:120 | 0:00 | 7.4528 | 7 | 9.4906 | 66.9066 | 76.3972 | 70.0738 | 4.7421 | 22.4876 | 3 | 7.4528 | 52.015 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5101 | 17114.748 | 44265.7525 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.8115 | 0:240:120 | 0:00 | 6.6943 | 7 | 17.9176 | 48.6603 | 66.5779 | 56.0506 | 7.9949 | 63.9192 | 3 | 6.6943 | 31.5557 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5104 | 17296.263 | 44265.7546 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 93.6463 | 0:240:120 | 0:00 | 5.7402 | 7 | 16.5317 | 29.0384 | 45.5701 | 34.8952 | 7.8789 | 62.0778 | 3 | 5.7402 | 19.2129 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5107 | 17400.871 | 44265.7558 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 96.4161 | 0:240:120 | 0:00 | 4.7057 | 7 | 1.3553 | 9.5615 | 10.9168 | 9.9504 | 0.5851 | 0.3423 | 3 | 4.7057 | 11.9825 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5110 | 17433.395 | 44265.7561 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 99.9933 | 0:240:120 | 0:00 | 3.7961 | 7 | 0.534 | 7.463 | 7.997 | 7.6424 | 0.2654 | 0.0704 | 3 | 3.7961 | 7.9864 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5113 | 17457.797 | 44265.7564 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 104.7893 | 0:240:120 | 0:00 | 2.9918 | 7 | 0.6653 | 4.7046 | 5.3699 | 4.9685 | 0.3045 | 0.0927 | 3 | 2.9918 | 5.4555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5116 | 17475.722 | 44265.7566 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 109.3587 | 0:240:120 | 0:00 | 2.4727 | 7 | 0.3353 | 3.8015 | 4.1368 | 3.9251 | 0.1592 | 0.0254 | 3 | 2.4727 | 4.1516 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5119 | 17490.54 | 44265.7568 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 113.5354 | 0:240:120 | 0:00 | 2.1238 | 7 | 0.2585 | 3.0231 | 3.2816 | 3.1338 | 0.115 | 0.0132 | 3 | 2.1238 | 3.3855 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5122 | 17503.033 | 44265.7569 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.5262 | 0:240:120 | 0:00 | 1.8644 | 7 | 0.0908 | 2.6751 | 2.7659 | 2.7061 | 0.0438 | 0.0019 | 3 | 1.8644 | 2.8642 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5125 | 17513.685 | 44265.7571 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 124.7136 | 0:240:120 | 0:00 | 1.5168 | 7 | 0.0785 | 2.0657 | 2.1442 | 2.1014 | 0.0327 | 0.0011 | 3 | 1.5168 | 2.222 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5128 | 17522.67 | 44265.7572 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.4575 | 0:240:120 | 0:00 | 1.2235 | 7 | 0.0601 | 1.6066 | 1.6667 | 1.6358 | 0.0246 | 0.0006 | 3 | 1.2235 | 1.7246 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5131 | 17530.408 | 44265.7573 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 144.5092 | 0:240:120 | 0:00 | 0.9706 | 7 | 0.0387 | 1.2526 | 1.2913 | 1.2666 | 0.0178 | 0.0003 | 3 | 0.9706 | 1.3248 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5134 | 17537.388 | 44265.7573 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 155.1902 | 0:240:120 | 0:00 | 0.8001 | 7 | 0.0336 | 1.0031 | 1.0367 | 1.0193 | 0.0136 | 0.0002 | 3 | 0.8001 | 1.0692 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5137 | 17543.401 | 44265.7574 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.3278 | 0:240:120 | 0:00 | 0.68 | 7 | 0.0291 | 0.8452 | 0.8743 | 0.856 | 0.0137 | 0.0002 | 3 | 0.68 | 0.8954 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5140 | 17549.193 | 44265.7575 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 178.9403 | 0:240:120 | 0:00 | 0.5601 | 7 | 0.0173 | 0.6905 | 0.7078 | 0.6973 | 0.0078 | 0.0001 | 3 | 0.5601 | 0.7268 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5143 | 17554.085 | 44265.7575 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 195.0894 | 0:240:120 | 0:00 | 0.4575 | 7 | 0.0137 | 0.5595 | 0.5732 | 0.5651 | 0.0055 | 0 | 3 | 0.4575 | 0.5862 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5146 | 17558.726 | 44265.7576 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 215.3701 | 0:240:120 | 0:00 | 0.3664 | 7 | 0.0074 | 0.4445 | 0.4519 | 0.4475 | 0.0032 | 0 | 3 | 0.3664 | 0.4643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5149 | 17563.015 | 44265.7576 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.7595 | 0:240:120 | 0:00 | 0.296 | 7 | 0.0081 | 0.3558 | 0.3639 | 0.3594 | 0.0034 | 0 | 3 | 0.296 | 0.3717 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5152 | 17567.292 | 44265.7577 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 256.2659 | 0:240:120 | 0:00 | 0.2529 | 7 | 0.0051 | 0.303 | 0.3081 | 0.305 | 0.002 | 0 | 3 | 0.2529 | 0.3158 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5155 | 17571.234 | 44265.7577 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 279.103 | 0:240:120 | 0:00 | 0.2123 | 7 | 0.0038 | 0.2522 | 0.256 | 0.2543 | 0.0014 | 0 | 3 | 0.2123 | 0.2636 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5158 | 17575.161 | 44265.7578 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 304.751 | 0:240:120 | 0:00 | 0.178 | 7 | 0.0041 | 0.2117 | 0.2158 | 0.2132 | 0.0017 | 0 | 3 | 0.178 | 0.22 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5161 | 17578.836 | 44265.7578 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 333.947 | 0:240:120 | 0:00 | 0.1488 | 7 | 0.004 | 0.1763 | 0.1803 | 0.1781 | 0.0013 | 0 | 3 | 0.1488 | 0.183 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5164 | 17582.592 | 44265.7579 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 368.27 | 0:240:120 | 0:00 | 0.1233 | 7 | 0.0042 | 0.1453 | 0.1495 | 0.1473 | 0.0013 | 0 | 3 | 0.1233 | 0.151 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5167 | 17586.105 | 44265.7579 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 405.768 | 0:240:120 | 0:00 | 0.1028 | 7 | 0.0033 | 0.121 | 0.1243 | 0.1226 | 0.0013 | 0 | 3 | 0.1028 | 0.1253 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5170 | 17589.475 | 44265.7579 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 449.82 | 0:240:120 | 0:00 | 0.0851 | 7 | 0.0032 | 0.099 | 0.1022 | 0.1007 | 0.001 | 0 | 3 | 0.0851 | 0.1033 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5173 | 17592.893 | 44265.758 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 493.489 | 0:240:120 | 0:00 | 0.0721 | 7 | 0.002 | 0.0844 | 0.0864 | 0.0854 | 0.0007 | 0 | 3 | 0.0721 | 0.0871 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5176 | 17596.52 | 44265.758 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 552.788 | 0:240:120 | 0:00 | 0.0591 | 7 | 0.0025 | 0.0683 | 0.0708 | 0.0696 | 0.0009 | 0 | 3 | 0.0591 | 0.0711 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5179 | 17599.948 | 44265.7581 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 610.253 | 0:240:120 | 0:00 | 0.05 | 7 | 0.0022 | 0.0581 | 0.0603 | 0.0591 | 0.0007 | 0 | 3 | 0.05 | 0.06 | P | NP | 1-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5182 | 17603.572 | 44265.7581 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 681.451 | 0:240:120 | 0:00 | 0.0417 | 7 | 0.0032 | 0.0474 | 0.0506 | 0.0491 | 0.0011 | 0 | 3 | 0.0417 | 0.0517 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5185 | 17606.867 | 44265.7581 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 771.325 | 0:240:120 | 0:00 | 0.0344 | 7 | 0.003 | 0.039 | 0.042 | 0.0407 | 0.0011 | 0 | 3 | 0.0344 | 0.0444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5188 | 17610.129 | 44265.7582 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 849.737 | 0:240:120 | 0:00 | 0.0297 | 7 | 0.0026 | 0.0337 | 0.0363 | 0.0352 | 0.0009 | 0 | 3 | 0.0297 | 0.0397 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5191 | 17613.586 | 44265.7582 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 941.006 | 0:240:120 | 0:00 | 0.0257 | 7 | 0.0034 | 0.0282 | 0.0316 | 0.0302 | 0.0013 | 0 | 3 | 0.0257 | 0.0357 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5194 | 17616.722 | 44265.7583 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1037.748 | 0:240:120 | 0:00 | 0.0225 | 7 | 0.0025 | 0.0253 | 0.0278 | 0.0268 | 0.001 | 0 | 3 | 0.0225 | 0.0325 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5197 | 17620.009 | 44265.7583 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1123.189 | 0:240:120 | 0:00 | 0.0203 | 7 | 0.0037 | 0.0222 | 0.0259 | 0.0244 | 0.0011 | 0 | 3 | 0.0203 | 0.0303 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5200 | 17623.113 | 44265.7583 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1249.02 | 0:240:120 | 0:00 | 0.0179 | 7 | 0.0027 | 0.0198 | 0.0225 | 0.0216 | 0.0009 | 0 | 3 | 0.0179 | 0.0279 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5203 | 17626.271 | 44265.7584 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1364.582 | 0:240:120 | 0:00 | 0.0162 | 7 | 0.0035 | 0.0179 | 0.0214 | 0.02 | 0.0013 | 0 | 3 | 0.0162 | 0.0262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5206 | 17629.691 | 44265.7584 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1492.389 | 0:240:120 | 0:00 | 0.0147 | 7 | 0.0027 | 0.0173 | 0.02 | 0.0187 | 0.0009 | 0 | 3 | 0.0147 | 0.0247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5209 | 17632.859 | 44265.7584 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1715.799 | 0:240:120 | 0:00 | 0.0129 | 7 | 0.0017 | 0.0153 | 0.017 | 0.0159 | 0.0006 | 0 | 3 | 0.0129 | 0.0229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5212 | 17636.052 | 44265.7585 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1974.707 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0035 | 0.0127 | 0.0162 | 0.0142 | 0.0012 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5215 | 17639.352 | 44265.7585 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2253.835 | 0:240:120 | 0:00 | 0.0105 | 7 | 0.0042 | 0.0116 | 0.0158 | 0.0137 | 0.0017 | 0 | 3 | 0.0105 | 0.0205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5218 | 17642.565 | 44265.7586 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2663.8471 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0043 | 0.0106 | 0.0149 | 0.0129 | 0.0016 | 0 | 3 | 0.0096 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5221 | 17645.682 | 44265.7586 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3424.9463 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0053 | 0.0097 | 0.015 | 0.0114 | 0.0017 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5224 | 17648.879 | 44265.7586 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4947.1446 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0048 | 0.0096 | 0.0144 | 0.0109 | 0.0015 | 0 | 3 | 0.008 | 0.014 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5227 | 17719.324 | 44265.7594 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 91.2 | 0:240:120 | 0:00 | 7.0821 | 7 | 9.7819 | 57.4519 | 67.2338 | 60.6903 | 4.8455 | 23.4784 | 3 | 7.0821 | 40.025 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5230 | 17913.727 | 44265.7617 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 92.7 | 0:240:120 | 0:00 | 6.1977 | 7 | 18.3251 | 38.6742 | 56.9993 | 46.0166 | 8.3305 | 69.3965 | 3 | 6.1977 | 24.0941 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5233 | 18059.699 | 44265.7634 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 95 | 0:240:120 | 0:00 | 5.1866 | 7 | 9.4865 | 19.5481 | 29.0346 | 22.7152 | 4.7389 | 22.4571 | 3 | 5.1866 | 14.8595 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5236 | 18129.677 | 44265.7642 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 98.2 | 0:240:120 | 0:00 | 4.207 | 7 | 0.5676 | 8.5138 | 9.0814 | 8.7014 | 0.2788 | 0.0777 | 3 | 4.207 | 9.6051 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5239 | 18157.863 | 44265.7645 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 102.4 | 0:240:120 | 0:00 | 3.349 | 7 | 0.9259 | 5.8929 | 6.8188 | 6.2154 | 0.4464 | 0.1993 | 3 | 3.349 | 6.4909 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5242 | 18179.159 | 44265.7648 | Vista Coord | Tap | 80Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 107.1 | 0:240:120 | 0:00 | 2.7071 | 7 | 0.1759 | 4.3219 | 4.4978 | 4.3809 | 0.0874 | 0.0076 | 3 | 2.7071 | 4.7138 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5245 | 18297.535 | 44265.7661 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110 | 0:240:120 | 0:00 | 10.0814 | 7 | 9.471 | 95.3467 | 104.8177 | 98.5033 | 4.7345 | 22.415 | 3 | 10.0814 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5248 | 18614.914 | 44265.7698 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.2299 | 0:240:120 | 0:00 | 9.8454 | 7 | 9.742 | 95.0728 | 104.8148 | 98.4392 | 4.7814 | 22.8622 | 3 | 9.8454 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5251 | 18922.921 | 44265.7734 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 110.8371 | 0:240:120 | 0:00 | 9.2701 | 7 | 9.4761 | 85.8684 | 95.3445 | 89.0297 | 4.7355 | 22.4248 | 3 | 9.2701 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5254 | 19194.373 | 44265.7765 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 112.8314 | 0:240:120 | 0:00 | 7.7645 | 7 | 10.7515 | 66.9265 | 77.678 | 70.697 | 5.1827 | 26.8606 | 3 | 7.7645 | 67.5249 | NP | NP | 0-0-1-0-0-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5257 | 19419.71 | 44265.7791 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 114.6354 | 0:240:120 | 0:00 | 6.7569 | 7 | 11.7263 | 55.201 | 66.9273 | 60.2856 | 5.0285 | 25.2858 | 3 | 6.7569 | 32.727 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5260 | 19597.289 | 44265.7812 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 117.1555 | 0:240:120 | 0:00 | 5.7053 | 7 | 12.3143 | 29.0365 | 41.3508 | 33.5114 | 5.6899 | 32.3754 | 3 | 5.7053 | 18.8955 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5263 | 19692.553 | 44265.7823 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 121.2739 | 0:240:120 | 0:00 | 4.5253 | 7 | 0.9208 | 9.1672 | 10.088 | 9.6182 | 0.3747 | 0.1404 | 3 | 4.5253 | 11.0619 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5266 | 19724.689 | 44265.7827 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 123.4167 | 0:240:120 | 0:00 | 4.0765 | 7 | 0.966 | 8.0749 | 9.0409 | 8.5551 | 0.3977 | 0.1582 | 3 | 4.0765 | 9.0619 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5269 | 19752.384 | 44265.783 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 128.1995 | 0:240:120 | 0:00 | 3.3227 | 7 | 0.5436 | 5.8913 | 6.4349 | 6.0743 | 0.266 | 0.0708 | 3 | 3.3227 | 6.4104 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5272 | 19772.677 | 44265.7832 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 133.7897 | 0:240:120 | 0:00 | 2.7148 | 7 | 0.1773 | 4.3218 | 4.4991 | 4.382 | 0.0869 | 0.0076 | 3 | 2.7148 | 4.733 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5275 | 19787.832 | 44265.7834 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 141.6723 | 0:240:120 | 0:00 | 2.1383 | 7 | 0.1773 | 3.1051 | 3.2824 | 3.165 | 0.0877 | 0.0077 | 3 | 2.1383 | 3.4157 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5278 | 19800.127 | 44265.7835 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 149.864 | 0:240:120 | 0:00 | 1.7358 | 7 | 0.1704 | 2.418 | 2.5884 | 2.4809 | 0.079 | 0.0062 | 3 | 1.7358 | 2.6194 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5281 | 19810.128 | 44265.7836 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 160.1875 | 0:240:120 | 0:00 | 1.3883 | 7 | 0.0525 | 1.8864 | 1.9389 | 1.9046 | 0.0256 | 0.0007 | 3 | 1.3883 | 1.9994 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5284 | 19818.749 | 44265.7837 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 170.1568 | 0:240:120 | 0:00 | 1.1528 | 7 | 0.051 | 1.5153 | 1.5663 | 1.5383 | 0.0214 | 0.0005 | 3 | 1.1528 | 1.6104 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5287 | 19826.021 | 44265.7838 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 183.0191 | 0:240:120 | 0:00 | 0.9359 | 7 | 0.0263 | 1.2053 | 1.2316 | 1.2145 | 0.0123 | 0.0002 | 3 | 0.9359 | 1.2719 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5290 | 19832.88 | 44265.7839 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 193.6011 | 0:240:120 | 0:00 | 0.8043 | 7 | 0.0283 | 1.0175 | 1.0458 | 1.0265 | 0.012 | 0.0001 | 3 | 0.8043 | 1.0754 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5293 | 19838.79 | 44265.784 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 208.8856 | 0:240:120 | 0:00 | 0.662 | 7 | 0.0158 | 0.8247 | 0.8405 | 0.8309 | 0.0068 | 0 | 3 | 0.662 | 0.8698 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5296 | 19844.474 | 44265.784 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 224.4407 | 0:240:120 | 0:00 | 0.5555 | 7 | 0.0106 | 0.6882 | 0.6988 | 0.6925 | 0.0045 | 0 | 3 | 0.5555 | 0.7205 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5299 | 19849.605 | 44265.7841 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 243.6775 | 0:240:120 | 0:00 | 0.4583 | 7 | 0.0115 | 0.5622 | 0.5737 | 0.5669 | 0.0049 | 0 | 3 | 0.4583 | 0.5873 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5302 | 19854.184 | 44265.7842 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 268.1679 | 0:240:120 | 0:00 | 0.3696 | 7 | 0.0075 | 0.4491 | 0.4566 | 0.4521 | 0.0028 | 0 | 3 | 0.3696 | 0.4685 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5305 | 19858.414 | 44265.7842 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 290.2449 | 0:240:120 | 0:00 | 0.3113 | 7 | 0.0068 | 0.3754 | 0.3822 | 0.3781 | 0.0028 | 0 | 3 | 0.3113 | 0.3917 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5308 | 19862.638 | 44265.7843 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 316.4359 | 0:240:120 | 0:00 | 0.2594 | 7 | 0.0066 | 0.3111 | 0.3177 | 0.3138 | 0.0025 | 0 | 3 | 0.2594 | 0.3242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5311 | 19866.467 | 44265.7843 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 339.2928 | 0:240:120 | 0:00 | 0.2247 | 7 | 0.0041 | 0.2686 | 0.2727 | 0.2705 | 0.0015 | 0 | 3 | 0.2247 | 0.2795 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5314 | 19870.266 | 44265.7843 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 365.6994 | 0:240:120 | 0:00 | 0.1931 | 7 | 0.0042 | 0.2301 | 0.2343 | 0.232 | 0.0017 | 0 | 3 | 0.1931 | 0.2391 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5317 | 19873.964 | 44265.7844 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 401.381 | 0:240:120 | 0:00 | 0.1606 | 7 | 0.003 | 0.191 | 0.194 | 0.1922 | 0.0013 | 0 | 3 | 0.1606 | 0.1979 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5320 | 19877.432 | 44265.7844 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 440.802 | 0:240:120 | 0:00 | 0.134 | 7 | 0.0038 | 0.1587 | 0.1625 | 0.1604 | 0.0015 | 0 | 3 | 0.134 | 0.1643 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5323 | 19881.221 | 44265.7845 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 485.103 | 0:240:120 | 0:00 | 0.1117 | 7 | 0.003 | 0.1312 | 0.1342 | 0.1327 | 0.001 | 0 | 3 | 0.1117 | 0.1365 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5326 | 19884.581 | 44265.7845 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 538.882 | 0:240:120 | 0:00 | 0.092 | 7 | 0.0032 | 0.1079 | 0.1111 | 0.1097 | 0.0012 | 0 | 3 | 0.092 | 0.1118 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5329 | 19887.912 | 44265.7845 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 599.87 | 0:240:120 | 0:00 | 0.0758 | 7 | 0.0028 | 0.0883 | 0.0911 | 0.0905 | 0.001 | 0 | 3 | 0.0758 | 0.0917 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5332 | 19891.326 | 44265.7846 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 672.644 | 0:240:120 | 0:00 | 0.062 | 7 | 0.0022 | 0.0721 | 0.0743 | 0.0731 | 0.0008 | 0 | 3 | 0.062 | 0.0745 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5335 | 19894.83 | 44265.7846 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 747.214 | 0:240:120 | 0:00 | 0.0518 | 7 | 0.0031 | 0.0592 | 0.0623 | 0.0612 | 0.0012 | 0 | 3 | 0.0518 | 0.0621 | P | NP | 1-1-1-1-1-1-0-1-0 | NP | 0-0-0-0-0-0-0-0-0
5338 | 19898.182 | 44265.7847 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 829.187 | 0:240:120 | 0:00 | 0.0436 | 7 | 0.0026 | 0.0496 | 0.0522 | 0.0512 | 0.001 | 0 | 3 | 0.0436 | 0.0536 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5341 | 19901.474 | 44265.7847 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 920.152 | 0:240:120 | 0:00 | 0.0369 | 7 | 0.0033 | 0.0418 | 0.0451 | 0.0437 | 0.0013 | 0 | 3 | 0.0369 | 0.0469 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5344 | 19904.689 | 44265.7847 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1032.327 | 0:240:120 | 0:00 | 0.031 | 7 | 0.0027 | 0.0348 | 0.0375 | 0.0363 | 0.001 | 0 | 3 | 0.031 | 0.041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5347 | 19907.935 | 44265.7848 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1150 | 0:240:120 | 0:00 | 0.0265 | 7 | 0.0034 | 0.0293 | 0.0327 | 0.0313 | 0.0013 | 0 | 3 | 0.0265 | 0.0365 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5350 | 19911.322 | 44265.7848 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1290.576 | 0:240:120 | 0:00 | 0.0226 | 7 | 0.0028 | 0.0254 | 0.0282 | 0.0269 | 0.001 | 0 | 3 | 0.0226 | 0.0326 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5353 | 19914.5 | 44265.7849 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1402.651 | 0:240:120 | 0:00 | 0.0203 | 7 | 0.0025 | 0.0224 | 0.0249 | 0.0241 | 0.0009 | 0 | 3 | 0.0203 | 0.0303 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5356 | 19917.897 | 44265.7849 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1519.705 | 0:240:120 | 0:00 | 0.0184 | 7 | 0.0042 | 0.0194 | 0.0236 | 0.0221 | 0.0014 | 0 | 3 | 0.0184 | 0.0284 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5359 | 19921.093 | 44265.7849 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1712.962 | 0:240:120 | 0:00 | 0.0161 | 7 | 0.0029 | 0.0182 | 0.0211 | 0.0198 | 0.0009 | 0 | 3 | 0.0161 | 0.0261 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5362 | 19924.283 | 44265.785 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1940.871 | 0:240:120 | 0:00 | 0.0142 | 7 | 0.0021 | 0.0167 | 0.0188 | 0.0175 | 0.0007 | 0 | 3 | 0.0142 | 0.0242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5365 | 19927.785 | 44265.785 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2212.88 | 0:240:120 | 0:00 | 0.0126 | 7 | 0.0029 | 0.0142 | 0.0171 | 0.0155 | 0.001 | 0 | 3 | 0.0126 | 0.0226 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5368 | 19930.881 | 44265.785 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2515.145 | 0:240:120 | 0:00 | 0.0114 | 7 | 0.0046 | 0.0122 | 0.0168 | 0.0142 | 0.0017 | 0 | 3 | 0.0114 | 0.0214 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5371 | 19933.992 | 44265.7851 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2799.797 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0052 | 0.0115 | 0.0167 | 0.0135 | 0.0018 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5374 | 19937.158 | 44265.7851 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3309.1292 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0044 | 0.0103 | 0.0147 | 0.0126 | 0.0017 | 0 | 3 | 0.0096 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5377 | 19940.664 | 44265.7852 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4254.5947 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0055 | 0.0095 | 0.015 | 0.011 | 0.0017 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5380 | 19944.096 | 44265.7852 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6145.5256 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0015 | 0.009 | 0.0105 | 0.0098 | 0.0005 | 0 | 3 | 0.008 | 0.014 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5383 | 20004.085 | 44265.7859 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 115.9 | 0:240:120 | 0:00 | 6.1874 | 7 | 18.3657 | 38.6803 | 57.046 | 47.4888 | 7.901 | 62.4266 | 3 | 6.1874 | 23.966 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5386 | 20149.637 | 44265.7876 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 119.2 | 0:240:120 | 0:00 | 5.0559 | 7 | 18.3482 | 10.0897 | 28.4379 | 17.9356 | 8.1115 | 65.7968 | 3 | 5.0559 | 14.0086 | NP | NP | 0-0-1-0-1-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
5389 | 20218.91 | 44265.7884 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 122.3 | 0:240:120 | 0:00 | 4.2996 | 7 | 0.7129 | 8.8515 | 9.5644 | 9.1704 | 0.3 | 0.09 | 3 | 4.2996 | 10.0084 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5392 | 20248.84 | 44265.7887 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 125.8 | 0:240:120 | 0:00 | 3.6656 | 7 | 0.9799 | 6.9444 | 7.9243 | 7.323 | 0.4415 | 0.195 | 3 | 3.6656 | 7.5241 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5395 | 20272.941 | 44265.789 | Vista Coord | Tap | 100Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 131 | 0:240:120 | 0:00 | 2.9904 | 7 | 0.6072 | 4.763 | 5.3702 | 4.996 | 0.2814 | 0.0792 | 3 | 2.9904 | 5.4516 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5398 | 20392.678 | 44265.7904 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165 | 0:240:120 | 0:00 | 10.0814 | 7 | 9.4715 | 95.3431 | 104.8146 | 98.5011 | 4.7339 | 22.4094 | 3 | 10.0814 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5401 | 20710.256 | 44265.7941 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 165.3872 | 0:240:120 | 0:00 | 9.8171 | 7 | 9.4716 | 95.3427 | 104.8143 | 98.4998 | 4.7341 | 22.412 | 3 | 9.8171 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5404 | 21018.1 | 44265.7976 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 166.9448 | 0:240:120 | 0:00 | 8.876 | 7 | 9.4738 | 85.8705 | 95.3443 | 89.0289 | 4.7359 | 22.4286 | 3 | 8.876 | 630.3053 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5407 | 21288.605 | 44265.8008 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 169.73 | 0:240:120 | 0:00 | 7.5643 | 7 | 9.4739 | 66.9227 | 76.3966 | 70.0881 | 4.7309 | 22.3817 | 3 | 7.5643 | 56.808 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5410 | 21501.499 | 44265.8032 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 173.8528 | 0:240:120 | 0:00 | 6.1866 | 7 | 11.5622 | 45.7026 | 57.2648 | 50.6653 | 4.9563 | 24.5651 | 3 | 6.1866 | 23.9565 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5413 | 21648.163 | 44265.8049 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 177.5334 | 0:240:120 | 0:00 | 5.3065 | 7 | 9.4802 | 19.561 | 29.0412 | 25.5064 | 4.4967 | 20.2203 | 3 | 5.3065 | 15.6923 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5416 | 21718.975 | 44265.8057 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 182.6847 | 0:240:120 | 0:00 | 4.4092 | 7 | 0.5244 | 9.0412 | 9.5656 | 9.2258 | 0.2548 | 0.0649 | 3 | 4.4092 | 10.5069 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5419 | 21748.974 | 44265.8061 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 188.1946 | 0:240:120 | 0:00 | 3.719 | 7 | 0.529 | 7.4632 | 7.9922 | 7.6411 | 0.2626 | 0.069 | 3 | 3.719 | 7.7104 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5422 | 21774.286 | 44265.8064 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 193.9476 | 0:240:120 | 0:00 | 3.1846 | 7 | 0.5234 | 5.3702 | 5.8936 | 5.6611 | 0.2322 | 0.0539 | 3 | 3.1846 | 5.9988 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5425 | 21793.934 | 44265.8066 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 199.8931 | 0:240:120 | 0:00 | 2.7633 | 7 | 0.1783 | 4.4943 | 4.6726 | 4.5544 | 0.0881 | 0.0078 | 3 | 2.7633 | 4.8549 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5428 | 21810.112 | 44265.8068 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 209.6996 | 0:240:120 | 0:00 | 2.2542 | 7 | 0.1761 | 3.4533 | 3.6294 | 3.5126 | 0.0872 | 0.0076 | 3 | 2.2542 | 3.6625 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5431 | 21823.31 | 44265.8069 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 218.845 | 0:240:120 | 0:00 | 1.9123 | 7 | 0.089 | 2.7609 | 2.8499 | 2.7908 | 0.0435 | 0.0019 | 3 | 1.9123 | 2.9576 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5434 | 21834.409 | 44265.8071 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 230.7789 | 0:240:120 | 0:00 | 1.5852 | 7 | 0.0531 | 2.1932 | 2.2463 | 2.2115 | 0.0257 | 0.0007 | 3 | 1.5852 | 2.3437 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5437 | 21844.077 | 44265.8072 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 243.6181 | 0:240:120 | 0:00 | 1.329 | 7 | 0.053 | 1.7843 | 1.8373 | 1.8028 | 0.0258 | 0.0007 | 3 | 1.329 | 1.8991 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5440 | 21852.571 | 44265.8073 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 257.7069 | 0:240:120 | 0:00 | 1.1205 | 7 | 0.033 | 1.4658 | 1.4988 | 1.4864 | 0.0155 | 0.0002 | 3 | 1.1205 | 1.5587 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5443 | 21859.712 | 44265.8074 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 274.3642 | 0:240:120 | 0:00 | 0.9374 | 7 | 0.025 | 1.2066 | 1.2316 | 1.2158 | 0.0116 | 0.0001 | 3 | 0.9374 | 1.2743 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5446 | 21866.444 | 44265.8074 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 292.611 | 0:240:120 | 0:00 | 0.7884 | 7 | 0.0201 | 0.9986 | 1.0187 | 1.0064 | 0.009 | 0.0001 | 3 | 0.7884 | 1.0521 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5449 | 21872.381 | 44265.8075 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 315.3898 | 0:240:120 | 0:00 | 0.6513 | 7 | 0.0105 | 0.8166 | 0.8271 | 0.8204 | 0.0046 | 0 | 3 | 0.6513 | 0.8546 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5452 | 21877.863 | 44265.8076 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 336.7705 | 0:240:120 | 0:00 | 0.5551 | 7 | 0.0104 | 0.6886 | 0.699 | 0.6936 | 0.0039 | 0 | 3 | 0.5551 | 0.7199 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5455 | 21882.882 | 44265.8076 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 365.6411 | 0:240:120 | 0:00 | 0.4579 | 7 | 0.0103 | 0.5631 | 0.5734 | 0.5676 | 0.0045 | 0 | 3 | 0.4579 | 0.5868 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5458 | 21887.686 | 44265.8077 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 394.515 | 0:240:120 | 0:00 | 0.3858 | 7 | 0.0077 | 0.4696 | 0.4773 | 0.4726 | 0.0034 | 0 | 3 | 0.3858 | 0.49 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5461 | 21892.185 | 44265.8077 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 424.3415 | 0:240:120 | 0:00 | 0.3289 | 7 | 0.0075 | 0.3982 | 0.4057 | 0.4012 | 0.003 | 0 | 3 | 0.3289 | 0.4148 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5464 | 21896.631 | 44265.8078 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 464.9799 | 0:240:120 | 0:00 | 0.2708 | 7 | 0.0058 | 0.326 | 0.3318 | 0.3283 | 0.0022 | 0 | 3 | 0.2708 | 0.339 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5467 | 21900.694 | 44265.8078 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 505.4522 | 0:240:120 | 0:00 | 0.2279 | 7 | 0.0063 | 0.2725 | 0.2788 | 0.2753 | 0.0024 | 0 | 3 | 0.2279 | 0.2836 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5470 | 21904.713 | 44265.8079 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 554.214 | 0:240:120 | 0:00 | 0.1892 | 7 | 0.005 | 0.2259 | 0.2309 | 0.2279 | 0.002 | 0 | 3 | 0.1892 | 0.2341 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5473 | 21908.14 | 44265.8079 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 610.561 | 0:240:120 | 0:00 | 0.1563 | 7 | 0.0041 | 0.185 | 0.1891 | 0.1871 | 0.0014 | 0 | 3 | 0.1563 | 0.1924 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5476 | 21911.606 | 44265.808 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 686.076 | 0:240:120 | 0:00 | 0.1249 | 7 | 0.0043 | 0.1472 | 0.1515 | 0.1491 | 0.0017 | 0 | 3 | 0.1249 | 0.1529 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5479 | 21915.123 | 44265.808 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 767.726 | 0:240:120 | 0:00 | 0.1011 | 7 | 0.0036 | 0.1189 | 0.1225 | 0.1202 | 0.0014 | 0 | 3 | 0.1011 | 0.1232 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5482 | 21918.476 | 44265.8081 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 850.081 | 0:240:120 | 0:00 | 0.0839 | 7 | 0.003 | 0.098 | 0.101 | 0.0996 | 0.0011 | 0 | 3 | 0.0839 | 0.1018 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5485 | 21921.873 | 44265.8081 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 933.566 | 0:240:120 | 0:00 | 0.071 | 7 | 0.0033 | 0.0823 | 0.0856 | 0.0842 | 0.0012 | 0 | 3 | 0.071 | 0.0857 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5488 | 21925.264 | 44265.8081 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1030.33 | 0:240:120 | 0:00 | 0.0598 | 7 | 0.003 | 0.0684 | 0.0714 | 0.0699 | 0.0009 | 0 | 3 | 0.0598 | 0.0718 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5491 | 21929.013 | 44265.8082 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1137.868 | 0:240:120 | 0:00 | 0.0505 | 7 | 0.0016 | 0.0585 | 0.0601 | 0.0594 | 0.0006 | 0 | 3 | 0.0505 | 0.0606 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5494 | 21932.358 | 44265.8082 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1254.511 | 0:240:120 | 0:00 | 0.043 | 7 | 0.0025 | 0.0491 | 0.0516 | 0.0504 | 0.0008 | 0 | 3 | 0.043 | 0.053 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5497 | 21935.664 | 44265.8083 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1379.769 | 0:240:120 | 0:00 | 0.037 | 7 | 0.0023 | 0.0421 | 0.0444 | 0.0436 | 0.0009 | 0 | 3 | 0.037 | 0.047 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5500 | 21938.857 | 44265.8083 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1534.259 | 0:240:120 | 0:00 | 0.0314 | 7 | 0.0021 | 0.0349 | 0.037 | 0.0363 | 0.0008 | 0 | 3 | 0.0314 | 0.0414 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5503 | 21942.267 | 44265.8083 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1706.16 | 0:240:120 | 0:00 | 0.0269 | 7 | 0.003 | 0.0299 | 0.0329 | 0.0315 | 0.0012 | 0 | 3 | 0.0269 | 0.0369 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5506 | 21945.396 | 44265.8084 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1945.18 | 0:240:120 | 0:00 | 0.0225 | 7 | 0.0028 | 0.0245 | 0.0273 | 0.0265 | 0.0012 | 0 | 3 | 0.0225 | 0.0325 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5509 | 21948.511 | 44265.8084 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2170.056 | 0:240:120 | 0:00 | 0.0196 | 7 | 0.0033 | 0.0213 | 0.0246 | 0.0231 | 0.0011 | 0 | 3 | 0.0196 | 0.0296 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5512 | 21951.562 | 44265.8084 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2515.816 | 0:240:120 | 0:00 | 0.0165 | 7 | 0.003 | 0.0187 | 0.0217 | 0.0202 | 0.0011 | 0 | 3 | 0.0165 | 0.0265 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5515 | 21954.858 | 44265.8085 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2762.956 | 0:240:120 | 0:00 | 0.0149 | 7 | 0.0016 | 0.0175 | 0.0191 | 0.0182 | 0.0006 | 0 | 3 | 0.0149 | 0.0249 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5518 | 21957.932 | 44265.8085 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3170.008 | 0:240:120 | 0:00 | 0.0131 | 7 | 0.0028 | 0.0144 | 0.0172 | 0.016 | 0.0009 | 0 | 3 | 0.0131 | 0.0231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5521 | 21961.208 | 44265.8085 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3584.398 | 0:240:120 | 0:00 | 0.0118 | 7 | 0.0041 | 0.0124 | 0.0165 | 0.0146 | 0.0015 | 0 | 3 | 0.0118 | 0.0218 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5524 | 21964.41 | 44265.8086 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4078.356 | 0:240:120 | 0:00 | 0.0108 | 7 | 0.0042 | 0.0117 | 0.0159 | 0.0139 | 0.0018 | 0 | 3 | 0.0108 | 0.0208 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5527 | 21967.486 | 44265.8086 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4820.2805 | 0:240:120 | 0:00 | 0.0097 | 7 | 0.0046 | 0.0102 | 0.0148 | 0.0124 | 0.0018 | 0 | 3 | 0.0097 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5530 | 21970.874 | 44265.8087 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6197.5035 | 0:240:120 | 0:00 | 0.0087 | 7 | 0.0059 | 0.0093 | 0.0152 | 0.0117 | 0.0021 | 0 | 3 | 0.0087 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5533 | 21974.188 | 44265.8087 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8951.9495 | 0:240:120 | 0:00 | 0.0078 | 7 | 0.0024 | 0.0093 | 0.0117 | 0.0103 | 0.0006 | 0 | 3 | 0.008 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5536 | 22044.309 | 44265.8095 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 171.8 | 0:240:120 | 0:00 | 6.8072 | 7 | 9.4806 | 57.4461 | 66.9267 | 60.6086 | 4.7372 | 22.4413 | 3 | 6.8072 | 33.7166 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5539 | 22220.835 | 44265.8116 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 175.7 | 0:240:120 | 0:00 | 5.7132 | 7 | 10.1538 | 29.4965 | 39.6503 | 35.8222 | 4.6647 | 21.7591 | 3 | 5.7132 | 18.9666 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5542 | 22322.079 | 44265.8127 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 180.1 | 0:240:120 | 0:00 | 4.8208 | 7 | 9.4767 | 10.0846 | 19.5613 | 13.2449 | 4.7369 | 22.4378 | 3 | 4.8208 | 12.611 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5545 | 22373.22 | 44265.8133 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 185.4 | 0:240:120 | 0:00 | 4.042 | 7 | 0.6568 | 8.1928 | 8.8496 | 8.5153 | 0.2561 | 0.0656 | 3 | 4.042 | 8.9227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5548 | 22400.859 | 44265.8136 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 191.1 | 0:240:120 | 0:00 | 3.4302 | 7 | 0.5293 | 6.4137 | 6.943 | 6.5919 | 0.2631 | 0.0692 | 3 | 3.4302 | 6.7449 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5551 | 22422.743 | 44265.8139 | Vista Coord | Tap | 150Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 196.9 | 0:240:120 | 0:00 | 2.9619 | 7 | 0.3257 | 4.6838 | 5.0095 | 4.8401 | 0.1296 | 0.0168 | 3 | 2.9619 | 5.3742 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5554 | 22542.021 | 44265.8153 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 220 | 0:240:120 | 0:00 | 10.0814 | 7 | 9.4707 | 95.343 | 104.8137 | 98.5009 | 4.7344 | 22.4147 | 3 | 10.0814 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5557 | 22857.859 | 44265.8189 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 220.7645 | 0:240:120 | 0:00 | 9.6947 | 7 | 7.7223 | 95.3437 | 103.066 | 97.892 | 3.8223 | 14.6101 | 3 | 9.6947 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5560 | 23152.847 | 44265.8223 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 223.6872 | 0:240:120 | 0:00 | 8.4467 | 7 | 9.3941 | 76.4787 | 85.8728 | 82.7758 | 4.6206 | 21.3501 | 3 | 8.4467 | 159.2083 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5563 | 23394.896 | 44265.8251 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 227.8518 | 0:240:120 | 0:00 | 7.1219 | 7 | 5.1791 | 61.7462 | 66.9253 | 65.6087 | 2.1095 | 4.45 | 3 | 7.1219 | 41.0907 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5566 | 23570.543 | 44265.8272 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 234.6795 | 0:240:120 | 0:00 | 5.6405 | 7 | 9.4732 | 29.0339 | 38.5071 | 35.3475 | 4.7307 | 22.3796 | 3 | 5.6405 | 18.3234 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5569 | 23661.073 | 44265.8282 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 240.658 | 0:240:120 | 0:00 | 4.7536 | 7 | 0.0521 | 10.0859 | 10.138 | 10.0964 | 0.0164 | 0.0003 | 3 | 4.7536 | 12.2398 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5572 | 23692.282 | 44265.8286 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 251.1641 | 0:240:120 | 0:00 | 3.7 | 7 | 0.525 | 7.4644 | 7.9894 | 7.6404 | 0.2604 | 0.0678 | 3 | 3.7 | 7.6437 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5575 | 23716.925 | 44265.8289 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 260.4789 | 0:240:120 | 0:00 | 3.0745 | 7 | 0.1152 | 5.2557 | 5.3709 | 5.3456 | 0.0396 | 0.0016 | 3 | 3.0745 | 5.6841 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5578 | 23735.087 | 44265.8291 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 269.8696 | 0:240:120 | 0:00 | 2.6146 | 7 | 0.1743 | 4.1507 | 4.325 | 4.2367 | 0.0762 | 0.0058 | 3 | 2.6146 | 4.487 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5581 | 23750.042 | 44265.8292 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 282.7616 | 0:240:120 | 0:00 | 2.1556 | 7 | 0.1762 | 3.1069 | 3.2831 | 3.2225 | 0.086 | 0.0074 | 3 | 2.1556 | 3.4521 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5584 | 23762.303 | 44265.8294 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 299.2627 | 0:240:120 | 0:00 | 1.7453 | 7 | 0.0573 | 2.5034 | 2.5607 | 2.5223 | 0.027 | 0.0007 | 3 | 1.7453 | 2.6373 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5587 | 23772.572 | 44265.8295 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 319.3971 | 0:240:120 | 0:00 | 1.402 | 7 | 0.0479 | 1.8917 | 1.9396 | 1.9241 | 0.0212 | 0.0005 | 3 | 1.402 | 2.0227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5590 | 23781.058 | 44265.8296 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 337.5042 | 0:240:120 | 0:00 | 1.1817 | 7 | 0.0338 | 1.5661 | 1.5999 | 1.588 | 0.016 | 0.0003 | 3 | 1.1817 | 1.6568 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5593 | 23788.625 | 44265.8297 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 362.2465 | 0:240:120 | 0:00 | 0.9633 | 7 | 0.0241 | 1.2539 | 1.278 | 1.2626 | 0.0115 | 0.0001 | 3 | 0.9633 | 1.3137 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5596 | 23795.293 | 44265.8298 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 392.0521 | 0:240:120 | 0:00 | 0.7785 | 7 | 0.0182 | 0.9834 | 1.0016 | 0.9946 | 0.0083 | 0.0001 | 3 | 0.7785 | 1.0375 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5599 | 23801.355 | 44265.8298 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 419.4817 | 0:240:120 | 0:00 | 0.6553 | 7 | 0.02 | 0.8175 | 0.8375 | 0.8265 | 0.0087 | 0.0001 | 3 | 0.6553 | 0.8603 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5602 | 23806.838 | 44265.8299 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 448.8308 | 0:240:120 | 0:00 | 0.5557 | 7 | 0.0079 | 0.6909 | 0.6988 | 0.6952 | 0.0033 | 0 | 3 | 0.5557 | 0.7207 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5605 | 23811.866 | 44265.83 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 482.7372 | 0:240:120 | 0:00 | 0.4684 | 7 | 0.0098 | 0.5749 | 0.5847 | 0.5795 | 0.0041 | 0 | 3 | 0.4684 | 0.6011 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5608 | 23816.483 | 44265.83 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 512.1666 | 0:240:120 | 0:00 | 0.4095 | 7 | 0.0143 | 0.4975 | 0.5118 | 0.5048 | 0.006 | 0 | 3 | 0.4095 | 0.5216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5611 | 23821.105 | 44265.8301 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 548.0684 | 0:240:120 | 0:00 | 0.3525 | 7 | 0.0074 | 0.4273 | 0.4347 | 0.4304 | 0.003 | 0 | 3 | 0.3525 | 0.4458 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5614 | 23825.185 | 44265.8301 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 587.0238 | 0:240:120 | 0:00 | 0.3039 | 7 | 0.0073 | 0.3661 | 0.3734 | 0.3697 | 0.0029 | 0 | 3 | 0.3039 | 0.3821 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5617 | 23829.688 | 44265.8302 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 652.0657 | 0:240:120 | 0:00 | 0.2438 | 7 | 0.0068 | 0.2916 | 0.2984 | 0.2952 | 0.0025 | 0 | 3 | 0.2438 | 0.3041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5620 | 23833.835 | 44265.8302 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 703.804 | 0:240:120 | 0:00 | 0.2086 | 7 | 0.006 | 0.2482 | 0.2542 | 0.2507 | 0.0023 | 0 | 3 | 0.2086 | 0.2589 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5623 | 23837.719 | 44265.8303 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 765.686 | 0:240:120 | 0:00 | 0.1763 | 7 | 0.0054 | 0.2098 | 0.2152 | 0.2117 | 0.0021 | 0 | 3 | 0.1763 | 0.2177 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5626 | 23841.247 | 44265.8303 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 846.11 | 0:240:120 | 0:00 | 0.145 | 7 | 0.0042 | 0.1718 | 0.176 | 0.1738 | 0.0016 | 0 | 3 | 0.145 | 0.1782 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5629 | 23844.773 | 44265.8303 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 909.083 | 0:240:120 | 0:00 | 0.1263 | 7 | 0.0038 | 0.1492 | 0.153 | 0.1511 | 0.0013 | 0 | 3 | 0.1263 | 0.1548 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5632 | 23848.087 | 44265.8304 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1021.559 | 0:240:120 | 0:00 | 0.1015 | 7 | 0.0037 | 0.1191 | 0.1228 | 0.1209 | 0.0013 | 0 | 3 | 0.1015 | 0.1237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5635 | 23851.437 | 44265.8304 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1120.528 | 0:240:120 | 0:00 | 0.0857 | 7 | 0.0031 | 0.1003 | 0.1034 | 0.1016 | 0.001 | 0 | 3 | 0.0857 | 0.104 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5638 | 23854.821 | 44265.8305 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1226.683 | 0:240:120 | 0:00 | 0.0728 | 7 | 0.0037 | 0.0847 | 0.0884 | 0.0864 | 0.0014 | 0 | 3 | 0.0728 | 0.088 | P | NP | 0-1-1-1-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5641 | 23858.193 | 44265.8305 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1354.119 | 0:240:120 | 0:00 | 0.0613 | 7 | 0.003 | 0.0699 | 0.0729 | 0.0718 | 0.0011 | 0 | 3 | 0.0613 | 0.0737 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5644 | 23861.761 | 44265.8305 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1519.885 | 0:240:120 | 0:00 | 0.0503 | 7 | 0.0016 | 0.0576 | 0.0592 | 0.0586 | 0.0006 | 0 | 3 | 0.0503 | 0.0604 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5647 | 23865.254 | 44265.8306 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1672.552 | 0:240:120 | 0:00 | 0.043 | 7 | 0.0026 | 0.0486 | 0.0512 | 0.0502 | 0.001 | 0 | 3 | 0.043 | 0.053 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5650 | 23868.512 | 44265.8306 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1854.007 | 0:240:120 | 0:00 | 0.0365 | 7 | 0.0025 | 0.0412 | 0.0437 | 0.0429 | 0.0008 | 0 | 3 | 0.0365 | 0.0465 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5653 | 23871.664 | 44265.8307 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2037.539 | 0:240:120 | 0:00 | 0.0316 | 7 | 0.0037 | 0.0352 | 0.0389 | 0.0372 | 0.0012 | 0 | 3 | 0.0316 | 0.0416 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5656 | 23875.006 | 44265.8307 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2200 | 0:240:120 | 0:00 | 0.0282 | 7 | 0.0035 | 0.0306 | 0.0341 | 0.0327 | 0.0011 | 0 | 3 | 0.0282 | 0.0382 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5659 | 23878.248 | 44265.8307 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2387.303 | 0:240:120 | 0:00 | 0.0252 | 7 | 0.0036 | 0.0272 | 0.0308 | 0.0291 | 0.0011 | 0 | 3 | 0.0252 | 0.0352 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5662 | 23881.487 | 44265.8308 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2784.706 | 0:240:120 | 0:00 | 0.0205 | 7 | 0.0039 | 0.0222 | 0.0261 | 0.024 | 0.0013 | 0 | 3 | 0.0205 | 0.0305 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5665 | 23884.995 | 44265.8308 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3180 | 0:240:120 | 0:00 | 0.0175 | 7 | 0.0033 | 0.0191 | 0.0224 | 0.0211 | 0.0015 | 0 | 3 | 0.0175 | 0.0275 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5668 | 23888.25 | 44265.8308 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3580 | 0:240:120 | 0:00 | 0.0154 | 7 | 0.0025 | 0.0173 | 0.0198 | 0.0191 | 0.0009 | 0 | 3 | 0.0154 | 0.0254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5671 | 23891.531 | 44265.8309 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3915.413 | 0:240:120 | 0:00 | 0.0141 | 7 | 0.0017 | 0.0165 | 0.0182 | 0.0173 | 0.0007 | 0 | 3 | 0.0141 | 0.0241 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5674 | 23894.595 | 44265.8309 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4388.925 | 0:240:120 | 0:00 | 0.0127 | 7 | 0.0032 | 0.0141 | 0.0173 | 0.0155 | 0.0012 | 0 | 3 | 0.0127 | 0.0227 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5677 | 23897.772 | 44265.831 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4945.927 | 0:240:120 | 0:00 | 0.0115 | 7 | 0.0042 | 0.0119 | 0.0161 | 0.0141 | 0.0017 | 0 | 3 | 0.0115 | 0.0215 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5680 | 23901.259 | 44265.831 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5556.466 | 0:240:120 | 0:00 | 0.0106 | 7 | 0.0043 | 0.0115 | 0.0158 | 0.0135 | 0.0016 | 0 | 3 | 0.0106 | 0.0206 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5683 | 23904.499 | 44265.831 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6567.2846 | 0:240:120 | 0:00 | 0.0096 | 7 | 0.0045 | 0.0105 | 0.015 | 0.0129 | 0.0017 | 0 | 3 | 0.0096 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5686 | 23907.728 | 44265.8311 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8443.6517 | 0:240:120 | 0:00 | 0.0086 | 7 | 0.0025 | 0.0111 | 0.0136 | 0.0117 | 0.0008 | 0 | 3 | 0.0086 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5689 | 23968.515 | 44265.8318 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 231.3 | 0:240:120 | 0:00 | 6.2926 | 7 | 9.4774 | 47.974 | 57.4514 | 51.1314 | 4.7318 | 22.3903 | 3 | 6.2926 | 25.3107 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5692 | 24115.746 | 44265.8335 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 237.7 | 0:240:120 | 0:00 | 5.157 | 7 | 9.4777 | 19.5564 | 29.0341 | 22.7178 | 4.7369 | 22.4381 | 3 | 5.157 | 14.6619 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5695 | 24186.174 | 44265.8343 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 245.9 | 0:240:120 | 0:00 | 4.1671 | 7 | 0.5251 | 8.5164 | 9.0415 | 8.7817 | 0.2396 | 0.0574 | 3 | 4.1671 | 9.4357 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5698 | 24213.686 | 44265.8346 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 255.8 | 0:240:120 | 0:00 | 3.3623 | 7 | 0.0939 | 6.4138 | 6.5077 | 6.4289 | 0.03 | 0.0009 | 3 | 3.3623 | 6.5319 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5701 | 24234.394 | 44265.8349 | Vista Coord | Tap | 200Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 265.2 | 0:240:120 | 0:00 | 2.8265 | 7 | 0.1761 | 4.4968 | 4.6729 | 4.6131 | 0.0865 | 0.0075 | 3 | 2.8265 | 5.0165 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5704 | 24353.173 | 44265.8362 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 275 | 0:240:120 | 0:00 | 10.0814 | 7 | 9.471 | 95.3434 | 104.8144 | 98.6224 | 4.6482 | 21.6056 | 3 | 10.0814 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5707 | 24670.975 | 44265.8399 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 275.55 | 0:240:120 | 0:00 | 9.8553 | 7 | 9.4717 | 95.3437 | 104.8154 | 98.5006 | 4.7329 | 22.4003 | 3 | 9.8553 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5710 | 24978.992 | 44265.8435 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 276.7402 | 0:240:120 | 0:00 | 9.3978 | 7 | 1.3124 | 94.0351 | 95.3475 | 95.0738 | 0.4721 | 0.2229 | 3 | 9.3978 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5713 | 25250.324 | 44265.8466 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 281.3844 | 0:240:120 | 0:00 | 7.9454 | 7 | 1.2418 | 76.3938 | 77.6356 | 76.7593 | 0.5571 | 0.3103 | 3 | 7.9454 | 80.6087 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5716 | 25465.558 | 44265.8491 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 287.3002 | 0:240:120 | 0:00 | 6.6202 | 7 | 0.0063 | 57.4468 | 57.4531 | 57.4507 | 0.0023 | 0 | 3 | 6.6202 | 30.2473 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5719 | 25622.248 | 44265.8509 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 294.5624 | 0:240:120 | 0:00 | 5.4762 | 7 | 9.4788 | 29.0272 | 38.506 | 32.1894 | 4.7368 | 22.4375 | 3 | 5.4762 | 16.9673 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5722 | 25712.6 | 44265.852 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 302.0083 | 0:240:120 | 0:00 | 4.6364 | 7 | 0.5238 | 9.5649 | 10.0887 | 9.866 | 0.2407 | 0.0579 | 3 | 4.6364 | 11.6198 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5725 | 25744.017 | 44265.8523 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 311.2571 | 0:240:120 | 0:00 | 3.8793 | 7 | 0.4054 | 7.9867 | 8.3921 | 8.1092 | 0.1801 | 0.0324 | 3 | 3.8793 | 8.293 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5728 | 25769.496 | 44265.8526 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 322.4617 | 0:240:120 | 0:00 | 3.223 | 7 | 0.0291 | 5.8913 | 5.9204 | 5.8986 | 0.0097 | 0.0001 | 3 | 3.223 | 6.1111 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5731 | 25788.739 | 44265.8528 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 337.2127 | 0:240:120 | 0:00 | 2.6188 | 7 | 0.1742 | 4.1501 | 4.3243 | 4.2655 | 0.0864 | 0.0075 | 3 | 2.6188 | 4.4972 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5734 | 25803.482 | 44265.853 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 355.2142 | 0:240:120 | 0:00 | 2.1141 | 7 | 0.1187 | 3.1049 | 3.2236 | 3.1413 | 0.0526 | 0.0028 | 3 | 2.1141 | 3.3653 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5737 | 25815.346 | 44265.8532 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 373.0111 | 0:240:120 | 0:00 | 1.7631 | 7 | 0.0867 | 2.5047 | 2.5914 | 2.5618 | 0.0424 | 0.0018 | 3 | 1.7631 | 2.6707 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5740 | 25825.662 | 44265.8533 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 395.3851 | 0:240:120 | 0:00 | 1.4467 | 7 | 0.0517 | 1.99 | 2.0417 | 2.0091 | 0.0242 | 0.0006 | 3 | 1.4467 | 2.0996 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5743 | 25834.279 | 44265.8534 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 424.3635 | 0:240:120 | 0:00 | 1.1612 | 7 | 0.0329 | 1.5328 | 1.5657 | 1.5542 | 0.0158 | 0.0003 | 3 | 1.1612 | 1.6237 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5746 | 25841.756 | 44265.8535 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 449.3489 | 0:240:120 | 0:00 | 0.9842 | 7 | 0.0238 | 1.2785 | 1.3023 | 1.2941 | 0.0112 | 0.0001 | 3 | 0.9842 | 1.3458 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5749 | 25848.45 | 44265.8535 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 483.2883 | 0:240:120 | 0:00 | 0.8074 | 7 | 0.0362 | 1.0184 | 1.0546 | 1.0361 | 0.015 | 0.0002 | 3 | 0.8074 | 1.08 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5752 | 25854.311 | 44265.8536 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 524.6791 | 0:240:120 | 0:00 | 0.6543 | 7 | 0.0217 | 0.8173 | 0.839 | 0.827 | 0.0086 | 0.0001 | 3 | 0.6543 | 0.8588 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5755 | 25859.998 | 44265.8537 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 573.7776 | 0:240:120 | 0:00 | 0.5268 | 7 | 0.0149 | 0.6489 | 0.6638 | 0.6556 | 0.0065 | 0 | 3 | 0.5268 | 0.6808 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5758 | 25864.602 | 44265.8537 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 624.8649 | 0:240:120 | 0:00 | 0.4325 | 7 | 0.0125 | 0.5261 | 0.5386 | 0.5319 | 0.0051 | 0 | 3 | 0.4325 | 0.5525 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5761 | 25869.097 | 44265.8538 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 669.2697 | 0:240:120 | 0:00 | 0.371 | 7 | 0.0106 | 0.4494 | 0.46 | 0.4546 | 0.0042 | 0 | 3 | 0.371 | 0.4703 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5764 | 25873.398 | 44265.8538 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 709.4021 | 0:240:120 | 0:00 | 0.3268 | 7 | 0.0076 | 0.3947 | 0.4023 | 0.3977 | 0.0031 | 0 | 3 | 0.3268 | 0.412 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5767 | 25877.619 | 44265.8539 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 771.7732 | 0:240:120 | 0:00 | 0.2732 | 7 | 0.0063 | 0.3282 | 0.3345 | 0.3314 | 0.0022 | 0 | 3 | 0.2732 | 0.342 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5770 | 25881.555 | 44265.8539 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 837.8711 | 0:240:120 | 0:00 | 0.2304 | 7 | 0.0074 | 0.2747 | 0.2821 | 0.2783 | 0.0026 | 0 | 3 | 0.2304 | 0.2868 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5773 | 25885.403 | 44265.854 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 913.775 | 0:240:120 | 0:00 | 0.1933 | 7 | 0.0041 | 0.231 | 0.2351 | 0.2329 | 0.0015 | 0 | 3 | 0.1933 | 0.2394 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5776 | 25889.11 | 44265.854 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 987.863 | 0:240:120 | 0:00 | 0.1656 | 7 | 0.0039 | 0.1969 | 0.2008 | 0.1983 | 0.0016 | 0 | 3 | 0.1656 | 0.2042 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5779 | 25892.849 | 44265.8541 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1090.524 | 0:240:120 | 0:00 | 0.1367 | 7 | 0.0028 | 0.162 | 0.1648 | 0.1635 | 0.001 | 0 | 3 | 0.1367 | 0.1677 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5782 | 25896.411 | 44265.8541 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1177.78 | 0:240:120 | 0:00 | 0.1181 | 7 | 0.0028 | 0.1403 | 0.1431 | 0.1412 | 0.001 | 0 | 3 | 0.1181 | 0.1444 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5785 | 25899.701 | 44265.8541 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1281.313 | 0:240:120 | 0:00 | 0.1009 | 7 | 0.0036 | 0.1181 | 0.1217 | 0.1193 | 0.0014 | 0 | 3 | 0.1009 | 0.1229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5788 | 25903.239 | 44265.8542 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1427.698 | 0:240:120 | 0:00 | 0.0828 | 7 | 0.0023 | 0.0965 | 0.0988 | 0.0976 | 0.0009 | 0 | 3 | 0.0828 | 0.1003 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5791 | 25906.494 | 44265.8542 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1610.788 | 0:240:120 | 0:00 | 0.0668 | 7 | 0.0039 | 0.0765 | 0.0804 | 0.0787 | 0.0012 | 0 | 3 | 0.0668 | 0.0805 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5794 | 25909.927 | 44265.8542 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1789.222 | 0:240:120 | 0:00 | 0.0557 | 7 | 0.0038 | 0.0635 | 0.0673 | 0.0657 | 0.0013 | 0 | 3 | 0.0557 | 0.0668 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5797 | 25913.259 | 44265.8543 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2018.674 | 0:240:120 | 0:00 | 0.0455 | 7 | 0.0028 | 0.052 | 0.0548 | 0.0535 | 0.001 | 0 | 3 | 0.0455 | 0.0555 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5800 | 25916.442 | 44265.8543 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2232.982 | 0:240:120 | 0:00 | 0.0387 | 7 | 0.0027 | 0.0436 | 0.0463 | 0.0452 | 0.0009 | 0 | 3 | 0.0387 | 0.0487 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5803 | 25919.774 | 44265.8544 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2477.76 | 0:240:120 | 0:00 | 0.0329 | 7 | 0.0034 | 0.036 | 0.0394 | 0.038 | 0.0013 | 0 | 3 | 0.0329 | 0.0429 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5806 | 25922.839 | 44265.8544 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2725 | 0:240:120 | 0:00 | 0.0286 | 7 | 0.0031 | 0.0316 | 0.0347 | 0.0331 | 0.0011 | 0 | 3 | 0.0286 | 0.0386 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5809 | 25926.102 | 44265.8544 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2957.027 | 0:240:120 | 0:00 | 0.0255 | 7 | 0.0029 | 0.028 | 0.0309 | 0.0297 | 0.0013 | 0 | 3 | 0.0255 | 0.0355 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5812 | 25929.171 | 44265.8545 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3257.371 | 0:240:120 | 0:00 | 0.0223 | 7 | 0.0036 | 0.0242 | 0.0278 | 0.0263 | 0.0013 | 0 | 3 | 0.0223 | 0.0323 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5815 | 25932.493 | 44265.8545 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3690.424 | 0:240:120 | 0:00 | 0.0191 | 7 | 0.0026 | 0.0216 | 0.0242 | 0.0228 | 0.001 | 0 | 3 | 0.0191 | 0.0291 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5818 | 25935.466 | 44265.8545 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4142.09 | 0:240:120 | 0:00 | 0.0167 | 7 | 0.0033 | 0.0188 | 0.0221 | 0.0206 | 0.0012 | 0 | 3 | 0.0167 | 0.0267 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5821 | 25938.588 | 44265.8546 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4615.307 | 0:240:120 | 0:00 | 0.0149 | 7 | 0.0025 | 0.0171 | 0.0196 | 0.0185 | 0.0009 | 0 | 3 | 0.0149 | 0.0249 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5824 | 25941.881 | 44265.8546 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5311.115 | 0:240:120 | 0:00 | 0.013 | 7 | 0.0026 | 0.0147 | 0.0173 | 0.016 | 0.0009 | 0 | 3 | 0.013 | 0.023 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5827 | 25944.999 | 44265.8547 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6143.693 | 0:240:120 | 0:00 | 0.0116 | 7 | 0.0036 | 0.0127 | 0.0163 | 0.0144 | 0.0013 | 0 | 3 | 0.0116 | 0.0216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5830 | 25948.249 | 44265.8547 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6866.981 | 0:240:120 | 0:00 | 0.0107 | 7 | 0.0046 | 0.0112 | 0.0158 | 0.0135 | 0.0018 | 0 | 3 | 0.0107 | 0.0207 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5833 | 25951.415 | 44265.8547 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8116.2053 | 0:240:120 | 0:00 | 0.0097 | 7 | 0.0041 | 0.0109 | 0.015 | 0.0126 | 0.0014 | 0 | 3 | 0.0097 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5836 | 25954.795 | 44265.8548 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10435.1211 | 0:240:120 | 0:00 | 0.0087 | 7 | 0.0038 | 0.0103 | 0.0141 | 0.0115 | 0.0012 | 0 | 3 | 0.0087 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5839 | 26005.994 | 44265.8554 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 290.9 | 0:240:120 | 0:00 | 6.0021 | 7 | 9.4722 | 38.5074 | 47.9796 | 44.4468 | 4.488 | 20.1423 | 3 | 6.0021 | 21.8265 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5842 | 26124.472 | 44265.8567 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 298.3 | 0:240:120 | 0:00 | 5.0221 | 7 | 0.0054 | 19.5565 | 19.5619 | 19.5597 | 0.0021 | 0 | 3 | 5.0221 | 13.7975 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5845 | 26175.527 | 44265.8573 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 306.6 | 0:240:120 | 0:00 | 4.2293 | 7 | 0.0702 | 8.9704 | 9.0406 | 9.0242 | 0.0247 | 0.0006 | 3 | 4.2293 | 9.7008 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5848 | 26203.583 | 44265.8576 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 316.9 | 0:240:120 | 0:00 | 3.521 | 7 | 0.0563 | 6.9396 | 6.9959 | 6.9542 | 0.0226 | 0.0005 | 3 | 3.521 | 7.0374 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5851 | 26225.664 | 44265.8579 | Vista Coord | Tap | 250Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 329.8 | 0:240:120 | 0:00 | 2.8941 | 7 | 0.1761 | 4.6698 | 4.8459 | 4.7295 | 0.0869 | 0.0076 | 3 | 2.8941 | 5.1932 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5854 | 26344.493 | 44265.8593 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 330 | 0:240:120 | 0:00 | 10.0814 | 7 | 9.469 | 95.3436 | 104.8126 | 100.5599 | 4.1877 | 17.5372 | 3 | 10.0814 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5857 | 26652.631 | 44265.8628 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 332.3551 | 0:240:120 | 0:00 | 9.3169 | 7 | 8.9352 | 86.4106 | 95.3458 | 92.4145 | 4.3963 | 19.3275 | 3 | 9.3169 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5860 | 26922.908 | 44265.866 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 338.3842 | 0:240:120 | 0:00 | 7.7879 | 7 | 0.0076 | 76.3919 | 76.3995 | 76.3962 | 0.0025 | 0 | 3 | 7.7879 | 69.0055 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5863 | 27136.256 | 44265.8684 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 345.972 | 0:240:120 | 0:00 | 6.4351 | 7 | 9.4742 | 47.9786 | 57.4528 | 54.2936 | 4.7345 | 22.4158 | 3 | 6.4351 | 27.304 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5866 | 27273.817 | 44265.87 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 357.9917 | 0:240:120 | 0:00 | 5.0191 | 7 | 4.8332 | 14.7291 | 19.5623 | 18.8381 | 1.5864 | 2.5166 | 3 | 5.0191 | 13.7792 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5869 | 27325.031 | 44265.8706 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 369.5329 | 0:240:120 | 0:00 | 4.1225 | 7 | 0.5255 | 8.5161 | 9.0416 | 8.734 | 0.2386 | 0.0569 | 3 | 4.1225 | 9.2498 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5872 | 27352.903 | 44265.8709 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 381.986 | 0:240:120 | 0:00 | 3.4401 | 7 | 0.5264 | 6.418 | 6.9444 | 6.7677 | 0.2614 | 0.0683 | 3 | 3.4401 | 6.7763 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
5875 | 27375.301 | 44265.8712 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 392.4404 | 0:240:120 | 0:00 | 3.0106 | 7 | 0.5267 | 4.8439 | 5.3706 | 5.1245 | 0.2336 | 0.0546 | 3 | 3.0106 | 5.5069 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5878 | 27393.034 | 44265.8714 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 409.563 | 0:240:120 | 0:00 | 2.4863 | 7 | 0.1783 | 3.9733 | 4.1516 | 4.0339 | 0.0878 | 0.0077 | 3 | 2.4863 | 4.1832 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5881 | 27407.507 | 44265.8716 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 425.8672 | 0:240:120 | 0:00 | 2.1217 | 7 | 0.176 | 3.1056 | 3.2816 | 3.165 | 0.0872 | 0.0076 | 3 | 2.1217 | 3.381 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5884 | 27419.454 | 44265.8717 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 449.911 | 0:240:120 | 0:00 | 1.7315 | 7 | 0.1048 | 2.4185 | 2.5233 | 2.4777 | 0.0446 | 0.002 | 3 | 1.7315 | 2.6113 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5887 | 27429.698 | 44265.8718 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 473.2882 | 0:240:120 | 0:00 | 1.4584 | 7 | 0.0505 | 1.9903 | 2.0408 | 2.0237 | 0.0249 | 0.0006 | 3 | 1.4584 | 2.1199 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5890 | 27438.544 | 44265.8719 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 502.2039 | 0:240:120 | 0:00 | 1.2107 | 7 | 0.067 | 1.5996 | 1.6666 | 1.6312 | 0.0266 | 0.0007 | 3 | 1.2107 | 1.7037 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5893 | 27446.261 | 44265.872 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 532.8873 | 0:240:120 | 0:00 | 1.0176 | 7 | 0.0239 | 1.3263 | 1.3502 | 1.3417 | 0.0115 | 0.0001 | 3 | 1.0176 | 1.3973 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5896 | 27452.904 | 44265.8721 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 571.3576 | 0:240:120 | 0:00 | 0.84 | 7 | 0.0292 | 1.0709 | 1.1001 | 1.0862 | 0.0117 | 0.0001 | 3 | 0.84 | 1.1281 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5899 | 27458.949 | 44265.8722 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 610.0622 | 0:240:120 | 0:00 | 0.7083 | 7 | 0.0271 | 0.8889 | 0.916 | 0.9017 | 0.0116 | 0.0001 | 3 | 0.7083 | 0.9359 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5902 | 27464.429 | 44265.8722 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 664.3923 | 0:240:120 | 0:00 | 0.5736 | 7 | 0.0174 | 0.7075 | 0.7249 | 0.7165 | 0.0072 | 0.0001 | 3 | 0.5736 | 0.7456 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5905 | 27469.628 | 44265.8723 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 704.2508 | 0:240:120 | 0:00 | 0.4996 | 7 | 0.014 | 0.614 | 0.628 | 0.62 | 0.0058 | 0 | 3 | 0.4996 | 0.6435 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5908 | 27474.313 | 44265.8724 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 752.7399 | 0:240:120 | 0:00 | 0.4287 | 7 | 0.0096 | 0.523 | 0.5326 | 0.5268 | 0.0041 | 0 | 3 | 0.4287 | 0.5474 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5911 | 27478.621 | 44265.8724 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 812.9814 | 0:240:120 | 0:00 | 0.3612 | 7 | 0.0089 | 0.4379 | 0.4468 | 0.4421 | 0.0036 | 0 | 3 | 0.3612 | 0.4573 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5914 | 27482.846 | 44265.8725 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 877.1312 | 0:240:120 | 0:00 | 0.3065 | 7 | 0.0063 | 0.3702 | 0.3765 | 0.3731 | 0.0026 | 0 | 3 | 0.3065 | 0.3854 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5917 | 27486.947 | 44265.8725 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 959.2297 | 0:240:120 | 0:00 | 0.2539 | 7 | 0.0053 | 0.3052 | 0.3105 | 0.3072 | 0.0021 | 0 | 3 | 0.2539 | 0.3171 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5920 | 27490.935 | 44265.8725 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1033.8438 | 0:240:120 | 0:00 | 0.2177 | 7 | 0.005 | 0.2606 | 0.2656 | 0.2627 | 0.0019 | 0 | 3 | 0.2177 | 0.2705 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5923 | 27494.613 | 44265.8726 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1084.965 | 0:240:120 | 0:00 | 0.1974 | 7 | 0.0047 | 0.2353 | 0.24 | 0.2374 | 0.0016 | 0 | 3 | 0.1974 | 0.2447 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5926 | 27498.536 | 44265.8726 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1185.359 | 0:240:120 | 0:00 | 0.1656 | 7 | 0.0035 | 0.1971 | 0.2006 | 0.1984 | 0.0016 | 0 | 3 | 0.1656 | 0.2043 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5929 | 27501.776 | 44265.8727 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1270.851 | 0:240:120 | 0:00 | 0.1446 | 7 | 0.0063 | 0.1696 | 0.1759 | 0.173 | 0.0024 | 0 | 3 | 0.1446 | 0.1777 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5932 | 27505.276 | 44265.8727 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1386.912 | 0:240:120 | 0:00 | 0.1224 | 7 | 0.0049 | 0.1437 | 0.1486 | 0.1458 | 0.0017 | 0 | 3 | 0.1224 | 0.1497 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5935 | 27508.87 | 44265.8728 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1535.78 | 0:240:120 | 0:00 | 0.1011 | 7 | 0.0045 | 0.1176 | 0.1221 | 0.1197 | 0.0017 | 0 | 3 | 0.1011 | 0.1231 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5938 | 27512.254 | 44265.8728 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1679.527 | 0:240:120 | 0:00 | 0.0858 | 7 | 0.0027 | 0.1008 | 0.1035 | 0.1016 | 0.0011 | 0 | 3 | 0.0858 | 0.1041 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5941 | 27515.611 | 44265.8728 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1831.004 | 0:240:120 | 0:00 | 0.0735 | 7 | 0.0026 | 0.085 | 0.0876 | 0.0868 | 0.0009 | 0 | 3 | 0.0735 | 0.0888 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5944 | 27518.913 | 44265.8729 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1996.143 | 0:240:120 | 0:00 | 0.0631 | 7 | 0.0035 | 0.0729 | 0.0764 | 0.0747 | 0.0011 | 0 | 3 | 0.0631 | 0.076 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
5947 | 27522.204 | 44265.8729 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2226.561 | 0:240:120 | 0:00 | 0.0524 | 7 | 0.0026 | 0.0604 | 0.063 | 0.0617 | 0.0009 | 0 | 3 | 0.0524 | 0.0628 | P | NP | 1-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
5950 | 27525.482 | 44265.8729 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2475.836 | 0:240:120 | 0:00 | 0.0439 | 7 | 0.0023 | 0.0494 | 0.0517 | 0.0508 | 0.0009 | 0 | 3 | 0.0439 | 0.0539 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5953 | 27528.997 | 44265.873 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2767.377 | 0:240:120 | 0:00 | 0.0368 | 7 | 0.0023 | 0.0415 | 0.0438 | 0.0429 | 0.0009 | 0 | 3 | 0.0368 | 0.0468 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5956 | 27532.756 | 44265.873 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3007.567 | 0:240:120 | 0:00 | 0.0324 | 7 | 0.0027 | 0.0363 | 0.039 | 0.0379 | 0.001 | 0 | 3 | 0.0324 | 0.0424 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5959 | 27536.118 | 44265.8731 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3295.921 | 0:240:120 | 0:00 | 0.0283 | 7 | 0.0018 | 0.0316 | 0.0334 | 0.0327 | 0.0007 | 0 | 3 | 0.0283 | 0.0383 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5962 | 27539.534 | 44265.8731 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3645.902 | 0:240:120 | 0:00 | 0.0245 | 7 | 0.0033 | 0.0266 | 0.0299 | 0.0284 | 0.0011 | 0 | 3 | 0.0245 | 0.0345 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5965 | 27543.11 | 44265.8732 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4020.477 | 0:240:120 | 0:00 | 0.0215 | 7 | 0.0025 | 0.0238 | 0.0263 | 0.0253 | 0.0007 | 0 | 3 | 0.0215 | 0.0315 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5968 | 27546.436 | 44265.8732 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4419.719 | 0:240:120 | 0:00 | 0.0191 | 7 | 0.0039 | 0.0205 | 0.0244 | 0.0227 | 0.0014 | 0 | 3 | 0.0191 | 0.0291 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5971 | 27549.891 | 44265.8732 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4894.12 | 0:240:120 | 0:00 | 0.017 | 7 | 0.0033 | 0.0185 | 0.0218 | 0.0206 | 0.0015 | 0 | 3 | 0.017 | 0.027 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5974 | 27553.136 | 44265.8733 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5363.351 | 0:240:120 | 0:00 | 0.0154 | 7 | 0.0023 | 0.0179 | 0.0202 | 0.0191 | 0.0009 | 0 | 3 | 0.0154 | 0.0254 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5977 | 27556.23 | 44265.8733 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5914.375 | 0:240:120 | 0:00 | 0.014 | 7 | 0.002 | 0.0168 | 0.0188 | 0.0175 | 0.0006 | 0 | 3 | 0.014 | 0.024 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5980 | 27559.321 | 44265.8733 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6522.01 | 0:240:120 | 0:00 | 0.0128 | 7 | 0.0029 | 0.0145 | 0.0174 | 0.0158 | 0.0011 | 0 | 3 | 0.0128 | 0.0228 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5983 | 27562.632 | 44265.8734 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7274.854 | 0:240:120 | 0:00 | 0.0117 | 7 | 0.0044 | 0.0119 | 0.0163 | 0.0142 | 0.0016 | 0 | 3 | 0.0117 | 0.0217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5986 | 27566.061 | 44265.8734 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7922.73 | 0:240:120 | 0:00 | 0.011 | 7 | 0.0052 | 0.0111 | 0.0163 | 0.0136 | 0.0018 | 0 | 3 | 0.011 | 0.021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5989 | 27569.252 | 44265.8735 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8637.286 | 0:240:120 | 0:00 | 0.0104 | 7 | 0.0042 | 0.011 | 0.0152 | 0.0132 | 0.0016 | 0 | 3 | 0.0104 | 0.0204 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5992 | 27572.436 | 44265.8735 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10208.5598 | 0:240:120 | 0:00 | 0.0095 | 7 | 0.0029 | 0.011 | 0.0139 | 0.0124 | 0.0011 | 0 | 3 | 0.0095 | 0.016 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
5995 | 27614.141 | 44265.874 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 352 | 0:240:120 | 0:00 | 5.6427 | 7 | 9.4741 | 29.034 | 38.5081 | 35.3416 | 4.7305 | 22.3776 | 3 | 5.6427 | 18.3428 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
5998 | 27704.31 | 44265.875 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 363.8 | 0:240:120 | 0:00 | 4.527 | 7 | 0.4195 | 9.5609 | 9.9804 | 9.6922 | 0.1927 | 0.0371 | 3 | 4.527 | 11.0701 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6001 | 27735.194 | 44265.8754 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 375.8 | 0:240:120 | 0:00 | 3.7508 | 7 | 0.526 | 7.4667 | 7.9927 | 7.7981 | 0.2501 | 0.0625 | 3 | 3.7508 | 7.8232 | P | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6004 | 27760.027 | 44265.8757 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 387.2 | 0:240:120 | 0:00 | 3.2129 | 7 | 0.3068 | 5.5913 | 5.8981 | 5.8157 | 0.1203 | 0.0145 | 3 | 3.2129 | 6.0814 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6007 | 27779.329 | 44265.8759 | Vista Coord | Tap | 300Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 401 | 0:240:120 | 0:00 | 2.726 | 7 | 0.1751 | 4.3229 | 4.498 | 4.4385 | 0.0859 | 0.0074 | 3 | 2.726 | 4.7609 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6010 | 27897.576 | 44265.8773 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 385 | 0:240:120 | 0:00 | 10.0814 | 7 | 9.4722 | 95.3427 | 104.8149 | 101.6378 | 4.7198 | 22.2768 | 3 | 10.0814 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6013 | 28205.804 | 44265.8808 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 388.52 | 0:240:120 | 0:00 | 9.1216 | 7 | 9.4774 | 85.8707 | 95.3481 | 92.1876 | 4.7364 | 22.4338 | 3 | 9.1216 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6016 | 28485.355 | 44265.8841 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 393.2984 | 0:240:120 | 0:00 | 8.0689 | 7 | 9.4771 | 76.3975 | 85.8746 | 79.5889 | 4.7129 | 22.2112 | 3 | 8.0689 | 92.3708 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6019 | 28727.049 | 44265.8869 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 401.6122 | 0:240:120 | 0:00 | 6.703 | 7 | 9.4742 | 57.4469 | 66.9211 | 60.5974 | 4.7206 | 22.284 | 3 | 6.703 | 31.7144 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6022 | 28902.723 | 44265.8889 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 410.927 | 0:240:120 | 0:00 | 5.6169 | 7 | 9.4735 | 29.0343 | 38.5078 | 35.3481 | 4.7347 | 22.4173 | 3 | 5.6169 | 18.1209 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6025 | 28992.542 | 44265.8899 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 426.591 | 0:240:120 | 0:00 | 4.3887 | 7 | 0.5243 | 9.0417 | 9.566 | 9.3895 | 0.2604 | 0.0678 | 3 | 4.3887 | 10.4121 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6028 | 29023.16 | 44265.8903 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 436.1764 | 0:240:120 | 0:00 | 3.8587 | 7 | 0.5263 | 7.9874 | 8.5137 | 8.1619 | 0.2578 | 0.0665 | 3 | 3.8587 | 8.2163 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6031 | 29049.489 | 44265.8906 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 450.4863 | 0:240:120 | 0:00 | 3.2572 | 7 | 0.5246 | 5.8938 | 6.4184 | 6.1196 | 0.2354 | 0.0554 | 3 | 3.2572 | 6.2126 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6034 | 29069.928 | 44265.8908 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 466.2273 | 0:240:120 | 0:00 | 2.7684 | 7 | 0.178 | 4.495 | 4.673 | 4.5551 | 0.0878 | 0.0077 | 3 | 2.7684 | 4.8678 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6037 | 29085.862 | 44265.891 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 488.0634 | 0:240:120 | 0:00 | 2.2773 | 7 | 0.1743 | 3.4549 | 3.6292 | 3.5703 | 0.086 | 0.0074 | 3 | 2.2773 | 3.7128 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6040 | 29098.932 | 44265.8912 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 510.9225 | 0:240:120 | 0:00 | 1.9084 | 7 | 0.0883 | 2.7617 | 2.85 | 2.8201 | 0.0428 | 0.0018 | 3 | 1.9084 | 2.9499 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6043 | 29109.833 | 44265.8913 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 537.0827 | 0:240:120 | 0:00 | 1.5993 | 7 | 0.0517 | 2.1938 | 2.2455 | 2.2283 | 0.0256 | 0.0007 | 3 | 1.5993 | 2.369 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6046 | 29119.189 | 44265.8914 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 562.2375 | 0:240:120 | 0:00 | 1.3759 | 7 | 0.1017 | 1.8369 | 1.9386 | 1.8874 | 0.0438 | 0.0019 | 3 | 1.3759 | 1.9783 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6049 | 29127.499 | 44265.8915 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 601.8782 | 0:240:120 | 0:00 | 1.1174 | 7 | 0.0344 | 1.4656 | 1.5 | 1.4876 | 0.0158 | 0.0002 | 3 | 1.1174 | 1.5538 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6052 | 29135.015 | 44265.8916 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 642.9841 | 0:240:120 | 0:00 | 0.9262 | 7 | 0.048 | 1.1831 | 1.2311 | 1.2066 | 0.0204 | 0.0004 | 3 | 0.9262 | 1.2573 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6055 | 29141.559 | 44265.8917 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 682.264 | 0:240:120 | 0:00 | 0.7899 | 7 | 0.0231 | 1.0005 | 1.0236 | 1.0131 | 0.0091 | 0.0001 | 3 | 0.7899 | 1.0543 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6058 | 29147.485 | 44265.8917 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 719.4385 | 0:240:120 | 0:00 | 0.6892 | 7 | 0.0268 | 0.8622 | 0.889 | 0.8749 | 0.0113 | 0.0001 | 3 | 0.6892 | 0.9086 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6061 | 29152.909 | 44265.8918 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 759.4279 | 0:240:120 | 0:00 | 0.6028 | 7 | 0.0225 | 0.7417 | 0.7642 | 0.7548 | 0.0098 | 0.0001 | 3 | 0.6028 | 0.7862 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6064 | 29158.143 | 44265.8918 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 818.4935 | 0:240:120 | 0:00 | 0.5041 | 7 | 0.0142 | 0.6206 | 0.6348 | 0.627 | 0.0058 | 0 | 3 | 0.5041 | 0.6497 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6067 | 29163.103 | 44265.8919 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 866.69 | 0:240:120 | 0:00 | 0.4418 | 7 | 0.0115 | 0.5384 | 0.5499 | 0.5446 | 0.0048 | 0 | 3 | 0.4418 | 0.565 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6070 | 29168.336 | 44265.892 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 934.098 | 0:240:120 | 0:00 | 0.3735 | 7 | 0.0127 | 0.4524 | 0.4651 | 0.4585 | 0.0054 | 0 | 3 | 0.3735 | 0.4737 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6073 | 29172.842 | 44265.892 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 997.3678 | 0:240:120 | 0:00 | 0.3238 | 7 | 0.0054 | 0.3921 | 0.3975 | 0.3944 | 0.0023 | 0 | 3 | 0.3238 | 0.4081 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6076 | 29177.064 | 44265.8921 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1051.7111 | 0:240:120 | 0:00 | 0.2891 | 7 | 0.0081 | 0.3471 | 0.3552 | 0.3508 | 0.0033 | 0 | 3 | 0.2891 | 0.3628 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6079 | 29181.046 | 44265.8921 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1133 | 0:240:120 | 0:00 | 0.2475 | 7 | 0.0064 | 0.2968 | 0.3032 | 0.2995 | 0.0029 | 0 | 3 | 0.2475 | 0.3088 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6082 | 29185.279 | 44265.8922 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1205 | 0:240:120 | 0:00 | 0.2181 | 7 | 0.0038 | 0.2616 | 0.2654 | 0.2629 | 0.0017 | 0 | 3 | 0.2181 | 0.271 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6085 | 29189.089 | 44265.8922 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1298.164 | 0:240:120 | 0:00 | 0.1877 | 7 | 0.0081 | 0.2214 | 0.2295 | 0.225 | 0.0027 | 0 | 3 | 0.1877 | 0.2323 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6088 | 29192.688 | 44265.8922 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1404.965 | 0:240:120 | 0:00 | 0.1606 | 7 | 0.0079 | 0.189 | 0.1969 | 0.1918 | 0.0026 | 0 | 3 | 0.1606 | 0.1979 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6091 | 29196.327 | 44265.8923 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1525.306 | 0:240:120 | 0:00 | 0.1369 | 7 | 0.0052 | 0.1617 | 0.1669 | 0.1637 | 0.0016 | 0 | 3 | 0.1369 | 0.168 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6094 | 29199.832 | 44265.8923 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1681.997 | 0:240:120 | 0:00 | 0.1137 | 7 | 0.0038 | 0.1327 | 0.1365 | 0.1344 | 0.0014 | 0 | 3 | 0.1137 | 0.1389 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6097 | 29203.418 | 44265.8924 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1839.412 | 0:240:120 | 0:00 | 0.0963 | 7 | 0.0026 | 0.1129 | 0.1155 | 0.1139 | 0.0008 | 0 | 3 | 0.0963 | 0.1172 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6100 | 29206.847 | 44265.8924 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1993 | 0:240:120 | 0:00 | 0.0832 | 7 | 0.0041 | 0.0966 | 0.1007 | 0.0984 | 0.0012 | 0 | 3 | 0.0832 | 0.1009 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6103 | 29210.382 | 44265.8924 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2177.052 | 0:240:120 | 0:00 | 0.071 | 7 | 0.0011 | 0.0825 | 0.0836 | 0.0834 | 0.0004 | 0 | 3 | 0.071 | 0.0858 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6106 | 29213.804 | 44265.8925 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2395.705 | 0:240:120 | 0:00 | 0.0601 | 7 | 0.0019 | 0.0693 | 0.0712 | 0.0703 | 0.0006 | 0 | 3 | 0.0601 | 0.0723 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6109 | 29216.962 | 44265.8925 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2639.063 | 0:240:120 | 0:00 | 0.051 | 7 | 0.0037 | 0.0579 | 0.0616 | 0.0598 | 0.0012 | 0 | 3 | 0.051 | 0.0612 | P | NP | 1-1-1-1-1-0-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6112 | 29220.178 | 44265.8926 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2874.064 | 0:240:120 | 0:00 | 0.0443 | 7 | 0.003 | 0.0496 | 0.0526 | 0.0515 | 0.0012 | 0 | 3 | 0.0443 | 0.0543 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6115 | 29223.471 | 44265.8926 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3123.486 | 0:240:120 | 0:00 | 0.0388 | 7 | 0.0023 | 0.0438 | 0.0461 | 0.045 | 0.0007 | 0 | 3 | 0.0388 | 0.0488 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6118 | 29226.723 | 44265.8926 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3391.024 | 0:240:120 | 0:00 | 0.0341 | 7 | 0.0037 | 0.0377 | 0.0414 | 0.0398 | 0.0011 | 0 | 3 | 0.0341 | 0.0441 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6121 | 29229.961 | 44265.8927 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3628.249 | 0:240:120 | 0:00 | 0.0308 | 7 | 0.0028 | 0.0342 | 0.037 | 0.036 | 0.0011 | 0 | 3 | 0.0308 | 0.0408 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6124 | 29233.382 | 44265.8927 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3947.226 | 0:240:120 | 0:00 | 0.0272 | 7 | 0.0034 | 0.0297 | 0.0331 | 0.0316 | 0.0011 | 0 | 3 | 0.0272 | 0.0372 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6127 | 29236.701 | 44265.8928 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4240.972 | 0:240:120 | 0:00 | 0.0246 | 7 | 0.0025 | 0.027 | 0.0295 | 0.0287 | 0.0008 | 0 | 3 | 0.0246 | 0.0346 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6130 | 29239.693 | 44265.8928 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4618.619 | 0:240:120 | 0:00 | 0.022 | 7 | 0.0036 | 0.024 | 0.0276 | 0.0258 | 0.0014 | 0 | 3 | 0.022 | 0.032 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6133 | 29242.933 | 44265.8928 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4967.494 | 0:240:120 | 0:00 | 0.02 | 7 | 0.0038 | 0.0211 | 0.0249 | 0.0236 | 0.0012 | 0 | 3 | 0.02 | 0.03 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6136 | 29246.141 | 44265.8929 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5494.913 | 0:240:120 | 0:00 | 0.0177 | 7 | 0.0031 | 0.0192 | 0.0223 | 0.0213 | 0.0013 | 0 | 3 | 0.0177 | 0.0277 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6139 | 29249.205 | 44265.8929 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5950 | 0:240:120 | 0:00 | 0.0162 | 7 | 0.0032 | 0.0183 | 0.0215 | 0.02 | 0.001 | 0 | 3 | 0.0162 | 0.0262 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6142 | 29252.636 | 44265.8929 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6564.728 | 0:240:120 | 0:00 | 0.0147 | 7 | 0.0017 | 0.0174 | 0.0191 | 0.0183 | 0.0005 | 0 | 3 | 0.0147 | 0.0247 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6145 | 29255.913 | 44265.893 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7112.209 | 0:240:120 | 0:00 | 0.0136 | 7 | 0.0022 | 0.0155 | 0.0177 | 0.0167 | 0.0008 | 0 | 3 | 0.0136 | 0.0236 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6148 | 29259.371 | 44265.893 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7818.389 | 0:240:120 | 0:00 | 0.0125 | 7 | 0.0036 | 0.0132 | 0.0168 | 0.0154 | 0.0012 | 0 | 3 | 0.0125 | 0.0225 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6151 | 29262.815 | 44265.8931 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8590 | 0:240:120 | 0:00 | 0.0116 | 7 | 0.004 | 0.012 | 0.016 | 0.0143 | 0.0014 | 0 | 3 | 0.0116 | 0.0216 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6154 | 29266.019 | 44265.8931 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9275 | 0:240:120 | 0:00 | 0.011 | 7 | 0.0048 | 0.011 | 0.0158 | 0.0136 | 0.0017 | 0 | 3 | 0.011 | 0.021 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6157 | 29269.306 | 44265.8931 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10236.008 | 0:240:120 | 0:00 | 0.0103 | 7 | 0.0041 | 0.0116 | 0.0157 | 0.0133 | 0.0016 | 0 | 3 | 0.0103 | 0.0203 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6160 | 29320.371 | 44265.8937 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 406.3 | 0:240:120 | 0:00 | 6.1113 | 7 | 9.4728 | 38.5087 | 47.9815 | 44.8219 | 4.733 | 22.4014 | 3 | 6.1113 | 23.0546 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6163 | 29438.9 | 44265.8951 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 418.8 | 0:240:120 | 0:00 | 4.9293 | 7 | 9.4723 | 10.0892 | 19.5615 | 16.4025 | 4.7342 | 22.4126 | 3 | 4.9293 | 13.236 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6166 | 29490.193 | 44265.8957 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 431.4 | 0:240:120 | 0:00 | 4.1071 | 7 | 0.5294 | 8.5119 | 9.0413 | 8.6987 | 0.2576 | 0.0664 | 3 | 4.1071 | 9.1865 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6169 | 29518.9 | 44265.896 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 443.3 | 0:240:120 | 0:00 | 3.536 | 7 | 0.5277 | 6.9399 | 7.4676 | 7.1176 | 0.2622 | 0.0687 | 3 | 3.536 | 7.0867 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6172 | 29542.571 | 44265.8963 | Vista Coord | Tap | 350Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 458.4 | 0:240:120 | 0:00 | 2.9935 | 7 | 0.5289 | 4.841 | 5.3699 | 5.0186 | 0.2633 | 0.0693 | 3 | 2.9935 | 5.46 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6175 | 29662.613 | 44265.8977 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 440 | 0:240:120 | 0:00 | 10.0814 | 7 | 9.4718 | 95.3432 | 104.815 | 101.6566 | 4.7341 | 22.4113 | 3 | 10.0814 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6178 | 29970.698 | 44265.9012 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 443.9094 | 0:240:120 | 0:00 | 9.1463 | 7 | 9.474 | 85.8708 | 95.3448 | 92.1864 | 4.7363 | 22.4322 | 3 | 9.1463 | 9999999 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6181 | 30250.389 | 44265.9045 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 448.7835 | 0:240:120 | 0:00 | 8.1907 | 7 | 9.4734 | 76.3992 | 85.8726 | 82.7138 | 4.7356 | 22.4255 | 3 | 8.1907 | 107.3554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6184 | 30485.3 | 44265.9072 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 459.4898 | 0:240:120 | 0:00 | 6.6427 | 7 | 2.7893 | 57.1809 | 59.9702 | 58.001 | 1.0434 | 1.0887 | 3 | 6.6427 | 30.636 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6187 | 30644.758 | 44265.909 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 469.0378 | 0:240:120 | 0:00 | 5.6686 | 7 | 9.4722 | 29.0347 | 38.5069 | 35.3478 | 4.7346 | 22.4167 | 3 | 5.6686 | 18.5685 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6190 | 30734.337 | 44265.9101 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 489.4285 | 0:240:120 | 0:00 | 4.2876 | 7 | 0.5277 | 9.0374 | 9.5651 | 9.2147 | 0.2622 | 0.0688 | 3 | 4.2876 | 9.9554 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6193 | 30763.831 | 44265.9104 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 506.5434 | 0:240:120 | 0:00 | 3.5391 | 7 | 0.5276 | 6.9402 | 7.4678 | 7.1185 | 0.2611 | 0.0682 | 3 | 3.5391 | 7.0969 | NP | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6196 | 30786.543 | 44265.9107 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 526.2675 | 0:240:120 | 0:00 | 2.9304 | 7 | 0.1754 | 4.6699 | 4.8453 | 4.7863 | 0.0861 | 0.0074 | 3 | 2.9304 | 5.2896 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6199 | 30803.49 | 44265.9109 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 539.7579 | 0:240:120 | 0:00 | 2.6142 | 7 | 0.1768 | 4.1492 | 4.326 | 4.2657 | 0.0868 | 0.0075 | 3 | 2.6142 | 4.4861 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6202 | 30818.857 | 44265.9111 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 564.6333 | 0:240:120 | 0:00 | 2.169 | 7 | 0.2959 | 3.1072 | 3.4031 | 3.261 | 0.1254 | 0.0157 | 3 | 2.169 | 3.4804 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6205 | 30831.335 | 44265.9112 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 598.0601 | 0:240:120 | 0:00 | 1.7502 | 7 | 0.1434 | 2.4476 | 2.591 | 2.5153 | 0.0611 | 0.0037 | 3 | 1.7502 | 2.6463 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6208 | 30841.611 | 44265.9113 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 629.1428 | 0:240:120 | 0:00 | 1.4729 | 7 | 0.1029 | 1.9896 | 2.0925 | 2.0405 | 0.0442 | 0.0019 | 3 | 1.4729 | 2.1451 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6211 | 30850.487 | 44265.9114 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 666.0412 | 0:240:120 | 0:00 | 1.2304 | 7 | 0.0334 | 1.6336 | 1.667 | 1.6553 | 0.016 | 0.0003 | 3 | 1.2304 | 1.736 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6214 | 30858.617 | 44265.9115 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 704.9735 | 0:240:120 | 0:00 | 1.0406 | 7 | 0.0277 | 1.3507 | 1.3784 | 1.3669 | 0.0119 | 0.0001 | 3 | 1.0406 | 1.433 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6217 | 30866.075 | 44265.9116 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 750.6477 | 0:240:120 | 0:00 | 0.874 | 7 | 0.0356 | 1.1072 | 1.1428 | 1.1242 | 0.015 | 0.0002 | 3 | 0.874 | 1.1787 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6220 | 30872.5 | 44265.9117 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 796.2438 | 0:240:120 | 0:00 | 0.748 | 7 | 0.0275 | 0.9425 | 0.97 | 0.9558 | 0.0114 | 0.0001 | 3 | 0.748 | 0.9933 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6223 | 30878.417 | 44265.9118 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 844.0234 | 0:240:120 | 0:00 | 0.6456 | 7 | 0.0218 | 0.8054 | 0.8272 | 0.8156 | 0.0089 | 0.0001 | 3 | 0.6456 | 0.8465 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6226 | 30884.014 | 44265.9118 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 907.7981 | 0:240:120 | 0:00 | 0.541 | 7 | 0.0161 | 0.6647 | 0.6808 | 0.6726 | 0.0067 | 0 | 3 | 0.541 | 0.7004 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6229 | 30889.166 | 44265.9119 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 984.555 | 0:240:120 | 0:00 | 0.4479 | 7 | 0.015 | 0.5479 | 0.5629 | 0.5551 | 0.006 | 0 | 3 | 0.4479 | 0.5732 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6232 | 30893.719 | 44265.9119 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1057.848 | 0:240:120 | 0:00 | 0.3811 | 7 | 0.0079 | 0.4655 | 0.4734 | 0.4686 | 0.0035 | 0 | 3 | 0.3811 | 0.4838 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6235 | 30898.068 | 44265.912 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1142.526 | 0:240:120 | 0:00 | 0.3222 | 7 | 0.0093 | 0.3885 | 0.3978 | 0.3934 | 0.0036 | 0 | 3 | 0.3222 | 0.406 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6238 | 30902.079 | 44265.912 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1228.8573 | 0:240:120 | 0:00 | 0.276 | 7 | 0.0105 | 0.3272 | 0.3377 | 0.3328 | 0.0041 | 0 | 3 | 0.276 | 0.3457 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6241 | 30906.485 | 44265.9121 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1320.3366 | 0:240:120 | 0:00 | 0.2377 | 7 | 0.0085 | 0.2818 | 0.2903 | 0.2857 | 0.0031 | 0 | 3 | 0.2377 | 0.2962 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6244 | 30910.537 | 44265.9121 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1446.9543 | 0:240:120 | 0:00 | 0.1974 | 7 | 0.0093 | 0.2312 | 0.2405 | 0.2364 | 0.0027 | 0 | 3 | 0.1974 | 0.2446 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6247 | 30914.347 | 44265.9122 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1583.091 | 0:240:120 | 0:00 | 0.1651 | 7 | 0.0049 | 0.1945 | 0.1994 | 0.1969 | 0.0017 | 0 | 3 | 0.1651 | 0.2036 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6250 | 30917.957 | 44265.9122 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1742.142 | 0:240:120 | 0:00 | 0.1371 | 7 | 0.0041 | 0.1619 | 0.166 | 0.1633 | 0.0016 | 0 | 3 | 0.1371 | 0.1682 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6253 | 30921.373 | 44265.9123 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 1917.172 | 0:240:120 | 0:00 | 0.1143 | 7 | 0.0039 | 0.1333 | 0.1372 | 0.1351 | 0.0016 | 0 | 3 | 0.1143 | 0.1397 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6256 | 30924.833 | 44265.9123 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2077.112 | 0:240:120 | 0:00 | 0.0985 | 7 | 0.0027 | 0.1155 | 0.1182 | 0.1163 | 0.0011 | 0 | 3 | 0.0985 | 0.1199 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6259 | 30928.143 | 44265.9123 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2275.558 | 0:240:120 | 0:00 | 0.0833 | 7 | 0.0025 | 0.0971 | 0.0996 | 0.0983 | 0.0008 | 0 | 3 | 0.0833 | 0.1011 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6262 | 30931.303 | 44265.9124 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2520.837 | 0:240:120 | 0:00 | 0.0694 | 7 | 0.0034 | 0.0796 | 0.083 | 0.0813 | 0.0012 | 0 | 3 | 0.0694 | 0.0838 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6265 | 30934.602 | 44265.9124 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 2800.039 | 0:240:120 | 0:00 | 0.0578 | 7 | 0.003 | 0.0665 | 0.0695 | 0.068 | 0.0012 | 0 | 3 | 0.0578 | 0.0695 | P | NP | 0-1-1-1-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6268 | 30937.844 | 44265.9124 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3090.99 | 0:240:120 | 0:00 | 0.049 | 7 | 0.0025 | 0.0555 | 0.058 | 0.0568 | 0.0009 | 0 | 3 | 0.049 | 0.059 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6271 | 30941.186 | 44265.9125 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3447.866 | 0:240:120 | 0:00 | 0.041 | 7 | 0.0026 | 0.0457 | 0.0483 | 0.0475 | 0.0009 | 0 | 3 | 0.041 | 0.051 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6274 | 30944.712 | 44265.9125 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 3790.322 | 0:240:120 | 0:00 | 0.0353 | 7 | 0.003 | 0.0399 | 0.0429 | 0.0415 | 0.001 | 0 | 3 | 0.0353 | 0.0453 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6277 | 30948.023 | 44265.9126 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4227.941 | 0:240:120 | 0:00 | 0.0299 | 7 | 0.0027 | 0.0331 | 0.0358 | 0.0348 | 0.0011 | 0 | 3 | 0.0299 | 0.0399 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6280 | 30951.301 | 44265.9126 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 4730.832 | 0:240:120 | 0:00 | 0.0255 | 7 | 0.0033 | 0.0278 | 0.0311 | 0.0296 | 0.0012 | 0 | 3 | 0.0255 | 0.0355 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6283 | 30954.625 | 44265.9126 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 5348.911 | 0:240:120 | 0:00 | 0.0216 | 7 | 0.0031 | 0.0237 | 0.0268 | 0.0253 | 0.0011 | 0 | 3 | 0.0216 | 0.0316 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6286 | 30957.71 | 44265.9127 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 6066.652 | 0:240:120 | 0:00 | 0.0185 | 7 | 0.003 | 0.0203 | 0.0233 | 0.0222 | 0.0014 | 0 | 3 | 0.0185 | 0.0285 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6289 | 30960.799 | 44265.9127 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7010.799 | 0:240:120 | 0:00 | 0.0157 | 7 | 0.0016 | 0.0185 | 0.0201 | 0.0191 | 0.0006 | 0 | 3 | 0.0157 | 0.0257 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6292 | 30963.824 | 44265.9127 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 7731.238 | 0:240:120 | 0:00 | 0.0142 | 7 | 0.0023 | 0.0163 | 0.0186 | 0.0174 | 0.0007 | 0 | 3 | 0.0142 | 0.0242 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6295 | 30966.928 | 44265.9128 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 8614.893 | 0:240:120 | 0:00 | 0.0129 | 7 | 0.0037 | 0.0143 | 0.018 | 0.016 | 0.0011 | 0 | 3 | 0.0129 | 0.0229 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6298 | 30970.113 | 44265.9128 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 9649.624 | 0:240:120 | 0:00 | 0.0117 | 7 | 0.0041 | 0.0125 | 0.0166 | 0.0144 | 0.0015 | 0 | 3 | 0.0117 | 0.0217 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6301 | 30973.227 | 44265.9129 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 10707.881 | 0:240:120 | 0:00 | 0.0109 | 7 | 0.0055 | 0.0111 | 0.0166 | 0.0135 | 0.0019 | 0 | 3 | 0.0109 | 0.0209 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6304 | 30976.457 | 44265.9129 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 11845.158 | 0:240:120 | 0:00 | 0.0102 | 7 | 0.0044 | 0.0112 | 0.0156 | 0.0132 | 0.0015 | 0 | 3 | 0.0102 | 0.0202 | P | P | P | NP | 0-0-0-0-0-0-0-0-0
6307 | 31027.855 | 44265.9135 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 464.3 | 0:240:120 | 0:00 | 6.1156 | 7 | 9.4742 | 38.5072 | 47.9814 | 44.8215 | 4.7352 | 22.4216 | 3 | 6.1156 | 23.1053 | NP | NP | 0-0-0-0-0-0-0-0-0 | NP | 0-0-0-0-0-0-0-0-0
6310 | 31146.353 | 44265.9149 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 479.2 | 0:240:120 | 0:00 | 4.8909 | 7 | 9.4722 | 10.0888 | 19.561 | 16.3947 | 4.7291 | 22.3641 | 3 | 4.8909 | 13.0113 | NP | NP | 0-0-1-0-0-1-0-0-1 | NP | 0-0-0-0-0-0-0-0-0
6313 | 31196.925 | 44265.9154 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 498 | 0:240:120 | 0:00 | 3.8798 | 7 | 0.5291 | 7.9872 | 8.5163 | 8.1651 | 0.2629 | 0.0691 | 3 | 3.8798 | 8.2949 | P | NP | 0-1-1-0-1-1-0-1-1 | NP | 0-0-0-0-0-0-0-0-0
6316 | 31223.106 | 44265.9157 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 516.4 | 0:240:120 | 0:00 | 3.2088 | 7 | 0.7198 | 5.3699 | 6.0897 | 5.7674 | 0.3053 | 0.0932 | 3 | 3.2088 | 6.0694 | P | NP | 1-1-1-0-1-1-1-1-1 | NP | 0-0-0-0-0-0-0-0-0
6319 | 31242.834 | 44265.916 | Vista Coord | Tap | 400Tap | Phase | Single/Single | Way 2 | Hot | 1 | 0 | 0 | 60 | 60 | 533 | 0:240:120 | 0:00 | 2.7644 | 7 | 0.2914 | 4.3804 | 4.6718 | 4.5201 | 0.1218 | 0.0148 | 3 | 2.7644 | 4.8578 | P | P | P | NP | 0-0-0-0-0-0-0-0-0