## 691-9-U1
S&C Vista Underground Distribution Switchgear Overcurrent Control | [11 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
US Moderately Inverse (U1) (TCC 691-9-U1) | [11 empty] | US Moderately Inverse (U1) (TCC 691-9-U1)
Average Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [11 empty] | Average Tripping Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: |  | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [9 empty] | Tolerance: |  | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of
|  | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is + 1.5 | [11 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is + 1.5
|  | cycles +10% of the time indicated on the selected curve at a specified value of current | [11 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current
|  | between 2 and 30 multiples of the pickup setting. | [11 empty] | between 2 and 30 multiples of the pickup setting.
|  | Instantaneous pickup current tolerance is -0% to +10^ of the selected instantaneous pickup | [11 empty] | Instantaneous pickup current tolerance is -0% to +10^ of the selected instantaneous pickup
|  | current level. Definite-time response tolerance is -0 to 8 milliseconds. | [11 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds.
Time Dial = 0.5 |  | Time Dial = 1.0 |  | Time Dial = 2.0 |  | Time Dial = 3.0 |  | Time Dial = 4.0 |  | Time Dial = 5.0 |  | Time Dial = 6.0 |  | Time Dial = 8.0 |  | Time Dial = 10.0 |  | Time Dial = 12.0 |  | Time Dial = 15.0
*of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s)
1.5 | 0.64994 | 1.5 | 1.2999 | 1.5 | 2.5998 | 1.5 | 3.8997 | 1.5 | 5.1995 | 1.5 | 6.4994 | 1.5 | 7.7993 | 1.5 | 10.3991 | 1.5 | 12.9988 | 1.5 | 15.5986 | 1.5 | 19.4983
1.6 | 0.56189 | 1.6 | 1.1238 | 1.6 | 2.2476 | 1.6 | 3.3713 | 1.6 | 4.4951 | 1.6 | 5.6189 | 1.6 | 6.7427 | 1.6 | 8.9903 | 1.6 | 11.2378 | 1.6 | 13.4854 | 1.6 | 16.8567
1.7 | 0.49869 | 1.7 | 0.99738 | 1.7 | 1.9948 | 1.7 | 2.9921 | 1.7 | 3.9895 | 1.7 | 4.9869 | 1.7 | 5.9843 | 1.7 | 7.979 | 1.7 | 9.9738 | 1.7 | 11.9686 | 1.7 | 14.9607
1.8 | 0.45104 | 1.8 | 0.90208 | 1.8 | 1.8042 | 1.8 | 2.7063 | 1.8 | 3.6083 | 1.8 | 4.5104 | 1.8 | 5.4125 | 1.8 | 7.2167 | 1.8 | 9.0208 | 1.8 | 10.825 | 1.8 | 13.5313
1.9 | 0.41378 | 1.9 | 0.82756 | 1.9 | 1.6551 | 1.9 | 2.4827 | 1.9 | 3.3103 | 1.9 | 4.1378 | 1.9 | 4.9654 | 1.9 | 6.6205 | 1.9 | 8.2756 | 1.9 | 9.9308 | 1.9 | 12.4135
2 | 0.38381 | 2 | 0.76761 | 2 | 1.5352 | 2 | 2.3028 | 2 | 3.0705 | 2 | 3.8381 | 2 | 4.6057 | 2 | 6.1409 | 2 | 7.6761 | 2 | 9.2114 | 2 | 11.5142
2.1 | 0.35914 | 2.1 | 0.71828 | 2.1 | 1.4366 | 2.1 | 2.1548 | 2.1 | 2.8731 | 2.1 | 3.5914 | 2.1 | 4.3097 | 2.1 | 5.7462 | 2.1 | 7.1828 | 2.1 | 8.6194 | 2.1 | 10.7742
2.2 | 0.33846 | 2.2 | 0.67693 | 2.2 | 1.3539 | 2.2 | 2.0308 | 2.2 | 2.7077 | 2.2 | 3.3846 | 2.2 | 4.0616 | 2.2 | 5.4154 | 2.2 | 6.7693 | 2.2 | 8.1232 | 2.2 | 10.1539
2.3 | 0.32087 | 2.3 | 0.64173 | 2.3 | 1.2835 | 2.3 | 1.9252 | 2.3 | 2.5669 | 2.3 | 3.2087 | 2.3 | 3.8504 | 2.3 | 5.1339 | 2.3 | 6.4173 | 2.3 | 7.7008 | 2.3 | 9.626
2.4 | 0.30569 | 2.4 | 0.61138 | 2.4 | 1.2228 | 2.4 | 1.8341 | 2.4 | 2.4455 | 2.4 | 3.0569 | 2.4 | 3.6683 | 2.4 | 4.8911 | 2.4 | 6.1138 | 2.4 | 7.3366 | 2.4 | 9.1707
2.5 | 0.29246 | 2.5 | 0.58492 | 2.5 | 1.1698 | 2.5 | 1.7548 | 2.5 | 2.3397 | 2.5 | 2.9246 | 2.5 | 3.5095 | 2.5 | 4.6794 | 2.5 | 5.8492 | 2.5 | 7.0191 | 2.5 | 8.7738
2.6 | 0.28081 | 2.6 | 0.56163 | 2.6 | 1.1233 | 2.6 | 1.6849 | 2.6 | 2.2465 | 2.6 | 2.8081 | 2.6 | 3.3698 | 2.6 | 4.493 | 2.6 | 5.6163 | 2.6 | 6.7395 | 2.6 | 8.4244
2.7 | 0.27048 | 2.7 | 0.54095 | 2.7 | 1.0819 | 2.7 | 1.6229 | 2.7 | 2.1638 | 2.7 | 2.7048 | 2.7 | 3.2457 | 2.7 | 4.3276 | 2.7 | 5.4095 | 2.7 | 6.4914 | 2.7 | 8.1143
2.8 | 0.26123 | 2.8 | 0.52246 | 2.8 | 1.0449 | 2.8 | 1.5674 | 2.8 | 2.0898 | 2.8 | 2.6123 | 2.8 | 3.1348 | 2.8 | 4.1797 | 2.8 | 5.2246 | 2.8 | 6.2695 | 2.8 | 7.8369
2.9 | 0.25291 | 2.9 | 0.50581 | 2.9 | 1.0116 | 2.9 | 1.5174 | 2.9 | 2.0233 | 2.9 | 2.5291 | 2.9 | 3.0349 | 2.9 | 4.0465 | 2.9 | 5.0581 | 2.9 | 6.0698 | 2.9 | 7.5872
3 | 0.24537 | 3 | 0.49074 | 3 | 0.98149 | 3 | 1.4722 | 3 | 1.963 | 3 | 2.4537 | 3 | 2.9445 | 3 | 3.9259 | 3 | 4.9074 | 3 | 5.8889 | 3 | 7.3612
3.1 | 0.23851 | 3.1 | 0.47703 | 3.1 | 0.95405 | 3.1 | 1.4311 | 3.1 | 1.9081 | 3.1 | 2.3851 | 3.1 | 2.8622 | 3.1 | 3.8162 | 3.1 | 4.7703 | 3.1 | 5.7243 | 3.1 | 7.1554
3.2 | 0.23224 | 3.2 | 0.46448 | 3.2 | 0.92896 | 3.2 | 1.3934 | 3.2 | 1.8579 | 3.2 | 2.3224 | 3.2 | 2.7869 | 3.2 | 3.7159 | 3.2 | 4.6448 | 3.2 | 5.5738 | 3.2 | 6.9672
3.3 | 0.22648 | 3.3 | 0.45296 | 3.3 | 0.90592 | 3.3 | 1.3589 | 3.3 | 1.8118 | 3.3 | 2.2648 | 3.3 | 2.7178 | 3.3 | 3.6237 | 3.3 | 4.5296 | 3.3 | 5.4355 | 3.3 | 6.7944
3.4 | 0.22117 | 3.4 | 0.44234 | 3.4 | 0.88467 | 3.4 | 1.327 | 3.4 | 1.7693 | 3.4 | 2.2117 | 3.4 | 2.654 | 3.4 | 3.5387 | 3.4 | 4.4234 | 3.4 | 5.308 | 3.4 | 6.635
3.5 | 0.21625 | 3.5 | 0.4325 | 3.5 | 0.86501 | 3.5 | 1.2975 | 3.5 | 1.73 | 3.5 | 2.1625 | 3.5 | 2.595 | 3.5 | 3.46 | 3.5 | 4.325 | 3.5 | 5.1901 | 3.5 | 6.4876
3.6 | 0.21169 | 3.6 | 0.42338 | 3.6 | 0.84675 | 3.6 | 1.2701 | 3.6 | 1.6935 | 3.6 | 2.1169 | 3.6 | 2.5403 | 3.6 | 3.387 | 3.6 | 4.2338 | 3.6 | 5.0805 | 3.6 | 6.3506
3.7 | 0.20744 | 3.7 | 0.41488 | 3.7 | 0.82975 | 3.7 | 1.2446 | 3.7 | 1.6595 | 3.7 | 2.0744 | 3.7 | 2.4893 | 3.7 | 3.319 | 3.7 | 4.1488 | 3.7 | 4.9785 | 3.7 | 6.2231
3.8 | 0.20347 | 3.8 | 0.40694 | 3.8 | 0.81387 | 3.8 | 1.2208 | 3.8 | 1.6277 | 3.8 | 2.0347 | 3.8 | 2.4416 | 3.8 | 3.2555 | 3.8 | 4.0694 | 3.8 | 4.8832 | 3.8 | 6.104
3.9 | 0.19975 | 3.9 | 0.3995 | 3.9 | 0.799 | 3.9 | 1.1985 | 3.9 | 1.598 | 3.9 | 1.9975 | 3.9 | 2.397 | 3.9 | 3.196 | 3.9 | 3.995 | 3.9 | 4.794 | 3.9 | 5.9925
4 | 0.19626 | 4 | 0.39252 | 4 | 0.78505 | 4 | 1.1776 | 4 | 1.5701 | 4 | 1.9626 | 4 | 2.3551 | 4 | 3.1402 | 4 | 3.9252 | 4 | 4.7103 | 4 | 5.8879
4.1 | 0.19298 | 4.1 | 0.38596 | 4.1 | 0.77192 | 4.1 | 1.1579 | 4.1 | 1.5438 | 4.1 | 1.9298 | 4.1 | 2.3158 | 4.1 | 3.0877 | 4.1 | 3.8596 | 4.1 | 4.6315 | 4.1 | 5.7894
4.2 | 0.18989 | 4.2 | 0.37977 | 4.2 | 0.75955 | 4.2 | 1.1393 | 4.2 | 1.5191 | 4.2 | 1.8989 | 4.2 | 2.2786 | 4.2 | 3.0382 | 4.2 | 3.7977 | 4.2 | 4.5573 | 4.2 | 5.6966
4.3 | 0.18696 | 4.3 | 0.37393 | 4.3 | 0.74786 | 4.3 | 1.1218 | 4.3 | 1.4957 | 4.3 | 1.8696 | 4.3 | 2.2436 | 4.3 | 2.9914 | 4.3 | 3.7393 | 4.3 | 4.4871 | 4.3 | 5.6089
4.4 | 0.1842 | 4.4 | 0.3684 | 4.4 | 0.73679 | 4.4 | 1.1052 | 4.4 | 1.4736 | 4.4 | 1.842 | 4.4 | 2.2104 | 4.4 | 2.9472 | 4.4 | 3.684 | 4.4 | 4.4208 | 4.4 | 5.5259
4.5 | 0.18158 | 4.5 | 0.36315 | 4.5 | 0.72631 | 4.5 | 1.0895 | 4.5 | 1.4526 | 4.5 | 1.8158 | 4.5 | 2.1789 | 4.5 | 2.9052 | 4.5 | 3.6315 | 4.5 | 4.3578 | 4.5 | 5.4473
4.6 | 0.17909 | 4.6 | 0.35817 | 4.6 | 0.71635 | 4.6 | 1.0745 | 4.6 | 1.4327 | 4.6 | 1.7909 | 4.6 | 2.149 | 4.6 | 2.8654 | 4.6 | 3.5817 | 4.6 | 4.2981 | 4.6 | 5.3726
4.7 | 0.17672 | 4.7 | 0.35344 | 4.7 | 0.70688 | 4.7 | 1.0603 | 4.7 | 1.4138 | 4.7 | 1.7672 | 4.7 | 2.1206 | 4.7 | 2.8275 | 4.7 | 3.5344 | 4.7 | 4.2413 | 4.7 | 5.3016
4.8 | 0.17446 | 4.8 | 0.34893 | 4.8 | 0.69786 | 4.8 | 1.0468 | 4.8 | 1.3957 | 4.8 | 1.7446 | 4.8 | 2.0936 | 4.8 | 2.7914 | 4.8 | 3.4893 | 4.8 | 4.1872 | 4.8 | 5.2339
4.9 | 0.17231 | 4.9 | 0.34463 | 4.9 | 0.68926 | 4.9 | 1.0339 | 4.9 | 1.3785 | 4.9 | 1.7231 | 4.9 | 2.0678 | 4.9 | 2.757 | 4.9 | 3.4463 | 4.9 | 4.1355 | 4.9 | 5.1694
5 | 0.17026 | 5 | 0.34052 | 5 | 0.68104 | 5 | 1.0216 | 5 | 1.3621 | 5 | 1.7026 | 5 | 2.0431 | 5 | 2.7242 | 5 | 3.4052 | 5 | 4.0863 | 5 | 5.1078
5.1 | 0.1683 | 5.1 | 0.3366 | 5.1 | 0.67319 | 5.1 | 1.0098 | 5.1 | 1.3464 | 5.1 | 1.683 | 5.1 | 2.0196 | 5.1 | 2.6928 | 5.1 | 3.366 | 5.1 | 4.0391 | 5.1 | 5.0489
5.2 | 0.16642 | 5.2 | 0.33284 | 5.2 | 0.66567 | 5.2 | 0.99851 | 5.2 | 1.3313 | 5.2 | 1.6642 | 5.2 | 1.997 | 5.2 | 2.6627 | 5.2 | 3.3284 | 5.2 | 3.994 | 5.2 | 4.9925
5.3 | 0.16462 | 5.3 | 0.32923 | 5.3 | 0.65847 | 5.3 | 0.9877 | 5.3 | 1.3169 | 5.3 | 1.6462 | 5.3 | 1.9754 | 5.3 | 2.6339 | 5.3 | 3.2923 | 5.3 | 3.9508 | 5.3 | 4.9385
5.4 | 0.16289 | 5.4 | 0.32578 | 5.4 | 0.65156 | 5.4 | 0.97734 | 5.4 | 1.3031 | 5.4 | 1.6289 | 5.4 | 1.9547 | 5.4 | 2.6062 | 5.4 | 3.2578 | 5.4 | 3.9093 | 5.4 | 4.8867
5.5 | 0.16123 | 5.5 | 0.32246 | 5.5 | 0.64492 | 5.5 | 0.96738 | 5.5 | 1.2898 | 5.5 | 1.6123 | 5.5 | 1.9348 | 5.5 | 2.5797 | 5.5 | 3.2246 | 5.5 | 3.8695 | 5.5 | 4.8369
5.6 | 0.15963 | 5.6 | 0.31927 | 5.6 | 0.63854 | 5.6 | 0.95781 | 5.6 | 1.2771 | 5.6 | 1.5963 | 5.6 | 1.9156 | 5.6 | 2.5542 | 5.6 | 3.1927 | 5.6 | 3.8312 | 5.6 | 4.789
5.7 | 0.1581 | 5.7 | 0.3162 | 5.7 | 0.6324 | 5.7 | 0.9486 | 5.7 | 1.2648 | 5.7 | 1.581 | 5.7 | 1.8972 | 5.7 | 2.5296 | 5.7 | 3.162 | 5.7 | 3.7944 | 5.7 | 4.743
5.8 | 0.15662 | 5.8 | 0.31325 | 5.8 | 0.62649 | 5.8 | 0.93974 | 5.8 | 1.253 | 5.8 | 1.5662 | 5.8 | 1.8795 | 5.8 | 2.506 | 5.8 | 3.1325 | 5.8 | 3.7589 | 5.8 | 4.6987
5.9 | 0.1552 | 5.9 | 0.3104 | 5.9 | 0.62079 | 5.9 | 0.93119 | 5.9 | 1.2416 | 5.9 | 1.552 | 5.9 | 1.8624 | 5.9 | 2.4832 | 5.9 | 3.104 | 5.9 | 3.7248 | 5.9 | 4.6559
6 | 0.15382 | 6 | 0.30765 | 6 | 0.6153 | 6 | 0.92295 | 6 | 1.2306 | 6 | 1.5382 | 6 | 1.8459 | 6 | 2.4612 | 6 | 3.0765 | 6 | 3.6918 | 6 | 4.6147
6.1 | 0.1525 | 6.1 | 0.305 | 6.1 | 0.60999 | 6.1 | 0.91499 | 6.1 | 1.22 | 6.1 | 1.525 | 6.1 | 1.83 | 6.1 | 2.44 | 6.1 | 3.05 | 6.1 | 3.66 | 6.1 | 4.5749
6.2 | 0.15122 | 6.2 | 0.30243 | 6.2 | 0.60487 | 6.2 | 0.9073 | 6.2 | 1.2097 | 6.2 | 1.5122 | 6.2 | 1.8146 | 6.2 | 2.4195 | 6.2 | 3.0243 | 6.2 | 3.6292 | 6.2 | 4.5365
6.3 | 0.14998 | 6.3 | 0.29996 | 6.3 | 0.59991 | 6.3 | 0.89987 | 6.3 | 1.1998 | 6.3 | 1.4998 | 6.3 | 1.7997 | 6.3 | 2.3996 | 6.3 | 2.9996 | 6.3 | 3.5995 | 6.3 | 4.4993
6.4 | 0.14878 | 6.4 | 0.29756 | 6.4 | 0.59512 | 6.4 | 0.89268 | 6.4 | 1.1902 | 6.4 | 1.4878 | 6.4 | 1.7854 | 6.4 | 2.3805 | 6.4 | 2.9756 | 6.4 | 3.5707 | 6.4 | 4.4634
6.5 | 0.14762 | 6.5 | 0.29524 | 6.5 | 0.59048 | 6.5 | 0.88572 | 6.5 | 1.181 | 6.5 | 1.4762 | 6.5 | 1.7714 | 6.5 | 2.3619 | 6.5 | 2.9524 | 6.5 | 3.5429 | 6.5 | 4.4286
6.6 | 0.1465 | 6.6 | 0.29299 | 6.6 | 0.58598 | 6.6 | 0.87898 | 6.6 | 1.172 | 6.6 | 1.465 | 6.6 | 1.758 | 6.6 | 2.3439 | 6.6 | 2.9299 | 6.6 | 3.5159 | 6.6 | 4.3949
6.7 | 0.14541 | 6.7 | 0.29081 | 6.7 | 0.58163 | 6.7 | 0.87244 | 6.7 | 1.1633 | 6.7 | 1.4541 | 6.7 | 1.7449 | 6.7 | 2.3265 | 6.7 | 2.9081 | 6.7 | 3.4898 | 6.7 | 4.3622
6.8 | 0.14435 | 6.8 | 0.2887 | 6.8 | 0.5774 | 6.8 | 0.8661 | 6.8 | 1.1548 | 6.8 | 1.4435 | 6.8 | 1.7322 | 6.8 | 2.3096 | 6.8 | 2.887 | 6.8 | 3.4644 | 6.8 | 4.3305
6.9 | 0.14333 | 6.9 | 0.28665 | 6.9 | 0.5733 | 6.9 | 0.85995 | 6.9 | 1.1466 | 6.9 | 1.4333 | 6.9 | 1.7199 | 6.9 | 2.2932 | 6.9 | 2.8665 | 6.9 | 3.4398 | 6.9 | 4.2998
7 | 0.14233 | 7 | 0.28466 | 7 | 0.56932 | 7 | 0.85398 | 7 | 1.1386 | 7 | 1.4233 | 7 | 1.708 | 7 | 2.2773 | 7 | 2.8466 | 7 | 3.4159 | 7 | 4.2699
7.1 | 0.14136 | 7.1 | 0.28273 | 7.1 | 0.56545 | 7.1 | 0.84818 | 7.1 | 1.1309 | 7.1 | 1.4136 | 7.1 | 1.6964 | 7.1 | 2.2618 | 7.1 | 2.8273 | 7.1 | 3.3927 | 7.1 | 4.2409
7.2 | 0.14042 | 7.2 | 0.28085 | 7.2 | 0.5617 | 7.2 | 0.84254 | 7.2 | 1.1234 | 7.2 | 1.4042 | 7.2 | 1.6851 | 7.2 | 2.2468 | 7.2 | 2.8085 | 7.2 | 3.3702 | 7.2 | 4.2127
7.3 | 0.13951 | 7.3 | 0.27902 | 7.3 | 0.55804 | 7.3 | 0.83706 | 7.3 | 1.1161 | 7.3 | 1.3951 | 7.3 | 1.6741 | 7.3 | 2.2322 | 7.3 | 2.7902 | 7.3 | 3.3482 | 7.3 | 4.1853
7.4 | 0.13862 | 7.4 | 0.27724 | 7.4 | 0.55448 | 7.4 | 0.83173 | 7.4 | 1.109 | 7.4 | 1.3862 | 7.4 | 1.6635 | 7.4 | 2.2179 | 7.4 | 2.7724 | 7.4 | 3.3269 | 7.4 | 4.1586
7.5 | 0.13776 | 7.5 | 0.27551 | 7.5 | 0.55102 | 7.5 | 0.82654 | 7.5 | 1.102 | 7.5 | 1.3776 | 7.5 | 1.6531 | 7.5 | 2.2041 | 7.5 | 2.7551 | 7.5 | 3.3061 | 7.5 | 4.1327
7.6 | 0.13691 | 7.6 | 0.27383 | 7.6 | 0.54765 | 7.6 | 0.82148 | 7.6 | 1.0953 | 7.6 | 1.3691 | 7.6 | 1.643 | 7.6 | 2.1906 | 7.6 | 2.7383 | 7.6 | 3.2859 | 7.6 | 4.1074
7.7 | 0.13609 | 7.7 | 0.27218 | 7.7 | 0.54437 | 7.7 | 0.81655 | 7.7 | 1.0887 | 7.7 | 1.3609 | 7.7 | 1.6331 | 7.7 | 2.1775 | 7.7 | 2.7218 | 7.7 | 3.2662 | 7.7 | 4.0828
7.8 | 0.13529 | 7.8 | 0.27058 | 7.8 | 0.54117 | 7.8 | 0.81175 | 7.8 | 1.0823 | 7.8 | 1.3529 | 7.8 | 1.6235 | 7.8 | 2.1647 | 7.8 | 2.7058 | 7.8 | 3.247 | 7.8 | 4.0588
7.9 | 0.13451 | 7.9 | 0.26902 | 7.9 | 0.53805 | 7.9 | 0.80707 | 7.9 | 1.0761 | 7.9 | 1.3451 | 7.9 | 1.6141 | 7.9 | 2.1522 | 7.9 | 2.6902 | 7.9 | 3.2283 | 7.9 | 4.0354
8 | 0.13375 | 8 | 0.2675 | 8 | 0.53501 | 8 | 0.80251 | 8 | 1.07 | 8 | 1.3375 | 8 | 1.605 | 8 | 2.14 | 8 | 2.675 | 8 | 3.21 | 8 | 4.0125
8.1 | 0.13301 | 8.1 | 0.26602 | 8.1 | 0.53204 | 8.1 | 0.79806 | 8.1 | 1.0641 | 8.1 | 1.3301 | 8.1 | 1.5961 | 8.1 | 2.1281 | 8.1 | 2.6602 | 8.1 | 3.1922 | 8.1 | 3.9903
8.2 | 0.13228 | 8.2 | 0.26457 | 8.2 | 0.52914 | 8.2 | 0.79371 | 8.2 | 1.0583 | 8.2 | 1.3228 | 8.2 | 1.5874 | 8.2 | 2.1166 | 8.2 | 2.6457 | 8.2 | 3.1748 | 8.2 | 3.9685
8.3 | 0.13158 | 8.3 | 0.26315 | 8.3 | 0.52631 | 8.3 | 0.78946 | 8.3 | 1.0526 | 8.3 | 1.3158 | 8.3 | 1.5789 | 8.3 | 2.1052 | 8.3 | 2.6315 | 8.3 | 3.1578 | 8.3 | 3.9473
8.4 | 0.13089 | 8.4 | 0.26177 | 8.4 | 0.52354 | 8.4 | 0.78531 | 8.4 | 1.0471 | 8.4 | 1.3089 | 8.4 | 1.5706 | 8.4 | 2.0942 | 8.4 | 2.6177 | 8.4 | 3.1413 | 8.4 | 3.9266
8.5 | 0.13021 | 8.5 | 0.26042 | 8.5 | 0.52084 | 8.5 | 0.78126 | 8.5 | 1.0417 | 8.5 | 1.3021 | 8.5 | 1.5625 | 8.5 | 2.0834 | 8.5 | 2.6042 | 8.5 | 3.125 | 8.5 | 3.9063
8.6 | 0.12955 | 8.6 | 0.2591 | 8.6 | 0.5182 | 8.6 | 0.7773 | 8.6 | 1.0364 | 8.6 | 1.2955 | 8.6 | 1.5546 | 8.6 | 2.0728 | 8.6 | 2.591 | 8.6 | 3.1092 | 8.6 | 3.8865
8.7 | 0.1289 | 8.7 | 0.25781 | 8.7 | 0.51562 | 8.7 | 0.77343 | 8.7 | 1.0312 | 8.7 | 1.289 | 8.7 | 1.5469 | 8.7 | 2.0625 | 8.7 | 2.5781 | 8.7 | 3.0937 | 8.7 | 3.8671
8.8 | 0.12827 | 8.8 | 0.25655 | 8.8 | 0.51309 | 8.8 | 0.76964 | 8.8 | 1.0262 | 8.8 | 1.2827 | 8.8 | 1.5393 | 8.8 | 2.0524 | 8.8 | 2.5655 | 8.8 | 3.0785 | 8.8 | 3.8482
8.9 | 0.12765 | 8.9 | 0.25531 | 8.9 | 0.51062 | 8.9 | 0.76593 | 8.9 | 1.0212 | 8.9 | 1.2765 | 8.9 | 1.5319 | 8.9 | 2.0425 | 8.9 | 2.5531 | 8.9 | 3.0637 | 8.9 | 3.8296
9 | 0.12705 | 9 | 0.2541 | 9 | 0.5082 | 9 | 0.7623 | 9 | 1.0164 | 9 | 1.2705 | 9 | 1.5246 | 9 | 2.0328 | 9 | 2.541 | 9 | 3.0492 | 9 | 3.8115
9.1 | 0.12646 | 9.1 | 0.25292 | 9.1 | 0.50583 | 9.1 | 0.75875 | 9.1 | 1.0117 | 9.1 | 1.2646 | 9.1 | 1.5175 | 9.1 | 2.0233 | 9.1 | 2.5292 | 9.1 | 3.035 | 9.1 | 3.7937
9.2 | 0.12588 | 9.2 | 0.25176 | 9.2 | 0.50351 | 9.2 | 0.75527 | 9.2 | 1.007 | 9.2 | 1.2588 | 9.2 | 1.5105 | 9.2 | 2.0141 | 9.2 | 2.5176 | 9.2 | 3.0211 | 9.2 | 3.7764
9.3 | 0.12531 | 9.3 | 0.25062 | 9.3 | 0.50124 | 9.3 | 0.75186 | 9.3 | 1.0025 | 9.3 | 1.2531 | 9.3 | 1.5037 | 9.3 | 2.005 | 9.3 | 2.5062 | 9.3 | 3.0075 | 9.3 | 3.7593
9.4 | 0.12475 | 9.4 | 0.24951 | 9.4 | 0.49902 | 9.4 | 0.74852 | 9.4 | 0.99803 | 9.4 | 1.2475 | 9.4 | 1.497 | 9.4 | 1.9961 | 9.4 | 2.4951 | 9.4 | 2.9941 | 9.4 | 3.7426
9.5 | 0.12421 | 9.5 | 0.24842 | 9.5 | 0.49684 | 9.5 | 0.74525 | 9.5 | 0.99367 | 9.5 | 1.2421 | 9.5 | 1.4905 | 9.5 | 1.9873 | 9.5 | 2.4842 | 9.5 | 2.981 | 9.5 | 3.7263
9.6 | 0.12367 | 9.6 | 0.24735 | 9.6 | 0.4947 | 9.6 | 0.74205 | 9.6 | 0.98939 | 9.6 | 1.2367 | 9.6 | 1.4841 | 9.6 | 1.9788 | 9.6 | 2.4735 | 9.6 | 2.9682 | 9.6 | 3.7102
9.7 | 0.12315 | 9.7 | 0.2463 | 9.7 | 0.4926 | 9.7 | 0.7389 | 9.7 | 0.9852 | 9.7 | 1.2315 | 9.7 | 1.4778 | 9.7 | 1.9704 | 9.7 | 2.463 | 9.7 | 2.9556 | 9.7 | 3.6945
9.8 | 0.12264 | 9.8 | 0.24527 | 9.8 | 0.49054 | 9.8 | 0.73582 | 9.8 | 0.98109 | 9.8 | 1.2264 | 9.8 | 1.4716 | 9.8 | 1.9622 | 9.8 | 2.4527 | 9.8 | 2.9433 | 9.8 | 3.6791
9.9 | 0.12213 | 9.9 | 0.24426 | 9.9 | 0.48853 | 9.9 | 0.73279 | 9.9 | 0.97705 | 9.9 | 1.2213 | 9.9 | 1.4656 | 9.9 | 1.9541 | 9.9 | 2.4426 | 9.9 | 2.9312 | 9.9 | 3.6639
10 | 0.12164 | 10 | 0.24327 | 10 | 0.48655 | 10 | 0.72982 | 10 | 0.97309 | 10 | 1.2164 | 10 | 1.4596 | 10 | 1.9462 | 10 | 2.4327 | 10 | 2.9193 | 10 | 3.6491
10.5 | 0.11929 | 10.5 | 0.23859 | 10.5 | 0.47718 | 10.5 | 0.71576 | 10.5 | 0.95435 | 10.5 | 1.1929 | 10.5 | 1.4315 | 10.5 | 1.9087 | 10.5 | 2.3859 | 10.5 | 2.8631 | 10.5 | 3.5788
11 | 0.11715 | 11 | 0.2343 | 11 | 0.4686 | 11 | 0.7029 | 11 | 0.93719 | 11 | 1.1715 | 11 | 1.4058 | 11 | 1.8744 | 11 | 2.343 | 11 | 2.8116 | 11 | 3.5145
11.5 | 0.11518 | 11.5 | 0.23035 | 11.5 | 0.4607 | 11.5 | 0.69106 | 11.5 | 0.92141 | 11.5 | 1.1518 | 11.5 | 1.3821 | 11.5 | 1.8428 | 11.5 | 2.3035 | 11.5 | 2.7642 | 11.5 | 3.4553
12 | 0.11335 | 12 | 0.22671 | 12 | 0.45341 | 12 | 0.68012 | 12 | 0.90683 | 12 | 1.1335 | 12 | 1.3602 | 12 | 1.8137 | 12 | 2.2671 | 12 | 2.7205 | 12 | 3.4006
12.5 | 0.11166 | 12.5 | 0.22332 | 12.5 | 0.44665 | 12.5 | 0.66997 | 12.5 | 0.8933 | 12.5 | 1.1166 | 12.5 | 1.3399 | 12.5 | 1.7866 | 12.5 | 2.2332 | 12.5 | 2.6799 | 12.5 | 3.3499
13 | 0.11009 | 13 | 0.22018 | 13 | 0.44036 | 13 | 0.66053 | 13 | 0.88071 | 13 | 1.1009 | 13 | 1.3211 | 13 | 1.7614 | 13 | 2.2018 | 13 | 2.6421 | 13 | 3.3027
13.5 | 0.10862 | 13.5 | 0.21724 | 13.5 | 0.43448 | 13.5 | 0.65172 | 13.5 | 0.86895 | 13.5 | 1.0862 | 13.5 | 1.3034 | 13.5 | 1.7379 | 13.5 | 2.1724 | 13.5 | 2.6069 | 13.5 | 3.2586
14 | 0.10724 | 14 | 0.21449 | 14 | 0.42897 | 14 | 0.64346 | 14 | 0.85794 | 14 | 1.0724 | 14 | 1.2869 | 14 | 1.7159 | 14 | 2.1449 | 14 | 2.5738 | 14 | 3.2173
14.5 | 0.10595 | 14.5 | 0.2119 | 14.5 | 0.4238 | 14.5 | 0.6357 | 14.5 | 0.8476 | 14.5 | 1.0595 | 14.5 | 1.2714 | 14.5 | 1.6952 | 14.5 | 2.119 | 14.5 | 2.5428 | 14.5 | 3.1785
15 | 0.10473 | 15 | 0.20947 | 15 | 0.41893 | 15 | 0.6284 | 15 | 0.83787 | 15 | 1.0473 | 15 | 1.2568 | 15 | 1.6757 | 15 | 2.0947 | 15 | 2.5136 | 15 | 3.142
16 | 0.1025 | 16 | 0.205 | 16 | 0.41 | 16 | 0.615 | 16 | 0.81999 | 16 | 1.025 | 16 | 1.23 | 16 | 1.64 | 16 | 2.05 | 16 | 2.46 | 16 | 3.075
17 | 0.10049 | 17 | 0.20099 | 17 | 0.40197 | 17 | 0.60296 | 17 | 0.80395 | 17 | 1.0049 | 17 | 1.2059 | 17 | 1.6079 | 17 | 2.0099 | 17 | 2.4118 | 17 | 3.0148
18 | 0.098679 | 18 | 0.19736 | 18 | 0.39472 | 18 | 0.59207 | 18 | 0.78943 | 18 | 0.98679 | 18 | 1.1841 | 18 | 1.5789 | 18 | 1.9736 | 18 | 2.3683 | 18 | 2.9604
19 | 0.097028 | 19 | 0.19406 | 19 | 0.38811 | 19 | 0.58217 | 19 | 0.77622 | 19 | 0.97028 | 19 | 1.1643 | 19 | 1.5524 | 19 | 1.9406 | 19 | 2.3287 | 19 | 2.9108
20 | 0.095516 | 20 | 0.19103 | 20 | 0.38206 | 20 | 0.5731 | 20 | 0.76413 | 20 | 0.95516 | 20 | 1.1462 | 20 | 1.5283 | 20 | 1.9103 | 20 | 2.2924 | 20 | 2.8655
21 | 0.094126 | 21 | 0.18825 | 21 | 0.3765 | 21 | 0.56475 | 21 | 0.75301 | 21 | 0.94126 | 21 | 1.1295 | 21 | 1.506 | 21 | 1.8825 | 21 | 2.259 | 21 | 2.8238
22 | 0.092841 | 22 | 0.18568 | 22 | 0.37136 | 22 | 0.55704 | 22 | 0.74273 | 22 | 0.92841 | 22 | 1.1141 | 22 | 1.4855 | 22 | 1.8568 | 22 | 2.2282 | 22 | 2.7852
23 | 0.091649 | 23 | 0.1833 | 23 | 0.36659 | 23 | 0.54989 | 23 | 0.73319 | 23 | 0.91649 | 23 | 1.0998 | 23 | 1.4664 | 23 | 1.833 | 23 | 2.1996 | 23 | 2.7495
24 | 0.090539 | 24 | 0.18108 | 24 | 0.36215 | 24 | 0.54323 | 24 | 0.72431 | 24 | 0.90539 | 24 | 1.0865 | 24 | 1.4486 | 24 | 1.8108 | 24 | 2.1729 | 24 | 2.7162
25 | 0.089501 | 25 | 0.179 | 25 | 0.35801 | 25 | 0.53701 | 25 | 0.71601 | 25 | 0.89501 | 25 | 1.074 | 25 | 1.432 | 25 | 1.79 | 25 | 2.148 | 25 | 2.685
26 | 0.088529 | 26 | 0.17706 | 26 | 0.35412 | 26 | 0.53118 | 26 | 0.70824 | 26 | 0.88529 | 26 | 1.0624 | 26 | 1.4165 | 26 | 1.7706 | 26 | 2.1247 | 26 | 2.6559
27 | 0.087616 | 27 | 0.17523 | 27 | 0.35046 | 27 | 0.5257 | 27 | 0.70093 | 27 | 0.87616 | 27 | 1.0514 | 27 | 1.4019 | 27 | 1.7523 | 27 | 2.1028 | 27 | 2.6285
28 | 0.086755 | 28 | 0.17351 | 28 | 0.34702 | 28 | 0.52053 | 28 | 0.69404 | 28 | 0.86755 | 28 | 1.0411 | 28 | 1.3881 | 28 | 1.7351 | 28 | 2.0821 | 28 | 2.6027
29 | 0.085942 | 29 | 0.17188 | 29 | 0.34377 | 29 | 0.51565 | 29 | 0.68754 | 29 | 0.85942 | 29 | 1.0313 | 29 | 1.3751 | 29 | 1.7188 | 29 | 2.0626 | 29 | 2.5783
30 | 0.085173 | 30 | 0.17035 | 30 | 0.34069 | 30 | 0.51104 | 30 | 0.68139 | 30 | 0.85173 | 30 | 1.0221 | 30 | 1.3628 | 30 | 1.7035 | 30 | 2.0442 | 30 | 2.5552
31 | 0.085173 | 31 | 0.17035 | 31 | 0.34069 | 31 | 0.51104 | 31 | 0.68139 | 31 | 0.85173 | 31 | 1.0221 | 31 | 1.3628 | 31 | 1.7035 | 31 | 2.0442 | 31 | 2.5552
32 | 0.085173 | 32 | 0.17035 | 32 | 0.34069 | 32 | 0.51104 | 32 | 0.68139 | 32 | 0.85173 | 32 | 1.0221 | 32 | 1.3628 | 32 | 1.7035 | 32 | 2.0442 | 32 | 2.5552
33 | 0.085173 | 33 | 0.17035 | 33 | 0.34069 | 33 | 0.51104 | 33 | 0.68139 | 33 | 0.85173 | 33 | 1.0221 | 33 | 1.3628 | 33 | 1.7035 | 33 | 2.0442 | 33 | 2.5552
34 | 0.085173 | 34 | 0.17035 | 34 | 0.34069 | 34 | 0.51104 | 34 | 0.68139 | 34 | 0.85173 | 34 | 1.0221 | 34 | 1.3628 | 34 | 1.7035 | 34 | 2.0442 | 34 | 2.5552
35 | 0.085173 | 35 | 0.17035 | 35 | 0.34069 | 35 | 0.51104 | 35 | 0.68139 | 35 | 0.85173 | 35 | 1.0221 | 35 | 1.3628 | 35 | 1.7035 | 35 | 2.0442 | 35 | 2.5552
36 | 0.085173 | 36 | 0.17035 | 36 | 0.34069 | 36 | 0.51104 | 36 | 0.68139 | 36 | 0.85173 | 36 | 1.0221 | 36 | 1.3628 | 36 | 1.7035 | 36 | 2.0442 | 36 | 2.5552
37 | 0.085173 | 37 | 0.17035 | 37 | 0.34069 | 37 | 0.51104 | 37 | 0.68139 | 37 | 0.85173 | 37 | 1.0221 | 37 | 1.3628 | 37 | 1.7035 | 37 | 2.0442 | 37 | 2.5552
38 | 0.085173 | 38 | 0.17035 | 38 | 0.34069 | 38 | 0.51104 | 38 | 0.68139 | 38 | 0.85173 | 38 | 1.0221 | 38 | 1.3628 | 38 | 1.7035 | 38 | 2.0442 | 38 | 2.5552
39 | 0.085173 | 39 | 0.17035 | 39 | 0.34069 | 39 | 0.51104 | 39 | 0.68139 | 39 | 0.85173 | 39 | 1.0221 | 39 | 1.3628 | 39 | 1.7035 | 39 | 2.0442 | 39 | 2.5552
40 | 0.085173 | 40 | 0.17035 | 40 | 0.34069 | 40 | 0.51104 | 40 | 0.68139 | 40 | 0.85173 | 40 | 1.0221 | 40 | 1.3628 | 40 | 1.7035 | 40 | 2.0442 | 40 | 2.5552
41 | 0.085173 | 41 | 0.17035 | 41 | 0.34069 | 41 | 0.51104 | 41 | 0.68139 | 41 | 0.85173 | 41 | 1.0221 | 41 | 1.3628 | 41 | 1.7035 | 41 | 2.0442 | 41 | 2.5552
42 | 0.085173 | 42 | 0.17035 | 42 | 0.34069 | 42 | 0.51104 | 42 | 0.68139 | 42 | 0.85173 | 42 | 1.0221 | 42 | 1.3628 | 42 | 1.7035 | 42 | 2.0442 | 42 | 2.5552
43 | 0.085173 | 43 | 0.17035 | 43 | 0.34069 | 43 | 0.51104 | 43 | 0.68139 | 43 | 0.85173 | 43 | 1.0221 | 43 | 1.3628 | 43 | 1.7035 | 43 | 2.0442 | 43 | 2.5552
44 | 0.085173 | 44 | 0.17035 | 44 | 0.34069 | 44 | 0.51104 | 44 | 0.68139 | 44 | 0.85173 | 44 | 1.0221 | 44 | 1.3628 | 44 | 1.7035 | 44 | 2.0442 | 44 | 2.5552
45 | 0.085173 | 45 | 0.17035 | 45 | 0.34069 | 45 | 0.51104 | 45 | 0.68139 | 45 | 0.85173 | 45 | 1.0221 | 45 | 1.3628 | 45 | 1.7035 | 45 | 2.0442 | 45 | 2.5552
46 | 0.085173 | 46 | 0.17035 | 46 | 0.34069 | 46 | 0.51104 | 46 | 0.68139 | 46 | 0.85173 | 46 | 1.0221 | 46 | 1.3628 | 46 | 1.7035 | 46 | 2.0442 | 46 | 2.5552
47 | 0.085173 | 47 | 0.17035 | 47 | 0.34069 | 47 | 0.51104 | 47 | 0.68139 | 47 | 0.85173 | 47 | 1.0221 | 47 | 1.3628 | 47 | 1.7035 | 47 | 2.0442 | 47 | 2.5552
48 | 0.085173 | 48 | 0.17035 | 48 | 0.34069 | 48 | 0.51104 | 48 | 0.68139 | 48 | 0.85173 | 48 | 1.0221 | 48 | 1.3628 | 48 | 1.7035 | 48 | 2.0442 | 48 | 2.5552
49 | 0.085173 | 49 | 0.17035 | 49 | 0.34069 | 49 | 0.51104 | 49 | 0.68139 | 49 | 0.85173 | 49 | 1.0221 | 49 | 1.3628 | 49 | 1.7035 | 49 | 2.0442 | 49 | 2.5552
50 | 0.085173 | 50 | 0.17035 | 50 | 0.34069 | 50 | 0.51104 | 50 | 0.68139 | 50 | 0.85173 | 50 | 1.0221 | 50 | 1.3628 | 50 | 1.7035 | 50 | 2.0442 | 50 | 2.5552
55 | 0.085173 | 55 | 0.17035 | 55 | 0.34069 | 55 | 0.51104 | 55 | 0.68139 | 55 | 0.85173 | 55 | 1.0221 | 55 | 1.3628 | 55 | 1.7035 | 55 | 2.0442 | 55 | 2.5552
60 | 0.085173 | 60 | 0.17035 | 60 | 0.34069 | 60 | 0.51104 | 60 | 0.68139 | 60 | 0.85173 | 60 | 1.0221 | 60 | 1.3628 | 60 | 1.7035 | 60 | 2.0442 | 60 | 2.5552
65 | 0.085173 | 65 | 0.17035 | 65 | 0.34069 | 65 | 0.51104 | 65 | 0.68139 | 65 | 0.85173 | 65 | 1.0221 | 65 | 1.3628 | 65 | 1.7035 | 65 | 2.0442 | 65 | 2.5552
70 | 0.085173 | 70 | 0.17035 | 70 | 0.34069 | 70 | 0.51104 | 70 | 0.68139 | 70 | 0.85173 | 70 | 1.0221 | 70 | 1.3628 | 70 | 1.7035 | 70 | 2.0442 | 70 | 2.5552
75 | 0.085173 | 75 | 0.17035 | 75 | 0.34069 | 75 | 0.51104 | 75 | 0.68139 | 75 | 0.85173 | 75 | 1.0221 | 75 | 1.3628 | 75 | 1.7035 | 75 | 2.0442 | 75 | 2.5552
80 | 0.085173 | 80 | 0.17035 | 80 | 0.34069 | 80 | 0.51104 | 80 | 0.68139 | 80 | 0.85173 | 80 | 1.0221 | 80 | 1.3628 | 80 | 1.7035 | 80 | 2.0442 | 80 | 2.5552
85 | 0.085173 | 85 | 0.17035 | 85 | 0.34069 | 85 | 0.51104 | 85 | 0.68139 | 85 | 0.85173 | 85 | 1.0221 | 85 | 1.3628 | 85 | 1.7035 | 85 | 2.0442 | 85 | 2.5552
90 | 0.085173 | 90 | 0.17035 | 90 | 0.34069 | 90 | 0.51104 | 90 | 0.68139 | 90 | 0.85173 | 90 | 1.0221 | 90 | 1.3628 | 90 | 1.7035 | 90 | 2.0442 | 90 | 2.5552
95 | 0.085173 | 95 | 0.17035 | 95 | 0.34069 | 95 | 0.51104 | 95 | 0.68139 | 95 | 0.85173 | 95 | 1.0221 | 95 | 1.3628 | 95 | 1.7035 | 95 | 2.0442 | 95 | 2.5552
100 | 0.085173 | 100 | 0.17035 | 100 | 0.34069 | 100 | 0.51104 | 100 | 0.68139 | 100 | 0.85173 | 100 | 1.0221 | 100 | 1.3628 | 100 | 1.7035 | 100 | 2.0442 | 100 | 2.5552