## 691-9-U2
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
US Inverse (U2) (TCC 691-9-U2) | [9 empty] | US Inverse (U2) (TCC 691-9-U2) | [9 empty] | US Inverse (U2) (TCC 691-9-U2)
Average Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Average Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Average Tripping Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of
| current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5
| cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between
| 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting.
| Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup
| current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds.
Time Dial = 0.5 |  | Time Dial = 1.0 |  | Time Dial = 2.0 |  | Time Dial = 3.0 |  | Time Dial = 4.0 |  | Time Dial = 5.0 |  | Time Dial = 6.0 |  | Time Dial = 8.0 |  | Time Dial = 10.0 |  | Time Dial = 12.0 |  | Time Dial = 15.0
*of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s)
1.5 | 2.47 | 1.5 | 4.94 | 1.5 | 9.88 | 1.5 | 14.82 | 1.5 | 19.76 | 1.5 | 24.7 | 1.5 | 29.64 | 1.5 | 39.52 | 1.5 | 49.4 | 1.5 | 59.28 | 1.5 | 74.1
1.6 | 1.9971 | 1.6 | 3.9941 | 1.6 | 7.9882 | 1.6 | 11.9823 | 1.6 | 15.9764 | 1.6 | 19.9705 | 1.6 | 23.9646 | 1.6 | 31.9528 | 1.6 | 39.941 | 1.6 | 47.9292 | 1.6 | 59.9115
1.7 | 1.6641 | 1.7 | 3.3281 | 1.7 | 6.6563 | 1.7 | 9.9844 | 1.7 | 13.3126 | 1.7 | 16.6407 | 1.7 | 19.9689 | 1.7 | 26.6252 | 1.7 | 33.2815 | 1.7 | 39.9378 | 1.7 | 49.9222
1.8 | 1.4181 | 1.8 | 2.8363 | 1.8 | 5.6725 | 1.8 | 8.5087 | 1.8 | 11.345 | 1.8 | 14.1813 | 1.8 | 17.0175 | 1.8 | 22.69 | 1.8 | 28.3625 | 1.8 | 34.035 | 1.8 | 42.5438
1.9 | 1.2298 | 1.9 | 2.4597 | 1.9 | 4.9194 | 1.9 | 7.3791 | 1.9 | 9.8388 | 1.9 | 12.2985 | 1.9 | 14.7582 | 1.9 | 19.6775 | 1.9 | 24.5969 | 1.9 | 29.5163 | 1.9 | 36.8954
2 | 1.0817 | 2 | 2.1633 | 2 | 4.3267 | 2 | 6.49 | 2 | 8.6533 | 2 | 10.8167 | 2 | 12.98 | 2 | 17.3067 | 2 | 21.6333 | 2 | 25.96 | 2 | 32.45
2.1 | 0.96243 | 2.1 | 1.9249 | 2.1 | 3.8497 | 2.1 | 5.7746 | 2.1 | 7.6995 | 2.1 | 9.6243 | 2.1 | 11.5492 | 2.1 | 15.3989 | 2.1 | 19.2487 | 2.1 | 23.0984 | 2.1 | 28.873
2.2 | 0.86474 | 2.2 | 1.7295 | 2.2 | 3.459 | 2.2 | 5.1884 | 2.2 | 6.9179 | 2.2 | 8.6474 | 2.2 | 10.3769 | 2.2 | 13.8358 | 2.2 | 17.2948 | 2.2 | 20.7538 | 2.2 | 25.9422
2.3 | 0.78347 | 2.3 | 1.5669 | 2.3 | 3.1339 | 2.3 | 4.7008 | 2.3 | 6.2678 | 2.3 | 7.8347 | 2.3 | 9.4017 | 2.3 | 12.5356 | 2.3 | 15.6695 | 2.3 | 18.8034 | 2.3 | 23.5042
2.4 | 0.715 | 2.4 | 1.43 | 2.4 | 2.86 | 2.4 | 4.29 | 2.4 | 5.72 | 2.4 | 7.15 | 2.4 | 8.58 | 2.4 | 11.44 | 2.4 | 14.3 | 2.4 | 17.16 | 2.4 | 21.45
2.5 | 0.65667 | 2.5 | 1.3133 | 2.5 | 2.6267 | 2.5 | 3.94 | 2.5 | 5.2533 | 2.5 | 6.5667 | 2.5 | 7.88 | 2.5 | 10.5067 | 2.5 | 13.1333 | 2.5 | 15.76 | 2.5 | 19.7
2.6 | 0.60649 | 2.6 | 1.213 | 2.6 | 2.426 | 2.6 | 3.639 | 2.6 | 4.8519 | 2.6 | 6.0649 | 2.6 | 7.2779 | 2.6 | 9.7039 | 2.6 | 12.1299 | 2.6 | 14.5558 | 2.6 | 18.1948
2.7 | 0.56297 | 2.7 | 1.1259 | 2.7 | 2.2519 | 2.7 | 3.3778 | 2.7 | 4.5038 | 2.7 | 5.6297 | 2.7 | 6.7557 | 2.7 | 9.0076 | 2.7 | 11.2595 | 2.7 | 13.5114 | 2.7 | 16.8892
2.8 | 0.52494 | 2.8 | 1.0499 | 2.8 | 2.0998 | 2.8 | 3.1496 | 2.8 | 4.1995 | 2.8 | 5.2494 | 2.8 | 6.2993 | 2.8 | 8.3991 | 2.8 | 10.4988 | 2.8 | 12.5986 | 2.8 | 15.7482
2.9 | 0.49148 | 2.9 | 0.98297 | 2.9 | 1.9659 | 2.9 | 2.9489 | 2.9 | 3.9319 | 2.9 | 4.9148 | 2.9 | 5.8978 | 2.9 | 7.8638 | 2.9 | 9.8297 | 2.9 | 11.7956 | 2.9 | 14.7445
3 | 0.46187 | 3 | 0.92375 | 3 | 1.8475 | 3 | 2.7713 | 3 | 3.695 | 3 | 4.6188 | 3 | 5.5425 | 3 | 7.39 | 3 | 9.2375 | 3 | 11.085 | 3 | 13.8562
3.1 | 0.43553 | 3.1 | 0.87106 | 3.1 | 1.7421 | 3.1 | 2.6132 | 3.1 | 3.4842 | 3.1 | 4.3553 | 3.1 | 5.2263 | 3.1 | 6.9685 | 3.1 | 8.7106 | 3.1 | 10.4527 | 3.1 | 13.0659
3.2 | 0.41197 | 3.2 | 0.82394 | 3.2 | 1.6479 | 3.2 | 2.4718 | 3.2 | 3.2958 | 3.2 | 4.1197 | 3.2 | 4.9436 | 3.2 | 6.5915 | 3.2 | 8.2394 | 3.2 | 9.8873 | 3.2 | 12.3591
3.3 | 0.39081 | 3.3 | 0.78162 | 3.3 | 1.5632 | 3.3 | 2.3449 | 3.3 | 3.1265 | 3.3 | 3.9081 | 3.3 | 4.6897 | 3.3 | 6.2529 | 3.3 | 7.8162 | 3.3 | 9.3794 | 3.3 | 11.7243
3.4 | 0.37172 | 3.4 | 0.74345 | 3.4 | 1.4869 | 3.4 | 2.2303 | 3.4 | 2.9738 | 3.4 | 3.7172 | 3.4 | 4.4607 | 3.4 | 5.9476 | 3.4 | 7.4345 | 3.4 | 8.9214 | 3.4 | 11.1517
3.5 | 0.35444 | 3.5 | 0.70889 | 3.5 | 1.4178 | 3.5 | 2.1267 | 3.5 | 2.8356 | 3.5 | 3.5444 | 3.5 | 4.2533 | 3.5 | 5.6711 | 3.5 | 7.0889 | 3.5 | 8.5067 | 3.5 | 10.6333
3.6 | 0.33875 | 3.6 | 0.67749 | 3.6 | 1.355 | 3.6 | 2.0325 | 3.6 | 2.71 | 3.6 | 3.3875 | 3.6 | 4.0649 | 3.6 | 5.4199 | 3.6 | 6.7749 | 3.6 | 8.1299 | 3.6 | 10.1624
3.7 | 0.32444 | 3.7 | 0.64887 | 3.7 | 1.2977 | 3.7 | 1.9466 | 3.7 | 2.5955 | 3.7 | 3.2444 | 3.7 | 3.8932 | 3.7 | 5.191 | 3.7 | 6.4887 | 3.7 | 7.7865 | 3.7 | 9.7331
3.8 | 0.31135 | 3.8 | 0.62271 | 3.8 | 1.2454 | 3.8 | 1.8681 | 3.8 | 2.4908 | 3.8 | 3.1135 | 3.8 | 3.7363 | 3.8 | 4.9817 | 3.8 | 6.2271 | 3.8 | 7.4725 | 3.8 | 9.3406
3.9 | 0.29936 | 3.9 | 0.59872 | 3.9 | 1.1974 | 3.9 | 1.7962 | 3.9 | 2.3949 | 3.9 | 2.9936 | 3.9 | 3.5923 | 3.9 | 4.7898 | 3.9 | 5.9872 | 3.9 | 7.1846 | 3.9 | 8.9808
4 | 0.28833 | 4 | 0.57667 | 4 | 1.1533 | 4 | 1.73 | 4 | 2.3067 | 4 | 2.8833 | 4 | 3.46 | 4 | 4.6133 | 4 | 5.7667 | 4 | 6.92 | 4 | 8.65
4.1 | 0.27817 | 4.1 | 0.55634 | 4.1 | 1.1127 | 4.1 | 1.669 | 4.1 | 2.2254 | 4.1 | 2.7817 | 4.1 | 3.3381 | 4.1 | 4.4508 | 4.1 | 5.5634 | 4.1 | 6.6761 | 4.1 | 8.3452
4.2 | 0.26879 | 4.2 | 0.53757 | 4.2 | 1.0751 | 4.2 | 1.6127 | 4.2 | 2.1503 | 4.2 | 2.6879 | 4.2 | 3.2254 | 4.2 | 4.3006 | 4.2 | 5.3757 | 4.2 | 6.4509 | 4.2 | 8.0636
4.3 | 0.2601 | 4.3 | 0.52019 | 4.3 | 1.0404 | 4.3 | 1.5606 | 4.3 | 2.0808 | 4.3 | 2.601 | 4.3 | 3.1212 | 4.3 | 4.1616 | 4.3 | 5.2019 | 4.3 | 6.2423 | 4.3 | 7.8029
4.4 | 0.25204 | 4.4 | 0.50407 | 4.4 | 1.0081 | 4.4 | 1.5122 | 4.4 | 2.0163 | 4.4 | 2.5204 | 4.4 | 3.0244 | 4.4 | 4.0326 | 4.4 | 5.0407 | 4.4 | 6.0489 | 4.4 | 7.5611
4.5 | 0.24455 | 4.5 | 0.48909 | 4.5 | 0.97818 | 4.5 | 1.4673 | 4.5 | 1.9564 | 4.5 | 2.4455 | 4.5 | 2.9345 | 4.5 | 3.9127 | 4.5 | 4.8909 | 4.5 | 5.8691 | 4.5 | 7.3364
4.6 | 0.23757 | 4.6 | 0.47514 | 4.6 | 0.95028 | 4.6 | 1.4254 | 4.6 | 1.9006 | 4.6 | 2.3757 | 4.6 | 2.8508 | 4.6 | 3.8011 | 4.6 | 4.7514 | 4.6 | 5.7017 | 4.6 | 7.1271
4.7 | 0.23106 | 4.7 | 0.46212 | 4.7 | 0.92425 | 4.7 | 1.3864 | 4.7 | 1.8485 | 4.7 | 2.3106 | 4.7 | 2.7727 | 4.7 | 3.697 | 4.7 | 4.6212 | 4.7 | 5.5455 | 4.7 | 6.9319
4.8 | 0.22498 | 4.8 | 0.44996 | 4.8 | 0.89993 | 4.8 | 1.3499 | 4.8 | 1.7999 | 4.8 | 2.2498 | 4.8 | 2.6998 | 4.8 | 3.5997 | 4.8 | 4.4996 | 4.8 | 5.3996 | 4.8 | 6.7495
4.9 | 0.21929 | 4.9 | 0.43858 | 4.9 | 0.87717 | 4.9 | 1.3157 | 4.9 | 1.7543 | 4.9 | 2.1929 | 4.9 | 2.6315 | 4.9 | 3.5087 | 4.9 | 4.3858 | 4.9 | 5.263 | 4.9 | 6.5787
5 | 0.21396 | 5 | 0.42792 | 5 | 0.85583 | 5 | 1.2837 | 5 | 1.7117 | 5 | 2.1396 | 5 | 2.5675 | 5 | 3.4233 | 5 | 4.2792 | 5 | 5.135 | 5 | 6.4188
5.1 | 0.20895 | 5.1 | 0.4179 | 5.1 | 0.83581 | 5.1 | 1.2537 | 5.1 | 1.6716 | 5.1 | 2.0895 | 5.1 | 2.5074 | 5.1 | 3.3432 | 5.1 | 4.179 | 5.1 | 5.0149 | 5.1 | 6.2686
5.2 | 0.20425 | 5.2 | 0.40849 | 5.2 | 0.81699 | 5.2 | 1.2255 | 5.2 | 1.634 | 5.2 | 2.0425 | 5.2 | 2.451 | 5.2 | 3.268 | 5.2 | 4.0849 | 5.2 | 4.9019 | 5.2 | 6.1274
5.3 | 0.19982 | 5.3 | 0.39964 | 5.3 | 0.79928 | 5.3 | 1.1989 | 5.3 | 1.5986 | 5.3 | 1.9982 | 5.3 | 2.3978 | 5.3 | 3.1971 | 5.3 | 3.9964 | 5.3 | 4.7957 | 5.3 | 5.9946
5.4 | 0.19565 | 5.4 | 0.39129 | 5.4 | 0.78259 | 5.4 | 1.1739 | 5.4 | 1.5652 | 5.4 | 1.9565 | 5.4 | 2.3478 | 5.4 | 3.1303 | 5.4 | 3.9129 | 5.4 | 4.6955 | 5.4 | 5.8694
5.5 | 0.19171 | 5.5 | 0.38342 | 5.5 | 0.76684 | 5.5 | 1.1503 | 5.5 | 1.5337 | 5.5 | 1.9171 | 5.5 | 2.3005 | 5.5 | 3.0674 | 5.5 | 3.8342 | 5.5 | 4.601 | 5.5 | 5.7513
5.6 | 0.18799 | 5.6 | 0.37598 | 5.6 | 0.75196 | 5.6 | 1.1279 | 5.6 | 1.5039 | 5.6 | 1.8799 | 5.6 | 2.2559 | 5.6 | 3.0079 | 5.6 | 3.7598 | 5.6 | 4.5118 | 5.6 | 5.6397
5.7 | 0.18447 | 5.7 | 0.36895 | 5.7 | 0.7379 | 5.7 | 1.1068 | 5.7 | 1.4758 | 5.7 | 1.8447 | 5.7 | 2.2137 | 5.7 | 2.9516 | 5.7 | 3.6895 | 5.7 | 4.4274 | 5.7 | 5.5342
5.8 | 0.18115 | 5.8 | 0.36229 | 5.8 | 0.72458 | 5.8 | 1.0869 | 5.8 | 1.4492 | 5.8 | 1.8115 | 5.8 | 2.1738 | 5.8 | 2.8983 | 5.8 | 3.6229 | 5.8 | 4.3475 | 5.8 | 5.4344
5.9 | 0.17799 | 5.9 | 0.35598 | 5.9 | 0.71197 | 5.9 | 1.068 | 5.9 | 1.4239 | 5.9 | 1.7799 | 5.9 | 2.1359 | 5.9 | 2.8479 | 5.9 | 3.5598 | 5.9 | 4.2718 | 5.9 | 5.3398
6 | 0.175 | 6 | 0.35 | 6 | 0.7 | 6 | 1.05 | 6 | 1.4 | 6 | 1.75 | 6 | 2.1 | 6 | 2.8 | 6 | 3.5 | 6 | 4.2 | 6 | 5.25
6.1 | 0.17216 | 6.1 | 0.34432 | 6.1 | 0.68864 | 6.1 | 1.033 | 6.1 | 1.3773 | 6.1 | 1.7216 | 6.1 | 2.0659 | 6.1 | 2.7546 | 6.1 | 3.4432 | 6.1 | 4.1318 | 6.1 | 5.1648
6.2 | 0.16946 | 6.2 | 0.33892 | 6.2 | 0.67784 | 6.2 | 1.0168 | 6.2 | 1.3557 | 6.2 | 1.6946 | 6.2 | 2.0335 | 6.2 | 2.7114 | 6.2 | 3.3892 | 6.2 | 4.0671 | 6.2 | 5.0838
6.3 | 0.16689 | 6.3 | 0.33379 | 6.3 | 0.66757 | 6.3 | 1.0014 | 6.3 | 1.3351 | 6.3 | 1.6689 | 6.3 | 2.0027 | 6.3 | 2.6703 | 6.3 | 3.3379 | 6.3 | 4.0054 | 6.3 | 5.0068
6.4 | 0.16445 | 6.4 | 0.3289 | 6.4 | 0.6578 | 6.4 | 0.9867 | 6.4 | 1.3156 | 6.4 | 1.6445 | 6.4 | 1.9734 | 6.4 | 2.6312 | 6.4 | 3.289 | 6.4 | 3.9468 | 6.4 | 4.9335
6.5 | 0.16212 | 6.5 | 0.32424 | 6.5 | 0.64848 | 6.5 | 0.97273 | 6.5 | 1.297 | 6.5 | 1.6212 | 6.5 | 1.9455 | 6.5 | 2.5939 | 6.5 | 3.2424 | 6.5 | 3.8909 | 6.5 | 4.8636
6.6 | 0.1599 | 6.6 | 0.3198 | 6.6 | 0.63961 | 6.6 | 0.95941 | 6.6 | 1.2792 | 6.6 | 1.599 | 6.6 | 1.9188 | 6.6 | 2.5584 | 6.6 | 3.198 | 6.6 | 3.8376 | 6.6 | 4.797
6.7 | 0.15778 | 6.7 | 0.31557 | 6.7 | 0.63113 | 6.7 | 0.9467 | 6.7 | 1.2623 | 6.7 | 1.5778 | 6.7 | 1.8934 | 6.7 | 2.5245 | 6.7 | 3.1557 | 6.7 | 3.7868 | 6.7 | 4.7335
6.8 | 0.15576 | 6.8 | 0.31152 | 6.8 | 0.62304 | 6.8 | 0.93456 | 6.8 | 1.2461 | 6.8 | 1.5576 | 6.8 | 1.8691 | 6.8 | 2.4922 | 6.8 | 3.1152 | 6.8 | 3.7382 | 6.8 | 4.6728
6.9 | 0.15383 | 6.9 | 0.30766 | 6.9 | 0.61531 | 6.9 | 0.92297 | 6.9 | 1.2306 | 6.9 | 1.5383 | 6.9 | 1.8459 | 6.9 | 2.4612 | 6.9 | 3.0766 | 6.9 | 3.6919 | 6.9 | 4.6148
7 | 0.15198 | 7 | 0.30396 | 7 | 0.60792 | 7 | 0.91187 | 7 | 1.2158 | 7 | 1.5198 | 7 | 1.8237 | 7 | 2.4317 | 7 | 3.0396 | 7 | 3.6475 | 7 | 4.5594
7.1 | 0.15021 | 7.1 | 0.30042 | 7.1 | 0.60084 | 7.1 | 0.90126 | 7.1 | 1.2017 | 7.1 | 1.5021 | 7.1 | 1.8025 | 7.1 | 2.4034 | 7.1 | 3.0042 | 7.1 | 3.6051 | 7.1 | 4.5063
7.2 | 0.14852 | 7.2 | 0.29703 | 7.2 | 0.59407 | 7.2 | 0.8911 | 7.2 | 1.1881 | 7.2 | 1.4852 | 7.2 | 1.7822 | 7.2 | 2.3763 | 7.2 | 2.9703 | 7.2 | 3.5644 | 7.2 | 4.4555
7.3 | 0.14689 | 7.3 | 0.29379 | 7.3 | 0.58758 | 7.3 | 0.88137 | 7.3 | 1.1752 | 7.3 | 1.4689 | 7.3 | 1.7627 | 7.3 | 2.3503 | 7.3 | 2.9379 | 7.3 | 3.5255 | 7.3 | 4.4068
7.4 | 0.14534 | 7.4 | 0.29068 | 7.4 | 0.58135 | 7.4 | 0.87203 | 7.4 | 1.1627 | 7.4 | 1.4534 | 7.4 | 1.7441 | 7.4 | 2.3254 | 7.4 | 2.9068 | 7.4 | 3.4881 | 7.4 | 4.3602
7.5 | 0.14385 | 7.5 | 0.28769 | 7.5 | 0.57538 | 7.5 | 0.86308 | 7.5 | 1.1508 | 7.5 | 1.4385 | 7.5 | 1.7262 | 7.5 | 2.3015 | 7.5 | 2.8769 | 7.5 | 3.4523 | 7.5 | 4.3154
7.6 | 0.14241 | 7.6 | 0.28483 | 7.6 | 0.56965 | 7.6 | 0.85448 | 7.6 | 1.1393 | 7.6 | 1.4241 | 7.6 | 1.709 | 7.6 | 2.2786 | 7.6 | 2.8483 | 7.6 | 3.4179 | 7.6 | 4.2724
7.7 | 0.14104 | 7.7 | 0.28208 | 7.7 | 0.56415 | 7.7 | 0.84623 | 7.7 | 1.1283 | 7.7 | 1.4104 | 7.7 | 1.6925 | 7.7 | 2.2566 | 7.7 | 2.8208 | 7.7 | 3.3849 | 7.7 | 4.2311
7.8 | 0.13972 | 7.8 | 0.27943 | 7.8 | 0.55886 | 7.8 | 0.8383 | 7.8 | 1.1177 | 7.8 | 1.3972 | 7.8 | 1.6766 | 7.8 | 2.2355 | 7.8 | 2.7943 | 7.8 | 3.3532 | 7.8 | 4.1915
7.9 | 0.13844 | 7.9 | 0.27689 | 7.9 | 0.55378 | 7.9 | 0.83067 | 7.9 | 1.1076 | 7.9 | 1.3844 | 7.9 | 1.6613 | 7.9 | 2.2151 | 7.9 | 2.7689 | 7.9 | 3.3227 | 7.9 | 4.1533
8 | 0.13722 | 8 | 0.27444 | 8 | 0.54889 | 8 | 0.82333 | 8 | 1.0978 | 8 | 1.3722 | 8 | 1.6467 | 8 | 2.1956 | 8 | 2.7444 | 8 | 3.2933 | 8 | 4.1167
8.1 | 0.13605 | 8.1 | 0.27209 | 8.1 | 0.54418 | 8.1 | 0.81627 | 8.1 | 1.0884 | 8.1 | 1.3605 | 8.1 | 1.6325 | 8.1 | 2.1767 | 8.1 | 2.7209 | 8.1 | 3.2651 | 8.1 | 4.0814
8.2 | 0.13491 | 8.2 | 0.26982 | 8.2 | 0.53965 | 8.2 | 0.80947 | 8.2 | 1.0793 | 8.2 | 1.3491 | 8.2 | 1.6189 | 8.2 | 2.1586 | 8.2 | 2.6982 | 8.2 | 3.2379 | 8.2 | 4.0474
8.3 | 0.13382 | 8.3 | 0.26764 | 8.3 | 0.53528 | 8.3 | 0.80293 | 8.3 | 1.0706 | 8.3 | 1.3382 | 8.3 | 1.6059 | 8.3 | 2.1411 | 8.3 | 2.6764 | 8.3 | 3.2117 | 8.3 | 4.0146
8.4 | 0.13277 | 8.4 | 0.26554 | 8.4 | 0.53108 | 8.4 | 0.79661 | 8.4 | 1.0622 | 8.4 | 1.3277 | 8.4 | 1.5932 | 8.4 | 2.1243 | 8.4 | 2.6554 | 8.4 | 3.1865 | 8.4 | 3.9831
8.5 | 0.13175 | 8.5 | 0.26351 | 8.5 | 0.52702 | 8.5 | 0.79053 | 8.5 | 1.054 | 8.5 | 1.3175 | 8.5 | 1.5811 | 8.5 | 2.1081 | 8.5 | 2.6351 | 8.5 | 3.1621 | 8.5 | 3.9526
8.6 | 0.13078 | 8.6 | 0.26155 | 8.6 | 0.5231 | 8.6 | 0.78465 | 8.6 | 1.0462 | 8.6 | 1.3078 | 8.6 | 1.5693 | 8.6 | 2.0924 | 8.6 | 2.6155 | 8.6 | 3.1386 | 8.6 | 3.9233
8.7 | 0.12983 | 8.7 | 0.25966 | 8.7 | 0.51933 | 8.7 | 0.77899 | 8.7 | 1.0387 | 8.7 | 1.2983 | 8.7 | 1.558 | 8.7 | 2.0773 | 8.7 | 2.5966 | 8.7 | 3.116 | 8.7 | 3.8949
8.8 | 0.12892 | 8.8 | 0.25784 | 8.8 | 0.51568 | 8.8 | 0.77352 | 8.8 | 1.0314 | 8.8 | 1.2892 | 8.8 | 1.547 | 8.8 | 2.0627 | 8.8 | 2.5784 | 8.8 | 3.0941 | 8.8 | 3.8676
8.9 | 0.12804 | 8.9 | 0.25608 | 8.9 | 0.51215 | 8.9 | 0.76823 | 8.9 | 1.0243 | 8.9 | 1.2804 | 8.9 | 1.5365 | 8.9 | 2.0486 | 8.9 | 2.5608 | 8.9 | 3.0729 | 8.9 | 3.8412
9 | 0.12719 | 9 | 0.25438 | 9 | 0.50875 | 9 | 0.76313 | 9 | 1.0175 | 9 | 1.2719 | 9 | 1.5263 | 9 | 2.035 | 9 | 2.5438 | 9 | 3.0525 | 9 | 3.8156
9.1 | 0.12636 | 9.1 | 0.25273 | 9.1 | 0.50546 | 9.1 | 0.75819 | 9.1 | 1.0109 | 9.1 | 1.2636 | 9.1 | 1.5164 | 9.1 | 2.0218 | 9.1 | 2.5273 | 9.1 | 3.0328 | 9.1 | 3.7909
9.2 | 0.12557 | 9.2 | 0.25114 | 9.2 | 0.50228 | 9.2 | 0.75341 | 9.2 | 1.0046 | 9.2 | 1.2557 | 9.2 | 1.5068 | 9.2 | 2.0091 | 9.2 | 2.5114 | 9.2 | 3.0137 | 9.2 | 3.7671
9.3 | 0.1248 | 9.3 | 0.2496 | 9.3 | 0.4992 | 9.3 | 0.7488 | 9.3 | 0.9984 | 9.3 | 1.248 | 9.3 | 1.4976 | 9.3 | 1.9968 | 9.3 | 2.496 | 9.3 | 2.9952 | 9.3 | 3.744
9.4 | 0.12405 | 9.4 | 0.24811 | 9.4 | 0.49622 | 9.4 | 0.74433 | 9.4 | 0.99244 | 9.4 | 1.2405 | 9.4 | 1.4887 | 9.4 | 1.9849 | 9.4 | 2.4811 | 9.4 | 2.9773 | 9.4 | 3.7216
9.5 | 0.12333 | 9.5 | 0.24667 | 9.5 | 0.49333 | 9.5 | 0.74 | 9.5 | 0.98667 | 9.5 | 1.2333 | 9.5 | 1.48 | 9.5 | 1.9733 | 9.5 | 2.4667 | 9.5 | 2.96 | 9.5 | 3.7
9.6 | 0.12263 | 9.6 | 0.24527 | 9.6 | 0.49054 | 9.6 | 0.73581 | 9.6 | 0.98108 | 9.6 | 1.2263 | 9.6 | 1.4716 | 9.6 | 1.9622 | 9.6 | 2.4527 | 9.6 | 2.9432 | 9.6 | 3.679
9.7 | 0.12196 | 9.7 | 0.24392 | 9.7 | 0.48783 | 9.7 | 0.73175 | 9.7 | 0.97567 | 9.7 | 1.2196 | 9.7 | 1.4635 | 9.7 | 1.9513 | 9.7 | 2.4392 | 9.7 | 2.927 | 9.7 | 3.6587
9.8 | 0.1213 | 9.8 | 0.24261 | 9.8 | 0.48521 | 9.8 | 0.72782 | 9.8 | 0.97042 | 9.8 | 1.213 | 9.8 | 1.4556 | 9.8 | 1.9408 | 9.8 | 2.4261 | 9.8 | 2.9113 | 9.8 | 3.6391
9.9 | 0.12067 | 9.9 | 0.24133 | 9.9 | 0.48267 | 9.9 | 0.724 | 9.9 | 0.96534 | 9.9 | 1.2067 | 9.9 | 1.448 | 9.9 | 1.9307 | 9.9 | 2.4133 | 9.9 | 2.896 | 9.9 | 3.62
10 | 0.12005 | 10 | 0.2401 | 10 | 0.4802 | 10 | 0.7203 | 10 | 0.9604 | 10 | 1.2005 | 10 | 1.4406 | 10 | 1.9208 | 10 | 2.401 | 10 | 2.8812 | 10 | 3.6015
10.5 | 0.11723 | 10.5 | 0.23446 | 10.5 | 0.46892 | 10.5 | 0.70339 | 10.5 | 0.93785 | 10.5 | 1.1723 | 10.5 | 1.4068 | 10.5 | 1.8757 | 10.5 | 2.3446 | 10.5 | 2.8135 | 10.5 | 3.5169
11 | 0.11479 | 11 | 0.22958 | 11 | 0.45917 | 11 | 0.68875 | 11 | 0.91833 | 11 | 1.1479 | 11 | 1.3775 | 11 | 1.8367 | 11 | 2.2958 | 11 | 2.755 | 11 | 3.4438
11.5 | 0.11267 | 11.5 | 0.22533 | 11.5 | 0.45067 | 11.5 | 0.676 | 11.5 | 0.90133 | 11.5 | 1.1267 | 11.5 | 1.352 | 11.5 | 1.8027 | 11.5 | 2.2533 | 11.5 | 2.704 | 11.5 | 3.38
12 | 0.1108 | 12 | 0.22161 | 12 | 0.44322 | 12 | 0.66483 | 12 | 0.88643 | 12 | 1.108 | 12 | 1.3297 | 12 | 1.7729 | 12 | 2.2161 | 12 | 2.6593 | 12 | 3.3241
12.5 | 0.10916 | 12.5 | 0.21833 | 12.5 | 0.43665 | 12.5 | 0.65498 | 12.5 | 0.8733 | 12.5 | 1.0916 | 12.5 | 1.31 | 12.5 | 1.7466 | 12.5 | 2.1833 | 12.5 | 2.6199 | 12.5 | 3.2749
13 | 0.10771 | 13 | 0.21542 | 13 | 0.43083 | 13 | 0.64625 | 13 | 0.86167 | 13 | 1.0771 | 13 | 1.2925 | 13 | 1.7233 | 13 | 2.1542 | 13 | 2.585 | 13 | 3.2313
13.5 | 0.10641 | 13.5 | 0.21283 | 13.5 | 0.42566 | 13.5 | 0.63848 | 13.5 | 0.85131 | 13.5 | 1.0641 | 13.5 | 1.277 | 13.5 | 1.7026 | 13.5 | 2.1283 | 13.5 | 2.5539 | 13.5 | 3.1924
14 | 0.10526 | 14 | 0.21051 | 14 | 0.42103 | 14 | 0.63154 | 14 | 0.84205 | 14 | 1.0526 | 14 | 1.2631 | 14 | 1.6841 | 14 | 2.1051 | 14 | 2.5262 | 14 | 3.1577
14.5 | 0.10422 | 14.5 | 0.20843 | 14.5 | 0.41687 | 14.5 | 0.6253 | 14.5 | 0.83374 | 14.5 | 1.0422 | 14.5 | 1.2506 | 14.5 | 1.6675 | 14.5 | 2.0843 | 14.5 | 2.5012 | 14.5 | 3.1265
15 | 0.10328 | 15 | 0.20656 | 15 | 0.41313 | 15 | 0.61969 | 15 | 0.82625 | 15 | 1.0328 | 15 | 1.2394 | 15 | 1.6525 | 15 | 2.0656 | 15 | 2.4787 | 15 | 3.0984
16 | 0.10167 | 16 | 0.20333 | 16 | 0.40667 | 16 | 0.61 | 16 | 0.81333 | 16 | 1.0167 | 16 | 1.22 | 16 | 1.6267 | 16 | 2.0333 | 16 | 2.44 | 16 | 3.05
17 | 0.10033 | 17 | 0.20066 | 17 | 0.40132 | 17 | 0.60198 | 17 | 0.80264 | 17 | 1.0033 | 17 | 1.204 | 17 | 1.6053 | 17 | 2.0066 | 17 | 2.4079 | 17 | 3.0099
18 | 0.099211 | 18 | 0.19842 | 18 | 0.39684 | 18 | 0.59526 | 18 | 0.79368 | 18 | 0.99211 | 18 | 1.1905 | 18 | 1.5874 | 18 | 1.9842 | 18 | 2.3811 | 18 | 2.9763
19 | 0.098264 | 19 | 0.19653 | 19 | 0.39306 | 19 | 0.58958 | 19 | 0.78611 | 19 | 0.98264 | 19 | 1.1792 | 19 | 1.5722 | 19 | 1.9653 | 19 | 2.3583 | 19 | 2.9479
20 | 0.097456 | 20 | 0.19491 | 20 | 0.38982 | 20 | 0.58474 | 20 | 0.77965 | 20 | 0.97456 | 20 | 1.1695 | 20 | 1.5593 | 20 | 1.9491 | 20 | 2.3389 | 20 | 2.9237
21 | 0.096761 | 21 | 0.19352 | 21 | 0.38705 | 21 | 0.58057 | 21 | 0.77409 | 21 | 0.96761 | 21 | 1.1611 | 21 | 1.5482 | 21 | 1.9352 | 21 | 2.3223 | 21 | 2.9028
22 | 0.096159 | 22 | 0.19232 | 22 | 0.38464 | 22 | 0.57696 | 22 | 0.76928 | 22 | 0.96159 | 22 | 1.1539 | 22 | 1.5386 | 22 | 1.9232 | 22 | 2.3078 | 22 | 2.8848
23 | 0.095634 | 23 | 0.19127 | 23 | 0.38254 | 23 | 0.57381 | 23 | 0.76508 | 23 | 0.95634 | 23 | 1.1476 | 23 | 1.5302 | 23 | 1.9127 | 23 | 2.2952 | 23 | 2.869
24 | 0.095174 | 24 | 0.19035 | 24 | 0.3807 | 24 | 0.57104 | 24 | 0.76139 | 24 | 0.95174 | 24 | 1.1421 | 24 | 1.5228 | 24 | 1.9035 | 24 | 2.2842 | 24 | 2.8552
25 | 0.094768 | 25 | 0.18954 | 25 | 0.37907 | 25 | 0.56861 | 25 | 0.75814 | 25 | 0.94768 | 25 | 1.1372 | 25 | 1.5163 | 25 | 1.8954 | 25 | 2.2744 | 25 | 2.843
26 | 0.094407 | 26 | 0.18881 | 26 | 0.37763 | 26 | 0.56644 | 26 | 0.75526 | 26 | 0.94407 | 26 | 1.1329 | 26 | 1.5105 | 26 | 1.8881 | 26 | 2.2658 | 26 | 2.8322
27 | 0.094087 | 27 | 0.18817 | 27 | 0.37635 | 27 | 0.56452 | 27 | 0.75269 | 27 | 0.94087 | 27 | 1.129 | 27 | 1.5054 | 27 | 1.8817 | 27 | 2.2581 | 27 | 2.8226
28 | 0.093799 | 28 | 0.1876 | 28 | 0.3752 | 28 | 0.5628 | 28 | 0.7504 | 28 | 0.93799 | 28 | 1.1256 | 28 | 1.5008 | 28 | 1.876 | 28 | 2.2512 | 28 | 2.814
29 | 0.093542 | 29 | 0.18708 | 29 | 0.37417 | 29 | 0.56125 | 29 | 0.74833 | 29 | 0.93542 | 29 | 1.1225 | 29 | 1.4967 | 29 | 1.8708 | 29 | 2.245 | 29 | 2.8062
30 | 0.093309 | 30 | 0.18662 | 30 | 0.37324 | 30 | 0.55986 | 30 | 0.74647 | 30 | 0.93309 | 30 | 1.1197 | 30 | 1.4929 | 30 | 1.8662 | 30 | 2.2394 | 30 | 2.7993
31 | 0.093309 | 31 | 0.18662 | 31 | 0.37324 | 31 | 0.55986 | 31 | 0.74647 | 31 | 0.93309 | 31 | 1.1197 | 31 | 1.4929 | 31 | 1.8662 | 31 | 2.2394 | 31 | 2.7993
32 | 0.093309 | 32 | 0.18662 | 32 | 0.37324 | 32 | 0.55986 | 32 | 0.74647 | 32 | 0.93309 | 32 | 1.1197 | 32 | 1.4929 | 32 | 1.8662 | 32 | 2.2394 | 32 | 2.7993
33 | 0.093309 | 33 | 0.18662 | 33 | 0.37324 | 33 | 0.55986 | 33 | 0.74647 | 33 | 0.93309 | 33 | 1.1197 | 33 | 1.4929 | 33 | 1.8662 | 33 | 2.2394 | 33 | 2.7993
34 | 0.093309 | 34 | 0.18662 | 34 | 0.37324 | 34 | 0.55986 | 34 | 0.74647 | 34 | 0.93309 | 34 | 1.1197 | 34 | 1.4929 | 34 | 1.8662 | 34 | 2.2394 | 34 | 2.7993
35 | 0.093309 | 35 | 0.18662 | 35 | 0.37324 | 35 | 0.55986 | 35 | 0.74647 | 35 | 0.93309 | 35 | 1.1197 | 35 | 1.4929 | 35 | 1.8662 | 35 | 2.2394 | 35 | 2.7993
36 | 0.093309 | 36 | 0.18662 | 36 | 0.37324 | 36 | 0.55986 | 36 | 0.74647 | 36 | 0.93309 | 36 | 1.1197 | 36 | 1.4929 | 36 | 1.8662 | 36 | 2.2394 | 36 | 2.7993
37 | 0.093309 | 37 | 0.18662 | 37 | 0.37324 | 37 | 0.55986 | 37 | 0.74647 | 37 | 0.93309 | 37 | 1.1197 | 37 | 1.4929 | 37 | 1.8662 | 37 | 2.2394 | 37 | 2.7993
38 | 0.093309 | 38 | 0.18662 | 38 | 0.37324 | 38 | 0.55986 | 38 | 0.74647 | 38 | 0.93309 | 38 | 1.1197 | 38 | 1.4929 | 38 | 1.8662 | 38 | 2.2394 | 38 | 2.7993
39 | 0.093309 | 39 | 0.18662 | 39 | 0.37324 | 39 | 0.55986 | 39 | 0.74647 | 39 | 0.93309 | 39 | 1.1197 | 39 | 1.4929 | 39 | 1.8662 | 39 | 2.2394 | 39 | 2.7993
40 | 0.093309 | 40 | 0.18662 | 40 | 0.37324 | 40 | 0.55986 | 40 | 0.74647 | 40 | 0.93309 | 40 | 1.1197 | 40 | 1.4929 | 40 | 1.8662 | 40 | 2.2394 | 40 | 2.7993
41 | 0.093309 | 41 | 0.18662 | 41 | 0.37324 | 41 | 0.55986 | 41 | 0.74647 | 41 | 0.93309 | 41 | 1.1197 | 41 | 1.4929 | 41 | 1.8662 | 41 | 2.2394 | 41 | 2.7993
42 | 0.093309 | 42 | 0.18662 | 42 | 0.37324 | 42 | 0.55986 | 42 | 0.74647 | 42 | 0.93309 | 42 | 1.1197 | 42 | 1.4929 | 42 | 1.8662 | 42 | 2.2394 | 42 | 2.7993
43 | 0.093309 | 43 | 0.18662 | 43 | 0.37324 | 43 | 0.55986 | 43 | 0.74647 | 43 | 0.93309 | 43 | 1.1197 | 43 | 1.4929 | 43 | 1.8662 | 43 | 2.2394 | 43 | 2.7993
44 | 0.093309 | 44 | 0.18662 | 44 | 0.37324 | 44 | 0.55986 | 44 | 0.74647 | 44 | 0.93309 | 44 | 1.1197 | 44 | 1.4929 | 44 | 1.8662 | 44 | 2.2394 | 44 | 2.7993
45 | 0.093309 | 45 | 0.18662 | 45 | 0.37324 | 45 | 0.55986 | 45 | 0.74647 | 45 | 0.93309 | 45 | 1.1197 | 45 | 1.4929 | 45 | 1.8662 | 45 | 2.2394 | 45 | 2.7993
46 | 0.093309 | 46 | 0.18662 | 46 | 0.37324 | 46 | 0.55986 | 46 | 0.74647 | 46 | 0.93309 | 46 | 1.1197 | 46 | 1.4929 | 46 | 1.8662 | 46 | 2.2394 | 46 | 2.7993
47 | 0.093309 | 47 | 0.18662 | 47 | 0.37324 | 47 | 0.55986 | 47 | 0.74647 | 47 | 0.93309 | 47 | 1.1197 | 47 | 1.4929 | 47 | 1.8662 | 47 | 2.2394 | 47 | 2.7993
48 | 0.093309 | 48 | 0.18662 | 48 | 0.37324 | 48 | 0.55986 | 48 | 0.74647 | 48 | 0.93309 | 48 | 1.1197 | 48 | 1.4929 | 48 | 1.8662 | 48 | 2.2394 | 48 | 2.7993
49 | 0.093309 | 49 | 0.18662 | 49 | 0.37324 | 49 | 0.55986 | 49 | 0.74647 | 49 | 0.93309 | 49 | 1.1197 | 49 | 1.4929 | 49 | 1.8662 | 49 | 2.2394 | 49 | 2.7993
50 | 0.093309 | 50 | 0.18662 | 50 | 0.37324 | 50 | 0.55986 | 50 | 0.74647 | 50 | 0.93309 | 50 | 1.1197 | 50 | 1.4929 | 50 | 1.8662 | 50 | 2.2394 | 50 | 2.7993
55 | 0.093309 | 55 | 0.18662 | 55 | 0.37324 | 55 | 0.55986 | 55 | 0.74647 | 55 | 0.93309 | 55 | 1.1197 | 55 | 1.4929 | 55 | 1.8662 | 55 | 2.2394 | 55 | 2.7993
60 | 0.093309 | 60 | 0.18662 | 60 | 0.37324 | 60 | 0.55986 | 60 | 0.74647 | 60 | 0.93309 | 60 | 1.1197 | 60 | 1.4929 | 60 | 1.8662 | 60 | 2.2394 | 60 | 2.7993
65 | 0.093309 | 65 | 0.18662 | 65 | 0.37324 | 65 | 0.55986 | 65 | 0.74647 | 65 | 0.93309 | 65 | 1.1197 | 65 | 1.4929 | 65 | 1.8662 | 65 | 2.2394 | 65 | 2.7993
70 | 0.093309 | 70 | 0.18662 | 70 | 0.37324 | 70 | 0.55986 | 70 | 0.74647 | 70 | 0.93309 | 70 | 1.1197 | 70 | 1.4929 | 70 | 1.8662 | 70 | 2.2394 | 70 | 2.7993
75 | 0.093309 | 75 | 0.18662 | 75 | 0.37324 | 75 | 0.55986 | 75 | 0.74647 | 75 | 0.93309 | 75 | 1.1197 | 75 | 1.4929 | 75 | 1.8662 | 75 | 2.2394 | 75 | 2.7993
80 | 0.093309 | 80 | 0.18662 | 80 | 0.37324 | 80 | 0.55986 | 80 | 0.74647 | 80 | 0.93309 | 80 | 1.1197 | 80 | 1.4929 | 80 | 1.8662 | 80 | 2.2394 | 80 | 2.7993
85 | 0.093309 | 85 | 0.18662 | 85 | 0.37324 | 85 | 0.55986 | 85 | 0.74647 | 85 | 0.93309 | 85 | 1.1197 | 85 | 1.4929 | 85 | 1.8662 | 85 | 2.2394 | 85 | 2.7993
90 | 0.093309 | 90 | 0.18662 | 90 | 0.37324 | 90 | 0.55986 | 90 | 0.74647 | 90 | 0.93309 | 90 | 1.1197 | 90 | 1.4929 | 90 | 1.8662 | 90 | 2.2394 | 90 | 2.7993
95 | 0.093309 | 95 | 0.18662 | 95 | 0.37324 | 95 | 0.55986 | 95 | 0.74647 | 95 | 0.93309 | 95 | 1.1197 | 95 | 1.4929 | 95 | 1.8662 | 95 | 2.2394 | 95 | 2.7993
100 | 0.093309 | 100 | 0.18662 | 100 | 0.37324 | 100 | 0.55986 | 100 | 0.74647 | 100 | 0.93309 | 100 | 1.1197 | 100 | 1.4929 | 100 | 1.8662 | 100 | 2.2394 | 100 | 2.7993