## 691-9-U5
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
US Short-Time Inverse (U5) (TCC 691-9-U5) | [9 empty] | US Short-Time Inverse (U5) (TCC 691-9-U5) | [9 empty] | US Short-Time Inverse (U5) (TCC 691-9-U5)
Average Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Average Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Average Tripping Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of
| current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5
| cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between
| 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting.
| Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup
| current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds.
Time Dial = 0.5 |  | Time Dial = 1.0 |  | Time Dial = 2.0 |  | Time Dial = 3.0 |  | Time Dial = 4.0 |  | Time Dial = 5.0 |  | Time Dial = 6.0 |  | Time Dial = 8.0 |  | Time Dial = 10.0 |  | Time Dial = 12.0 |  | Time Dial = 15.0
*of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s)
1.5 | 0.21133 | 1.5 | 0.42265 | 1.5 | 0.8453 | 1.5 | 1.268 | 1.5 | 1.6906 | 1.5 | 2.1133 | 1.5 | 2.5359 | 1.5 | 3.3812 | 1.5 | 4.2265 | 1.5 | 5.0718 | 1.5 | 6.3398
1.6 | 0.18237 | 1.6 | 0.36474 | 1.6 | 0.72948 | 1.6 | 1.0942 | 1.6 | 1.459 | 1.6 | 1.8237 | 1.6 | 2.1884 | 1.6 | 2.9179 | 1.6 | 3.6474 | 1.6 | 4.3769 | 1.6 | 5.4711
1.7 | 0.16159 | 1.7 | 0.32317 | 1.7 | 0.64635 | 1.7 | 0.96952 | 1.7 | 1.2927 | 1.7 | 1.6159 | 1.7 | 1.939 | 1.7 | 2.5854 | 1.7 | 3.2317 | 1.7 | 3.8781 | 1.7 | 4.8476
1.8 | 0.14592 | 1.8 | 0.29184 | 1.8 | 0.58367 | 1.8 | 0.87551 | 1.8 | 1.1673 | 1.8 | 1.4592 | 1.8 | 1.751 | 1.8 | 2.3347 | 1.8 | 2.9184 | 1.8 | 3.502 | 1.8 | 4.3775
1.9 | 0.13366 | 1.9 | 0.26733 | 1.9 | 0.53466 | 1.9 | 0.80199 | 1.9 | 1.0693 | 1.9 | 1.3366 | 1.9 | 1.604 | 1.9 | 2.1386 | 1.9 | 2.6733 | 1.9 | 3.208 | 1.9 | 4.0099
2 | 0.12381 | 2 | 0.24761 | 2 | 0.49523 | 2 | 0.74284 | 2 | 0.99046 | 2 | 1.2381 | 2 | 1.4857 | 2 | 1.9809 | 2 | 2.4761 | 2 | 2.9714 | 2 | 3.7142
2.1 | 0.1157 | 2.1 | 0.23139 | 2.1 | 0.46278 | 2.1 | 0.69418 | 2.1 | 0.92557 | 2.1 | 1.157 | 2.1 | 1.3884 | 2.1 | 1.8511 | 2.1 | 2.3139 | 2.1 | 2.7767 | 2.1 | 3.4709
2.2 | 0.1089 | 2.2 | 0.21779 | 2.2 | 0.43559 | 2.2 | 0.65338 | 2.2 | 0.87117 | 2.2 | 1.089 | 2.2 | 1.3068 | 2.2 | 1.7423 | 2.2 | 2.1779 | 2.2 | 2.6135 | 2.2 | 3.2669
2.3 | 0.10311 | 2.3 | 0.20622 | 2.3 | 0.41244 | 2.3 | 0.61866 | 2.3 | 0.82488 | 2.3 | 1.0311 | 2.3 | 1.2373 | 2.3 | 1.6498 | 2.3 | 2.0622 | 2.3 | 2.4746 | 2.3 | 3.0933
2.4 | 0.098119 | 2.4 | 0.19624 | 2.4 | 0.39248 | 2.4 | 0.58872 | 2.4 | 0.78496 | 2.4 | 0.98119 | 2.4 | 1.1774 | 2.4 | 1.5699 | 2.4 | 1.9624 | 2.4 | 2.3549 | 2.4 | 2.9436
2.5 | 0.093769 | 2.5 | 0.18754 | 2.5 | 0.37507 | 2.5 | 0.56261 | 2.5 | 0.75015 | 2.5 | 0.93769 | 2.5 | 1.1252 | 2.5 | 1.5003 | 2.5 | 1.8754 | 2.5 | 2.2504 | 2.5 | 2.8131
2.55 | 0.091795 | 2.55 | 0.18359 | 2.55 | 0.36718 | 2.55 | 0.55077 | 2.55 | 0.73436 | 2.55 | 0.91795 | 2.55 | 1.1015 | 2.55 | 1.4687 | 2.55 | 1.8359 | 2.55 | 2.2031 | 2.55 | 2.7538
2.6 | 0.089939 | 2.6 | 0.17988 | 2.6 | 0.35975 | 2.6 | 0.53963 | 2.6 | 0.71951 | 2.6 | 0.89939 | 2.6 | 1.0793 | 2.6 | 1.439 | 2.6 | 1.7988 | 2.6 | 2.1585 | 2.6 | 2.6982
2.65 | 0.08819 | 2.65 | 0.17638 | 2.65 | 0.35276 | 2.65 | 0.52914 | 2.65 | 0.70552 | 2.65 | 0.8819 | 2.65 | 1.0583 | 2.65 | 1.411 | 2.65 | 1.7638 | 2.65 | 2.1166 | 2.65 | 2.6457
2.7 | 0.086539 | 2.7 | 0.17308 | 2.7 | 0.34615 | 2.7 | 0.51923 | 2.7 | 0.69231 | 2.7 | 0.86539 | 2.7 | 1.0385 | 2.7 | 1.3846 | 2.7 | 1.7308 | 2.7 | 2.0769 | 2.7 | 2.5962
2.75 | 0.084977 | 2.75 | 0.16995 | 2.75 | 0.33991 | 2.75 | 0.50986 | 2.75 | 0.67982 | 2.75 | 0.84977 | 2.75 | 1.0197 | 2.75 | 1.3596 | 2.75 | 1.6995 | 2.75 | 2.0395 | 2.75 | 2.5493
2.8 | 0.083498 | 2.8 | 0.167 | 2.8 | 0.33399 | 2.8 | 0.50099 | 2.8 | 0.66799 | 2.8 | 0.83498 | 2.8 | 1.002 | 2.8 | 1.336 | 2.8 | 1.67 | 2.8 | 2.004 | 2.8 | 2.5049
2.85 | 0.082095 | 2.85 | 0.16419 | 2.85 | 0.32838 | 2.85 | 0.49257 | 2.85 | 0.65676 | 2.85 | 0.82095 | 2.85 | 0.98514 | 2.85 | 1.3135 | 2.85 | 1.6419 | 2.85 | 1.9703 | 2.85 | 2.4629
2.9 | 0.080762 | 2.9 | 0.16152 | 2.9 | 0.32305 | 2.9 | 0.48457 | 2.9 | 0.64609 | 2.9 | 0.80762 | 2.9 | 0.96914 | 2.9 | 1.2922 | 2.9 | 1.6152 | 2.9 | 1.9383 | 2.9 | 2.4228
2.95 | 0.079493 | 2.95 | 0.15899 | 2.95 | 0.31797 | 2.95 | 0.47696 | 2.95 | 0.63594 | 2.95 | 0.79493 | 2.95 | 0.95391 | 2.95 | 1.2719 | 2.95 | 1.5899 | 2.95 | 1.9078 | 2.95 | 2.3848
3 | 0.078284 | 3 | 0.15657 | 3 | 0.31313 | 3 | 0.4697 | 3 | 0.62627 | 3 | 0.78284 | 3 | 0.9394 | 3 | 1.2525 | 3 | 1.5657 | 3 | 1.8788 | 3 | 2.3485
3.05 | 0.07713 | 3.05 | 0.15426 | 3.05 | 0.30852 | 3.05 | 0.46278 | 3.05 | 0.61704 | 3.05 | 0.7713 | 3.05 | 0.92556 | 3.05 | 1.2341 | 3.05 | 1.5426 | 3.05 | 1.8511 | 3.05 | 2.3139
3.1 | 0.076028 | 3.1 | 0.15206 | 3.1 | 0.30411 | 3.1 | 0.45617 | 3.1 | 0.60823 | 3.1 | 0.76028 | 3.1 | 0.91234 | 3.1 | 1.2165 | 3.1 | 1.5206 | 3.1 | 1.8247 | 3.1 | 2.2808
3.15 | 0.074974 | 3.15 | 0.14995 | 3.15 | 0.2999 | 3.15 | 0.44985 | 3.15 | 0.5998 | 3.15 | 0.74974 | 3.15 | 0.89969 | 3.15 | 1.1996 | 3.15 | 1.4995 | 3.15 | 1.7994 | 3.15 | 2.2492
3.2 | 0.073966 | 3.2 | 0.14793 | 3.2 | 0.29586 | 3.2 | 0.44379 | 3.2 | 0.59172 | 3.2 | 0.73966 | 3.2 | 0.88759 | 3.2 | 1.1834 | 3.2 | 1.4793 | 3.2 | 1.7752 | 3.2 | 2.219
3.25 | 0.072999 | 3.25 | 0.146 | 3.25 | 0.29199 | 3.25 | 0.43799 | 3.25 | 0.58399 | 3.25 | 0.72999 | 3.25 | 0.87598 | 3.25 | 1.168 | 3.25 | 1.46 | 3.25 | 1.752 | 3.25 | 2.19
3.3 | 0.072071 | 3.3 | 0.14414 | 3.3 | 0.28828 | 3.3 | 0.43243 | 3.3 | 0.57657 | 3.3 | 0.72071 | 3.3 | 0.86485 | 3.3 | 1.1531 | 3.3 | 1.4414 | 3.3 | 1.7297 | 3.3 | 2.1621
3.35 | 0.07118 | 3.35 | 0.14236 | 3.35 | 0.28472 | 3.35 | 0.42708 | 3.35 | 0.56944 | 3.35 | 0.7118 | 3.35 | 0.85416 | 3.35 | 1.1389 | 3.35 | 1.4236 | 3.35 | 1.7083 | 3.35 | 2.1354
3.4 | 0.070324 | 3.4 | 0.14065 | 3.4 | 0.2813 | 3.4 | 0.42195 | 3.4 | 0.56259 | 3.4 | 0.70324 | 3.4 | 0.84389 | 3.4 | 1.1252 | 3.4 | 1.4065 | 3.4 | 1.6878 | 3.4 | 2.1097
3.45 | 0.069501 | 3.45 | 0.139 | 3.45 | 0.278 | 3.45 | 0.417 | 3.45 | 0.55601 | 3.45 | 0.69501 | 3.45 | 0.83401 | 3.45 | 1.112 | 3.45 | 1.39 | 3.45 | 1.668 | 3.45 | 2.085
3.5 | 0.068708 | 3.5 | 0.13742 | 3.5 | 0.27483 | 3.5 | 0.41225 | 3.5 | 0.54966 | 3.5 | 0.68708 | 3.5 | 0.82449 | 3.5 | 1.0993 | 3.5 | 1.3742 | 3.5 | 1.649 | 3.5 | 2.0612
3.55 | 0.067944 | 3.55 | 0.13589 | 3.55 | 0.27177 | 3.55 | 0.40766 | 3.55 | 0.54355 | 3.55 | 0.67944 | 3.55 | 0.81532 | 3.55 | 1.0871 | 3.55 | 1.3589 | 3.55 | 1.6306 | 3.55 | 2.0383
3.6 | 0.067207 | 3.6 | 0.13441 | 3.6 | 0.26883 | 3.6 | 0.40324 | 3.6 | 0.53765 | 3.6 | 0.67207 | 3.6 | 0.80648 | 3.6 | 1.0753 | 3.6 | 1.3441 | 3.6 | 1.613 | 3.6 | 2.0162
3.65 | 0.066496 | 3.65 | 0.13299 | 3.65 | 0.26598 | 3.65 | 0.39897 | 3.65 | 0.53197 | 3.65 | 0.66496 | 3.65 | 0.79795 | 3.65 | 1.0639 | 3.65 | 1.3299 | 3.65 | 1.5959 | 3.65 | 1.9949
3.7 | 0.065809 | 3.7 | 0.13162 | 3.7 | 0.26324 | 3.7 | 0.39485 | 3.7 | 0.52647 | 3.7 | 0.65809 | 3.7 | 0.78971 | 3.7 | 1.0529 | 3.7 | 1.3162 | 3.7 | 1.5794 | 3.7 | 1.9743
3.75 | 0.065145 | 3.75 | 0.13029 | 3.75 | 0.26058 | 3.75 | 0.39087 | 3.75 | 0.52116 | 3.75 | 0.65145 | 3.75 | 0.78175 | 3.75 | 1.0423 | 3.75 | 1.3029 | 3.75 | 1.5635 | 3.75 | 1.9544
3.8 | 0.064504 | 3.8 | 0.12901 | 3.8 | 0.25801 | 3.8 | 0.38702 | 3.8 | 0.51603 | 3.8 | 0.64504 | 3.8 | 0.77404 | 3.8 | 1.0321 | 3.8 | 1.2901 | 3.8 | 1.5481 | 3.8 | 1.9351
3.85 | 0.063883 | 3.85 | 0.12777 | 3.85 | 0.25553 | 3.85 | 0.3833 | 3.85 | 0.51106 | 3.85 | 0.63883 | 3.85 | 0.76659 | 3.85 | 1.0221 | 3.85 | 1.2777 | 3.85 | 1.5332 | 3.85 | 1.9165
3.9 | 0.063281 | 3.9 | 0.12656 | 3.9 | 0.25313 | 3.9 | 0.37969 | 3.9 | 0.50625 | 3.9 | 0.63281 | 3.9 | 0.75938 | 3.9 | 1.0125 | 3.9 | 1.2656 | 3.9 | 1.5188 | 3.9 | 1.8984
3.95 | 0.062699 | 3.95 | 0.1254 | 3.95 | 0.2508 | 3.95 | 0.37619 | 3.95 | 0.50159 | 3.95 | 0.62699 | 3.95 | 0.75239 | 3.95 | 1.0032 | 3.95 | 1.254 | 3.95 | 1.5048 | 3.95 | 1.881
4 | 0.062134 | 4 | 0.12427 | 4 | 0.24854 | 4 | 0.3728 | 4 | 0.49707 | 4 | 0.62134 | 4 | 0.74561 | 4 | 0.99415 | 4 | 1.2427 | 4 | 1.4912 | 4 | 1.864
4.05 | 0.061586 | 4.05 | 0.12317 | 4.05 | 0.24635 | 4.05 | 0.36952 | 4.05 | 0.49269 | 4.05 | 0.61586 | 4.05 | 0.73904 | 4.05 | 0.98538 | 4.05 | 1.2317 | 4.05 | 1.4781 | 4.05 | 1.8476
4.1 | 0.061055 | 4.1 | 0.12211 | 4.1 | 0.24422 | 4.1 | 0.36633 | 4.1 | 0.48844 | 4.1 | 0.61055 | 4.1 | 0.73266 | 4.1 | 0.97688 | 4.1 | 1.2211 | 4.1 | 1.4653 | 4.1 | 1.8316
4.15 | 0.060539 | 4.15 | 0.12108 | 4.15 | 0.24216 | 4.15 | 0.36323 | 4.15 | 0.48431 | 4.15 | 0.60539 | 4.15 | 0.72647 | 4.15 | 0.96862 | 4.15 | 1.2108 | 4.15 | 1.4529 | 4.15 | 1.8162
4.2 | 0.060037 | 4.2 | 0.12007 | 4.2 | 0.24015 | 4.2 | 0.36022 | 4.2 | 0.4803 | 4.2 | 0.60037 | 4.2 | 0.72045 | 4.2 | 0.9606 | 4.2 | 1.2007 | 4.2 | 1.4409 | 4.2 | 1.8011
4.25 | 0.05955 | 4.25 | 0.1191 | 4.25 | 0.2382 | 4.25 | 0.3573 | 4.25 | 0.4764 | 4.25 | 0.5955 | 4.25 | 0.7146 | 4.25 | 0.9528 | 4.25 | 1.191 | 4.25 | 1.4292 | 4.25 | 1.7865
4.3 | 0.059076 | 4.3 | 0.11815 | 4.3 | 0.23631 | 4.3 | 0.35446 | 4.3 | 0.47261 | 4.3 | 0.59076 | 4.3 | 0.70892 | 4.3 | 0.94522 | 4.3 | 1.1815 | 4.3 | 1.4178 | 4.3 | 1.7723
4.35 | 0.058615 | 4.35 | 0.11723 | 4.35 | 0.23446 | 4.35 | 0.35169 | 4.35 | 0.46892 | 4.35 | 0.58615 | 4.35 | 0.70339 | 4.35 | 0.93785 | 4.35 | 1.1723 | 4.35 | 1.4068 | 4.35 | 1.7585
4.4 | 0.058167 | 4.4 | 0.11633 | 4.4 | 0.23267 | 4.4 | 0.349 | 4.4 | 0.46534 | 4.4 | 0.58167 | 4.4 | 0.698 | 4.4 | 0.93067 | 4.4 | 1.1633 | 4.4 | 1.396 | 4.4 | 1.745
4.45 | 0.05773 | 4.45 | 0.11546 | 4.45 | 0.23092 | 4.45 | 0.34638 | 4.45 | 0.46184 | 4.45 | 0.5773 | 4.45 | 0.69276 | 4.45 | 0.92368 | 4.45 | 1.1546 | 4.45 | 1.3855 | 4.45 | 1.7319
4.5 | 0.057305 | 4.5 | 0.11461 | 4.5 | 0.22922 | 4.5 | 0.34383 | 4.5 | 0.45844 | 4.5 | 0.57305 | 4.5 | 0.68766 | 4.5 | 0.91688 | 4.5 | 1.1461 | 4.5 | 1.3753 | 4.5 | 1.7191
4.55 | 0.05689 | 4.55 | 0.11378 | 4.55 | 0.22756 | 4.55 | 0.34134 | 4.55 | 0.45512 | 4.55 | 0.5689 | 4.55 | 0.68268 | 4.55 | 0.91024 | 4.55 | 1.1378 | 4.55 | 1.3654 | 4.55 | 1.7067
4.6 | 0.056486 | 4.6 | 0.11297 | 4.6 | 0.22594 | 4.6 | 0.33892 | 4.6 | 0.45189 | 4.6 | 0.56486 | 4.6 | 0.67783 | 4.6 | 0.90378 | 4.6 | 1.1297 | 4.6 | 1.3557 | 4.6 | 1.6946
4.65 | 0.056092 | 4.65 | 0.11218 | 4.65 | 0.22437 | 4.65 | 0.33655 | 4.65 | 0.44874 | 4.65 | 0.56092 | 4.65 | 0.6731 | 4.65 | 0.89747 | 4.65 | 1.1218 | 4.65 | 1.3462 | 4.65 | 1.6828
4.7 | 0.055708 | 4.7 | 0.11142 | 4.7 | 0.22283 | 4.7 | 0.33425 | 4.7 | 0.44566 | 4.7 | 0.55708 | 4.7 | 0.66849 | 4.7 | 0.89132 | 4.7 | 1.1142 | 4.7 | 1.337 | 4.7 | 1.6712
4.75 | 0.055332 | 4.75 | 0.11066 | 4.75 | 0.22133 | 4.75 | 0.33199 | 4.75 | 0.44266 | 4.75 | 0.55332 | 4.75 | 0.66399 | 4.75 | 0.88532 | 4.75 | 1.1066 | 4.75 | 1.328 | 4.75 | 1.66
4.8 | 0.054966 | 4.8 | 0.10993 | 4.8 | 0.21986 | 4.8 | 0.3298 | 4.8 | 0.43973 | 4.8 | 0.54966 | 4.8 | 0.65959 | 4.8 | 0.87946 | 4.8 | 1.0993 | 4.8 | 1.3192 | 4.8 | 1.649
4.85 | 0.054608 | 4.85 | 0.10922 | 4.85 | 0.21843 | 4.85 | 0.32765 | 4.85 | 0.43687 | 4.85 | 0.54608 | 4.85 | 0.6553 | 4.85 | 0.87373 | 4.85 | 1.0922 | 4.85 | 1.3106 | 4.85 | 1.6383
4.9 | 0.054259 | 4.9 | 0.10852 | 4.9 | 0.21704 | 4.9 | 0.32555 | 4.9 | 0.43407 | 4.9 | 0.54259 | 4.9 | 0.65111 | 4.9 | 0.86814 | 4.9 | 1.0852 | 4.9 | 1.3022 | 4.9 | 1.6278
4.95 | 0.053918 | 4.95 | 0.10784 | 4.95 | 0.21567 | 4.95 | 0.32351 | 4.95 | 0.43134 | 4.95 | 0.53918 | 4.95 | 0.64701 | 4.95 | 0.86268 | 4.95 | 1.0784 | 4.95 | 1.294 | 4.95 | 1.6175
5 | 0.053584 | 5 | 0.10717 | 5 | 0.21433 | 5 | 0.3215 | 5 | 0.42867 | 5 | 0.53584 | 5 | 0.643 | 5 | 0.85734 | 5 | 1.0717 | 5 | 1.286 | 5 | 1.6075
5.05 | 0.053257 | 5.05 | 0.10651 | 5.05 | 0.21303 | 5.05 | 0.31954 | 5.05 | 0.42606 | 5.05 | 0.53257 | 5.05 | 0.63909 | 5.05 | 0.85212 | 5.05 | 1.0651 | 5.05 | 1.2782 | 5.05 | 1.5977
5.1 | 0.052938 | 5.1 | 0.10588 | 5.1 | 0.21175 | 5.1 | 0.31763 | 5.1 | 0.4235 | 5.1 | 0.52938 | 5.1 | 0.63526 | 5.1 | 0.84701 | 5.1 | 1.0588 | 5.1 | 1.2705 | 5.1 | 1.5881
5.15 | 0.052626 | 5.15 | 0.10525 | 5.15 | 0.2105 | 5.15 | 0.31575 | 5.15 | 0.42101 | 5.15 | 0.52626 | 5.15 | 0.63151 | 5.15 | 0.84201 | 5.15 | 1.0525 | 5.15 | 1.263 | 5.15 | 1.5788
5.2 | 0.05232 | 5.2 | 0.10464 | 5.2 | 0.20928 | 5.2 | 0.31392 | 5.2 | 0.41856 | 5.2 | 0.5232 | 5.2 | 0.62784 | 5.2 | 0.83712 | 5.2 | 1.0464 | 5.2 | 1.2557 | 5.2 | 1.5696
5.25 | 0.052021 | 5.25 | 0.10404 | 5.25 | 0.20808 | 5.25 | 0.31212 | 5.25 | 0.41617 | 5.25 | 0.52021 | 5.25 | 0.62425 | 5.25 | 0.83233 | 5.25 | 1.0404 | 5.25 | 1.2485 | 5.25 | 1.5606
5.3 | 0.051728 | 5.3 | 0.10346 | 5.3 | 0.20691 | 5.3 | 0.31037 | 5.3 | 0.41382 | 5.3 | 0.51728 | 5.3 | 0.62073 | 5.3 | 0.82764 | 5.3 | 1.0346 | 5.3 | 1.2415 | 5.3 | 1.5518
5.35 | 0.051441 | 5.35 | 0.10288 | 5.35 | 0.20576 | 5.35 | 0.30864 | 5.35 | 0.41153 | 5.35 | 0.51441 | 5.35 | 0.61729 | 5.35 | 0.82305 | 5.35 | 1.0288 | 5.35 | 1.2346 | 5.35 | 1.5432
5.4 | 0.05116 | 5.4 | 0.10232 | 5.4 | 0.20464 | 5.4 | 0.30696 | 5.4 | 0.40928 | 5.4 | 0.5116 | 5.4 | 0.61391 | 5.4 | 0.81855 | 5.4 | 1.0232 | 5.4 | 1.2278 | 5.4 | 1.5348
5.45 | 0.050884 | 5.45 | 0.10177 | 5.45 | 0.20354 | 5.45 | 0.3053 | 5.45 | 0.40707 | 5.45 | 0.50884 | 5.45 | 0.61061 | 5.45 | 0.81414 | 5.45 | 1.0177 | 5.45 | 1.2212 | 5.45 | 1.5265
5.5 | 0.050614 | 5.5 | 0.10123 | 5.5 | 0.20246 | 5.5 | 0.30368 | 5.5 | 0.40491 | 5.5 | 0.50614 | 5.5 | 0.60737 | 5.5 | 0.80982 | 5.5 | 1.0123 | 5.5 | 1.2147 | 5.5 | 1.5184
5.6 | 0.050089 | 5.6 | 0.10018 | 5.6 | 0.20036 | 5.6 | 0.30054 | 5.6 | 0.40072 | 5.6 | 0.50089 | 5.6 | 0.60107 | 5.6 | 0.80143 | 5.6 | 1.0018 | 5.6 | 1.2021 | 5.6 | 1.5027
5.65 | 0.049835 | 5.65 | 0.099669 | 5.65 | 0.19934 | 5.65 | 0.29901 | 5.65 | 0.39868 | 5.65 | 0.49835 | 5.65 | 0.59802 | 5.65 | 0.79735 | 5.65 | 0.99669 | 5.65 | 1.196 | 5.65 | 1.495
5.7 | 0.049585 | 5.7 | 0.099169 | 5.7 | 0.19834 | 5.7 | 0.29751 | 5.7 | 0.39668 | 5.7 | 0.49585 | 5.7 | 0.59502 | 5.7 | 0.79336 | 5.7 | 0.99169 | 5.7 | 1.19 | 5.7 | 1.4875
5.75 | 0.049339 | 5.75 | 0.098679 | 5.75 | 0.19736 | 5.75 | 0.29604 | 5.75 | 0.39472 | 5.75 | 0.49339 | 5.75 | 0.59207 | 5.75 | 0.78943 | 5.75 | 0.98679 | 5.75 | 1.1841 | 5.75 | 1.4802
5.8 | 0.049099 | 5.8 | 0.098198 | 5.8 | 0.1964 | 5.8 | 0.29459 | 5.8 | 0.39279 | 5.8 | 0.49099 | 5.8 | 0.58919 | 5.8 | 0.78558 | 5.8 | 0.98198 | 5.8 | 1.1784 | 5.8 | 1.473
5.85 | 0.048862 | 5.85 | 0.097725 | 5.85 | 0.19545 | 5.85 | 0.29317 | 5.85 | 0.3909 | 5.85 | 0.48862 | 5.85 | 0.58635 | 5.85 | 0.7818 | 5.85 | 0.97725 | 5.85 | 1.1727 | 5.85 | 1.4659
5.9 | 0.04863 | 5.9 | 0.097261 | 5.9 | 0.19452 | 5.9 | 0.29178 | 5.9 | 0.38904 | 5.9 | 0.4863 | 5.9 | 0.58356 | 5.9 | 0.77809 | 5.9 | 0.97261 | 5.9 | 1.1671 | 5.9 | 1.4589
5.95 | 0.048402 | 5.95 | 0.096805 | 5.95 | 0.19361 | 5.95 | 0.29041 | 5.95 | 0.38722 | 5.95 | 0.48402 | 5.95 | 0.58083 | 5.95 | 0.77444 | 5.95 | 0.96805 | 5.95 | 1.1617 | 5.95 | 1.4521
6 | 0.048179 | 6 | 0.096357 | 6 | 0.19271 | 6 | 0.28907 | 6 | 0.38543 | 6 | 0.48179 | 6 | 0.57814 | 6 | 0.77086 | 6 | 0.96357 | 6 | 1.1563 | 6 | 1.4454
6.05 | 0.047959 | 6.05 | 0.095917 | 6.05 | 0.19183 | 6.05 | 0.28775 | 6.05 | 0.38367 | 6.05 | 0.47959 | 6.05 | 0.5755 | 6.05 | 0.76734 | 6.05 | 0.95917 | 6.05 | 1.151 | 6.05 | 1.4388
6.1 | 0.047742 | 6.1 | 0.095485 | 6.1 | 0.19097 | 6.1 | 0.28645 | 6.1 | 0.38194 | 6.1 | 0.47742 | 6.1 | 0.57291 | 6.1 | 0.76388 | 6.1 | 0.95485 | 6.1 | 1.1458 | 6.1 | 1.4323
6.15 | 0.04753 | 6.15 | 0.09506 | 6.15 | 0.19012 | 6.15 | 0.28518 | 6.15 | 0.38024 | 6.15 | 0.4753 | 6.15 | 0.57036 | 6.15 | 0.76048 | 6.15 | 0.9506 | 6.15 | 1.1407 | 6.15 | 1.4259
6.2 | 0.047321 | 6.2 | 0.094642 | 6.2 | 0.18928 | 6.2 | 0.28393 | 6.2 | 0.37857 | 6.2 | 0.47321 | 6.2 | 0.56785 | 6.2 | 0.75714 | 6.2 | 0.94642 | 6.2 | 1.1357 | 6.2 | 1.4196
6.25 | 0.047116 | 6.25 | 0.094231 | 6.25 | 0.18846 | 6.25 | 0.28269 | 6.25 | 0.37693 | 6.25 | 0.47116 | 6.25 | 0.56539 | 6.25 | 0.75385 | 6.25 | 0.94231 | 6.25 | 1.1308 | 6.25 | 1.4135
6.3 | 0.046914 | 6.3 | 0.093828 | 6.3 | 0.18766 | 6.3 | 0.28148 | 6.3 | 0.37531 | 6.3 | 0.46914 | 6.3 | 0.56297 | 6.3 | 0.75062 | 6.3 | 0.93828 | 6.3 | 1.1259 | 6.3 | 1.4074
6.35 | 0.046715 | 6.35 | 0.09343 | 6.35 | 0.18686 | 6.35 | 0.28029 | 6.35 | 0.37372 | 6.35 | 0.46715 | 6.35 | 0.56058 | 6.35 | 0.74744 | 6.35 | 0.9343 | 6.35 | 1.1212 | 6.35 | 1.4015
6.4 | 0.04652 | 6.4 | 0.093039 | 6.4 | 0.18608 | 6.4 | 0.27912 | 6.4 | 0.37216 | 6.4 | 0.4652 | 6.4 | 0.55824 | 6.4 | 0.74432 | 6.4 | 0.93039 | 6.4 | 1.1165 | 6.4 | 1.3956
6.45 | 0.046327 | 6.45 | 0.092655 | 6.45 | 0.18531 | 6.45 | 0.27796 | 6.45 | 0.37062 | 6.45 | 0.46327 | 6.45 | 0.55593 | 6.45 | 0.74124 | 6.45 | 0.92655 | 6.45 | 1.1119 | 6.45 | 1.3898
6.5 | 0.046138 | 6.5 | 0.092276 | 6.5 | 0.18455 | 6.5 | 0.27683 | 6.5 | 0.36911 | 6.5 | 0.46138 | 6.5 | 0.55366 | 6.5 | 0.73821 | 6.5 | 0.92276 | 6.5 | 1.1073 | 6.5 | 1.3841
6.55 | 0.045952 | 6.55 | 0.091904 | 6.55 | 0.18381 | 6.55 | 0.27571 | 6.55 | 0.36762 | 6.55 | 0.45952 | 6.55 | 0.55142 | 6.55 | 0.73523 | 6.55 | 0.91904 | 6.55 | 1.1028 | 6.55 | 1.3786
6.6 | 0.045769 | 6.6 | 0.091537 | 6.6 | 0.18307 | 6.6 | 0.27461 | 6.6 | 0.36615 | 6.6 | 0.45769 | 6.6 | 0.54922 | 6.6 | 0.7323 | 6.6 | 0.91537 | 6.6 | 1.0984 | 6.6 | 1.3731
6.65 | 0.045588 | 6.65 | 0.091177 | 6.65 | 0.18235 | 6.65 | 0.27353 | 6.65 | 0.36471 | 6.65 | 0.45588 | 6.65 | 0.54706 | 6.65 | 0.72941 | 6.65 | 0.91177 | 6.65 | 1.0941 | 6.65 | 1.3676
6.7 | 0.045411 | 6.7 | 0.090821 | 6.7 | 0.18164 | 6.7 | 0.27246 | 6.7 | 0.36328 | 6.7 | 0.45411 | 6.7 | 0.54493 | 6.7 | 0.72657 | 6.7 | 0.90821 | 6.7 | 1.0899 | 6.7 | 1.3623
6.75 | 0.045236 | 6.75 | 0.090471 | 6.75 | 0.18094 | 6.75 | 0.27141 | 6.75 | 0.36188 | 6.75 | 0.45236 | 6.75 | 0.54283 | 6.75 | 0.72377 | 6.75 | 0.90471 | 6.75 | 1.0857 | 6.75 | 1.3571
6.8 | 0.045063 | 6.8 | 0.090126 | 6.8 | 0.18025 | 6.8 | 0.27038 | 6.8 | 0.36051 | 6.8 | 0.45063 | 6.8 | 0.54076 | 6.8 | 0.72101 | 6.8 | 0.90126 | 6.8 | 1.0815 | 6.8 | 1.3519
6.85 | 0.044893 | 6.85 | 0.089787 | 6.85 | 0.17957 | 6.85 | 0.26936 | 6.85 | 0.35915 | 6.85 | 0.44893 | 6.85 | 0.53872 | 6.85 | 0.71829 | 6.85 | 0.89787 | 6.85 | 1.0774 | 6.85 | 1.3468
6.9 | 0.044726 | 6.9 | 0.089452 | 6.9 | 0.1789 | 6.9 | 0.26836 | 6.9 | 0.35781 | 6.9 | 0.44726 | 6.9 | 0.53671 | 6.9 | 0.71562 | 6.9 | 0.89452 | 6.9 | 1.0734 | 6.9 | 1.3418
6.95 | 0.044561 | 6.95 | 0.089123 | 6.95 | 0.17825 | 6.95 | 0.26737 | 6.95 | 0.35649 | 6.95 | 0.44561 | 6.95 | 0.53474 | 6.95 | 0.71298 | 6.95 | 0.89123 | 6.95 | 1.0695 | 6.95 | 1.3368
7 | 0.044399 | 7 | 0.088798 | 7 | 0.1776 | 7 | 0.26639 | 7 | 0.35519 | 7 | 0.44399 | 7 | 0.53279 | 7 | 0.71038 | 7 | 0.88798 | 7 | 1.0656 | 7 | 1.332
7.05 | 0.044239 | 7.05 | 0.088477 | 7.05 | 0.17695 | 7.05 | 0.26543 | 7.05 | 0.35391 | 7.05 | 0.44239 | 7.05 | 0.53086 | 7.05 | 0.70782 | 7.05 | 0.88477 | 7.05 | 1.0617 | 7.05 | 1.3272
7.1 | 0.044081 | 7.1 | 0.088162 | 7.1 | 0.17632 | 7.1 | 0.26449 | 7.1 | 0.35265 | 7.1 | 0.44081 | 7.1 | 0.52897 | 7.1 | 0.70529 | 7.1 | 0.88162 | 7.1 | 1.0579 | 7.1 | 1.3224
7.15 | 0.043925 | 7.15 | 0.087851 | 7.15 | 0.1757 | 7.15 | 0.26355 | 7.15 | 0.3514 | 7.15 | 0.43925 | 7.15 | 0.5271 | 7.15 | 0.70281 | 7.15 | 0.87851 | 7.15 | 1.0542 | 7.15 | 1.3178
7.2 | 0.043772 | 7.2 | 0.087544 | 7.2 | 0.17509 | 7.2 | 0.26263 | 7.2 | 0.35018 | 7.2 | 0.43772 | 7.2 | 0.52526 | 7.2 | 0.70035 | 7.2 | 0.87544 | 7.2 | 1.0505 | 7.2 | 1.3132
7.25 | 0.043621 | 7.25 | 0.087241 | 7.25 | 0.17448 | 7.25 | 0.26172 | 7.25 | 0.34897 | 7.25 | 0.43621 | 7.25 | 0.52345 | 7.25 | 0.69793 | 7.25 | 0.87241 | 7.25 | 1.0469 | 7.25 | 1.3086
7.3 | 0.043471 | 7.3 | 0.086943 | 7.3 | 0.17389 | 7.3 | 0.26083 | 7.3 | 0.34777 | 7.3 | 0.43471 | 7.3 | 0.52166 | 7.3 | 0.69554 | 7.3 | 0.86943 | 7.3 | 1.0433 | 7.3 | 1.3041
7.35 | 0.043324 | 7.35 | 0.086649 | 7.35 | 0.1733 | 7.35 | 0.25995 | 7.35 | 0.34659 | 7.35 | 0.43324 | 7.35 | 0.51989 | 7.35 | 0.69319 | 7.35 | 0.86649 | 7.35 | 1.0398 | 7.35 | 1.2997
7.4 | 0.043179 | 7.4 | 0.086358 | 7.4 | 0.17272 | 7.4 | 0.25907 | 7.4 | 0.34543 | 7.4 | 0.43179 | 7.4 | 0.51815 | 7.4 | 0.69087 | 7.4 | 0.86358 | 7.4 | 1.0363 | 7.4 | 1.2954
7.45 | 0.043036 | 7.45 | 0.086072 | 7.45 | 0.17214 | 7.45 | 0.25822 | 7.45 | 0.34429 | 7.45 | 0.43036 | 7.45 | 0.51643 | 7.45 | 0.68857 | 7.45 | 0.86072 | 7.45 | 1.0329 | 7.45 | 1.2911
7.5 | 0.042895 | 7.5 | 0.085789 | 7.5 | 0.17158 | 7.5 | 0.25737 | 7.5 | 0.34316 | 7.5 | 0.42895 | 7.5 | 0.51473 | 7.5 | 0.68631 | 7.5 | 0.85789 | 7.5 | 1.0295 | 7.5 | 1.2868
7.55 | 0.042755 | 7.55 | 0.08551 | 7.55 | 0.17102 | 7.55 | 0.25653 | 7.55 | 0.34204 | 7.55 | 0.42755 | 7.55 | 0.51306 | 7.55 | 0.68408 | 7.55 | 0.8551 | 7.55 | 1.0261 | 7.55 | 1.2827
7.6 | 0.042617 | 7.6 | 0.085235 | 7.6 | 0.17047 | 7.6 | 0.2557 | 7.6 | 0.34094 | 7.6 | 0.42617 | 7.6 | 0.51141 | 7.6 | 0.68188 | 7.6 | 0.85235 | 7.6 | 1.0228 | 7.6 | 1.2785
7.65 | 0.042482 | 7.65 | 0.084963 | 7.65 | 0.16993 | 7.65 | 0.25489 | 7.65 | 0.33985 | 7.65 | 0.42482 | 7.65 | 0.50978 | 7.65 | 0.67971 | 7.65 | 0.84963 | 7.65 | 1.0196 | 7.65 | 1.2744
7.7 | 0.042348 | 7.7 | 0.084695 | 7.7 | 0.16939 | 7.7 | 0.25409 | 7.7 | 0.33878 | 7.7 | 0.42348 | 7.7 | 0.50817 | 7.7 | 0.67756 | 7.7 | 0.84695 | 7.7 | 1.0163 | 7.7 | 1.2704
7.75 | 0.042215 | 7.75 | 0.08443 | 7.75 | 0.16886 | 7.75 | 0.25329 | 7.75 | 0.33772 | 7.75 | 0.42215 | 7.75 | 0.50658 | 7.75 | 0.67544 | 7.75 | 0.8443 | 7.75 | 1.0132 | 7.75 | 1.2665
7.8 | 0.042084 | 7.8 | 0.084169 | 7.8 | 0.16834 | 7.8 | 0.25251 | 7.8 | 0.33668 | 7.8 | 0.42084 | 7.8 | 0.50501 | 7.8 | 0.67335 | 7.8 | 0.84169 | 7.8 | 1.01 | 7.8 | 1.2625
7.85 | 0.041955 | 7.85 | 0.083911 | 7.85 | 0.16782 | 7.85 | 0.25173 | 7.85 | 0.33564 | 7.85 | 0.41955 | 7.85 | 0.50346 | 7.85 | 0.67129 | 7.85 | 0.83911 | 7.85 | 1.0069 | 7.85 | 1.2587
7.9 | 0.041828 | 7.9 | 0.083656 | 7.9 | 0.16731 | 7.9 | 0.25097 | 7.9 | 0.33462 | 7.9 | 0.41828 | 7.9 | 0.50194 | 7.9 | 0.66925 | 7.9 | 0.83656 | 7.9 | 1.0039 | 7.9 | 1.2548
7.95 | 0.041702 | 7.95 | 0.083404 | 7.95 | 0.16681 | 7.95 | 0.25021 | 7.95 | 0.33362 | 7.95 | 0.41702 | 7.95 | 0.50042 | 7.95 | 0.66723 | 7.95 | 0.83404 | 7.95 | 1.0008 | 7.95 | 1.2511
8 | 0.041578 | 8 | 0.083155 | 8 | 0.16631 | 8 | 0.24947 | 8 | 0.33262 | 8 | 0.41578 | 8 | 0.49893 | 8 | 0.66524 | 8 | 0.83155 | 8 | 0.99787 | 8 | 1.2473
8.05 | 0.041455 | 8.05 | 0.08291 | 8.05 | 0.16582 | 8.05 | 0.24873 | 8.05 | 0.33164 | 8.05 | 0.41455 | 8.05 | 0.49746 | 8.05 | 0.66328 | 8.05 | 0.8291 | 8.05 | 0.99492 | 8.05 | 1.2436
8.1 | 0.041334 | 8.1 | 0.082667 | 8.1 | 0.16533 | 8.1 | 0.248 | 8.1 | 0.33067 | 8.1 | 0.41334 | 8.1 | 0.496 | 8.1 | 0.66134 | 8.1 | 0.82667 | 8.1 | 0.99201 | 8.1 | 1.24
8.15 | 0.041214 | 8.15 | 0.082427 | 8.15 | 0.16485 | 8.15 | 0.24728 | 8.15 | 0.32971 | 8.15 | 0.41214 | 8.15 | 0.49456 | 8.15 | 0.65942 | 8.15 | 0.82427 | 8.15 | 0.98913 | 8.15 | 1.2364
8.2 | 0.041095 | 8.2 | 0.082191 | 8.2 | 0.16438 | 8.2 | 0.24657 | 8.2 | 0.32876 | 8.2 | 0.41095 | 8.2 | 0.49314 | 8.2 | 0.65752 | 8.2 | 0.82191 | 8.2 | 0.98629 | 8.2 | 1.2329
8.25 | 0.040978 | 8.25 | 0.081956 | 8.25 | 0.16391 | 8.25 | 0.24587 | 8.25 | 0.32783 | 8.25 | 0.40978 | 8.25 | 0.49174 | 8.25 | 0.65565 | 8.25 | 0.81956 | 8.25 | 0.98348 | 8.25 | 1.2293
8.3 | 0.040863 | 8.3 | 0.081725 | 8.3 | 0.16345 | 8.3 | 0.24518 | 8.3 | 0.3269 | 8.3 | 0.40863 | 8.3 | 0.49035 | 8.3 | 0.6538 | 8.3 | 0.81725 | 8.3 | 0.9807 | 8.3 | 1.2259
8.35 | 0.040748 | 8.35 | 0.081497 | 8.35 | 0.16299 | 8.35 | 0.24449 | 8.35 | 0.32599 | 8.35 | 0.40748 | 8.35 | 0.48898 | 8.35 | 0.65197 | 8.35 | 0.81497 | 8.35 | 0.97796 | 8.35 | 1.2224
8.4 | 0.040635 | 8.4 | 0.081271 | 8.4 | 0.16254 | 8.4 | 0.24381 | 8.4 | 0.32508 | 8.4 | 0.40635 | 8.4 | 0.48762 | 8.4 | 0.65016 | 8.4 | 0.81271 | 8.4 | 0.97525 | 8.4 | 1.2191
8.45 | 0.040524 | 8.45 | 0.081047 | 8.45 | 0.16209 | 8.45 | 0.24314 | 8.45 | 0.32419 | 8.45 | 0.40524 | 8.45 | 0.48628 | 8.45 | 0.64838 | 8.45 | 0.81047 | 8.45 | 0.97257 | 8.45 | 1.2157
8.5 | 0.040413 | 8.5 | 0.080826 | 8.5 | 0.16165 | 8.5 | 0.24248 | 8.5 | 0.32331 | 8.5 | 0.40413 | 8.5 | 0.48496 | 8.5 | 0.64661 | 8.5 | 0.80826 | 8.5 | 0.96992 | 8.5 | 1.2124
8.55 | 0.040304 | 8.55 | 0.080608 | 8.55 | 0.16122 | 8.55 | 0.24182 | 8.55 | 0.32243 | 8.55 | 0.40304 | 8.55 | 0.48365 | 8.55 | 0.64486 | 8.55 | 0.80608 | 8.55 | 0.96729 | 8.55 | 1.2091
8.6 | 0.040196 | 8.6 | 0.080392 | 8.6 | 0.16078 | 8.6 | 0.24118 | 8.6 | 0.32157 | 8.6 | 0.40196 | 8.6 | 0.48235 | 8.6 | 0.64314 | 8.6 | 0.80392 | 8.6 | 0.9647 | 8.6 | 1.2059
8.65 | 0.040089 | 8.65 | 0.080179 | 8.65 | 0.16036 | 8.65 | 0.24054 | 8.65 | 0.32071 | 8.65 | 0.40089 | 8.65 | 0.48107 | 8.65 | 0.64143 | 8.65 | 0.80179 | 8.65 | 0.96214 | 8.65 | 1.2027
8.7 | 0.039984 | 8.7 | 0.079967 | 8.7 | 0.15993 | 8.7 | 0.2399 | 8.7 | 0.31987 | 8.7 | 0.39984 | 8.7 | 0.4798 | 8.7 | 0.63974 | 8.7 | 0.79967 | 8.7 | 0.95961 | 8.7 | 1.1995
8.75 | 0.039879 | 8.75 | 0.079759 | 8.75 | 0.15952 | 8.75 | 0.23928 | 8.75 | 0.31903 | 8.75 | 0.39879 | 8.75 | 0.47855 | 8.75 | 0.63807 | 8.75 | 0.79759 | 8.75 | 0.9571 | 8.75 | 1.1964
8.8 | 0.039776 | 8.8 | 0.079552 | 8.8 | 0.1591 | 8.8 | 0.23866 | 8.8 | 0.31821 | 8.8 | 0.39776 | 8.8 | 0.47731 | 8.8 | 0.63642 | 8.8 | 0.79552 | 8.8 | 0.95462 | 8.8 | 1.1933
8.85 | 0.039674 | 8.85 | 0.079348 | 8.85 | 0.1587 | 8.85 | 0.23804 | 8.85 | 0.31739 | 8.85 | 0.39674 | 8.85 | 0.47609 | 8.85 | 0.63478 | 8.85 | 0.79348 | 8.85 | 0.95217 | 8.85 | 1.1902
8.9 | 0.039573 | 8.9 | 0.079146 | 8.9 | 0.15829 | 8.9 | 0.23744 | 8.9 | 0.31658 | 8.9 | 0.39573 | 8.9 | 0.47487 | 8.9 | 0.63317 | 8.9 | 0.79146 | 8.9 | 0.94975 | 8.9 | 1.1872
8.95 | 0.039473 | 8.95 | 0.078946 | 8.95 | 0.15789 | 8.95 | 0.23684 | 8.95 | 0.31578 | 8.95 | 0.39473 | 8.95 | 0.47367 | 8.95 | 0.63157 | 8.95 | 0.78946 | 8.95 | 0.94735 | 8.95 | 1.1842
9 | 0.039374 | 9 | 0.078748 | 9 | 0.1575 | 9 | 0.23624 | 9 | 0.31499 | 9 | 0.39374 | 9 | 0.47249 | 9 | 0.62998 | 9 | 0.78748 | 9 | 0.94498 | 9 | 1.1812
9.05 | 0.039276 | 9.05 | 0.078552 | 9.05 | 0.1571 | 9.05 | 0.23566 | 9.05 | 0.31421 | 9.05 | 0.39276 | 9.05 | 0.47131 | 9.05 | 0.62842 | 9.05 | 0.78552 | 9.05 | 0.94263 | 9.05 | 1.1783
9.1 | 0.039179 | 9.1 | 0.078359 | 9.1 | 0.15672 | 9.1 | 0.23508 | 9.1 | 0.31343 | 9.1 | 0.39179 | 9.1 | 0.47015 | 9.1 | 0.62687 | 9.1 | 0.78359 | 9.1 | 0.9403 | 9.1 | 1.1754
9.15 | 0.039083 | 9.15 | 0.078167 | 9.15 | 0.15633 | 9.15 | 0.2345 | 9.15 | 0.31267 | 9.15 | 0.39083 | 9.15 | 0.469 | 9.15 | 0.62534 | 9.15 | 0.78167 | 9.15 | 0.938 | 9.15 | 1.1725
9.2 | 0.038989 | 9.2 | 0.077977 | 9.2 | 0.15595 | 9.2 | 0.23393 | 9.2 | 0.31191 | 9.2 | 0.38989 | 9.2 | 0.46786 | 9.2 | 0.62382 | 9.2 | 0.77977 | 9.2 | 0.93573 | 9.2 | 1.1697
9.25 | 0.038895 | 9.25 | 0.07779 | 9.25 | 0.15558 | 9.25 | 0.23337 | 9.25 | 0.31116 | 9.25 | 0.38895 | 9.25 | 0.46674 | 9.25 | 0.62232 | 9.25 | 0.7779 | 9.25 | 0.93348 | 9.25 | 1.1668
9.3 | 0.038802 | 9.3 | 0.077604 | 9.3 | 0.15521 | 9.3 | 0.23281 | 9.3 | 0.31042 | 9.3 | 0.38802 | 9.3 | 0.46562 | 9.3 | 0.62083 | 9.3 | 0.77604 | 9.3 | 0.93125 | 9.3 | 1.1641
9.35 | 0.03871 | 9.35 | 0.07742 | 9.35 | 0.15484 | 9.35 | 0.23226 | 9.35 | 0.30968 | 9.35 | 0.3871 | 9.35 | 0.46452 | 9.35 | 0.61936 | 9.35 | 0.7742 | 9.35 | 0.92904 | 9.35 | 1.1613
9.4 | 0.038619 | 9.4 | 0.077238 | 9.4 | 0.15448 | 9.4 | 0.23171 | 9.4 | 0.30895 | 9.4 | 0.38619 | 9.4 | 0.46343 | 9.4 | 0.6179 | 9.4 | 0.77238 | 9.4 | 0.92685 | 9.4 | 1.1586
9.45 | 0.038529 | 9.45 | 0.077058 | 9.45 | 0.15412 | 9.45 | 0.23117 | 9.45 | 0.30823 | 9.45 | 0.38529 | 9.45 | 0.46235 | 9.45 | 0.61646 | 9.45 | 0.77058 | 9.45 | 0.92469 | 9.45 | 1.1559
9.5 | 0.03844 | 9.5 | 0.076879 | 9.5 | 0.15376 | 9.5 | 0.23064 | 9.5 | 0.30752 | 9.5 | 0.3844 | 9.5 | 0.46128 | 9.5 | 0.61503 | 9.5 | 0.76879 | 9.5 | 0.92255 | 9.5 | 1.1532
9.55 | 0.038351 | 9.55 | 0.076703 | 9.55 | 0.15341 | 9.55 | 0.23011 | 9.55 | 0.30681 | 9.55 | 0.38351 | 9.55 | 0.46022 | 9.55 | 0.61362 | 9.55 | 0.76703 | 9.55 | 0.92043 | 9.55 | 1.1505
9.6 | 0.038264 | 9.6 | 0.076528 | 9.6 | 0.15306 | 9.6 | 0.22958 | 9.6 | 0.30611 | 9.6 | 0.38264 | 9.6 | 0.45917 | 9.6 | 0.61222 | 9.6 | 0.76528 | 9.6 | 0.91833 | 9.6 | 1.1479
9.65 | 0.038177 | 9.65 | 0.076354 | 9.65 | 0.15271 | 9.65 | 0.22906 | 9.65 | 0.30542 | 9.65 | 0.38177 | 9.65 | 0.45813 | 9.65 | 0.61084 | 9.65 | 0.76354 | 9.65 | 0.91625 | 9.65 | 1.1453
9.7 | 0.038091 | 9.7 | 0.076183 | 9.7 | 0.15237 | 9.7 | 0.22855 | 9.7 | 0.30473 | 9.7 | 0.38091 | 9.7 | 0.4571 | 9.7 | 0.60946 | 9.7 | 0.76183 | 9.7 | 0.91419 | 9.7 | 1.1427
9.75 | 0.038006 | 9.75 | 0.076013 | 9.75 | 0.15203 | 9.75 | 0.22804 | 9.75 | 0.30405 | 9.75 | 0.38006 | 9.75 | 0.45608 | 9.75 | 0.6081 | 9.75 | 0.76013 | 9.75 | 0.91216 | 9.75 | 1.1402
9.8 | 0.037922 | 9.8 | 0.075845 | 9.8 | 0.15169 | 9.8 | 0.22753 | 9.8 | 0.30338 | 9.8 | 0.37922 | 9.8 | 0.45507 | 9.8 | 0.60676 | 9.8 | 0.75845 | 9.8 | 0.91014 | 9.8 | 1.1377
9.85 | 0.037839 | 9.85 | 0.075678 | 9.85 | 0.15136 | 9.85 | 0.22703 | 9.85 | 0.30271 | 9.85 | 0.37839 | 9.85 | 0.45407 | 9.85 | 0.60542 | 9.85 | 0.75678 | 9.85 | 0.90814 | 9.85 | 1.1352
9.9 | 0.037756 | 9.9 | 0.075513 | 9.9 | 0.15103 | 9.9 | 0.22654 | 9.9 | 0.30205 | 9.9 | 0.37756 | 9.9 | 0.45308 | 9.9 | 0.6041 | 9.9 | 0.75513 | 9.9 | 0.90616 | 9.9 | 1.1327
9.95 | 0.037675 | 9.95 | 0.075349 | 9.95 | 0.1507 | 9.95 | 0.22605 | 9.95 | 0.3014 | 9.95 | 0.37675 | 9.95 | 0.4521 | 9.95 | 0.6028 | 9.95 | 0.75349 | 9.95 | 0.90419 | 9.95 | 1.1302
10 | 0.037594 | 10 | 0.075187 | 10 | 0.15037 | 10 | 0.22556 | 10 | 0.30075 | 10 | 0.37594 | 10 | 0.45112 | 10 | 0.6015 | 10 | 0.75187 | 10 | 0.90225 | 10 | 1.1278
10.25 | 0.0372 | 10.25 | 0.0744 | 10.25 | 0.1488 | 10.25 | 0.2232 | 10.25 | 0.2976 | 10.25 | 0.372 | 10.25 | 0.4464 | 10.25 | 0.5952 | 10.25 | 0.744 | 10.25 | 0.8928 | 10.25 | 1.116
10.5 | 0.036823 | 10.5 | 0.073647 | 10.5 | 0.14729 | 10.5 | 0.22094 | 10.5 | 0.29459 | 10.5 | 0.36823 | 10.5 | 0.44188 | 10.5 | 0.58917 | 10.5 | 0.73647 | 10.5 | 0.88376 | 10.5 | 1.1047
10.75 | 0.036463 | 10.75 | 0.072926 | 10.75 | 0.14585 | 10.75 | 0.21878 | 10.75 | 0.29171 | 10.75 | 0.36463 | 10.75 | 0.43756 | 10.75 | 0.58341 | 10.75 | 0.72926 | 10.75 | 0.87512 | 10.75 | 1.0939
11 | 0.036118 | 11 | 0.072236 | 11 | 0.14447 | 11 | 0.21671 | 11 | 0.28894 | 11 | 0.36118 | 11 | 0.43342 | 11 | 0.57789 | 11 | 0.72236 | 11 | 0.86683 | 11 | 1.0835
11.25 | 0.035787 | 11.25 | 0.071574 | 11.25 | 0.14315 | 11.25 | 0.21472 | 11.25 | 0.2863 | 11.25 | 0.35787 | 11.25 | 0.42945 | 11.25 | 0.57259 | 11.25 | 0.71574 | 11.25 | 0.85889 | 11.25 | 1.0736
11.5 | 0.035469 | 11.5 | 0.070939 | 11.5 | 0.14188 | 11.5 | 0.21282 | 11.5 | 0.28375 | 11.5 | 0.35469 | 11.5 | 0.42563 | 11.5 | 0.56751 | 11.5 | 0.70939 | 11.5 | 0.85126 | 11.5 | 1.0641
11.75 | 0.035164 | 11.75 | 0.070328 | 11.75 | 0.14066 | 11.75 | 0.21098 | 11.75 | 0.28131 | 11.75 | 0.35164 | 11.75 | 0.42197 | 11.75 | 0.56262 | 11.75 | 0.70328 | 11.75 | 0.84393 | 11.75 | 1.0549
12 | 0.03487 | 12 | 0.06974 | 12 | 0.13948 | 12 | 0.20922 | 12 | 0.27896 | 12 | 0.3487 | 12 | 0.41844 | 12 | 0.55792 | 12 | 0.6974 | 12 | 0.83688 | 12 | 1.0461
12.25 | 0.034587 | 12.25 | 0.069173 | 12.25 | 0.13835 | 12.25 | 0.20752 | 12.25 | 0.27669 | 12.25 | 0.34587 | 12.25 | 0.41504 | 12.25 | 0.55339 | 12.25 | 0.69173 | 12.25 | 0.83008 | 12.25 | 1.0376
12.5 | 0.034314 | 12.5 | 0.068628 | 12.5 | 0.13726 | 12.5 | 0.20588 | 12.5 | 0.27451 | 12.5 | 0.34314 | 12.5 | 0.41177 | 12.5 | 0.54902 | 12.5 | 0.68628 | 12.5 | 0.82353 | 12.5 | 1.0294
12.75 | 0.034051 | 12.75 | 0.068101 | 12.75 | 0.1362 | 12.75 | 0.2043 | 12.75 | 0.2724 | 12.75 | 0.34051 | 12.75 | 0.40861 | 12.75 | 0.54481 | 12.75 | 0.68101 | 12.75 | 0.81721 | 12.75 | 1.0215
13 | 0.033796 | 13 | 0.067593 | 13 | 0.13519 | 13 | 0.20278 | 13 | 0.27037 | 13 | 0.33796 | 13 | 0.40556 | 13 | 0.54074 | 13 | 0.67593 | 13 | 0.81111 | 13 | 1.0139
13.25 | 0.033551 | 13.25 | 0.067101 | 13.25 | 0.1342 | 13.25 | 0.2013 | 13.25 | 0.26841 | 13.25 | 0.33551 | 13.25 | 0.40261 | 13.25 | 0.53681 | 13.25 | 0.67101 | 13.25 | 0.80522 | 13.25 | 1.0065
13.5 | 0.033313 | 13.5 | 0.066626 | 13.5 | 0.13325 | 13.5 | 0.19988 | 13.5 | 0.2665 | 13.5 | 0.33313 | 13.5 | 0.39976 | 13.5 | 0.53301 | 13.5 | 0.66626 | 13.5 | 0.79951 | 13.5 | 0.99939
13.75 | 0.033083 | 13.75 | 0.066166 | 13.75 | 0.13233 | 13.75 | 0.1985 | 13.75 | 0.26466 | 13.75 | 0.33083 | 13.75 | 0.397 | 13.75 | 0.52933 | 13.75 | 0.66166 | 13.75 | 0.79399 | 13.75 | 0.99249
14 | 0.03286 | 14 | 0.065721 | 14 | 0.13144 | 14 | 0.19716 | 14 | 0.26288 | 14 | 0.3286 | 14 | 0.39433 | 14 | 0.52577 | 14 | 0.65721 | 14 | 0.78865 | 14 | 0.98581
14.25 | 0.032645 | 14.25 | 0.065289 | 14.25 | 0.13058 | 14.25 | 0.19587 | 14.25 | 0.26116 | 14.25 | 0.32645 | 14.25 | 0.39174 | 14.25 | 0.52231 | 14.25 | 0.65289 | 14.25 | 0.78347 | 14.25 | 0.97934
14.5 | 0.032435 | 14.5 | 0.064871 | 14.5 | 0.12974 | 14.5 | 0.19461 | 14.5 | 0.25948 | 14.5 | 0.32435 | 14.5 | 0.38922 | 14.5 | 0.51897 | 14.5 | 0.64871 | 14.5 | 0.77845 | 14.5 | 0.97306
14.75 | 0.032232 | 14.75 | 0.064465 | 14.75 | 0.12893 | 14.75 | 0.19339 | 14.75 | 0.25786 | 14.75 | 0.32232 | 14.75 | 0.38679 | 14.75 | 0.51572 | 14.75 | 0.64465 | 14.75 | 0.77358 | 14.75 | 0.96697
15 | 0.032035 | 15 | 0.06407 | 15 | 0.12814 | 15 | 0.19221 | 15 | 0.25628 | 15 | 0.32035 | 15 | 0.38442 | 15 | 0.51256 | 15 | 0.6407 | 15 | 0.76885 | 15 | 0.96106
15.5 | 0.031658 | 15.5 | 0.063315 | 15.5 | 0.12663 | 15.5 | 0.18995 | 15.5 | 0.25326 | 15.5 | 0.31658 | 15.5 | 0.37989 | 15.5 | 0.50652 | 15.5 | 0.63315 | 15.5 | 0.75978 | 15.5 | 0.94973
16 | 0.031301 | 16 | 0.062601 | 16 | 0.1252 | 16 | 0.1878 | 16 | 0.2504 | 16 | 0.31301 | 16 | 0.37561 | 16 | 0.50081 | 16 | 0.62601 | 16 | 0.75121 | 16 | 0.93902
16.5 | 0.030962 | 16.5 | 0.061924 | 16.5 | 0.12385 | 16.5 | 0.18577 | 16.5 | 0.2477 | 16.5 | 0.30962 | 16.5 | 0.37155 | 16.5 | 0.49539 | 16.5 | 0.61924 | 16.5 | 0.74309 | 16.5 | 0.92886
17 | 0.030641 | 17 | 0.061282 | 17 | 0.12256 | 17 | 0.18384 | 17 | 0.24513 | 17 | 0.30641 | 17 | 0.36769 | 17 | 0.49025 | 17 | 0.61282 | 17 | 0.73538 | 17 | 0.91922
17.5 | 0.030335 | 17.5 | 0.060671 | 17.5 | 0.12134 | 17.5 | 0.18201 | 17.5 | 0.24268 | 17.5 | 0.30335 | 17.5 | 0.36402 | 17.5 | 0.48536 | 17.5 | 0.60671 | 17.5 | 0.72805 | 17.5 | 0.91006
18 | 0.030044 | 18 | 0.060088 | 18 | 0.12018 | 18 | 0.18027 | 18 | 0.24035 | 18 | 0.30044 | 18 | 0.36053 | 18 | 0.48071 | 18 | 0.60088 | 18 | 0.72106 | 18 | 0.90133
18.5 | 0.029767 | 18.5 | 0.059533 | 18.5 | 0.11907 | 18.5 | 0.1786 | 18.5 | 0.23813 | 18.5 | 0.29767 | 18.5 | 0.3572 | 18.5 | 0.47626 | 18.5 | 0.59533 | 18.5 | 0.7144 | 18.5 | 0.893
19 | 0.029501 | 19 | 0.059002 | 19 | 0.118 | 19 | 0.17701 | 19 | 0.23601 | 19 | 0.29501 | 19 | 0.35401 | 19 | 0.47202 | 19 | 0.59002 | 19 | 0.70803 | 19 | 0.88504
19.5 | 0.029247 | 19.5 | 0.058495 | 19.5 | 0.11699 | 19.5 | 0.17548 | 19.5 | 0.23398 | 19.5 | 0.29247 | 19.5 | 0.35097 | 19.5 | 0.46796 | 19.5 | 0.58495 | 19.5 | 0.70194 | 19.5 | 0.87742
20 | 0.029004 | 20 | 0.058008 | 20 | 0.11602 | 20 | 0.17402 | 20 | 0.23203 | 20 | 0.29004 | 20 | 0.34805 | 20 | 0.46407 | 20 | 0.58008 | 20 | 0.6961 | 20 | 0.87012
20.5 | 0.028771 | 20.5 | 0.057542 | 20.5 | 0.11508 | 20.5 | 0.17263 | 20.5 | 0.23017 | 20.5 | 0.28771 | 20.5 | 0.34525 | 20.5 | 0.46033 | 20.5 | 0.57542 | 20.5 | 0.6905 | 20.5 | 0.86313
21 | 0.028547 | 21 | 0.057094 | 21 | 0.11419 | 21 | 0.17128 | 21 | 0.22838 | 21 | 0.28547 | 21 | 0.34256 | 21 | 0.45675 | 21 | 0.57094 | 21 | 0.68513 | 21 | 0.85641
21.5 | 0.028332 | 21.5 | 0.056663 | 21.5 | 0.11333 | 21.5 | 0.16999 | 21.5 | 0.22665 | 21.5 | 0.28332 | 21.5 | 0.33998 | 21.5 | 0.45331 | 21.5 | 0.56663 | 21.5 | 0.67996 | 21.5 | 0.84995
22 | 0.028124 | 22 | 0.056249 | 22 | 0.1125 | 22 | 0.16875 | 22 | 0.225 | 22 | 0.28124 | 22 | 0.33749 | 22 | 0.44999 | 22 | 0.56249 | 22 | 0.67499 | 22 | 0.84373
22.5 | 0.027925 | 22.5 | 0.05585 | 22.5 | 0.1117 | 22.5 | 0.16755 | 22.5 | 0.2234 | 22.5 | 0.27925 | 22.5 | 0.3351 | 22.5 | 0.4468 | 22.5 | 0.5585 | 22.5 | 0.6702 | 22.5 | 0.83774
23 | 0.027732 | 23 | 0.055465 | 23 | 0.11093 | 23 | 0.16639 | 23 | 0.22186 | 23 | 0.27732 | 23 | 0.33279 | 23 | 0.44372 | 23 | 0.55465 | 23 | 0.66558 | 23 | 0.83197
23.5 | 0.027547 | 23.5 | 0.055093 | 23.5 | 0.11019 | 23.5 | 0.16528 | 23.5 | 0.22037 | 23.5 | 0.27547 | 23.5 | 0.33056 | 23.5 | 0.44075 | 23.5 | 0.55093 | 23.5 | 0.66112 | 23.5 | 0.8264
24 | 0.027367 | 24 | 0.054735 | 24 | 0.10947 | 24 | 0.1642 | 24 | 0.21894 | 24 | 0.27367 | 24 | 0.32841 | 24 | 0.43788 | 24 | 0.54735 | 24 | 0.65682 | 24 | 0.82102
24.5 | 0.027194 | 24.5 | 0.054388 | 24.5 | 0.10878 | 24.5 | 0.16316 | 24.5 | 0.21755 | 24.5 | 0.27194 | 24.5 | 0.32633 | 24.5 | 0.4351 | 24.5 | 0.54388 | 24.5 | 0.65265 | 24.5 | 0.81582
25 | 0.027026 | 25 | 0.054052 | 25 | 0.1081 | 25 | 0.16216 | 25 | 0.21621 | 25 | 0.27026 | 25 | 0.32431 | 25 | 0.43242 | 25 | 0.54052 | 25 | 0.64863 | 25 | 0.81079
25.5 | 0.026864 | 25.5 | 0.053728 | 25.5 | 0.10746 | 25.5 | 0.16118 | 25.5 | 0.21491 | 25.5 | 0.26864 | 25.5 | 0.32237 | 25.5 | 0.42982 | 25.5 | 0.53728 | 25.5 | 0.64473 | 25.5 | 0.80592
26 | 0.026707 | 26 | 0.053413 | 26 | 0.10683 | 26 | 0.16024 | 26 | 0.21365 | 26 | 0.26707 | 26 | 0.32048 | 26 | 0.42731 | 26 | 0.53413 | 26 | 0.64096 | 26 | 0.8012
26.5 | 0.026554 | 26.5 | 0.053108 | 26.5 | 0.10622 | 26.5 | 0.15932 | 26.5 | 0.21243 | 26.5 | 0.26554 | 26.5 | 0.31865 | 26.5 | 0.42487 | 26.5 | 0.53108 | 26.5 | 0.6373 | 26.5 | 0.79662
27 | 0.026406 | 27 | 0.052812 | 27 | 0.10562 | 27 | 0.15844 | 27 | 0.21125 | 27 | 0.26406 | 27 | 0.31687 | 27 | 0.4225 | 27 | 0.52812 | 27 | 0.63375 | 27 | 0.79219
27.5 | 0.026263 | 27.5 | 0.052525 | 27.5 | 0.10505 | 27.5 | 0.15758 | 27.5 | 0.2101 | 27.5 | 0.26263 | 27.5 | 0.31515 | 27.5 | 0.4202 | 27.5 | 0.52525 | 27.5 | 0.6303 | 27.5 | 0.78788
28 | 0.026123 | 28 | 0.052246 | 28 | 0.10449 | 28 | 0.15674 | 28 | 0.20899 | 28 | 0.26123 | 28 | 0.31348 | 28 | 0.41797 | 28 | 0.52246 | 28 | 0.62696 | 28 | 0.7837
28.5 | 0.025988 | 28.5 | 0.051975 | 28.5 | 0.10395 | 28.5 | 0.15593 | 28.5 | 0.2079 | 28.5 | 0.25988 | 28.5 | 0.31185 | 28.5 | 0.4158 | 28.5 | 0.51975 | 28.5 | 0.6237 | 28.5 | 0.77963
29 | 0.025856 | 29 | 0.051712 | 29 | 0.10342 | 29 | 0.15514 | 29 | 0.20685 | 29 | 0.25856 | 29 | 0.31027 | 29 | 0.41369 | 29 | 0.51712 | 29 | 0.62054 | 29 | 0.77568
29.5 | 0.025728 | 29.5 | 0.051455 | 29.5 | 0.10291 | 29.5 | 0.15437 | 29.5 | 0.20582 | 29.5 | 0.25728 | 29.5 | 0.30873 | 29.5 | 0.41164 | 29.5 | 0.51455 | 29.5 | 0.61746 | 29.5 | 0.77183
30 | 0.025603 | 30 | 0.051206 | 30 | 0.10241 | 30 | 0.15362 | 30 | 0.20482 | 30 | 0.25603 | 30 | 0.30723 | 30 | 0.40965 | 30 | 0.51206 | 30 | 0.61447 | 30 | 0.76809
31 | 0.025603 | 31 | 0.051206 | 31 | 0.10241 | 31 | 0.15362 | 31 | 0.20482 | 31 | 0.25603 | 31 | 0.30723 | 31 | 0.40965 | 31 | 0.51206 | 31 | 0.61447 | 31 | 0.76809
32 | 0.025603 | 32 | 0.051206 | 32 | 0.10241 | 32 | 0.15362 | 32 | 0.20482 | 32 | 0.25603 | 32 | 0.30723 | 32 | 0.40965 | 32 | 0.51206 | 32 | 0.61447 | 32 | 0.76809
33 | 0.025603 | 33 | 0.051206 | 33 | 0.10241 | 33 | 0.15362 | 33 | 0.20482 | 33 | 0.25603 | 33 | 0.30723 | 33 | 0.40965 | 33 | 0.51206 | 33 | 0.61447 | 33 | 0.76809
34 | 0.025603 | 34 | 0.051206 | 34 | 0.10241 | 34 | 0.15362 | 34 | 0.20482 | 34 | 0.25603 | 34 | 0.30723 | 34 | 0.40965 | 34 | 0.51206 | 34 | 0.61447 | 34 | 0.76809
35 | 0.025603 | 35 | 0.051206 | 35 | 0.10241 | 35 | 0.15362 | 35 | 0.20482 | 35 | 0.25603 | 35 | 0.30723 | 35 | 0.40965 | 35 | 0.51206 | 35 | 0.61447 | 35 | 0.76809
36 | 0.025603 | 36 | 0.051206 | 36 | 0.10241 | 36 | 0.15362 | 36 | 0.20482 | 36 | 0.25603 | 36 | 0.30723 | 36 | 0.40965 | 36 | 0.51206 | 36 | 0.61447 | 36 | 0.76809
37 | 0.025603 | 37 | 0.051206 | 37 | 0.10241 | 37 | 0.15362 | 37 | 0.20482 | 37 | 0.25603 | 37 | 0.30723 | 37 | 0.40965 | 37 | 0.51206 | 37 | 0.61447 | 37 | 0.76809
38 | 0.025603 | 38 | 0.051206 | 38 | 0.10241 | 38 | 0.15362 | 38 | 0.20482 | 38 | 0.25603 | 38 | 0.30723 | 38 | 0.40965 | 38 | 0.51206 | 38 | 0.61447 | 38 | 0.76809
39 | 0.025603 | 39 | 0.051206 | 39 | 0.10241 | 39 | 0.15362 | 39 | 0.20482 | 39 | 0.25603 | 39 | 0.30723 | 39 | 0.40965 | 39 | 0.51206 | 39 | 0.61447 | 39 | 0.76809
40 | 0.025603 | 40 | 0.051206 | 40 | 0.10241 | 40 | 0.15362 | 40 | 0.20482 | 40 | 0.25603 | 40 | 0.30723 | 40 | 0.40965 | 40 | 0.51206 | 40 | 0.61447 | 40 | 0.76809
41 | 0.025603 | 41 | 0.051206 | 41 | 0.10241 | 41 | 0.15362 | 41 | 0.20482 | 41 | 0.25603 | 41 | 0.30723 | 41 | 0.40965 | 41 | 0.51206 | 41 | 0.61447 | 41 | 0.76809
42 | 0.025603 | 42 | 0.051206 | 42 | 0.10241 | 42 | 0.15362 | 42 | 0.20482 | 42 | 0.25603 | 42 | 0.30723 | 42 | 0.40965 | 42 | 0.51206 | 42 | 0.61447 | 42 | 0.76809
43 | 0.025603 | 43 | 0.051206 | 43 | 0.10241 | 43 | 0.15362 | 43 | 0.20482 | 43 | 0.25603 | 43 | 0.30723 | 43 | 0.40965 | 43 | 0.51206 | 43 | 0.61447 | 43 | 0.76809
44 | 0.025603 | 44 | 0.051206 | 44 | 0.10241 | 44 | 0.15362 | 44 | 0.20482 | 44 | 0.25603 | 44 | 0.30723 | 44 | 0.40965 | 44 | 0.51206 | 44 | 0.61447 | 44 | 0.76809
45 | 0.025603 | 45 | 0.051206 | 45 | 0.10241 | 45 | 0.15362 | 45 | 0.20482 | 45 | 0.25603 | 45 | 0.30723 | 45 | 0.40965 | 45 | 0.51206 | 45 | 0.61447 | 45 | 0.76809
46 | 0.025603 | 46 | 0.051206 | 46 | 0.10241 | 46 | 0.15362 | 46 | 0.20482 | 46 | 0.25603 | 46 | 0.30723 | 46 | 0.40965 | 46 | 0.51206 | 46 | 0.61447 | 46 | 0.76809
47 | 0.025603 | 47 | 0.051206 | 47 | 0.10241 | 47 | 0.15362 | 47 | 0.20482 | 47 | 0.25603 | 47 | 0.30723 | 47 | 0.40965 | 47 | 0.51206 | 47 | 0.61447 | 47 | 0.76809
48 | 0.025603 | 48 | 0.051206 | 48 | 0.10241 | 48 | 0.15362 | 48 | 0.20482 | 48 | 0.25603 | 48 | 0.30723 | 48 | 0.40965 | 48 | 0.51206 | 48 | 0.61447 | 48 | 0.76809
49 | 0.025603 | 49 | 0.051206 | 49 | 0.10241 | 49 | 0.15362 | 49 | 0.20482 | 49 | 0.25603 | 49 | 0.30723 | 49 | 0.40965 | 49 | 0.51206 | 49 | 0.61447 | 49 | 0.76809
50 | 0.025603 | 50 | 0.051206 | 50 | 0.10241 | 50 | 0.15362 | 50 | 0.20482 | 50 | 0.25603 | 50 | 0.30723 | 50 | 0.40965 | 50 | 0.51206 | 50 | 0.61447 | 50 | 0.76809
55 | 0.025603 | 55 | 0.051206 | 55 | 0.10241 | 55 | 0.15362 | 55 | 0.20482 | 55 | 0.25603 | 55 | 0.30723 | 55 | 0.40965 | 55 | 0.51206 | 55 | 0.61447 | 55 | 0.76809
60 | 0.025603 | 60 | 0.051206 | 60 | 0.10241 | 60 | 0.15362 | 60 | 0.20482 | 60 | 0.25603 | 60 | 0.30723 | 60 | 0.40965 | 60 | 0.51206 | 60 | 0.61447 | 60 | 0.76809
65 | 0.025603 | 65 | 0.051206 | 65 | 0.10241 | 65 | 0.15362 | 65 | 0.20482 | 65 | 0.25603 | 65 | 0.30723 | 65 | 0.40965 | 65 | 0.51206 | 65 | 0.61447 | 65 | 0.76809
70 | 0.025603 | 70 | 0.051206 | 70 | 0.10241 | 70 | 0.15362 | 70 | 0.20482 | 70 | 0.25603 | 70 | 0.30723 | 70 | 0.40965 | 70 | 0.51206 | 70 | 0.61447 | 70 | 0.76809
75 | 0.025603 | 75 | 0.051206 | 75 | 0.10241 | 75 | 0.15362 | 75 | 0.20482 | 75 | 0.25603 | 75 | 0.30723 | 75 | 0.40965 | 75 | 0.51206 | 75 | 0.61447 | 75 | 0.76809
80 | 0.025603 | 80 | 0.051206 | 80 | 0.10241 | 80 | 0.15362 | 80 | 0.20482 | 80 | 0.25603 | 80 | 0.30723 | 80 | 0.40965 | 80 | 0.51206 | 80 | 0.61447 | 80 | 0.76809
85 | 0.025603 | 85 | 0.051206 | 85 | 0.10241 | 85 | 0.15362 | 85 | 0.20482 | 85 | 0.25603 | 85 | 0.30723 | 85 | 0.40965 | 85 | 0.51206 | 85 | 0.61447 | 85 | 0.76809
90 | 0.025603 | 90 | 0.051206 | 90 | 0.10241 | 90 | 0.15362 | 90 | 0.20482 | 90 | 0.25603 | 90 | 0.30723 | 90 | 0.40965 | 90 | 0.51206 | 90 | 0.61447 | 90 | 0.76809
95 | 0.025603 | 95 | 0.051206 | 95 | 0.10241 | 95 | 0.15362 | 95 | 0.20482 | 95 | 0.25603 | 95 | 0.30723 | 95 | 0.40965 | 95 | 0.51206 | 95 | 0.61447 | 95 | 0.76809
100 | 0.025603 | 100 | 0.051206 | 100 | 0.10241 | 100 | 0.15362 | 100 | 0.20482 | 100 | 0.25603 | 100 | 0.30723 | 100 | 0.40965 | 100 | 0.51206 | 100 | 0.61447 | 100 | 0.76809