## 692-9-C1
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Standard Inverse I.E.C (C1) (TCC 692-9-C1) | [9 empty] | Standard Inverse I.E.C (C1) (TCC 692-9-C1) | [9 empty] | Standard Inverse I.E.C (C1) (TCC 692-9-C1)
Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of | [8 empty] | Tolerance: | Curves are plotted to average test points. Time-overcurrent tolerance, expressed in terms of
| current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5 | [9 empty] | current, is +5% of the selected pickup setting. Tolerance, expressed in terms of time, is +1.5
| cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between | [9 empty] | cycles +10% of the time indicated on the selected curve at a specified value of current between
| 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting. | [9 empty] | 2 and 30 multiples of the pickup setting.
| Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup | [9 empty] | Instantaneous pickup current tolerance is -0% to +10% of the selected instantaneous pickup
| current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds. | [9 empty] | current level. Definite-time response tolerance is -0 to 8 milliseconds.
Time Dial = 0.05 |  | Time Dial = 0.1 |  | Time Dial = 0.2 |  | Time Dial = 0.3 |  | Time Dial = 0.4 |  | Time Dial = 0.5 |  | Time Dial = 0.6 |  | Time Dial = 0.7 |  | Time Dial = 0.8 |  | Time Dial = 0.9 |  | Time Dial = 1.0
*of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s) | *of PU | Time (s)
1.5 | 0.85971 | 1.5 | 1.7194 | 1.5 | 3.4388 | 1.5 | 5.1583 | 1.5 | 6.8777 | 1.5 | 8.5971 | 1.5 | 10.3165 | 1.5 | 12.036 | 1.5 | 13.7554 | 1.5 | 15.4748 | 1.5 | 17.1942
1.6 | 0.74118 | 1.6 | 1.4824 | 1.6 | 2.9647 | 1.6 | 4.4471 | 1.6 | 5.9294 | 1.6 | 7.4118 | 1.6 | 8.8942 | 1.6 | 10.3765 | 1.6 | 11.8589 | 1.6 | 13.3413 | 1.6 | 14.8236
1.7 | 0.6561 | 1.7 | 1.3122 | 1.7 | 2.6244 | 1.7 | 3.9366 | 1.7 | 5.2488 | 1.7 | 6.561 | 1.7 | 7.8732 | 1.7 | 9.1854 | 1.7 | 10.4976 | 1.7 | 11.8098 | 1.7 | 13.122
1.8 | 0.59196 | 1.8 | 1.1839 | 1.8 | 2.3678 | 1.8 | 3.5518 | 1.8 | 4.7357 | 1.8 | 5.9196 | 1.8 | 7.1035 | 1.8 | 8.2875 | 1.8 | 9.4714 | 1.8 | 10.6553 | 1.8 | 11.8392
1.9 | 0.5418 | 1.9 | 1.0836 | 1.9 | 2.1672 | 1.9 | 3.2508 | 1.9 | 4.3344 | 1.9 | 5.418 | 1.9 | 6.5016 | 1.9 | 7.5852 | 1.9 | 8.6688 | 1.9 | 9.7525 | 1.9 | 10.8361
2 | 0.50145 | 2 | 1.0029 | 2 | 2.0058 | 2 | 3.0087 | 2 | 4.0116 | 2 | 5.0145 | 2 | 6.0174 | 2 | 7.0203 | 2 | 8.0232 | 2 | 9.0261 | 2 | 10.029
2.1 | 0.46825 | 2.1 | 0.93649 | 2.1 | 1.873 | 2.1 | 2.8095 | 2.1 | 3.746 | 2.1 | 4.6825 | 2.1 | 5.619 | 2.1 | 6.5555 | 2.1 | 7.4919 | 2.1 | 8.4284 | 2.1 | 9.3649
2.2 | 0.44041 | 2.2 | 0.88083 | 2.2 | 1.7617 | 2.2 | 2.6425 | 2.2 | 3.5233 | 2.2 | 4.4041 | 2.2 | 5.285 | 2.2 | 6.1658 | 2.2 | 7.0466 | 2.2 | 7.9275 | 2.2 | 8.8083
2.3 | 0.41672 | 2.3 | 0.83345 | 2.3 | 1.6669 | 2.3 | 2.5003 | 2.3 | 3.3338 | 2.3 | 4.1672 | 2.3 | 5.0007 | 2.3 | 5.8341 | 2.3 | 6.6676 | 2.3 | 7.501 | 2.3 | 8.3345
2.4 | 0.3963 | 2.4 | 0.79259 | 2.4 | 1.5852 | 2.4 | 2.3778 | 2.4 | 3.1704 | 2.4 | 3.963 | 2.4 | 4.7556 | 2.4 | 5.5481 | 2.4 | 6.3407 | 2.4 | 7.1333 | 2.4 | 7.9259
2.5 | 0.37849 | 2.5 | 0.75697 | 2.5 | 1.5139 | 2.5 | 2.2709 | 2.5 | 3.0279 | 2.5 | 3.7849 | 2.5 | 4.5418 | 2.5 | 5.2988 | 2.5 | 6.0558 | 2.5 | 6.8127 | 2.5 | 7.5697
2.6 | 0.36281 | 2.6 | 0.72561 | 2.6 | 1.4512 | 2.6 | 2.1768 | 2.6 | 2.9025 | 2.6 | 3.6281 | 2.6 | 4.3537 | 2.6 | 5.0793 | 2.6 | 5.8049 | 2.6 | 6.5305 | 2.6 | 7.2561
2.7 | 0.34889 | 2.7 | 0.69778 | 2.7 | 1.3956 | 2.7 | 2.0933 | 2.7 | 2.7911 | 2.7 | 3.4889 | 2.7 | 4.1867 | 2.7 | 4.8845 | 2.7 | 5.5822 | 2.7 | 6.28 | 2.7 | 6.9778
2.8 | 0.33644 | 2.8 | 0.67289 | 2.8 | 1.3458 | 2.8 | 2.0187 | 2.8 | 2.6915 | 2.8 | 3.3644 | 2.8 | 4.0373 | 2.8 | 4.7102 | 2.8 | 5.3831 | 2.8 | 6.056 | 2.8 | 6.7289
2.9 | 0.32524 | 2.9 | 0.65048 | 2.9 | 1.301 | 2.9 | 1.9514 | 2.9 | 2.6019 | 2.9 | 3.2524 | 2.9 | 3.9029 | 2.9 | 4.5534 | 2.9 | 5.2038 | 2.9 | 5.8543 | 2.9 | 6.5048
3 | 0.3151 | 3 | 0.63019 | 3 | 1.2604 | 3 | 1.8906 | 3 | 2.5208 | 3 | 3.151 | 3 | 3.7812 | 3 | 4.4114 | 3 | 5.0415 | 3 | 5.6717 | 3 | 6.3019
3.1 | 0.30586 | 3.1 | 0.61173 | 3.1 | 1.2235 | 3.1 | 1.8352 | 3.1 | 2.4469 | 3.1 | 3.0586 | 3.1 | 3.6704 | 3.1 | 4.2821 | 3.1 | 4.8938 | 3.1 | 5.5055 | 3.1 | 6.1173
3.2 | 0.29742 | 3.2 | 0.59484 | 3.2 | 1.1897 | 3.2 | 1.7845 | 3.2 | 2.3794 | 3.2 | 2.9742 | 3.2 | 3.569 | 3.2 | 4.1639 | 3.2 | 4.7587 | 3.2 | 5.3536 | 3.2 | 5.9484
3.3 | 0.28967 | 3.3 | 0.57933 | 3.3 | 1.1587 | 3.3 | 1.738 | 3.3 | 2.3173 | 3.3 | 2.8967 | 3.3 | 3.476 | 3.3 | 4.0553 | 3.3 | 4.6346 | 3.3 | 5.214 | 3.3 | 5.7933
3.4 | 0.28251 | 3.4 | 0.56503 | 3.4 | 1.1301 | 3.4 | 1.6951 | 3.4 | 2.2601 | 3.4 | 2.8251 | 3.4 | 3.3902 | 3.4 | 3.9552 | 3.4 | 4.5202 | 3.4 | 5.0853 | 3.4 | 5.6503
3.5 | 0.2759 | 3.5 | 0.55179 | 3.5 | 1.1036 | 3.5 | 1.6554 | 3.5 | 2.2072 | 3.5 | 2.759 | 3.5 | 3.3108 | 3.5 | 3.8626 | 3.5 | 4.4144 | 3.5 | 4.9661 | 3.5 | 5.5179
3.6 | 0.26975 | 3.6 | 0.53951 | 3.6 | 1.079 | 3.6 | 1.6185 | 3.6 | 2.158 | 3.6 | 2.6975 | 3.6 | 3.237 | 3.6 | 3.7765 | 3.6 | 4.316 | 3.6 | 4.8556 | 3.6 | 5.3951
3.7 | 0.26403 | 3.7 | 0.52806 | 3.7 | 1.0561 | 3.7 | 1.5842 | 3.7 | 2.1123 | 3.7 | 2.6403 | 3.7 | 3.1684 | 3.7 | 3.6964 | 3.7 | 4.2245 | 3.7 | 4.7526 | 3.7 | 5.2806
3.8 | 0.25869 | 3.8 | 0.51738 | 3.8 | 1.0348 | 3.8 | 1.5521 | 3.8 | 2.0695 | 3.8 | 2.5869 | 3.8 | 3.1043 | 3.8 | 3.6216 | 3.8 | 4.139 | 3.8 | 4.6564 | 3.8 | 5.1738
3.9 | 0.25368 | 3.9 | 0.50737 | 3.9 | 1.0147 | 3.9 | 1.5221 | 3.9 | 2.0295 | 3.9 | 2.5368 | 3.9 | 3.0442 | 3.9 | 3.5516 | 3.9 | 4.0589 | 3.9 | 4.5663 | 3.9 | 5.0737
4 | 0.24899 | 4 | 0.49798 | 4 | 0.99595 | 4 | 1.4939 | 4 | 1.9919 | 4 | 2.4899 | 4 | 2.9879 | 4 | 3.4858 | 4 | 3.9838 | 4 | 4.4818 | 4 | 4.9798
4.1 | 0.24457 | 4.1 | 0.48914 | 4.1 | 0.97828 | 4.1 | 1.4674 | 4.1 | 1.9566 | 4.1 | 2.4457 | 4.1 | 2.9348 | 4.1 | 3.424 | 4.1 | 3.9131 | 4.1 | 4.4023 | 4.1 | 4.8914
4.2 | 0.2404 | 4.2 | 0.48081 | 4.2 | 0.96162 | 4.2 | 1.4424 | 4.2 | 1.9232 | 4.2 | 2.404 | 4.2 | 2.8849 | 4.2 | 3.3657 | 4.2 | 3.8465 | 4.2 | 4.3273 | 4.2 | 4.8081
4.3 | 0.23647 | 4.3 | 0.47294 | 4.3 | 0.94588 | 4.3 | 1.4188 | 4.3 | 1.8918 | 4.3 | 2.3647 | 4.3 | 2.8376 | 4.3 | 3.3106 | 4.3 | 3.7835 | 4.3 | 4.2565 | 4.3 | 4.7294
4.4 | 0.23275 | 4.4 | 0.4655 | 4.4 | 0.93099 | 4.4 | 1.3965 | 4.4 | 1.862 | 4.4 | 2.3275 | 4.4 | 2.793 | 4.4 | 3.2585 | 4.4 | 3.724 | 4.4 | 4.1895 | 4.4 | 4.655
4.5 | 0.22922 | 4.5 | 0.45844 | 4.5 | 0.91687 | 4.5 | 1.3753 | 4.5 | 1.8337 | 4.5 | 2.2922 | 4.5 | 2.7506 | 4.5 | 3.2091 | 4.5 | 3.6675 | 4.5 | 4.1259 | 4.5 | 4.5844
4.6 | 0.22587 | 4.6 | 0.45173 | 4.6 | 0.90347 | 4.6 | 1.3552 | 4.6 | 1.8069 | 4.6 | 2.2587 | 4.6 | 2.7104 | 4.6 | 3.1621 | 4.6 | 3.6139 | 4.6 | 4.0656 | 4.6 | 4.5173
4.7 | 0.22268 | 4.7 | 0.44536 | 4.7 | 0.89072 | 4.7 | 1.3361 | 4.7 | 1.7814 | 4.7 | 2.2268 | 4.7 | 2.6722 | 4.7 | 3.1175 | 4.7 | 3.5629 | 4.7 | 4.0082 | 4.7 | 4.4536
4.8 | 0.21964 | 4.8 | 0.43929 | 4.8 | 0.87858 | 4.8 | 1.3179 | 4.8 | 1.7572 | 4.8 | 2.1964 | 4.8 | 2.6357 | 4.8 | 3.075 | 4.8 | 3.5143 | 4.8 | 3.9536 | 4.8 | 4.3929
4.9 | 0.21675 | 4.9 | 0.4335 | 4.9 | 0.867 | 4.9 | 1.3005 | 4.9 | 1.734 | 4.9 | 2.1675 | 4.9 | 2.601 | 4.9 | 3.0345 | 4.9 | 3.468 | 4.9 | 3.9015 | 4.9 | 4.335
5 | 0.21399 | 5 | 0.42797 | 5 | 0.85594 | 5 | 1.2839 | 5 | 1.7119 | 5 | 2.1399 | 5 | 2.5678 | 5 | 2.9958 | 5 | 3.4238 | 5 | 3.8517 | 5 | 4.2797
5.1 | 0.21134 | 5.1 | 0.42269 | 5.1 | 0.84537 | 5.1 | 1.2681 | 5.1 | 1.6907 | 5.1 | 2.1134 | 5.1 | 2.5361 | 5.1 | 2.9588 | 5.1 | 3.3815 | 5.1 | 3.8042 | 5.1 | 4.2269
5.2 | 0.20881 | 5.2 | 0.41763 | 5.2 | 0.83525 | 5.2 | 1.2529 | 5.2 | 1.6705 | 5.2 | 2.0881 | 5.2 | 2.5058 | 5.2 | 2.9234 | 5.2 | 3.341 | 5.2 | 3.7586 | 5.2 | 4.1763
5.3 | 0.20639 | 5.3 | 0.41278 | 5.3 | 0.82555 | 5.3 | 1.2383 | 5.3 | 1.6511 | 5.3 | 2.0639 | 5.3 | 2.4767 | 5.3 | 2.8894 | 5.3 | 3.3022 | 5.3 | 3.715 | 5.3 | 4.1278
5.4 | 0.20406 | 5.4 | 0.40812 | 5.4 | 0.81625 | 5.4 | 1.2244 | 5.4 | 1.6325 | 5.4 | 2.0406 | 5.4 | 2.4487 | 5.4 | 2.8569 | 5.4 | 3.265 | 5.4 | 3.6731 | 5.4 | 4.0812
5.5 | 0.20183 | 5.5 | 0.40366 | 5.5 | 0.80732 | 5.5 | 1.211 | 5.5 | 1.6146 | 5.5 | 2.0183 | 5.5 | 2.4219 | 5.5 | 2.8256 | 5.5 | 3.2293 | 5.5 | 3.6329 | 5.5 | 4.0366
5.6 | 0.19968 | 5.6 | 0.39936 | 5.6 | 0.79873 | 5.6 | 1.1981 | 5.6 | 1.5975 | 5.6 | 1.9968 | 5.6 | 2.3962 | 5.6 | 2.7955 | 5.6 | 3.1949 | 5.6 | 3.5943 | 5.6 | 3.9936
5.7 | 0.19762 | 5.7 | 0.39523 | 5.7 | 0.79046 | 5.7 | 1.1857 | 5.7 | 1.5809 | 5.7 | 1.9762 | 5.7 | 2.3714 | 5.7 | 2.7666 | 5.7 | 3.1619 | 5.7 | 3.5571 | 5.7 | 3.9523
5.8 | 0.19563 | 5.8 | 0.39125 | 5.8 | 0.78251 | 5.8 | 1.1738 | 5.8 | 1.565 | 5.8 | 1.9563 | 5.8 | 2.3475 | 5.8 | 2.7388 | 5.8 | 3.13 | 5.8 | 3.5213 | 5.8 | 3.9125
5.9 | 0.19371 | 5.9 | 0.38742 | 5.9 | 0.77484 | 5.9 | 1.1623 | 5.9 | 1.5497 | 5.9 | 1.9371 | 5.9 | 2.3245 | 5.9 | 2.7119 | 5.9 | 3.0993 | 5.9 | 3.4868 | 5.9 | 3.8742
6 | 0.19186 | 6 | 0.38372 | 6 | 0.76744 | 6 | 1.1512 | 6 | 1.5349 | 6 | 1.9186 | 6 | 2.3023 | 6 | 2.686 | 6 | 3.0698 | 6 | 3.4535 | 6 | 3.8372
6.1 | 0.19007 | 6.1 | 0.38015 | 6.1 | 0.7603 | 6.1 | 1.1404 | 6.1 | 1.5206 | 6.1 | 1.9007 | 6.1 | 2.2809 | 6.1 | 2.661 | 6.1 | 3.0412 | 6.1 | 3.4213 | 6.1 | 3.8015
6.2 | 0.18835 | 6.2 | 0.3767 | 6.2 | 0.7534 | 6.2 | 1.1301 | 6.2 | 1.5068 | 6.2 | 1.8835 | 6.2 | 2.2602 | 6.2 | 2.6369 | 6.2 | 3.0136 | 6.2 | 3.3903 | 6.2 | 3.767
6.3 | 0.18668 | 6.3 | 0.37336 | 6.3 | 0.74673 | 6.3 | 1.1201 | 6.3 | 1.4935 | 6.3 | 1.8668 | 6.3 | 2.2402 | 6.3 | 2.6135 | 6.3 | 2.9869 | 6.3 | 3.3603 | 6.3 | 3.7336
6.4 | 0.18507 | 6.4 | 0.37014 | 6.4 | 0.74028 | 6.4 | 1.1104 | 6.4 | 1.4806 | 6.4 | 1.8507 | 6.4 | 2.2208 | 6.4 | 2.591 | 6.4 | 2.9611 | 6.4 | 3.3312 | 6.4 | 3.7014
6.5 | 0.18351 | 6.5 | 0.36701 | 6.5 | 0.73403 | 6.5 | 1.101 | 6.5 | 1.4681 | 6.5 | 1.8351 | 6.5 | 2.2021 | 6.5 | 2.5691 | 6.5 | 2.9361 | 6.5 | 3.3031 | 6.5 | 3.6701
6.6 | 0.18199 | 6.6 | 0.36399 | 6.6 | 0.72798 | 6.6 | 1.092 | 6.6 | 1.456 | 6.6 | 1.8199 | 6.6 | 2.1839 | 6.6 | 2.5479 | 6.6 | 2.9119 | 6.6 | 3.2759 | 6.6 | 3.6399
6.7 | 0.18053 | 6.7 | 0.36106 | 6.7 | 0.72211 | 6.7 | 1.0832 | 6.7 | 1.4442 | 6.7 | 1.8053 | 6.7 | 2.1663 | 6.7 | 2.5274 | 6.7 | 2.8885 | 6.7 | 3.2495 | 6.7 | 3.6106
6.8 | 0.17911 | 6.8 | 0.35821 | 6.8 | 0.71643 | 6.8 | 1.0746 | 6.8 | 1.4329 | 6.8 | 1.7911 | 6.8 | 2.1493 | 6.8 | 2.5075 | 6.8 | 2.8657 | 6.8 | 3.2239 | 6.8 | 3.5821
6.9 | 0.17773 | 6.9 | 0.35545 | 6.9 | 0.71091 | 6.9 | 1.0664 | 6.9 | 1.4218 | 6.9 | 1.7773 | 6.9 | 2.1327 | 6.9 | 2.4882 | 6.9 | 2.8436 | 6.9 | 3.1991 | 6.9 | 3.5545
7 | 0.17639 | 7 | 0.35277 | 7 | 0.70555 | 7 | 1.0583 | 7 | 1.4111 | 7 | 1.7639 | 7 | 2.1166 | 7 | 2.4694 | 7 | 2.8222 | 7 | 3.175 | 7 | 3.5277
7.1 | 0.17509 | 7.1 | 0.35017 | 7.1 | 0.70034 | 7.1 | 1.0505 | 7.1 | 1.4007 | 7.1 | 1.7509 | 7.1 | 2.101 | 7.1 | 2.4512 | 7.1 | 2.8014 | 7.1 | 3.1515 | 7.1 | 3.5017
7.2 | 0.17382 | 7.2 | 0.34764 | 7.2 | 0.69528 | 7.2 | 1.0429 | 7.2 | 1.3906 | 7.2 | 1.7382 | 7.2 | 2.0858 | 7.2 | 2.4335 | 7.2 | 2.7811 | 7.2 | 3.1288 | 7.2 | 3.4764
7.3 | 0.17259 | 7.3 | 0.34518 | 7.3 | 0.69036 | 7.3 | 1.0355 | 7.3 | 1.3807 | 7.3 | 1.7259 | 7.3 | 2.0711 | 7.3 | 2.4163 | 7.3 | 2.7615 | 7.3 | 3.1066 | 7.3 | 3.4518
7.4 | 0.17139 | 7.4 | 0.34279 | 7.4 | 0.68558 | 7.4 | 1.0284 | 7.4 | 1.3712 | 7.4 | 1.7139 | 7.4 | 2.0567 | 7.4 | 2.3995 | 7.4 | 2.7423 | 7.4 | 3.0851 | 7.4 | 3.4279
7.5 | 0.17023 | 7.5 | 0.34046 | 7.5 | 0.68092 | 7.5 | 1.0214 | 7.5 | 1.3618 | 7.5 | 1.7023 | 7.5 | 2.0427 | 7.5 | 2.3832 | 7.5 | 2.7237 | 7.5 | 3.0641 | 7.5 | 3.4046
7.6 | 0.16909 | 7.6 | 0.33819 | 7.6 | 0.67638 | 7.6 | 1.0146 | 7.6 | 1.3528 | 7.6 | 1.6909 | 7.6 | 2.0291 | 7.6 | 2.3673 | 7.6 | 2.7055 | 7.6 | 3.0437 | 7.6 | 3.3819
7.7 | 0.16799 | 7.7 | 0.33598 | 7.7 | 0.67196 | 7.7 | 1.0079 | 7.7 | 1.3439 | 7.7 | 1.6799 | 7.7 | 2.0159 | 7.7 | 2.3519 | 7.7 | 2.6878 | 7.7 | 3.0238 | 7.7 | 3.3598
7.8 | 0.16691 | 7.8 | 0.33383 | 7.8 | 0.66765 | 7.8 | 1.0015 | 7.8 | 1.3353 | 7.8 | 1.6691 | 7.8 | 2.003 | 7.8 | 2.3368 | 7.8 | 2.6706 | 7.8 | 3.0044 | 7.8 | 3.3383
7.9 | 0.16586 | 7.9 | 0.33173 | 7.9 | 0.66345 | 7.9 | 0.99518 | 7.9 | 1.3269 | 7.9 | 1.6586 | 7.9 | 1.9904 | 7.9 | 2.3221 | 7.9 | 2.6538 | 7.9 | 2.9855 | 7.9 | 3.3173
8 | 0.16484 | 8 | 0.32968 | 8 | 0.65935 | 8 | 0.98903 | 8 | 1.3187 | 8 | 1.6484 | 8 | 1.9781 | 8 | 2.3077 | 8 | 2.6374 | 8 | 2.9671 | 8 | 3.2968
8.1 | 0.16384 | 8.1 | 0.32768 | 8.1 | 0.65536 | 8.1 | 0.98304 | 8.1 | 1.3107 | 8.1 | 1.6384 | 8.1 | 1.9661 | 8.1 | 2.2938 | 8.1 | 2.6214 | 8.1 | 2.9491 | 8.1 | 3.2768
8.2 | 0.16286 | 8.2 | 0.32573 | 8.2 | 0.65146 | 8.2 | 0.97718 | 8.2 | 1.3029 | 8.2 | 1.6286 | 8.2 | 1.9544 | 8.2 | 2.2801 | 8.2 | 2.6058 | 8.2 | 2.9315 | 8.2 | 3.2573
8.3 | 0.16191 | 8.3 | 0.32382 | 8.3 | 0.64764 | 8.3 | 0.97147 | 8.3 | 1.2953 | 8.3 | 1.6191 | 8.3 | 1.9429 | 8.3 | 2.2668 | 8.3 | 2.5906 | 8.3 | 2.9144 | 8.3 | 3.2382
8.4 | 0.16098 | 8.4 | 0.32196 | 8.4 | 0.64392 | 8.4 | 0.96588 | 8.4 | 1.2878 | 8.4 | 1.6098 | 8.4 | 1.9318 | 8.4 | 2.2537 | 8.4 | 2.5757 | 8.4 | 2.8977 | 8.4 | 3.2196
8.5 | 0.16007 | 8.5 | 0.32014 | 8.5 | 0.64029 | 8.5 | 0.96043 | 8.5 | 1.2806 | 8.5 | 1.6007 | 8.5 | 1.9209 | 8.5 | 2.241 | 8.5 | 2.5611 | 8.5 | 2.8813 | 8.5 | 3.2014
8.6 | 0.15918 | 8.6 | 0.31836 | 8.6 | 0.63673 | 8.6 | 0.95509 | 8.6 | 1.2735 | 8.6 | 1.5918 | 8.6 | 1.9102 | 8.6 | 2.2286 | 8.6 | 2.5469 | 8.6 | 2.8653 | 8.6 | 3.1836
8.7 | 0.15831 | 8.7 | 0.31663 | 8.7 | 0.63325 | 8.7 | 0.94988 | 8.7 | 1.2665 | 8.7 | 1.5831 | 8.7 | 1.8998 | 8.7 | 2.2164 | 8.7 | 2.533 | 8.7 | 2.8496 | 8.7 | 3.1663
8.8 | 0.15746 | 8.8 | 0.31493 | 8.8 | 0.62985 | 8.8 | 0.94478 | 8.8 | 1.2597 | 8.8 | 1.5746 | 8.8 | 1.8896 | 8.8 | 2.2045 | 8.8 | 2.5194 | 8.8 | 2.8343 | 8.8 | 3.1493
8.9 | 0.15663 | 8.9 | 0.31326 | 8.9 | 0.62653 | 8.9 | 0.93979 | 8.9 | 1.2531 | 8.9 | 1.5663 | 8.9 | 1.8796 | 8.9 | 2.1928 | 8.9 | 2.5061 | 8.9 | 2.8194 | 8.9 | 3.1326
9 | 0.15582 | 9 | 0.31163 | 9 | 0.62327 | 9 | 0.9349 | 9 | 1.2465 | 9 | 1.5582 | 9 | 1.8698 | 9 | 2.1814 | 9 | 2.4931 | 9 | 2.8047 | 9 | 3.1163
9.1 | 0.15502 | 9.1 | 0.31004 | 9.1 | 0.62008 | 9.1 | 0.93012 | 9.1 | 1.2402 | 9.1 | 1.5502 | 9.1 | 1.8602 | 9.1 | 2.1703 | 9.1 | 2.4803 | 9.1 | 2.7904 | 9.1 | 3.1004
9.2 | 0.15424 | 9.2 | 0.30848 | 9.2 | 0.61696 | 9.2 | 0.92544 | 9.2 | 1.2339 | 9.2 | 1.5424 | 9.2 | 1.8509 | 9.2 | 2.1594 | 9.2 | 2.4678 | 9.2 | 2.7763 | 9.2 | 3.0848
9.3 | 0.15348 | 9.3 | 0.30695 | 9.3 | 0.6139 | 9.3 | 0.92085 | 9.3 | 1.2278 | 9.3 | 1.5348 | 9.3 | 1.8417 | 9.3 | 2.1487 | 9.3 | 2.4556 | 9.3 | 2.7626 | 9.3 | 3.0695
9.4 | 0.15273 | 9.4 | 0.30545 | 9.4 | 0.61091 | 9.4 | 0.91636 | 9.4 | 1.2218 | 9.4 | 1.5273 | 9.4 | 1.8327 | 9.4 | 2.1382 | 9.4 | 2.4436 | 9.4 | 2.7491 | 9.4 | 3.0545
9.5 | 0.15199 | 9.5 | 0.30399 | 9.5 | 0.60797 | 9.5 | 0.91196 | 9.5 | 1.2159 | 9.5 | 1.5199 | 9.5 | 1.8239 | 9.5 | 2.1279 | 9.5 | 2.4319 | 9.5 | 2.7359 | 9.5 | 3.0399
9.6 | 0.15127 | 9.6 | 0.30255 | 9.6 | 0.60509 | 9.6 | 0.90764 | 9.6 | 1.2102 | 9.6 | 1.5127 | 9.6 | 1.8153 | 9.6 | 2.1178 | 9.6 | 2.4204 | 9.6 | 2.7229 | 9.6 | 3.0255
9.7 | 0.15057 | 9.7 | 0.30113 | 9.7 | 0.60227 | 9.7 | 0.9034 | 9.7 | 1.2045 | 9.7 | 1.5057 | 9.7 | 1.8068 | 9.7 | 2.1079 | 9.7 | 2.4091 | 9.7 | 2.7102 | 9.7 | 3.0113
9.8 | 0.14988 | 9.8 | 0.29975 | 9.8 | 0.5995 | 9.8 | 0.89925 | 9.8 | 1.199 | 9.8 | 1.4988 | 9.8 | 1.7985 | 9.8 | 2.0983 | 9.8 | 2.398 | 9.8 | 2.6978 | 9.8 | 2.9975
9.9 | 0.1492 | 9.9 | 0.29839 | 9.9 | 0.59678 | 9.9 | 0.89518 | 9.9 | 1.1936 | 9.9 | 1.492 | 9.9 | 1.7904 | 9.9 | 2.0887 | 9.9 | 2.3871 | 9.9 | 2.6855 | 9.9 | 2.9839
10 | 0.14853 | 10 | 0.29706 | 10 | 0.59412 | 10 | 0.89118 | 10 | 1.1882 | 10 | 1.4853 | 10 | 1.7824 | 10 | 2.0794 | 10 | 2.3765 | 10 | 2.6735 | 10 | 2.9706
10.5 | 0.14538 | 10.5 | 0.29075 | 10.5 | 0.58151 | 10.5 | 0.87226 | 10.5 | 1.163 | 10.5 | 1.4538 | 10.5 | 1.7445 | 10.5 | 2.0353 | 10.5 | 2.326 | 10.5 | 2.6168 | 10.5 | 2.9075
11 | 0.14249 | 11 | 0.28498 | 11 | 0.56996 | 11 | 0.85494 | 11 | 1.1399 | 11 | 1.4249 | 11 | 1.7099 | 11 | 1.9949 | 11 | 2.2798 | 11 | 2.5648 | 11 | 2.8498
11.5 | 0.13983 | 11.5 | 0.27967 | 11.5 | 0.55933 | 11.5 | 0.839 | 11.5 | 1.1187 | 11.5 | 1.3983 | 11.5 | 1.678 | 11.5 | 1.9577 | 11.5 | 2.2373 | 11.5 | 2.517 | 11.5 | 2.7967
12 | 0.13738 | 12 | 0.27476 | 12 | 0.54952 | 12 | 0.82428 | 12 | 1.099 | 12 | 1.3738 | 12 | 1.6486 | 12 | 1.9233 | 12 | 2.1981 | 12 | 2.4728 | 12 | 2.7476
12.5 | 0.1351 | 12.5 | 0.27021 | 12.5 | 0.54041 | 12.5 | 0.81062 | 12.5 | 1.0808 | 12.5 | 1.351 | 12.5 | 1.6212 | 12.5 | 1.8914 | 12.5 | 2.1617 | 12.5 | 2.4319 | 12.5 | 2.7021
13 | 0.13298 | 13 | 0.26597 | 13 | 0.53194 | 13 | 0.79791 | 13 | 1.0639 | 13 | 1.3298 | 13 | 1.5958 | 13 | 1.8618 | 13 | 2.1278 | 13 | 2.3937 | 13 | 2.6597
13.5 | 0.13101 | 13.5 | 0.26201 | 13.5 | 0.52403 | 13.5 | 0.78604 | 13.5 | 1.0481 | 13.5 | 1.3101 | 13.5 | 1.5721 | 13.5 | 1.8341 | 13.5 | 2.0961 | 13.5 | 2.3581 | 13.5 | 2.6201
14 | 0.12915 | 14 | 0.25831 | 14 | 0.51662 | 14 | 0.77492 | 14 | 1.0332 | 14 | 1.2915 | 14 | 1.5498 | 14 | 1.8082 | 14 | 2.0665 | 14 | 2.3248 | 14 | 2.5831
14.5 | 0.12741 | 14.5 | 0.25483 | 14.5 | 0.50966 | 14.5 | 0.76448 | 14.5 | 1.0193 | 14.5 | 1.2741 | 14.5 | 1.529 | 14.5 | 1.7838 | 14.5 | 2.0386 | 14.5 | 2.2935 | 14.5 | 2.5483
15 | 0.12578 | 15 | 0.25155 | 15 | 0.5031 | 15 | 0.75466 | 15 | 1.0062 | 15 | 1.2578 | 15 | 1.5093 | 15 | 1.7609 | 15 | 2.0124 | 15 | 2.264 | 15 | 2.5155
16 | 0.12277 | 16 | 0.24554 | 16 | 0.49107 | 16 | 0.73661 | 16 | 0.98215 | 16 | 1.2277 | 16 | 1.4732 | 16 | 1.7188 | 16 | 1.9643 | 16 | 2.2098 | 16 | 2.4554
17 | 0.12007 | 17 | 0.24014 | 17 | 0.48027 | 17 | 0.72041 | 17 | 0.96054 | 17 | 1.2007 | 17 | 1.4408 | 17 | 1.6809 | 17 | 1.9211 | 17 | 2.1612 | 17 | 2.4014
18 | 0.11763 | 18 | 0.23525 | 18 | 0.4705 | 18 | 0.70575 | 18 | 0.941 | 18 | 1.1763 | 18 | 1.4115 | 18 | 1.6468 | 18 | 1.882 | 18 | 2.1173 | 18 | 2.3525
19 | 0.1154 | 19 | 0.2308 | 19 | 0.46161 | 19 | 0.69241 | 19 | 0.92322 | 19 | 1.154 | 19 | 1.3848 | 19 | 1.6156 | 19 | 1.8464 | 19 | 2.0772 | 19 | 2.308
20 | 0.11337 | 20 | 0.22674 | 20 | 0.45347 | 20 | 0.68021 | 20 | 0.90694 | 20 | 1.1337 | 20 | 1.3604 | 20 | 1.5871 | 20 | 1.8139 | 20 | 2.0406 | 20 | 2.2674
21 | 0.1115 | 21 | 0.22299 | 21 | 0.44598 | 21 | 0.66898 | 21 | 0.89197 | 21 | 1.115 | 21 | 1.338 | 21 | 1.5609 | 21 | 1.7839 | 21 | 2.0069 | 21 | 2.2299
22 | 0.10977 | 22 | 0.21953 | 22 | 0.43907 | 22 | 0.6586 | 22 | 0.87813 | 22 | 1.0977 | 22 | 1.3172 | 22 | 1.5367 | 22 | 1.7563 | 22 | 1.9758 | 22 | 2.1953
23 | 0.10816 | 23 | 0.21632 | 23 | 0.43265 | 23 | 0.64897 | 23 | 0.86529 | 23 | 1.0816 | 23 | 1.2979 | 23 | 1.5143 | 23 | 1.7306 | 23 | 1.9469 | 23 | 2.1632
24 | 0.10667 | 24 | 0.21333 | 24 | 0.42667 | 24 | 0.64 | 24 | 0.85334 | 24 | 1.0667 | 24 | 1.28 | 24 | 1.4933 | 24 | 1.7067 | 24 | 1.92 | 24 | 2.1333
25 | 0.10527 | 25 | 0.21054 | 25 | 0.42108 | 25 | 0.63163 | 25 | 0.84217 | 25 | 1.0527 | 25 | 1.2633 | 25 | 1.4738 | 25 | 1.6843 | 25 | 1.8949 | 25 | 2.1054
26 | 0.10396 | 26 | 0.20793 | 26 | 0.41585 | 26 | 0.62378 | 26 | 0.8317 | 26 | 1.0396 | 26 | 1.2476 | 26 | 1.4555 | 26 | 1.6634 | 26 | 1.8713 | 26 | 2.0793
27 | 0.10273 | 27 | 0.20547 | 27 | 0.41093 | 27 | 0.6164 | 27 | 0.82186 | 27 | 1.0273 | 27 | 1.2328 | 27 | 1.4383 | 27 | 1.6437 | 27 | 1.8492 | 27 | 2.0547
28 | 0.10157 | 28 | 0.20315 | 28 | 0.4063 | 28 | 0.60945 | 28 | 0.8126 | 28 | 1.0157 | 28 | 1.2189 | 28 | 1.422 | 28 | 1.6252 | 28 | 1.8283 | 28 | 2.0315
29 | 0.10048 | 29 | 0.20096 | 29 | 0.40192 | 29 | 0.60288 | 29 | 0.80384 | 29 | 1.0048 | 29 | 1.2058 | 29 | 1.4067 | 29 | 1.6077 | 29 | 1.8086 | 29 | 2.0096
30 | 0.099445 | 30 | 0.19889 | 30 | 0.39778 | 30 | 0.59667 | 30 | 0.79556 | 30 | 0.99445 | 30 | 1.1933 | 30 | 1.3922 | 30 | 1.5911 | 30 | 1.79 | 30 | 1.9889
31 | 0.099445 | 31 | 0.19889 | 31 | 0.39778 | 31 | 0.59667 | 31 | 0.79556 | 31 | 0.99445 | 31 | 1.1933 | 31 | 1.3922 | 31 | 1.5911 | 31 | 1.79 | 31 | 1.9889
32 | 0.099445 | 32 | 0.19889 | 32 | 0.39778 | 32 | 0.59667 | 32 | 0.79556 | 32 | 0.99445 | 32 | 1.1933 | 32 | 1.3922 | 32 | 1.5911 | 32 | 1.79 | 32 | 1.9889
33 | 0.099445 | 33 | 0.19889 | 33 | 0.39778 | 33 | 0.59667 | 33 | 0.79556 | 33 | 0.99445 | 33 | 1.1933 | 33 | 1.3922 | 33 | 1.5911 | 33 | 1.79 | 33 | 1.9889
34 | 0.099445 | 34 | 0.19889 | 34 | 0.39778 | 34 | 0.59667 | 34 | 0.79556 | 34 | 0.99445 | 34 | 1.1933 | 34 | 1.3922 | 34 | 1.5911 | 34 | 1.79 | 34 | 1.9889
35 | 0.099445 | 35 | 0.19889 | 35 | 0.39778 | 35 | 0.59667 | 35 | 0.79556 | 35 | 0.99445 | 35 | 1.1933 | 35 | 1.3922 | 35 | 1.5911 | 35 | 1.79 | 35 | 1.9889
36 | 0.099445 | 36 | 0.19889 | 36 | 0.39778 | 36 | 0.59667 | 36 | 0.79556 | 36 | 0.99445 | 36 | 1.1933 | 36 | 1.3922 | 36 | 1.5911 | 36 | 1.79 | 36 | 1.9889
37 | 0.099445 | 37 | 0.19889 | 37 | 0.39778 | 37 | 0.59667 | 37 | 0.79556 | 37 | 0.99445 | 37 | 1.1933 | 37 | 1.3922 | 37 | 1.5911 | 37 | 1.79 | 37 | 1.9889
38 | 0.099445 | 38 | 0.19889 | 38 | 0.39778 | 38 | 0.59667 | 38 | 0.79556 | 38 | 0.99445 | 38 | 1.1933 | 38 | 1.3922 | 38 | 1.5911 | 38 | 1.79 | 38 | 1.9889
39 | 0.099445 | 39 | 0.19889 | 39 | 0.39778 | 39 | 0.59667 | 39 | 0.79556 | 39 | 0.99445 | 39 | 1.1933 | 39 | 1.3922 | 39 | 1.5911 | 39 | 1.79 | 39 | 1.9889
40 | 0.099445 | 40 | 0.19889 | 40 | 0.39778 | 40 | 0.59667 | 40 | 0.79556 | 40 | 0.99445 | 40 | 1.1933 | 40 | 1.3922 | 40 | 1.5911 | 40 | 1.79 | 40 | 1.9889
41 | 0.099445 | 41 | 0.19889 | 41 | 0.39778 | 41 | 0.59667 | 41 | 0.79556 | 41 | 0.99445 | 41 | 1.1933 | 41 | 1.3922 | 41 | 1.5911 | 41 | 1.79 | 41 | 1.9889
42 | 0.099445 | 42 | 0.19889 | 42 | 0.39778 | 42 | 0.59667 | 42 | 0.79556 | 42 | 0.99445 | 42 | 1.1933 | 42 | 1.3922 | 42 | 1.5911 | 42 | 1.79 | 42 | 1.9889
43 | 0.099445 | 43 | 0.19889 | 43 | 0.39778 | 43 | 0.59667 | 43 | 0.79556 | 43 | 0.99445 | 43 | 1.1933 | 43 | 1.3922 | 43 | 1.5911 | 43 | 1.79 | 43 | 1.9889
44 | 0.099445 | 44 | 0.19889 | 44 | 0.39778 | 44 | 0.59667 | 44 | 0.79556 | 44 | 0.99445 | 44 | 1.1933 | 44 | 1.3922 | 44 | 1.5911 | 44 | 1.79 | 44 | 1.9889
45 | 0.099445 | 45 | 0.19889 | 45 | 0.39778 | 45 | 0.59667 | 45 | 0.79556 | 45 | 0.99445 | 45 | 1.1933 | 45 | 1.3922 | 45 | 1.5911 | 45 | 1.79 | 45 | 1.9889
46 | 0.099445 | 46 | 0.19889 | 46 | 0.39778 | 46 | 0.59667 | 46 | 0.79556 | 46 | 0.99445 | 46 | 1.1933 | 46 | 1.3922 | 46 | 1.5911 | 46 | 1.79 | 46 | 1.9889
47 | 0.099445 | 47 | 0.19889 | 47 | 0.39778 | 47 | 0.59667 | 47 | 0.79556 | 47 | 0.99445 | 47 | 1.1933 | 47 | 1.3922 | 47 | 1.5911 | 47 | 1.79 | 47 | 1.9889
48 | 0.099445 | 48 | 0.19889 | 48 | 0.39778 | 48 | 0.59667 | 48 | 0.79556 | 48 | 0.99445 | 48 | 1.1933 | 48 | 1.3922 | 48 | 1.5911 | 48 | 1.79 | 48 | 1.9889
49 | 0.099445 | 49 | 0.19889 | 49 | 0.39778 | 49 | 0.59667 | 49 | 0.79556 | 49 | 0.99445 | 49 | 1.1933 | 49 | 1.3922 | 49 | 1.5911 | 49 | 1.79 | 49 | 1.9889
50 | 0.099445 | 50 | 0.19889 | 50 | 0.39778 | 50 | 0.59667 | 50 | 0.79556 | 50 | 0.99445 | 50 | 1.1933 | 50 | 1.3922 | 50 | 1.5911 | 50 | 1.79 | 50 | 1.9889
55 | 0.099445 | 55 | 0.19889 | 55 | 0.39778 | 55 | 0.59667 | 55 | 0.79556 | 55 | 0.99445 | 55 | 1.1933 | 55 | 1.3922 | 55 | 1.5911 | 55 | 1.79 | 55 | 1.9889
60 | 0.099445 | 60 | 0.19889 | 60 | 0.39778 | 60 | 0.59667 | 60 | 0.79556 | 60 | 0.99445 | 60 | 1.1933 | 60 | 1.3922 | 60 | 1.5911 | 60 | 1.79 | 60 | 1.9889
65 | 0.099445 | 65 | 0.19889 | 65 | 0.39778 | 65 | 0.59667 | 65 | 0.79556 | 65 | 0.99445 | 65 | 1.1933 | 65 | 1.3922 | 65 | 1.5911 | 65 | 1.79 | 65 | 1.9889
70 | 0.099445 | 70 | 0.19889 | 70 | 0.39778 | 70 | 0.59667 | 70 | 0.79556 | 70 | 0.99445 | 70 | 1.1933 | 70 | 1.3922 | 70 | 1.5911 | 70 | 1.79 | 70 | 1.9889
75 | 0.099445 | 75 | 0.19889 | 75 | 0.39778 | 75 | 0.59667 | 75 | 0.79556 | 75 | 0.99445 | 75 | 1.1933 | 75 | 1.3922 | 75 | 1.5911 | 75 | 1.79 | 75 | 1.9889
80 | 0.099445 | 80 | 0.19889 | 80 | 0.39778 | 80 | 0.59667 | 80 | 0.79556 | 80 | 0.99445 | 80 | 1.1933 | 80 | 1.3922 | 80 | 1.5911 | 80 | 1.79 | 80 | 1.9889
85 | 0.099445 | 85 | 0.19889 | 85 | 0.39778 | 85 | 0.59667 | 85 | 0.79556 | 85 | 0.99445 | 85 | 1.1933 | 85 | 1.3922 | 85 | 1.5911 | 85 | 1.79 | 85 | 1.9889
90 | 0.099445 | 90 | 0.19889 | 90 | 0.39778 | 90 | 0.59667 | 90 | 0.79556 | 90 | 0.99445 | 90 | 1.1933 | 90 | 1.3922 | 90 | 1.5911 | 90 | 1.79 | 90 | 1.9889
95 | 0.099445 | 95 | 0.19889 | 95 | 0.39778 | 95 | 0.59667 | 95 | 0.79556 | 95 | 0.99445 | 95 | 1.1933 | 95 | 1.3922 | 95 | 1.5911 | 95 | 1.79 | 95 | 1.9889
100 | 0.099445 | 100 | 0.19889 | 100 | 0.39778 | 100 | 0.59667 | 100 | 0.79556 | 100 | 0.99445 | 100 | 1.1933 | 100 | 1.3922 | 100 | 1.5911 | 100 | 1.79 | 100 | 1.9889