## 695-9-2 Min Trip (1)
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Tap Interrupter - Instantaneous Speed (TCC 695-9-2) | [9 empty] | Tap Interrupter - Instantaneous Speed (TCC 695-9-2)
Minimum Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Minimum Tripping Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: | Miminum tripping curves are plotted to minimum test points. | [8 empty] | Tolerance: | Miminum tripping curves are plotted to minimum test points.
| Maximum variations expressed in terms of current are plus 10%. | [9 empty] | Maximum variations expressed in terms of current are plus 10%.
50 A |  | 0.2 kA |  | 0.3 kA |  | 0.4 kA |  | 0.5 kA |  | 0.6 kA |  | 0.7 kA |  | 0.8 kA |  | 0.9 kA
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
1422.396 | 0.01 | 200 | 0.01 | 300 | 0.01 | 400 | 0.01 | 500 | 0.01 | 600 | 0.01 | 700 | 0.01 | 800 | 0.01 | 900 | 0.01
1350.266 | 0.0106 | 200 | 0.15 | 300 | 0.076 | 400 | 0.0482 | 500 | 0.0342 | 600 | 0.0266 | 700 | 0.022 | 800 | 0.0185 | 900 | 0.0162
1269.842 | 0.0113 | 192.81 | 0.1643 | 274.675 | 0.0883 | 380.059 | 0.0531 | 468.499 | 0.038 | 556.859 | 0.0295 | 648.923 | 0.0242 | 767.307 | 0.01956 | 877.567 | 0.0166
1269.842 | 0.0113 | 177.776 | 0.1919 | 256.173 | 0.1 | 356.679 | 0.0587 | 440.136 | 0.0419 | 535 | 0.0314 | 640 | 0.0248 | 745 | 0.0202 | 850 | 0.0173
1183.074 | 0.0121 | 167.187 | 0.2182 | 239.415 | 0.1127 | 326.14 | 0.0679
1098.799 | 0.0131 | 155.763 | 0.2504 | 221.437 | 0.129
1045.252 | 0.014 | 143.767 | 0.2952 | 215 | 0.135
988.124 | 0.0149 | 135.204 | 0.3427
932.176 | 0.0158 | 124.921 | 0.4118
877.567 | 0.0168 | 118.34 | 0.4726
833.065 | 0.018 | 112.573 | 0.5284
767.307 | 0.0197 | 104.881 | 0.6238
714.877 | 0.0216 | 98.02 | 0.7219
648.923 | 0.0242 | 92.277 | 0.8433
609.637 | 0.0263 | 87.053 | 0.9841
556.859 | 0.0297
504.432 | 0.0342
468.499 | 0.038
440.136 | 0.0419
400.362 | 0.0482
380.059 | 0.0531
356.679 | 0.0587
326.14 | 0.0679
297.285 | 0.0782
274.675 | 0.0883
256.173 | 0.1
239.415 | 0.1127
221.437 | 0.1275
209.116 | 0.1427
192.81 | 0.1643
177.776 | 0.1919
167.187 | 0.2182
155.763 | 0.2504
143.767 | 0.2952
135.204 | 0.3427
124.921 | 0.4118
118.34 | 0.4726
112.573 | 0.5284
104.881 | 0.6238
98.02 | 0.7219
92.277 | 0.8433
87.053 | 0.9841
82.552 | 1.1246
78.04 | 1.3138
73.775 | 1.5622
69.743 | 1.8731
66.275 | 2.2273
66 | 2.2319
63.374 | 2.6264
61.235 | 3.0016
59.106 | 3.4411
57.888 | 3.9533
56.401 | 4.5369
55.01 | 5.2833
54.045 | 5.9381
53.374 | 6.7652
52.111 | 8.2828
51.465 | 9.8386
50.773 | 11.8709
50.3 | 14.1154
50.091 | 16.9072
50.3 | 19.8953
50.143 | 24.8198
50.038 | 29.7599
50.143 | 34.7284
49.934 | 39.7311
49.986 | 49.9288
49.934 | 59.8041
49.779 | 69.9343
49.779 | 79.9249
49.779 | 99.2931
49.572 | 120.4303
49.675 | 148.9912
49.624 | 188.8017
49.572 | 188.6048
49.675 | 296.917
49.727 | 394.3375
49.934 | 497.6237
49.52 | 592.9466
49.727 | 221.2439
49.624 | 241.5064

## 695-9-2 Min Trip (2)
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Main Interrupter - Instantaneous Speed (TCC 695-9-2) | [9 empty] | Main Interrupter - Instantaneous Speed (TCC 695-9-2)
Minimum Tripping Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Minimum Tripping Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: | Miminum tripping curves are plotted to minimum test points. | [8 empty] | Tolerance: | Miminum tripping curves are plotted to minimum test points.
| Maximum variations expressed in terms of current are plus 10%. | [9 empty] | Maximum variations expressed in terms of current are plus 10%.
400 A |  | 1kA |  | 2kA |  | 3kA |  | 4kA |  | 5kA |  | 6kA
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
11845.158 | 0.01 | 1000 | 0.01 | 2000 | 0.01 | 3000 | 0.01 | 4000 | 0.01 | 5000 | 0.01 | 6000 | 0.01
10707.881 | 0.0113 | 1000 | 0.4221 | 2000 | 0.111 | 3000 | 0.058 | 4000 | 0.039 | 5000 | 0.028 | 6000 | 0.023
9649.624 | 0.0127 | 961.68 | 0.4821 | 1917.172 | 0.1222 | 2800.039 | 0.0666 | 3790.322 | 0.0431 | 4730.832 | 0.0314 | 5348.911 | 0.0268
8614.893 | 0.0146 | 895.05 | 0.5738 | 1742.142 | 0.1427 | 2533.837 | 0.0791 | 3447.866 | 0.0496 | 4270 | 0.03645
7731.238 | 0.0167 | 825.271 | 0.6909 | 1583.091 | 0.1702 | 2290.558 | 0.0924 | 3220 | 0.055
7010.799 | 0.0189 | 767.294 | 0.8276 | 1434.076 | 0.2026 | 2160 | 0.101
6066.652 | 0.0227 | 723.858 | 0.9759 | 1315.413 | 0.2409
5348.911 | 0.0268 |  |  | 1200.306 | 0.2898
4730.832 | 0.0314 |  |  | 1117.143 | 0.3388
4227.941 | 0.0367
3790.322 | 0.0431
3447.866 | 0.0496
3090.99 | 0.058
2800.039 | 0.0666
2533.837 | 0.0791
2290.558 | 0.0924
2077.112 | 0.1059
1917.172 | 0.1222
1742.142 | 0.1427
1583.091 | 0.1702
1434.076 | 0.2026
1315.413 | 0.2409
1200.306 | 0.2898
1117.143 | 0.3388
1038.66 | 0.4021
961.68 | 0.4821
895.05 | 0.5738
825.271 | 0.6909
767.294 | 0.8276
723.858 | 0.9759
674.407 | 1.1665
642.885 | 1.3669
606.492 | 1.6407
573.948 | 1.9489
547.691 | 2.2981
518.303 | 2.8018
497.689 | 3.3074
486.425 | 3.768
470.494 | 4.6374
457.935 | 5.6776
443.398 | 7.1648
434.718 | 8.5105
427.985 | 10.067
423.554 | 11.9829
421.795 | 14.4883
421.356 | 17.8125
420.918 | 22.572
419.169 | 30.2608
420.48 | 40.6959
419.169 | 53.3761
420.918 | 66.588
418.298 | 87.5182
420.043 | 109.6378
420.918 | 137.3478
420.918 | 169.0368
419.169 | 212.4232
420.043 | 273.9991
420.918 | 346.8497
419.606 | 419.8091
417.863 | 507.0563
419.169 | 597.9159

## 695-9-2 Total Clear (1)
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Tap Interrupter - Instantaneous Speed (TCC 695-9-2) | [9 empty] | Tap Interrupter - Instantaneous Speed (TCC 695-9-2)
Total Clearing Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated February 16, 2009
Tolerance in Terms of Current: |  |  | Curves are plotted to maximum test points. All variations are minus. | [6 empty] | Tolerance in Terms of Current: |  |  | Curves are plotted to maximum test points. All variations are minus.
50 |  | 0.2 kA |  | 0.3 kA |  | 0.4 kA |  | 0.5 kA |  | 0.6 kA |  | 0.7 kA |  | 0.8 kA |  | 0.9 kA
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
54.472 | 592.9766 | 101.5047 | 0.8733 | 243.5807 | 0.16 | 358.754 | 0.0979 | 484.1496 | 0.0719 | 590 | 0.0613 | 700 | 0.0548 | 822 | 0.05035 | 932 | 0.0476
54.5292 | 120.4603 | 107.822 | 0.7519 | 263.3565 | 0.1427 | 392.3469 | 0.0887 | 515.3489 | 0.068 | 612.5449 | 0.0597 | 713.8153 | 0.0542 | 844.0377 | 0.0497 | 965.3237 | 0.0468
54.5292 | 188.6348 | 115.3691 | 0.6538 | 281.7903 | 0.13 | 418.0649 | 0.0831 | 550 | 0.0642 | 660 | 0.0568 | 770 | 0.0523 | 880 | 0.0488 | 990 | 0.0465
54.5864 | 188.8317 | 123.8303 | 0.5584 | 302.1425 | 0.1183 | 440 | 0.0782 | 550 | 0.04 | 660 | 0.04 | 770 | 0.04 | 880 | 0.04 | 990 | 0.04
54.5864 | 241.5364 | 130.174 | 0.5026 | 330 | 0.1082 | 440 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.04
54.6425 | 149.0212 | 137.4131 | 0.4418 | 330 | 0.04 | 25000 | 0.04 | 25000 | 0.01 | 25000 | 0.01 | 25000 | 0.01 | 25000 | 0.01 | 25000 | 0.01
54.6425 | 296.947 | 148.7244 | 0.3727 | 25000 | 0.04 | 25000 | 0.01
54.6997 | 394.3675 | 158.1437 | 0.3252 | 25000 | 0.01
54.6997 | 221.2739 | 171.3393 | 0.2804
54.7569 | 69.9643 | 183.9057 | 0.2482
54.7569 | 79.9549 | 195.5536 | 0.2219
54.7569 | 99.3231 | 212.091 | 0.1943
54.9274 | 39.7611 | 220 | 0.182
54.9274 | 59.8341 | 220 | 0.04
54.9274 | 497.6537 | 25000 | 0.04
54.9846 | 49.9588 | 25000 | 0.01
55.0418 | 29.7899
55.1001 | 16.9372
55.1573 | 24.8498
55.1573 | 34.7584
55.33 | 14.1454
55.33 | 19.9253
55.8503 | 11.9009
56.6115 | 9.8686
57.3221 | 8.3128
58.7114 | 6.7952
59.4495 | 5.9681
60.511 | 5.3133
62.0411 | 4.5669
63.6768 | 3.9833
65.0166 | 3.4711
67.3585 | 3.0316
69.7114 | 2.6564
72.6 | 2.2619
72.9025 | 2.2573
76.7173 | 1.9031
81.1525 | 1.5922
85.844 | 1.3438
90.8072 | 1.1546
95.7583 | 1.0141
101.5047 | 0.8733
107.822 | 0.7519
115.3691 | 0.6538
123.8303 | 0.5584
130.174 | 0.5026
137.4131 | 0.4418
148.7244 | 0.3727
158.1437 | 0.3252
171.3393 | 0.2804
183.9057 | 0.2482
195.5536 | 0.2219
212.091 | 0.1943
230.0276 | 0.1727
243.5807 | 0.1575
263.3565 | 0.1427
281.7903 | 0.13
302.1425 | 0.1183
327.0135 | 0.1082
358.754 | 0.0979
392.3469 | 0.0887
418.0649 | 0.0831
440.3982 | 0.0782
484.1496 | 0.0719
515.3489 | 0.068
554.8752 | 0.0642
612.5449 | 0.0597
670.6007 | 0.0563
713.8153 | 0.0542
786.3647 | 0.0516
844.0377 | 0.0497
916.3715 | 0.048
965.3237 | 0.0468
1025.3936 | 0.0458
1086.9364 | 0.0449
1149.7772 | 0.044
1208.6789 | 0.0431
1301.3814 | 0.0421
1396.8262 | 0.0413
1396.8262 | 0.0413
1485.2926 | 0.0406
1564.6356 | 0.04
12500 | 0.04

## 695-9-2 Total Clear (2)
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Main Interrupter - Instantaneous Speed (TCC 695-9-2) | [9 empty] | Main Interrupter - Instantaneous Speed (TCC 695-9-2)
Total Clearing Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Total Clearing Time-Current Characteristic Curves Dated February 16, 2009
Tolerance in Terms of Current: |  |  | Curves are plotted to maximum test points. All variations are minus. | [6 empty] | Tolerance in Terms of Current: |  |  | Curves are plotted to maximum test points. All variations are minus.
400 |  | 1kA |  | 2kA |  | 3kA |  | 4kA |  | 5kA |  | 6kA
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
459.6493 | 507.0863 | 844.0234 | 0.8576 | 1228.857 | 0.3688 | 2519.614 | 0.1224 | 3600 | 0.0837 | 4800 | 0.0654 | 6000 | 0.056
460.1278 | 87.5482 | 907.7981 | 0.7209 | 1320.337 | 0.3198 | 2787.221 | 0.1091 | 3792.653 | 0.0796 | 5203.915 | 0.0612 | 6600 | 0.0527
461.0859 | 30.2908 | 984.555 | 0.6038 | 1446.954 | 0.2709 | 3080.043 | 0.0966 | 4169.354 | 0.0731 | 5500 | 0.058 | 6600 | 0.04
461.0859 | 53.4061 | 1057.848 | 0.5121 | 1577.484 | 0.2326 | 3300 | 0.09 | 4400 | 0.0685 | 5500 | 0.04 | 25000 | 0.04
461.0859 | 212.4532 | 1100 | 0.47 | 1741.4 | 0.2002 | 3300 | 0.04 | 4400 | 0.04 | 25000 | 0.04 | 25000 | 0.01
461.0859 | 597.9459 | 1100 | 0.04 | 1916.356 | 0.1727 | 25000 | 0.04 | 25000 | 0.04 | 25000 | 0.01
461.5666 | 419.8391 | 25000 | 0.04 | 2108.889 | 0.1522 | 25000 | 0.01 | 25000 | 0.01
462.0473 | 109.6678 | 25000 | 0.01 | 2200 | 0.142
462.0473 | 274.0291 |  |  | 2200 | 0.04
462.528 | 40.7259 |  |  | 25000 | 0.04
463.0098 | 22.602 |  |  | 25000 | 0.01
463.0098 | 66.618
463.0098 | 137.3778
463.0098 | 169.0668
463.0098 | 346.8797
463.4916 | 17.8425
463.9745 | 14.5183
465.9094 | 12.0129
470.7835 | 10.097
478.1898 | 8.5405
487.7378 | 7.1948
503.7285 | 5.7076
517.5434 | 4.6674
535.0675 | 3.798
547.4579 | 3.3374
570.1333 | 2.8318
602.4601 | 2.3281
631.3428 | 1.9789
667.1412 | 1.6707
707.1735 | 1.3969
741.8477 | 1.1965
796.2438 | 1.0059
844.0234 | 0.8576
907.7981 | 0.7209
984.555 | 0.6038
1057.848 | 0.5121
1142.526 | 0.4321
1228.857 | 0.3688
1320.337 | 0.3198
1446.954 | 0.2709
1577.484 | 0.2326
1741.4 | 0.2002
1916.356 | 0.1727
2108.889 | 0.1522
2284.823 | 0.1359
2519.614 | 0.1224
2787.221 | 0.1091
3080.043 | 0.0966
3400.089 | 0.088
3792.653 | 0.0796
4169.354 | 0.0731
4650.735 | 0.0667
5203.915 | 0.0614
5883.802 | 0.0568
6673.317 | 0.0527
7711.879 | 0.0489
8504.362 | 0.0467
9476.382 | 0.0446
10614.59 | 0.0427
11778.67 | 0.0413
12500 | 0.04