## Data
S&C Vista Underground Distribution Switchgear Overcurrent Control | [9 empty] | S&C Vista Underground Distribution Switchgear Overcurrent Control
Definite Time Delay (TCC 696-9-2) | [9 empty] | Definite Time Delay (TCC 696-9-2)
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated February 16, 2009 | [9 empty] | Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: | Minimum tripping curves are plotted to minimum test points. | [8 empty] | Tolerance: | Minimum tripping curves are plotted to minimum test points.
| Maximum variations expressed in terms of time are plus 8 milliseconds. | [9 empty] | Maximum variations expressed in terms of time are plus 8 milliseconds.
| Total clearing curves are plotted to maximum test points. All variations are minus. | [9 empty] | Total clearing curves are plotted to maximum test points. All variations are minus.
A - example |  | B |  | C |  | D |  | E |  | F |  | G
Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time | Current | Time
92.277 | 0.8433 | 5100 | 0.048 | 4700 | 0.064 | 3500 | 0.08 | 2600 | 0.096 | 2000 | 0.112 | 1500 | 0.128
98.02 | 0.7219 | 20000 | 0.048 | 12000 | 0.064 | 9000 | 0.08 | 6000 | 0.096 | 4500 | 0.112 | 3200 | 0.128
104.881 | 0.6238 | 20000 | 0.086 | 12000 | 0.102 | 9000 | 0.118 | 6000 | 0.134 | 4500 | 0.15 | 3200 | 0.166
112.573 | 0.5284 | 13000 | 0.086 | 9500 | 0.102 | 6500 | 0.118 | 5000 | 0.134 | 3500 | 0.15 | 2300 | 0.166
118.34 | 0.4726
124.921 | 0.4118
135.204 | 0.3427
143.767 | 0.2952
155.763 | 0.2504
167.187 | 0.2182
177.776 | 0.1919
192.81 | 0.1643
209.116 | 0.1427
221.437 | 0.1275
239.415 | 0.1127
256.173 | 0.1
274.675 | 0.0883
297.285 | 0.0782
326.14 | 0.0679
356.679 | 0.0587
380.059 | 0.0531
400.362 | 0.0482
440.136 | 0.0419
468.499 | 0.038
504.432 | 0.0342
540 | 0.032
25000 | 0.032
25000 | 0.07
500 | 0.07
392.3469 | 0.0887
358.754 | 0.0979
327.0135 | 0.1082
302.1425 | 0.1183
281.7903 | 0.13
263.3565 | 0.1427
243.5807 | 0.1575
230.0276 | 0.1727
212.091 | 0.1943
195.5536 | 0.2219
183.9057 | 0.2482
171.3393 | 0.2804
158.1437 | 0.3252
148.7244 | 0.3727
137.4131 | 0.4418
130.174 | 0.5026
123.8303 | 0.5584
115.3691 | 0.6538
107.822 | 0.7519
101.5047 | 0.8733
95.7583 | 1.0141