## Data
S&C Vista Underground Distribution Switchgear Overcurrent Control
Instaneous and Definite Time Delay (TCC 697-9-2)
Minimum Tripping and Total Clearing Time-Current Characteristic Curves Dated February 16, 2009
Tolerance: | Minimum tripping curves are plotted to minimum test points.
Maximum variations expresed in terms of time are plus 8 milliseconds.
Maximum variations expressed in terms of current are plus 10%.
Total clearing curves are plotted to maximum test points. All variations are minus.
50 |  | 50
Minimum Trip |  | Total Clear
Current | Time | Current | Time
3000 | 0.01 | 90.8072 | 1.1546
3000 | 0.032 | 95.7583 | 1.0141
535 | 0.032 | 101.5047 | 0.8733
504.432 | 0.0342 | 107.822 | 0.7519
468.499 | 0.038 | 115.3691 | 0.6538
440.136 | 0.0419 | 123.8303 | 0.5584
400.362 | 0.0482 | 130.174 | 0.5026
380.059 | 0.0531 | 137.4131 | 0.4418
356.679 | 0.0587 | 148.7244 | 0.3727
326.14 | 0.0679 | 158.1437 | 0.3252
297.285 | 0.0782 | 171.3393 | 0.2804
274.675 | 0.0883 | 183.9057 | 0.2482
256.173 | 0.1 | 195.5536 | 0.2219
239.415 | 0.1127 | 212.091 | 0.1943
221.437 | 0.1275 | 230.0276 | 0.1727
209.116 | 0.1427 | 243.5807 | 0.1575
192.81 | 0.1643 | 263.3565 | 0.1427
177.776 | 0.1919 | 281.7903 | 0.13
167.187 | 0.2182 | 302.1425 | 0.1183
155.763 | 0.2504 | 327.0135 | 0.1082
143.767 | 0.2952 | 358.754 | 0.0979
135.204 | 0.3427 | 392.3469 | 0.0887
124.921 | 0.4118 | 418.0649 | 0.0831
118.34 | 0.4726 | 440.3982 | 0.0782
112.573 | 0.5284 | 484.1496 | 0.0719
104.881 | 0.6238 | 515.3489 | 0.07
98.02 | 0.7219 | 3300 | 0.07
92.277 | 0.8433 | 3300 | 0.04
87.053 | 0.9841 | 25000 | 0.04
82.552 | 1.1246 | 25000 | 0.01